## gdmar2004to2009
| Date | State | Cause of Loss | Name of Installation | Name of Owner | Text | Loss Estimated ($) | Link
0 | 2004-02-27 | AZ | leaks and spills | UNKNOWN (MARICOPA COUNTY) | SOUTHWEST GAS CORP | <P>SOUTHWEST GAS EXPERIENCED A GAS LEAK ON A 4" PE MAIN THAT WAS INSTALLED IN JOINT TRENCH WITH A 12" WATER MAIN. THE GAS LINE WAS BELOW THE WATER LINE AND AS A RESULT SOUTHWEST GAS USED VALVES TO CONTROL THE LEAK. WE WERE UNABLE TO DETERMINE THE CAUSE DUE TO THE PROXIMITY TO THE WATER LINE. AS A RESULT A 300' SECTION OF MAIN WAS ABANDONED AND REPLACED WITH A NEW SECTION. TESTING IS UNDERWAY TO DETERMINE THE CAUSE OF THE LEAK. A SUPPLEMENTAL REPORT WILL BE SUBMITTED WHEN THE INVESTIGATION IS COMPLETE. </P> <P>PL 2003-0408. SUPPLEMENTAL REPORT AS OF FEBRUARY 25, 2005: A SAMPLE OF THE FAILED PIPE REMOVED FROM THE LEAK SITE WAS SENT IN FOR LABORATORY ANALYSIS. THE CRACK THAT WAS FOUND ON THE PIPE WAS DETERMINED TO BE THE RESULT OF A MATERIAL DEFECT, NOTABLY POLYMIDE (NYLON) CONTAMINATION THAT APPARENTLY OCCURED IN THE MANUFACTURING PROCESS. THE CORRESPONDING SECTIONS OF THIS REPORT HAVE BEEN AMENDED TO REFLECT THIS RESULT. </P> | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1 | 2004-02-21 | UT | natural disasters | UNKNOWN (UTAH COUNTY) | QUESTAR GAS COMPANY | PERSONNEL FROM THE UTAH STATE FIRE MARSHAL'S OFFICE DETERMINED THAT THE FIRE WAS CAUSED AS A RESULT OF SNOW SLIDING OFF THE ROOF OF THE STRUCTURE AND IMPACTING THE NATURAL GAS METER. THE IMPACT OF THIS SNOW DISPLACED THE METER ASSEMBLY BREAKING THE PIPE AT THE REGULATOR (QUESTAR OWNED PIPING) AND AT A TEE INSIDE THE STRUCTURE (CUSTOMER OWNED PIPING). NATURAL GAS WAS RELEASED AT THESE POINTS THEN IGNITED BY THE FURNACE, THE PRESUMED IGNITION SOURCE, INSIDE THE STRUCTURE. | 100771 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
2 | 2004-02-15 | GA | maintenance | UNKNOWN (MUSCOGEE COUNTY) | ATMOS ENERGY CORPORATION | FRACTURED PIPE UNEARTHED ON FEB.20TH 2004. THE SECTION OF PIPE WHERE THE FRACTURE WAS FOUND WAS TAKEN INTO CUSTODY BY THE GEORGIA PSC FOR METALLURGICAL ANALYSIS, WHICH BEGAN ON MARCH 15, 2004. THE METALLURGICAL ANALYSIS OF THE PIPES REVEALED A STRESS FRACTURE, THE ROOT CAUSE OF WHICH WAS NOT KNOWN BY THE METALLURGIST HIRED BY THE GEORGIA PSC. THE INVESTIGATION OF SOIL CONDITIONS AROUND THE GAS MAIN REVEALED THE INSTALLATION OF A SANITARY SEWER PIPE THAT INITIALLY APPEARED TO BE APPROX 10 FEET BELOW THE GAS MAIN. (AS PER ANALYSIS BY EXPERTS). SUBSEQUENT INVESTIGATION REVEALED DATA OF A DEPTH OF THE BOTTOM OF THE SEWER BETWEEN 7.5 FEET AND 10.5 FEET BELOW THE GAS MAIN. THIS 42 INCH DIAMETER SEWER PIPE WAS INSTALLED SEVERAL YEARS AGO AFTER THE GAS MAIN WAS INSTALLED. THE FOLLOWING REPRESENTS THE OPINIONS OF INVESTIGATING SOIL AND ENGINEERING EXPERTS: THE SEWER PIPE INSTALLATION AT THE DEPTH PROBABLY INVOLVED A TRENCH 20 TO 25 FEET WIDE AT THE ELEVATION OF THE GAS MAIN. THE BACKFILL OF THE SEWER PIPE TRENCH IS PRESENTLY IN A LOOSE CONDITION INFERRING LOOSE COMPACTION DURING PLACEMENT. AS A RESULT, THE BACKFILL CONSOLIDATED FROM UNDER THE GAS MAIN AND SETTLED AWAY FROM THE PIPE 20 FEET TO 25 FEET IN LENGTH. THE CAST IRON PIPE COULD SUPPORT THE OVERHEAD FORCES OF SOIL COVER AS ORIGINALLY INSTALLED. BUT, WHEN AN EVER INCREASING AMOUNT OF FILL WAS PLACED OVER THE GAS MAIN, THE OVERHEAD FORCES EXCEEDED THE SPECIFICATIONS FOR THE PIPE WITH A LOSS OF SUPPORT BELOW. THE METALLURGICAL ANALYSIS BY THE PSC EXPERT REVEALED A SUBSTANTIAL AMOUNT OF INTACT WALL THICKNESS (87.5 % AS PER REPORT OF JAMES LANE), WHICH WOULD HAVE BEEN SUFFICIENT TO WITHSTAND FORESEEABLE OPERATING PRESSURES AND LOADS. | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
3 | 2004-02-17 | CO | other | UNKNOWN (SAN MIGUEL COUNTY) | KINDER MORGAN RETAIL |  | 1000427 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
4 | 2004-03-05 | TX | sabotage | UNKNOWN (TRAVIS COUNTY) | TEXAS GAS SERVICE COMPANY | A CONTRACTOR STRUCK A 12" STEEL NATURAL GAS MAIN WITH A 36" AUGER ATTACHMENT FROM THE REAR OF A DRILLING TRUCK CAUSING NATURAL GAS TO ESCAPE. THE LOCAL FIRE DEPARTMENT TEMPORARILY CLOSED A SECTION OF RM 620 UNTIL THE AREA WAS BROUGHT UNDER CONTROL. TEXAS GAS SERVICE PERSONNEL CONDUCTED PERMANENT REPAIRS REPLACING THE SECTION OF DAMAGED PIPE AFTER IT WAS ISOLATED. | 101759 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
5 | 2004-02-01 | MI | technical failure | UNKNOWN (LIVINGSTON COUNTY) | CONSUMERS ENERGY CO | ON FEBRUARY 1, 2004 AN EMPLOYEE WAS INVESTIGATION A POSSIBLE GAS LEAK ON A PLASTIC MAIN LOCATE IN THE STREET ROW. DURING THE LEAK INVESTIGATION PROCEDURE THE EMPLOYEE, FOLLOWING COMPANY STANDARDS, BEGAN TO CHECK FOR GAS IN THE GROUND BEGINNING AT THE HOUSE NEAR THE SERVICE ENTRANCE. THE FIRST SURVEY PROBE RESULTED IN ZERO GAS FOUND NEAR THE METER INSTALLATION. THE EMPLOYEE THEN MOVED TO A LOCATION APPROXIMATELY 7 FEET AWAY FROM THE METER INSTALLATION AND ATTEMPTED TO COMPLETE ANOTHER PROBE TO CHECK FOR GAS IN THE GROUND. THE EMPLOYEE INADVERTENTLY DAMAGED THE 5/8 INCH PLASTIC GAS SERVICE LINE RESULTING IN GAS ESCAPING TO THE ATMOSPHERE. DUE TO FROST IN THE GROUND THE GAS MIGRATED TOWARD THE HOUSE AND ENTERED THE WEEPING TILE SYSTEM BURIED ALONG THE PERIMETER OF THE HOUSE. THE GAS SUBSEQUENTLY ENTERED THE BASEMENT OF THE HOUSE WHERE IT IGNITED CAUSING STRUCTURAL DAMAGE AND SUBSEQUENTLY RESULTED IN A STRUCTURE FIRE. | 251010 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
6 | 2004-03-18 | VA | technical failure | UNKNOWN (nan COUNTY) | RICHMOND DEPT OF PUBLIC UTILITIES, CITY OF | ON THURSDAY, 03/19/2004 AT APPROXIMATELY 2240 HOURS, HENKELS & MCKOY CREW #8 WAS KILLING TWO GAS SERVICES TO 1709 AND 1711 NORTH 21ST STREET. THE SERVICE TO 1711 NORTH 21ST STREET WAS KILLED AND THE CREW WAS WORKING TO KILL THE SERVICE TO 1709 NORTH 21ST STREET. TWO HENKELS & MCKOY PERSONS WERE IN THE EXCAVATION (MR. BEN MULLES AND MR. ANDY PENINGTON). MR. PENINGTON CUT THE PLASTIC SERVICE AND UNSCREWED THE TEE. MR. PENINGTON REACHED BACK TO GET A PLUG TO SCREW INTO THE GAS MAIN WHEN THE CONSTRUCTION LIGHT FELL AND IGNITED THE GAS. MR. PENINGTON WAS BURNED ON HIS FACE AND ARMS. HE WAS TRANSPORTED TO THE MEDICAL COLLEGE OF VIRGINIA HOSPITAL FOR TREATMENT. BEN MULLENS WAS TRANSPORTED TO THE MEDICAL COLLEGE OF VIRGINIA HOSPITAL FOR TREATMENT LATER THAT EVENING. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
7 | 2004-04-13 | MA | other | UNKNOWN (NORFOLK COUNTY) | BAY STATE GAS CO | APRIL 21 2006 ----------------- THE INCIDENT WAS INVESTIGATED BY THE MASSACHUSETTS STATE FIRE MARSHALLS OFFICE , TROOPER MARK VARKAS. SEE THE ATTACHED REPORT. THE INCIDENT HAS BEEN DETERMINED TO BE ACCIDENTAL. IT IS BELIEVED THE HOMEOWNER, WHILE HAMMERING NAILS INTO THE SIDE OF THE HOUSE CAUSED AN OBJECT TO FALL FROM A WOODEN SHELF ONTO THE GAS REGULATOR. THE REGULATOR BECAME DAMAGED AND AS A RESULT A SMALL LEAK DEVELOPED WHICH RESULTED IN THE ABOVE DESCRIBED INCIDENT. | 151010 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
8 | 2004-03-26 | PA | other | UNKNOWN (LANCASTER COUNTY) | UGI UTILITIES INC | AT 20:20 (APPROXIMATELY) MARCH 26, 2004 AN EXPLOSION OCCURRED AT THE RESIDENCE OF 403 SOUTH QUEEN STREET, LANCASTER, PENNSYLVANIA DUE TO AN UNKNOWN IGNITION SOURCE. A UGI UTILITY, INC (UGI) EMERGENCY RESPONDER WAS IN THE PROCESS OF INVESTIGATION AN INSIDE LEAK CALL WHEN THE EXPLOSION OCCURRED. THE SERVICEMAN WAS INJURED AND TAKEN TO LANCASTER GENERAL HOSPITAL AND THEN FLOWN TO CROZER-CHESTER MEDICAL CENTER, IN CHESTER COUNTY. HE WAS DIAGNOSED WITH FIRST AND SECOND DEGREE BURNS OF HIS HANDS, FOREARM, AND FACE. INSPECTION REVEALED THAT THE SERVICE LINE TO THE METER SET INSIDE THE BASEMENT WAS DAMAGED BY AN OUTSIDE FORCE. THE PIPING TO THE GAS METER WAS DEFLECTED BACK TOWARD THE WALL AND THE THREADED JOINT AT THE OUTLET OF A SERVICE TEE WAS CRACKED. THE CRACK WAS THE SOURCE OF THE ESCAPING GAS. THIS WAS A LOW PRESSURE (7 INCHES WATER COLUMN) SERVICE, SERVED FROM A LOW PRESSURE MAIN. THE CAUSE OF DAMAGE IS UNDER INVESTIGATION, BUT PRELIMINARY REPORTS FROM FIRE PERSONNEL ON SITE, WHO SPOKE TO RESIDENTS, NOTED THAT A RESIDENT OF 403 SOUTH QUEEN STREET HAD ROLLED TIRES DOWN THE BASEMENT STEPS AND ONE TIRE HIT THE NATURAL GAS SERVICE LINE. | 60200 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
9 | 2004-04-03 | IN | technical failure | UNKNOWN (VANDERBURGH COUNTY) | SOUTHERN INDIANA GAS & ELECTRIC CO | AT APPROXIMATELY 7:42 AM ON 4/3/04. VECTREN RECEIVED NOTICE THAT A THIRD PARTY HAD MISTAKENLY TURNED A GAS SERVICE VALVE AND RUPTURED A 1/2" PE PLASTIC SERVICE LINE AT 33007 LINCOLN AVE. IN EVANSVILLE IN. THE SERVICE HAD BEEN INSTALLED THROUGH A PREVIOUS USED STEEL "CURB" VALVE IN JUNE OF 2001. A CONTRACTOR WHICH VECTREN HAD HIRED TO INSTALL THE PLASTIC SERVICE LINE HAD FAILED TO REMOVE THE CURB BOX, AS REQUIRED BY THE CONTRACT WITH VECTREN. THR CURB BOX PROVIDED ACCESS TO THE CURB VALVE. THE CONTRACTOR ALSO FAILED TO OTHERWISE DISABLE THE CURB VALVE. THESE FAILURE BY THE CONTRACTOR CONTRIBUTED TO THE EVENT. AFTER REPAIRS WERE MADE TO THE DAMAGED SERVICE AT APPROXIMATELY 10:55 AM, A VECTREN EMPLOYEE ATTEMPTED TO RE-LIGHT THE WATER HEATER INSIDE THE STRUCTURE. AS THE ATTEMPT TO RELIGHT TOOK PLACE, AN EXPLOSION OCCURRED. | 605000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
10 | 2004-04-27 | AK | other | UNKNOWN (nan COUNTY) | ENSTAR NATURAL GAS CO | ON TUESDAY MORNING, APRIL 27, 2004 AT APPROXIMATELY 9:30 AM ADT, ENSTAR NATURAL GAS COMPANY WAS NOTIFIED OF A STRUCTURE FIRE AT 6304 BIRCH LANE, NORTH KENAI, ALASKA. AN ENSTAR SERVICEMAN WAS DISPATCHED TO THE SCENE. UPON ARRIVAL THE SERVICEMAN FOUND A RESIDENTIAL STRUCTURE ON FIRE. HEAT FROM THE FIRE MELTED THE POLYETHYLENE SERVICE LINE RISER AND GAS METER, CAUSING A RELEASE OF NATURAL GAS. A DISTRIBUTION CREW DUG UP THE SERVICE LINE, PINCHED IT OFF, AND CAPPED IT. NATURAL GAS FROM ENSTAR'S FACILITIES DID NOT CAUSE OR CONTRIBUTE TO THE FIRE. | 120510 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
11 | 2004-04-01 | OH | sabotage | UNKNOWN (LUCAS COUNTY) | COLUMBIA GAS OF OHIO INC | A THIRD PARTY CONTRACTOR DIRECTIONALLY BORED INTO AN UNDERGROUND 2-INCH PLASTIC MEDIUM PRESSURE GAS MAIN. THE THIRD PARTY CONTRACTOR NOTIFIED COLUMBIA GAS OF OHIO VIA THE ONE CALL SYSTEM AT 14:08 ON 04/01/04. COLUMBIA PERSONNEL ARRIVED AT THE SITE AT APPROXIMATELY 14:43. COLUMBIA PERSONNEL PROCEEDED TO ASSESS THE SITUATION TO ASSESS THE SITUATION AND MAKE THE AREA SAFE. A HOLE WAS DUE TO VENT THE ESCAPING GAS INTO THE ATMOSPHERE, AND THEN THE MAIN WAS EXCAVATED AND SQUEEZED OFF AT APPROXIMATELY 15:34. AN EXPLOSION OCCURRED AT APPROXIMATELY 15:34 AT A NEARBY RESIDENCE (APPROX. 75 FT AWAY), 9015 WHISPERING PINE. COLUMBIA PERSONNEL CONTINUED WORKING TO MAKE THE AREA SAFE. THE RESIDENT AT 9015 WHISPERING PINE WAS HOSPITALIZED OVERNIGHT FOR OBSERVATION; HOWEVER, SHE WAS RELEASED AFTER SUSTAINING MINOR INJURIES. A SMALL FIRE WAS EXTINGUISHED AT 9015 WHISPERING PINE; HOWEVER, THE HOUSE WAS SEVERLY DAMAGED. A NEIGHBORING HOUSE HAD MINOR DAMAGE INCLUING A FEW BROKEN WINDOWS AND SIDING DAMAGE. | 437100 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
12 | 2004-04-06 | IL | other | UNKNOWN (LASALLE COUNTY) | NORTHERN ILLINOIS GAS CO | SUPPLEMENTAL REPORT FILED TO INDICATE SUM THE TOTAL ESTIMAGED DAMAGES. ************************************************************************** FIRE/EXPLOSION ORIGINATED INSIDE THE HOUSE (STILL UNDER CONSTRUCTION), NEAR THE GARAGE AREA. FLAMES SPREAD TO THE OPPOSITE SIDE OF THE HOUSE WHERE THE NATURAL GAS METER WAS LOCATED. THE METER SET (SERVICE REGULATOR AND METER) MELTED AS A RESULT OF THE INTENSE HEAT, THUS CAUSING A RELEASE OF NATURAL GAS. | 150500 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
13 | 2004-04-25 | PA | other | UNKNOWN (ALLEGHENY COUNTY) | T W PHILLIPS GAS & OIL CO | FIRE DESTOYED SINGLE FAMILY HOME AT 342 MOYHEND STREET, SPRINGDALE, PA 15144. SINGLE OCCUPANT, DAVID HUMMEL, WAS INJURED IN FIRE AND TAKEN TO LOCAL HOSPITAL. ALTHOUGH NO DIRECT INFORMATION, ACCORDING TO NEWS REPORTS, MR. HUMMEL IS IN CRITICAL CONDITION. INVESTIGATION OF CAUSE OF FIRE IS CONTINUING. T.W. PHILLIPS HAS CONFIRMED THAT THERE ARE NO LEAKS IN ANY OF ITS GAS PIPELINES OR METER INSTALLATIONS IN THE INCIDENT AREA. | 157400 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
14 | 2004-04-26 | IL | other | UNKNOWN (COOK COUNTY) | NORTHERN ILLINOIS GAS CO | SUPPLEMENTAL REPORT SUBMITTED WITH THE 3 PROPERTY DAMAGE SUBCATEGORIES SUMMING UP TO THE TOTAL VALUE. ****************************************************************************** HOMEOWNER OF MOBILE HOME WAS HEATING GREASE IN MICROWAVE. GREASE CONTAINEER WAS COVERED WITH ALUMINUM FOIL. FIRE DESTROYED UNIT THEN HIGH WINDS SPREAD FIRE TO 8 OTHER MOBILE HOMES. THE METER SETS (SERVICE REGULATOR AND METER(MELTED AS A RESULT OF THE INTENSE HEAT, THUS CAUSING A RELEASE OF NATURAL GAS. | 300000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
15 | 2004-04-28 | IL | other | UNKNOWN (WILL COUNTY) | NORTHERN ILLINOIS GAS CO | SUPPLIMENTAL REPORT SUBMITTED WITH THE 3 PROPERTY DAMAGE SUBCATEGORIES SUMMING UP TO THE TOTAL VALUE. **************************************************************************** MULCH FIRE ORIGINATED NEAR THE METER SET. THE METER SET (SERVICE REGULATOR AND METER) MELTED AS A RESULT OF THE INTENSE HEAT, THUS CAUSING A RELEASE OF NATURAL GAS. | 50500 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
16 | 2004-06-18 | WI | sabotage | UNKNOWN (LACROSSE COUNTY) | NORTHERN STATES POWER CO, A WISCONSIN CORPORATION DBA XCEL ENERGY | THE 5/8" PE SERVICE FEEDING THE BUILDING WAS PUNCTURED BY A CURB STAKE INSTALLED BY CONCRETE PAVING CONTRACTOR (JAMES CAPE AND SONS, CO.). GAS FROM THE PUNCTURED SERVICE MIGRATED INTO THE BUILDING AND WAS IGNITED BY AN UNKNOWN SOURCE CAUSING THE EXPLOSION AND SUBSEQUENT FIRE. | 500000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
17 | 2004-04-28 | IL | other | UNKNOWN (WILL COUNTY) | NORTHERN ILLINOIS GAS CO | SUPPLEMENTAL REPORT SUBMITTED WITH THE 3 PROPERTY DAMAGE SUBCATEGORIES SUMMING UP TO THE TOTAL VALUE. ****************************************************************************** FIRE WAS STARTED BY ELECTRICAL SHORT. FIRE SPREAD TO THE LOCATION WHERE THE METER SET WAS LOCATED. THE METER SET MELTED AS A RESULT OF THE INTENSE HEAT, THUS CAUSING A RELEASE OF NATURAL GAS. | 150500 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
18 | 2004-05-17 | AK | other | UNKNOWN (KENAI PENINSULA BOROUGH COUNTY) | ENSTAR NATURAL GAS CO | ON MONDAY MORNING, MAY 17, 2004 AT APPROXIMATELY 11:00 PM ADT, ENSTAR NATURAL GAS COMPANY WAS NOTIFIED OF A STRUCTURE FIRE AT 36235 SCHULTZ COURT, SOLDOTNA, ALASKA. AN ENSTAR SERVICEMAN WAS DISPATCHED TO THE SCENE. UPON ARRIVAL THE SERVICEMAN FOUND A RESIDENTIAL STRUCTURE ON FIRE. HEAT FROM THE FIRE MELTED THE POLYETHYLENE SERVICE LINE RISER AND GAS METER, CAUSING A RELEASE OF NATURAL GAS. A DISTRIBUTION CREW DUG UP THE SERVICE LINE, PUNCHED IT OFF, AND CAPPED IT. NATURAL GAS FROM ENSTAR'S FACILITIES DID NOT CAUSE OR CONTRIBUTE TO THE FIRE. | 201010 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
19 | 2004-05-19 | AK | other | UNKNOWN (nan COUNTY) | ENSTAR NATURAL GAS CO | ON WEDNESDAY MORNING, MAY 19, 2004 AT APPROXIMATELY 3:37 AM ADT, ENSTAR NATURAL GAS COMPANY WAS NOTIFIED OF A STRUCTURE FIRE AT 16346 E BREADFORD DR, PALMER, AK. AN ENSTAR SERVICEMAN WAS DISPATCHED TO THE SCENE. UPON ARRIVAL THE SERVICEMAN FOUND A RESIDENTIAL STRUCTURE ON FIRE. HEAT FROM THE FIRE MELTED THE POLYETHLENE SERVICE LINE RISER, CAUSING A RELEASE OF NATURAL GAS. THE STRUCTURE WAS UNDER CONSTRUCTION AND NO GAS METER WAS SET AT THIS LOCATION. A DISTRIBUTION CREW DUG UP THE SERVICE LINE, PINCHED IT OFF, AND CAPPED IT. NATURAL GAS FROM ENSTAR'S FACILITIES DID NOT CAUSE OR CONTRIBUTE TO THE FIRE. | 51010 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
20 | 2004-04-13 | LA | sabotage | UNKNOWN (TERREBONNE COUNTY) | SOUTH COAST GAS CO INC |  | 410 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
21 | 2004-05-07 | AZ | technical failure | UNKNOWN (MARICOPA COUNTY) | SOUTHWEST GAS CORP | SERVICE WAS INSTALLED BY DIRECTIONAL BORE THROUGH SEWER LATERAL. DURING SEWER LATERAL, CLEAN OUT ROTOR STUCK AND DAMAGED THE GAS SERVICE LINE. GAS MIGRATED THROUGH SEWER LATERAL INTO MOBILE HOME. THERE WAS IGNITION OF NATURAL GAS AND ONE MOBILE HOME WAS TOTALLY DESTROYED. FOUR PEOPLE WERE TRANSPORTED TO THE HOSPITAL WITH BURNS. | 58000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
22 | 2004-04-09 | NY | sabotage | UNKNOWN (ULSTER COUNTY) | CENTRAL HUDSON GAS & ELECTRIC CORP | C.M. APPLER AND SONS, INC. WAS REMOVING BLACKTOP AND CURBING FROM THE DRIVEWAY TO 7 TILLSON AVENUE IN HIGHLAND. THIS CONTRACTOR, UTILIZING AN EXCAVATOR, PULLED UP CURBING AND A 3/4" STEEL NATURAL GAS SERVICE LINE OPERATING AT 30 PSIG. THE SERVICE LINE SEPARATED AT A JOINT INSIDE THE BUILDING WALL AND IT WAS PULLED THROUGH THE BUILDING WALL. NO REQUEST TO MARK-OUT FACILITIES IN THE AREA HAD BEEN MADE BY THE CONTRACTOR PRIOR TO THIS INCIDENT. PROPERTY DAMAGE ESTIMATE REVISED ON 2/16/2006. | 2011200 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
23 | 2004-05-14 | NY | other | UNKNOWN (ST LAWRENCE COUNTY) | ST LAWRENCE GAS CO INC | GAS SERVICE INSTALLED IN 1993 UTILIZING PNEUMATIC BORING TOOL. LOCATIONS OF SEWER LATERALS WERE UNATTAINABLE OR UNKNOWN AT THE TIME OF GAS SERVICE INSTALLATION. BORING TOOL APPARENTLY PENETRATED A SHALLOW SEWER LATERAL (40" DEEP) TO RESIDENCE AT 1000 MECHANIC ST., RESULTING IN A SERVICE INSTALLATION WITHIN THE SEWER LATERAL. SEWER BLOCKAGE REPORTED TO CITY DPW 11 YEARS LATER BY HOMEOWNER. CITY EMPLOYEES USED ROOT CUTTING AUGER TO CLEAR SEWER BLOCKAGE. AUGER PUNCTURED 1/2" GAS LINE IN SEWER. LEAKING GAS FOLLOWED THE SEWER LINE TO BASEMENT OF 100O MECHANIC ST. AT SOME TIME LATER, UNKNOWN IGNITION SOURCE IGNITED GAS RESULTING IN THE EXPLOSION AND ENSUING FIRE. TWO CITY EMPLOYEES AND THREE OCCUPANTS OF THE HOUSE WERE EVACUATED AND WERE INJURED FROM THE EXPLOSION (THREE OF THE FIVE INJURED REQUIRED IN-PATIENT HOSPITALIZATION). ONE OCCUPANT NOT EVACUATED FROM THE HOUSE WAS INSIDE WHEN THE EXPLOSING OCCURRED, AND DIED OF INJURIES SUSTAINED. | 101000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
24 | 2004-05-12 | TX | sabotage | UNKNOWN (COLLIN COUNTY) | COSEAY GAS | THIRD PARTY EXCAVATOR CUT 3/4" SERVICE LINE BETWEEN STREET AND HOUSE WHILE DRILLING PIER HOLES FOR SCREENING WALL. FLASH FIRE OCCURRED, HOWEVER, EXCESS FLOW VALVE ACTIVATED SHUTTING OFF THE FLOW OF GAS ALMOST IMMEDIATELY. | 500 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
25 | 2004-06-22 | WA | technical failure | UNKNOWN (KING COUNTY) | PUGET SOUND ENERGY | DURING A PURGING OPERATION RELATED TO A MAIN REPLACEMENT PROJECT, AN EMPLOYEE OF A PUGET SOUND ENERGY CONTRACTOR SUFFERED BURNS WHEN THE PURGE GAS IGNITED. THE INCIDENT OCCURRED WHEN THE VALVE CONTROLLING INJECTION OF THE PURGE GAS WAS OPENED BEFORE A VENT STACK COULD BE INSTALLED THAT WOULD HAVE DIRECTED THE PURGE GAS UPWARD AND OUT OF THE EXCAVATION. THIS WAS CAUSED BY A LACK OF COMMUNICATION BETWEEN TWO CONTRACTOR EMPLOYEES WHO WERE NOT IN A VISUAL CONTACT. SINCE NO CONTROL VALVE HAD BEEN INSTALLED AT THE DOWNSTREAM (OPEN) END OF THE PIPE SECTION BEING PURGED, THE EMPLOYEE STATIONED THERE ATTEMPTED TO SQUEEZE THE POLYETHYLENE PIPE TO CONTROL THE GAS FLOW BUT IGNITION OCCURRED WHEN THE CONTACTED THE PIPE. PSE PROCEDURES, "PREVENTING ACCIDENTAL IGNITION" AND "PURGING" WERE NOT FOLLOWED. APRIL 24, 2009 - FINALIZING FORM ON 04/24/09 FOR COMPLETION PURPOSES ONLY. ENTRY BY HELGE FERCHERT, MANAGER, COMPLIANCE AND REGULATORY AUDITS (PUGET SOUND ENERGY) | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
26 | 2004-05-12 | PA | maintenance | UNKNOWN (WESTMORELAND COUNTY) | DOMINION PEOPLES | ON MAY 12, 2004 AT 9:40 AM, A REPORT OF AN ODOR OF GAS WAS RECEIVED BY DOMINION PEOPLES FROM CORDIA COMMONS, A NURSING HOME IN NORTH HUNTINGDON TOWNSHIP, WESTMORELAND COUNTY, PA. DOMINION PEOPLES PERSONNEL ARRIVED AT THE SCENE, PERFORMED THE INITIAL LEAK INVESTIGATION AND IMPLEMENTED THE NECESSARY EMERGENCY PROCEDURES AND EVACUATION. BECAUSE A SECOND UTILIITY HAS PIPELINES NEAR THE NURSING HOME, THAT LDC WAS CONTACTED AND ARRIVED AT THE SCENE TO ALSO INITIATE A LEAK INVESTIGATION ON THEIR ADJACENT FACILITIES. THE OTHER LDC CONCLUDED ITS LEAK INVESTIGATION LATE ON MAY 12, 2004. PEOPLES CONTINUED ITS INVESTIGATION AND PERFORMED TEMPORARY REPAIRS UNTIL THE PIPELINE WAS REMOVED FROM SERVICE ON MAY 15, 2004. PRELIMINARY NOTIFICATION WAS MADE TO THE NRC BY TELEPHONE ON MAY 17, 2004 WHEN IT WAS DETERMINED THAT THE LEAKAGE WAS FROM DOMINION PEOPLES PIPELINE AND THE ESTIMATED PROPERTY DAMAGE RELATED TO REPORTABLE INCIDENTS APPROACHED THE REPORTABLE LEVEL. NRC #722019 WAS ASSIGNED TO THIS EVENT AT THAT TIME. RESIDENTS RETURNED TO THE NURSING HOME ON MAY 20, 2004. | 181810 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
27 | 2004-05-20 | CA | sabotage | UNKNOWN (ORANGE COUNTY) | SOUTHERN CALIFORNIA GAS CO | CONTRACTOR WORKING FOR CITY OF GARDEN GROVE STRUCK 3" PE MAIN WITH BACKHOE. CREW EXCAVATED CONTROL EXCAVATIONS AND PROCEEDED TO INSTALL TEMPORARY BY PASS. AT APPROXIMATELY 13:00, ESCAPING GAS IGNITED, DAMAGING BACKHOE AND OVERHEAD UTILITY LINES. FACILITES PROPERLY MARKED. CONTRACTOR WAS AWARE OF FACILITY LOCATION. | 95000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
28 | 2004-06-04 | KY | sabotage | UNKNOWN (FAYETTE COUNTY) | COLUMBIA GAS OF KENTUCKY INC | AT APPROXIMATELY 11:55 AM ON JUNE 4, 2004 THE COLUMBIA GAS OF EENTUCKY (CKY) EMERGENCY LINE RECEIVED A CALL FROM THE LEXINGTON FIRE DEPARTMENT. THE CALLER STATED THAT A GAS LINE AT 741 SOUTH LIMESTONE SREET HAD BEEN DAMAGED RESULTING IN A FIRE AND INJURY. A CONTRACTOR EMPLOYEE TRENCHING TO INSTALL UNDERGROUND ELECTRICAL CONDUIT AT THE ABOVE ADDRESS CUT A 1" PLASTIC MEDIUM PRESSURE SERVICE LINE. THE ESCAPING GAS IGNITED AND BURNED THE CONTRACTOR'S EMPLOYEE OPERATING THE TRENCHER. THIS INCIDENT WAS REPORTED TO THE PUBLIC SERVICE COMMISSION DUE TO THE UNINTENTIONAL IGNITION OF GAS, INJURY, AND COVERAGE OF THE INCIDENT BY LOCAL TV STATIONS CHANNEL 18 & 27. THIS INCIDENT WAS ALSO REPORTED TO THE NATIONAL RESPONSE CENTER, ONE THE CONTRACTOR'S EMPLOYEE WAS ADMITTED TO THE HOSPITAL. CAUSE: THE CONTRACTOR INSTALLING THE UNDERGROUND ELECTRICAL CONDUIT AT THE SITE HAD REQUESTED THE AREA BE LOCATED ON MAY 6, 2004 FOR WORK TO BEGIN MAY 10. COLUMBIA'S CONTRACT LOCATER MARKED THE SITE PER THE REQUEST. THE TRENCHING OPERATION THAT RESULTED IN THE DAMAGE TOOK PLACE JUNE 4, 2004. PRIOR TO THE DATE OF THE INCIDENT THE WORK SITE HAD BEEN GRADED. THE DAY OF THE INCIDENT NO TEMPORARY FACILITY MARKINGS WERE VISIBLE AT THE SITE, HOWEVER THE DAMAGE OCCURRED APPROXIMATELY 15 FEET FROM A PERMANENT GAS LINE MARKER AND A GAS CURB VALVE BOX EXTENDED SEVERAL INCHES ABOVE GRADE. COLUMBIA BELIEVES THIS INCIDENT IS THE RESULT OF A CONTRACTOR NOT COMPLYING WITH THE KENTUCKY DIG LAW BY NOT MAINTAINING MARKINGS, NOT REQUESTING A RELOCATE WHEN MARKINGS ARE REMOVED, AND BY NOT REQUESTING A RELOCATE OF AN AREA AFTER 21 DAYS. RESPONSE: THE COLUMBIA EMERGENCY LINE RECEIVED NOTIFICATION OF THE INCIDENT AT APPROXIMATELY 11:55 AM. A SERVICE EMPLOYEE WAS DISPATCHED IMMEDIATELY TO INVESTIGATE. THE SERVICE EMPLOYEE ARRIVED AT 12:25 PM TO FIND THAT THE LEXINGTON FIRE DEPARTMENT PRIOR TO HIS ARRIVAL HAD SHUT OFF THE BLOWING GAS AT A CURB VALVE. AT THIS TIME THE SERVICE PERSON REQUESTED ASSISTANCE FROM FIELD OPERATIONS TO REPAIR THE DAMAGED LINE. THE SERVICE LINE WAS TESTED AND REPAIRED AND READY TO BE PUT BACK IN SERVICE AT THE PROPERTY OWNER'S REQUEST BY 4:30 THE SAME DAY. STEPS TAKEN TO PREVENT RECURRENCE: THE CONTRACTOR RESPONSIBLE FOR THIS DAMAGE HAS BEEN ADVISED OF THE REQUIREMENTS OF THE KENTUCKY DIG LAW. THE CONTRACTOR WILL BE BILLED $589.75 FOR ALL EXPENSES ASSOCIATED WITH THIS INCIDENT. | 5589 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
29 | 2004-07-23 | IN | other | UNKNOWN (ALLEN COUNTY) | NORTHERN INDIANA PUBLIC SERVICE CO | AT APPROXIMATELY 12:35 AM THE OWNER OF ERNIE'S RESTAURANT WAS USING HIS VEHICLE TO JUMP-START ANOTHER VEHICLE WHEN HIS VEHICLE SURGED FORWARD AND STRUCK THE GAS METER SET FOR THE ADJACENT FURNITURE STORE AND CONTINUED THROUGH THE BUILDING WALL. THE METER SET WAS UNDER THE CAR AND GAS WAS ESCAPING AT 50-PSI. THE DRIVER OF THE CAR MAY HAVE BEEN SLIGHTLY INJURED DUE TO THE IMPACT BUT IS BELIEVED TO HAVE DECLINED MEDICAL ATTENTION. UTILITY WAS NOTIFIED AT 12:50. UTILITY SERVICEMAN WAS DISPATCHED AND ARRIVED ON THE SCENE AT 1:05 JUST AS GAS IN THE BUILDING WAS IGNITED BY AN UNKNOWN SOURCE. THE FIRE DEPARTMENT WAS ON THE SCENE AND EXTINGUISHED THE RESULTING FIRE. SERVICEMAN CALLED FOR A STREET CREW WHO SHUT OFF THE FEEDING GAS MAIN AT 3:30 AM. | 1006070 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
30 | 2004-05-25 | LA | sabotage | UNKNOWN (LAFOURCHE COUNTY) | SOUTH COAST GAS CO INC |  | 56 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
31 | 2004-06-07 | LA | sabotage | UNKNOWN (TERREBONNE COUNTY) | SOUTH COAST GAS CO INC |  | 182 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
32 | 2004-06-08 | LA | sabotage | UNKNOWN (TERREBONNE COUNTY) | SOUTH COAST GAS CO INC |  | 350 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
33 | 2004-05-10 | CA | sabotage | UNKNOWN (RIVERSIDE COUNTY) | SOUTHERN CALIFORNIA GAS CO | CONTRACTOR WORKING FOR CALTRANS STRUCK MAIN WITH TRACKHOE, RIPPING OFF A ONE INCH NIPPLE. FACILITIES HAD BEEN RECENTLY RELOCATED FOR CALTRANS, AND CALTRANS WAS AWARE OF LOCATION. DAMAGE CAUSED BY CONTRACTOR ERROR. | 120000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
34 | 2004-06-09 | MO | sabotage | UNKNOWN (JACKSON COUNTY) | MISSOURI GAS ENERGY | THE DEVELOPER'S EXCAVATOR WAS GRADING FOR SIDEWALK INSTALLATION WHEN A TOOTH FROM A BULL DOZER STRUCK OUR 12 INCH HIGH PRESSURE MAIN. THE EXCAVATOR INDICATED THAT HE WAS MOVING ROCKS AND HAD NOT INTENDED TO DIG. THE EXCAVATOR HAD NOT MADE A FACILITY LOCATE REQUEST PRIOR TO HIS EXCAVATION ACTIVITES. THE 12 INCH LINE HAD STOPPLE FITTINGS WELDED ON AND THE LINE WAS SHUT DOWN BETWEEN THE FITTINGS TO ALLOW FOR TEMPORARY REPAIRS. A SEGMENT OF THIS PIPE WILL NEED TO BE REPLACED IN ORDER TO ALLOW FOR FUTURE PIGGING OPERATIONS. | 132131 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
35 | 2004-06-15 | NJ | natural disasters | UNKNOWN (CAMDEN COUNTY) | PUBLIC SERVICE ELECTRIC & GAS CO | AT 19:02 ON TUESDAY JUNE 15, 2004, PSE&G RECEIVED AN EMERGENCY GAS LEAK CALL FROM THE CAMDEN FIRE DEPARTMENT. THE CALL WAS DISPATCHED TO A SERVICE TECHNICIAN AT 19:04. THE TECHNICIAN ARRIVED ON SITE AT 19:19. UPON ARRIVAL, THE TECHNICIAN CONFIRMED THAT GAS WAS LEAKING, REQUESTED A DISTRIBUTION CREW BE DISPATCHED, AND WORKED WITH EMERGENCY OFFICIALS TO EVACUATE BUILDINGS AS NECESSARY. AT ABOUT 19:40, THE FOUNDATION WALL TO BUILDING N COLLAPSED AND THEN AN EXPLOSION OCCURRED. PRIOR TO THE TECHNICIAN'S ARRIVAL, THE BASEMENT FOUNDATION WALL TO BUILDING N BUCKLED INWARD 6-8 INCHES APPARENTLY DUE TO EXTERNAL WATER PRESSURE (TORRENTIAL RAIN HAD BEEN IN PROGRESS). THE BUCKLING OF THE FOUNDATION WALL CAUSED THE 1 1/4 INCH STEEL, 15-PSIG-DESIGN GAS SERVICE TO PULL OUT NEAR THE 3 INCH STEEL GAS MAIN AND DAMAGED GAS PIPING INSIDE OF BUILDING N. GAS ESCAPED AND WAS IGNITED BY AN UNKNOWN SOURCE. THE DISTRIBUTION STAND-BY STREET LEADER ARRIVED ON SITE AT 19:42. THE GAS WAS SHUT OFFAT 20:45 BY CLOSING TWO VALVES ON THE 3-INCH GAS MAIN. EYEWITNESS ACCOUNTS AND PHYSICAL EVIDENCE SUPPORT THE CONCLUSION THAT THE CAUSE OF THE DAMAGE TO THE GAS SERVICE AND INSIDE BUILDING N GAS PIPING WAS CAUSED BY THE BUILDING'S FOUNDATION WALL BUCKLING INWARD LIKELY FROM HYDROSTATIC PRESSURE ON THE FOUNDATION WALL. TORRENTIAL RAIN HAD BEEN IN PROGRESS AND IS LIKELY THE TRIGGERING FACTOR TO THE FOUNDATION WALL BUCKLING AND SUBSEQUENT EVENTS. | 782900 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
36 | 2004-06-24 | VA | other | UNKNOWN (nan COUNTY) | RICHMOND DEPT OF PUBLIC UTILITIES, CITY OF | ON JUNE 24, 2004 SOMEONE ALLEGEDLY BROKE INTO THE CRAWLSPACE OF A VACANT HOME LOCATED AT 4705 CASTLEWOOD ROAD. THEY APPARENTLY STOLE COPPER HOUSE PIPE FEEDING THE GAS HOT WATER HEATER. THE OPEN END OF THE GAS PIPE ALLOWED GAS TO FLOW FREELY INTO THE CRAWLSPACE UNTIL THE CONCENTRATION OF GAS IN AIR REACHED THE EXPLOSION LIMIT AND THE GAS EXPLODED. THE EXPLOSION OCCURRED AT APPROXIMATELY 1830 HOURS. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
37 | 2004-06-29 | OH | sabotage | UNKNOWN (MIAMI COUNTY) | VECTREN ENERGY DELIVERY OF OHIO | A CONSTRUCTION CREW WAS EXCAVATING FOR WATER MAIN INSTALLATION WHEN THEIR TRENCHER HIT THE VECTREN'S 8 INCH GAS LINE AND IGNITED THE EXCAPING GAS CAUSING A BRIEF EXPLOSION AND ENSUING FIRE. THE FIRE DESTROYED THE TRENCHER AND CAUSED DAMAGE TO OVERHEAD COMMUNICATION LINES AND TO THE ROADWAY (FINAL DAMGAE ESTIMATES ARE STILL PENDING). VECTREN'S LOCATING CONTRACTOR HAD MISLOCATED THE 8 INCH LINE THE DAY BEFORE, MARKING A SERVICE LINE APPROXIMATELY 40 FEET SOUTH OF AND PARALLEL WITHT HE 8 INCH GAS LINE. THE EXCAVATION TRAVEL WAS FROM NORTH TO SOUTH AND THE 8 INCH GAS LINE WAS ENCOUNTERED PRIOR TO THE LOCATION MARKS. | 470528 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
38 | 2004-07-05 | CA | other | UNKNOWN (TULARE COUNTY) | SOUTHERN CALIFORNIA GAS CO | FIRE ORIGINATING AT PALLET FACTORY SPREAD ACROSS STREET TO HOMES. WALL FROM BURNING HOME TOPPLED, BREAKING METER SET ASSEMBLY AND RISER. FIRE IGNITED ESCAPING GAS. NO FIRE DAMAGE ATTRIBUTED TO ESCAPING GAS. | 501000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
39 | 2004-07-15 | NY | other | UNKNOWN (nan COUNTY) | NATIONAL FUEL GAS DISTRIBUTION CORP - NEW YORK | SEE ATTACHED REPORTS (1) NEW YORK PUBLIC SERVICE COMMISSION 30 DAY REPORT (2) EXPERT FORENSIC ENGINEERING REPORT PREPARED BY ENGINEERING AND FIRE INVESTIGATIONS INC. | 375000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
40 | 2004-07-26 | WA | sabotage | UNKNOWN (PIERCE COUNTY) | PUGET SOUND ENERGY | CONTRACTOR VERTICALLY AUGERING FOR GUARD RAIL POSTS AS PART OF MAJOR BRIDGE CONSTRUCTION PROJECT. UTILITY LOCATOR PAINT MARKS NOT PRESERVED WHEN PAVEMENT WAS REMOVED BY ANOTHER CONTRACTOR MAKING IT IMPOSSIBLE TO DETERMINE THEIR ACCURACY WITH CERTAINTY. AUGER HIT 4" POLYETHYLENE GAS MAIN. IGNITION OCCURRED. AUGERING EQUIPMENT SEVERELY DAMAGED BY FIRE ACCOUNTING FOR HIGH INCIDENT COST. EMERGENCY WAS CONTROLLED BY VALVE CLOSURE BY OPERATOR'S FIRST RESPONDERS. REPAIRED SAME DAY. | 111466 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
41 | 2004-08-06 | LA | sabotage | UNKNOWN (nan COUNTY) | SOUTH COAST GAS CO INC |  | 120 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
42 | 2004-08-20 | LA | sabotage | UNKNOWN (ASSUMPTION COUNTY) | PIERRE PART NATURAL GAS INC |  | 145 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
43 | 2004-08-02 | OH | leaks and spills | UNKNOWN (FRANKLIN COUNTY) | COLUMBIA GAS OF OHIO INC | COMPANY CREW WAS WORKING IN AN EXCAVATION ON A LEAK REPAIR INVOLVING A PLASTIC ELBOW THAT WAS LEAKING AT THE JOINT. IN PREPARATION TO INSTALL A BY-PASS THAT WOULD ENABLE THE COMPANY TO MAKE REPAIRS, THE CREW CONTINUED WITH THE EXCAVATION OF THE PIPELINE IN THE VICINITY OF THE LEAKING ELBOW. DURING THE EXCAVATION ACTIVITY, LEAKING GAS IGNITED IN THE HOLE RESULTING IN A CONTROLLED OUTAGE OF 1300 CUSTOMERS. THE SOURCE OF THE IGNITION WAS DETERMINED TO BE A SPARK OF UNKNOWN ORIGIN. | 133700 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
44 | 2004-09-08 | AZ | other | UNKNOWN (NAVAJO COUNTY) | UNISOURCE ENERGY SERVICES | AT APPROXIMATELY 09:57 ON 9/8/04, A VEHICLE DRIVEN BY AN UNKNOWN PERSON (HIT-AND-RUN) WAS DRIVING IN THE ALLEY BETWEEN 2ND STREET AND 3RD STREET AND CAMPBELL AND HICKS IN WINSLOW ARIZONA WHEN IT STRUCK A RESIDENTIAL NATURAL GAS SERVICE RISER AND CAUSED THE PIPE TO BREAK. AS A RESULT, NATURAL GAS WAS RELEASED AND IGNITED. THE DRIVER AND VECHICLE LEFT THE SCENE. THE RESULTED IN ADJACENT STRUCTURES TO CATCH FIRE AND BURN. CITY FIRE AND POLICE DEPARTMENT PERSONNEL REPONDED TO THE SERVICE RISER. THIS IS BEING FILED AS A FINAL REPORT. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
45 | 2004-08-03 | NV | sabotage | UNKNOWN (CLARK COUNTY) | SOUTHWEST GAS CORP | AN EXPLOSION AND FIRE OCCURRED AT 2819 GLENDEVON CIRCLE DUE TO THE FAILURE OF A 1" PE FITTING (PE GAS TUBING TEE). THE LEAK WAS CAUSED BY THIRD PARTY DAMAGE. SPECIFICALLY, ONE OR MORE EXCAVATORS CREATED AT LEAST ONE EXCAVATION BELOW SOUTHWEST'S PE GAS TUBING TEE. THE EXCAVATOR(S) FAILED TO PROVIDE ADEQUATE COMPACTION OF THE BACKFILLE MATERIAL. OVER TIME, THIS BACKFILL MATERIAL SETTLED AND IMPOSED EXCESSIVE STRESSES ON SOUTHWEST'S PE GAS TUBING TEE, CAUSING THE TEE TO FAIL. THERE WERE APPROXIMATELY 376 THERMS OF GAS LOST. ONE PERSON RECEIVED MINOR INJURIES, BUT DID NOT REQUIRE HOSPITALIZATION. | 457000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
46 | 2004-08-21 | PA | leaks and spills | UNKNOWN (CLEARFIELD COUNTY) | NATIONAL FUEL GAS DISTRIBUTION CORP - NEW YORK | AT 8:45 AM ON AUGUST 21,2004, AN EXPLOSION OCCURRED AT 48 WOODLAND LANE IN SANDY TOWNSHIP NEAR BUBOIS, PENNSYLVANIA. FIRE FOLLOWED THE EXPLOSION, WHICH CONSUMED MUCH OF THE EXPLOSION DEBRIS THAT REMAINED IN AND AROUND THE HOUSE FOUNDATION. MR. AND MRS, THE OCCUPANTS OF THE HOUSE, WERE FATALITIES. SEE ATTACHED EXPERT FORENSIC ENGINEERING REPORT PREPARED BY ENGINEERING AND FIRE INVESTIGATIONS. | 751000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
47 | 2004-08-19 | CA | other | UNKNOWN (LOS ANGELES COUNTY) | SOUTHERN CALIFORNIA GAS CO | ELECTRIC TRANSFORMER FAILED, ENERGIZING WATER LINE THAT ARCED ONTO GAS MAIN, CREATING HOLE THAT ALLOWED WATER TO ENTER GAS MAIN, CAUSING SIGNIFICANT CUSTOMER OUTAGES. NOTE: INCIDENT BECAME REPORTABLE AT APPROXIMATELY 10:30 ON 8/20/04 WHEN FURTHER WATER DAMAGE WAS DISCOVERED, AN POTENTIAL COSTS WERE PROJECTED TO EXCEED $50K. | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
48 | 2004-08-21 | PA | natural disasters | UNKNOWN (PA COUNTY) | EQUITABLE RESOURCES (A.K.A EQUITABLE GAS CO) | A 16" STEEL GAS MAIN PULLED OUT OF A 16" STEEL COUPLER. | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
49 | 2004-09-02 | WA | maintenance | UNKNOWN (KING COUNTY) | PUGET SOUND ENERGY | A PSE EMPLOYEE WAS PERFORMING A PRELIMINARY LEAK INVESTIGATION IN RESPONSE TO A GAS ODOR CALL. AS HE WAS WORKING NEAR THE HOUSE WHERE THE ODOR CALL ORIGINATED, THE HOUSE NEXT DOOR EXPLODED AND BURNED. THE SOLE RESIDENT WAS BURNED, REQUIRING HOSPITALIZATION AT THE HARBORVIEW REGIONAL BURN CENTER IN SEATTLE. THE HOUSE WAS DESTROYED. OCCUPANT DIED ON SEPTEMBER 27, 2004. FATALITY REPORTED TO NRC 9-27-04 AT 11:55 HOURS (RECEIVED BY MR. THREAT). THE CONCLUSIONS OF THE INCIDENT INVESTIGATION CONDUCTED JOINTLY BY PUGET SOUND ENERGY AND THE WASHINGTON UTILITIES AND TRANSPORTATION COMMISSION HAVE BEEN AGREED TO BY BOTH PARTIES. THE INCIDENT WAS CAUSED PRIMARILY BY A LONG TERM BUILD-UP OF CORROSION ON THE HOME'S BURIED SERVICE LINE, ITS EVENTUAL LEAK, AND UNIQUE CIRUCUMSTANCES THAT ALLOWED ESCAPING GAS TO ENTER THE HOME. | 357761 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
50 | 2004-09-01 | CT | other | UNKNOWN (FAIRFIELD COUNTY) | YANKEE GAS SERVICES CO | ON WED., 9/1/04 AT 1442 THE YANKEE GAS DISPATCHER RECEIVED A CALL FROM THE NORWALK FIRE DEPT. THERE WAS AN ODOR OF GAS AT THE GAS METERS IN THE BASEMENT. DISPATCH WAS INFORMED THAT THE FIRE DEPT HAD PUT OUT A STRUCTURE FIRE ABOUT AN HOUR PRIOR TO THE CALL. THE FIRE MARSHALL STATED TO THE FIELD SUPERVISOR WHO ARRIVED ON THE JOB LATER THAT AFTERNOON, THAT THE INITIAL CALL CAME IN ABOUT 1239 TO THE FIRE DEPT. THE METER & SERVICE MECHANIC, THE FIRST RESPONDER, ARRIVED ON SITE TO FIND THE INSIDE GAS SERVICE VALVE WAS ALREADY SHUT OFF AT THE METERS, AND THE 2 GAS METERS HAD RECEIVED EXTENSIVE DAMAGE FROM THE FIRE. ACCORDING TO THE CUSTOMER'S INSURANCE ADJUSTER, THE PROBABLE CAUSE OF THE FIRE WAS AN ACCIDENTAL SPILLAGE OF GASOLINE IGNITED BY THE GAS WATER HEATER. THERE APPEARED TO BE A MINOR RELEASE OF GAS AS A RESULT OF THE DAMAGE TO TEH 2 GAS METERS IN THE BASEMENT AREA. | 50290 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
51 | 2004-06-23 | UT | other | UNKNOWN (SALT LAKE COUNTY) | QUESTAR GAS COMPANY | A PLUMBING COMPANY WAS PERFORMING MAINTENANCE ON A LEAKING WATER SERVICE LINE. THE PLUMBING COMPANY CALLED THE ONE CALL SYSTEM. THE LINE WAS ACCURATELY LOCATED. THE PLUBMING COMPANY EXCAVATED THE HOLE TO REPAIR THE WATER LINE. THE WATER LEAK WAS LOCATED IN CLOSE PROXIMITY TO THE NATURAL GAS SERVICE LINE, IN THAT THE NATURAL GAS SERVICE LINE WAS EXPOSED IN THE EXCAVATION WHERE THE WATER LINE REPAIR WAS BEING MADE. THE NATURAL GAS SERVICE LINE HAD NO APPARENT DAMAGE DUE TO THE EXCAVATION. THE HEAT FROM THE TORCH USED BY THE EMPLOYEE OF THE PLUMBING COMPANY MELTED THE 3/4" PLASTIC NATURAL GAS SERVICE LINE AND IGNITED THE GAS. AS A RESULT OF THE IGNITED GAS THE EMPLOYEE OF THE PLUMBING COMPANY WAS BURNED REQUIRING HOSPITALIZATION. | 4835 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
52 | 2004-08-28 | WA | other | UNKNOWN (KING COUNTY) | PUGET SOUND ENERGY | PLUMBER WORKING FOR PRIVATE PARTY WAS PREPARING TO SOLDER A COPPER JOINT IN A WATER SERVICE. ONE-CALL HAD CORRECTLY LOCATED A NEARBY 5/8" POLYETHYLENE GAS SERVICE AND IT HAD BEEN SAFELY EXPOSED. THE PLUMBER FAILED TO USE A HEAT SHIELD TO PROTECT THE PE SERVICE FROM THE SOLDERING TORCH. THE HEAT MELTED THE SERVICE AND GAS ESCAPED THEN IGNITED. PLUMBER ADMITTED TO HARBORVIEW REGIONAL BURN CENTER WITH FACIAL BURNS. OPERATOR'S EMERGENCY RESPONDERS, WHO ARRIVED AFTER PLUMBER HAD BEEN TRANSPORTED, SQUEEZED LINE THEN REPAIRED THE SAME DAY. THIS SUPPLEMENTAL REPORT IS TO REPORT THE INCIDENT COST ONLY. NO OTHER CHANGES | 361 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
53 | 2004-09-09 | CA | other | UNKNOWN (KERN COUNTY) | SOUTHERN CALIFORNIA GAS CO | VEHICLE BEING CHASED ON HIGHWAY LOST CONTROL, FLIPPED NUMEROUS TIMES, EJECTING PASSENGERS. VEHICLE CAME TO REST ON PRIMARY REGULATION OF METER SET ASSEMBLY, APPROXIMATELY 50' FROM ROADWAY. FIVE FATALITIES, NONE RELATED TO RELEASE OF GAS. | 1500 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
54 | 2004-09-22 | LA | sabotage | UNKNOWN (TERREBONNE COUNTY) | SOUTH COAST GAS CO INC | THOMPSON CONSTRUCTION HIT OUR LINE WORKING FOR SCHLUMBER. IN DOING CONSTRUCTION THEY HIT THE WATER LINE. WHILE HELPING THE WATER DISTRICT REPAIR THEIR LINE THEY HIT THE GAS LINE. | 333 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
55 | 2004-08-27 | NM | leaks and spills | UNKNOWN (LEA COUNTY) | ZIA NATURAL GAS CO |  | 158115 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
56 | 2004-08-23 | IL | other | UNKNOWN (COOK COUNTY) | PEOPLES GAS LIGHT & COKE CO | ON MONDAY, AUGUST 23, 2004, A TWO_MAN DISTRIBUTION DEPARTMENT CREW WAS ASSIGNED TO RENEW AN 1-1/2" STEEL CATHODICALLY PROTECTED SERVICE PIPE (INSTALLED IN 1965) WITH 5/8" POLYETHYLENE PLASTIC. DURING THE SERVICE PIPE RENEWAL PROCESS ONE OF THE TWO CREW MEMBERS WAS WORKING ALONE IN THE OPENING AT THE SERVICE TAP. THE RENEWAL PROCEDURE BEING PERFORMED IS SUCH THAT NO GAS ESCAPES BECAUSE THERE IS A SHUTOFF VALVE AT THE SERVICE TAP. THE EMPLOYEE STATED THAT HE BACKED OFF THE THREADED RETAINER NUT ON THE END OF THE CORE OF THE BRASS CORPORATION COCK IN THE 6" MEDIUM PRESSURE (20 PSI) MAIN AND THEN TAPPED THE CORE WITH A HAMMER. THE CORE FLEW OUT OF THE COCK ALLOWING GAS TO ESCAPE UNDER PRESSURE INTO THE OPENING. THE EMPLOYEE ATTEMPTED TO RE-INSERT THE CORE INTO THE COCK UNSUCCESSFULLY AND WAS OVERCOME BY THE GAS IN THE PROCESS. WITH THE ASSISTANCE OF A NEIGHBOR, THE OTHER CREW MEMBER PULLED THE OVERCOME EMPLOYEE OUT OF THE OPENING. AN EMERGENCY CALL WAS MADE TO THE COMPANY'S DISPATCH CENTER, WHICH IN TURN IMMEDIATELY NOTIFIED THE CHICAGO FIRE DEPARTMENT. THE SECOND CREW MEMBER PERFORMED MOUTH TO MOUTH RESUSSITATION UNTIL THE AMBULANCE ARRIVED. THE COMPANY EMPLOYEE WAS THEN GIVEN OXYGEN AND TRANSPORTED TO THE HOSPITAL. THE HOSPITAL KEPT THE EMPLOYEE OVERNIGHT AND HE WAS RELEASED THE FOLLOWING DAY. THE EMPLOYEE HAS RECOVERED AND UPON RETURNING TO WORK WENT THROUGH RETRAINING AND TESTING. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
57 | 2004-08-29 | PA | other | UNKNOWN (WESTMORELAND COUNTY) | DOMINION PEOPLES | ON AUGUST 29, 2004 AT 10:37 PM, DOMINION PEOPLES RECEIVED A REPORT FROM 911 THAT A VEHICLE HAD COLLIDED INTO OUR REGULATOR STATION FACILITY LS-3414 LOCATED AT ARONA ROAD, IRWIN, WESTMORELAND COUNTY, PA. DOMINION PEOPLES PERSONNEL ARRIVED AT THE SCENE, FOUND THE VEHICLE HAD HIT AND DAMAGED THE REGULATOR STATION & BREAKING OF OFF A 1/4" PIPE NIPPLE. OUR PERSONNEL REPLACED THE NIPPLE SHUTTING OFF THE LEAKING GAS, THEN SHUT DOWN THE REGULATOR STATION. SERVICE WAS LOST TO APPROXIMATELY 120 CUSTOMERS. ON AUGUST 30, 2004 TEMPORARY REPAIRS WERE MADE TO LS-3414 AND SERVICE WAS RESTORED TO APPROXIMATELY 120 CUSTOMERS. A PRLIMINARY DAMAGE ASSESSMENT WAS MADE ON AUGUST 30, 2004. PRELIMINARY NOTIFICATION WAS MADE TO NRC AND THE PA-PUC BY TELEPHONE ON AUGUST 30, 2004 WHEN IT WAS DETERMINED THAT THE ESTIMATED PROPERTY DAMAGE RELATED TO REPORTABLE INCIDENTS APPROACHED THE REPORTABLE LEVEL. NRC #733536 WAS ASSIGNED TO THIS EVENT AT THAT TIME. THE PA-PUC CONDUCTED AN INVESTIGATION OF THIS INCIDENT ON SEPTEMBER 3, 2004. PERMANENT REPAIRS ARE SCHEDULED FOR SEPTEMBER/OCTOBER 2004. | 83257 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
58 | 2004-08-14 | LA | sabotage | UNKNOWN (nan COUNTY) | SOUTH COAST GAS CO INC |  | 247 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
59 | 2004-08-20 | LA | sabotage | UNKNOWN (LAFOURCHE COUNTY) | SOUTH COAST GAS CO INC |  | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
60 | 2004-06-14 | UT | other | UNKNOWN (SALT LAKE COUNTY) | QUESTAR GAS COMPANY | VEHICLE WAS SOUTHBOUND ON 700 EAST. VEHICLE RAN OFF ROAD TO THE RIGHTSIDE AT ABOUT 4700 SOUTH AND 700 EAST. VEHICLE RAN OVER VEGETATION, STOP SIGN AND APARTMENT SIGN. VEHICLE CONTINUED OFF ROAD SOUTHBOUND UNTIL IT HIT A FOUR-METER HEADER ATTACHED TO THE APARTMENT BUILDING. IMPACT OF VEHICLE BROKE SERVICE LINE VALVE AT RISER. RELEASE OF NATURAL GAS WAS IGNITED. DRIVER OF VEHICLE WAS PULLED FROM WRECKAGE BY A BYSTANDER. DRIVER WAS TAKEN TO UNIVERSITY OF UTAH HOSPITAL VIA HELICOPTER WITH MODERATE INJURIES ACCORDING TO MURRAY CITY POLICE. POLICE REPORT INDICATES THAT THE DAMAGE TO THE APARTMENT BUILDING WAS SUBSTANTIAL AND THE BUILDING IS A PROBABLE LOSS. VEHICLE IS AT FAULT FOR UNSAFE LANE TRAVEL, DRIVING ON SIDEWALK AND COLLISION WITH A FIXED OBJECT. DRIVER OF VEHICLE WAS TALKING ON CELL PHONE AT THE TIME OF THE ACCIDENT. PROPERTY DAMAGES ARE AN ESTIMATE. | 755489 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
61 | 2004-07-23 | LA | sabotage | UNKNOWN (ASSUMPTION COUNTY) | PIERRE PART NATURAL GAS INC |  | 367 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
62 | 2004-07-14 | NM | sabotage | UNKNOWN (SANTA FE COUNTY) | PUBLIC SERVICE COMPANY OF NEW MEXICO - GAS SVCS | SUPPLEMENTAL: HORIZON UTILITIES AND EXCAVATING HIT A CAPPED GAS STUB THAT THEN CAUSED A RELEASE OF GAS RESULTING IN DAMAGE TO A NEARBY MOBILE HOME. DAMAGE TO PRIVATE PROPERTY/MOBILE HOME AND CONTENTS IS REVISED TO AN ESTIMATED VALUE OF $35,000. NO PHYSICAL INJURIES WERE CLAIMED. | 37412 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
63 | 2004-08-08 | AK | other | UNKNOWN (nan COUNTY) | ENSTAR NATURAL GAS CO | ON SUNDAY AFTERNOON, AUGUST 8, 2004 AT APPROXIMATELY 12:56 PM ADT, ENSTAR NATURAL GAS COMPANY WAS NOTIFIED OF A STRUCTURE FIRE AT LOT 15, BLOCK 2 SKYLINE ESTATES (TWILIGHT DRIVE) WASILLA, ALASKA. AN ENSTAR SERVICEMAN WAS DISPATCHED TO THE SCENE. UPON ARRIVAL THE SERVICEMAN FOUND A RESIDENTIAL STRUCTURE ON FIRE. HEAT FROM THE FIRE MELTED THE POLYETHYLENE SERVICE LINE RISER AND GAS METER, CAUSING A RELEASE OF NATURAL GAS. A DISTRIBUTION CREW DUG UP THE SERVICE LINE, PINCHED IT OFF, AND CAPPED IT. NATURAL GAS FROM ENSTAR'S FACILITIES DID NOT CAUSE OR CONTRIBUTE TO THE FIRE. | 51010 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
64 | 2004-08-14 | VA | sabotage | UNKNOWN (PRINCE WILLIAM COUNTY) | WASHINGTON GAS LIGHT CO | CONTRACTOR PRK DRILLING & BLASTING, WERE BLASTING IN PREPARATION OF SEWER MAIN INSTALLATION IN THE VICINITY OF WASHINGTON GAS FACILITIES WHICH CAUSED THE 12" PLASTIC GAS MAIN TO BE SEVERED BY THE EXPLOSION. THIS CAUSED A LOSS OF GAS SERVICE TO APPROXIMATELY THREE THOUSAND CUSTOMERS. REPORT STATES 38 UNITS WERE EVACUATED. | 425000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
65 | 2004-07-31 | IL | other | UNKNOWN (COOK COUNTY) | NORTHERN ILLINOIS GAS CO | STRUCTURE FIRE CAUSED THE ROOF AND THE CUSTOMER FUEL LINE TO COLLAPSE WHICH THEN DAMAGED THE GAS METER WHICH WAS LOCATED INSIDE THE STURCTURE. | 1500000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
66 | 2004-08-09 | MD | other | UNKNOWN (MONTGOMERY COUNTY) | WASHINGTON GAS LIGHT CO | THE NATURAL GAS METER WAS DAMAGED BY A FIRE THAT STARTED IN A SINGLE FAMILY RESIDENCE. THE ROCKVILLE CITY FIRE DEPARTMENT THAT THE PRIMARY CAUSE OF THE FIRE WAS FLAMMABLE MATERIAL STORED NEAR THE WATER HEATER. IGNITION FROM THE WATER HEATER CAUSED THE FLAMMABLE MATERIAL TO IGNITE. NATURAL GAS WAS A SECONDARY CONTRIBUTOR TO THIS FIRE. | 300110 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
67 | 2004-09-18 | PA | natural disasters | UNKNOWN (ALLEGHENY COUNTY) | EQUITABLE RESOURCES (A.K.A EQUITABLE GAS CO) | AN 12" STEEL GAS MAIN FAILED AS A RESULT OF HEAVY RAINS. PIPELINE SECTION IS PHYSICALLY SEPARATED AND ABANDONED. | 500000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
68 | 2004-09-21 | PA | sabotage | UNKNOWN (BERKS COUNTY) | PPL GAS UTILITIES CORP | TOWNSHIP WAS GRADING DIRT ROADWAY AND SHOULDER WITH A FRONT END LOADER. THE PIPELINE IN THE SHOULDER OF THE ROAD WAS STRUCK AND PUNCTURED. LEAK SITE WAS SECURED, AND GAS ALLOWED TO VENT WHILE A TEMPORARY BYPASS INSTALLED TO MAINTAIN GAS SERVICE WHILE REPAIRS WERE MADE. THERE WERE NO CUSTOMER OUTAGES. | 98288 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
69 | 2004-06-05 | NY | other | UNKNOWN (nan COUNTY) | CONSOLIDATED EDISON CO OF NEW YORK | THIS IS THE FOLLOW UP TO THE VERBAL REPORT OF AN INCIDENT ON JUNE 5, 2004 AT 23:45 HOURS HOURS AT 52-15 VAN DAM STREET IN QUEENS, NEW YORK. COMPANY PERSONNEL RESPONED TO A NEW YORK CITY FIRE DEPARTMENT REPORT OF A BUILDING FIRE IN PROGRESS WITH GAS INVOLVED. UPON ARRIVAL, WE FOUND THE FDNY ON LOCATION AND A CLASS 1000 GAS METER ON FIRE INSIDE SKYWAY AUTOBODY/REPAIR SHOP. THE FDNY TURNED OFF THE GAS METER VALVE FOR SAFETY. UPON FURTHER INVESTIGATION, FIRE MARSHALL DEPIZIO (BADGE #15) INFORMED US THAT THERE WAS 3 FIRES INSIDE THE SHOP (2 FIRES AT THE REAR OF THE SHOP AND 1 FIRE AT THE GAS METER AT THE FRONT OF THE SHOP). MR. DEPRIZIO ALSO STATED THAT IT APPEARED THAT THE FIRE STARTED AT THE REAR OF THE SHOP AND TRAVELED TOWARD THE FRONT OF THE SHOP. FIRE CHIEF WHITE (BATALLION 45) STATED THAT THE FIRE IS OF SUSPICIOUS NATURE AND THE CAUSE OF THE FIRE IS UNDER INVESTIGATION. WE CHECKED THE AREA AND FOUND NO GAS LEAKS OR ANY INDICATION OF GAS. THERE WAS PROPERTY DAMAGE GREATER THAN $50,000. THE GAS METER, ELECTRIC METER, THE SHOP OFFICE, AND SOME CARS INSIDE THE SHOP WERE DAMAGED. THERE WERE ALSO SMOKE DAMAGE TO AN ADJACENT WAREHOUSE AT #52-13 VAN DAM STREET. THRE WERE NO INJURIES, NO EVACUATION, AND NO MEDIA ON LOCATION. WE REMOVED THE GAS METER, LOCKED THE CURB VALVE AND HEAD OF SERVICE VALVE, AND ISSUED A WARNING TAG. A CON EDISON PHOTOGRAPHER WAS ON LOCATION. THIS WAS AN UPGRADGED LEVEL INCIDENT. IT WAS RULED BY THE FDNY THAT GAS WAS NOT THE PRIMARY SOURCE OF IGNITION FOR THE BUILDING FIRE. THEREFORE, NO FURTHER COMPANY ACTION IS REQUIRED. PLEASE NOTE, THE OPERATOR 5 DIGIT IDENTIFICATION PERTAINS TO OUR HEADQUARTERS LOCATED AT 4 IRVING PLACE, NEW YORK, NY 10003 ALTHOUGH THE ADMINISTRATIVE SITE WHERE THIS FORM WAS COMPLETED IS THE GAS EMERGENCY REPSPONSE CENTER LOCATED AT 1615 BRONXDALE AVE, BLDG 21A, BRONX, NY 10462. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
70 | 2004-09-21 | PA | natural disasters | UNKNOWN (ALLEGHENY COUNTY) | COLUMBIA GAS OF PENNSYLVANIA | IN ALLEGHENY COUNTY, CRECENT TOWNSHIP AN 8-INCH CROSS COUNTRY LINE KNOWN AS D-74 IN THE AREA OF RIVERVIEW ROAD, THERE WAS A LANDSLIDE WHICH CAUSED A SEPARATION OF A COMPRESSION COUPLING ON A HILLSIDE. IT WAS A TWO WAY FEED AND COULD BE ISOLATED BY A VALVE ON ONE END AND SQUEEZING OFF OF PLASTIC, ON THE OTHER SIDE OF THE SEPARATION. NO CUSTOMERS WERE AFFECTED. | 438000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
71 | 2004-09-18 | PA | natural disasters | UNKNOWN (ALLEGHENY COUNTY) | DOMINION PEOPLES | ON SEPTEMBER 18, 2004, DOMINION PEOPLES DISCOVERED A BROKEN GAS PIPELINE (#P-1163) CAUSED BY A MUDSLIDE FROM EARTH MOVEMENT DUE TO HEAVY RAINS ON SEPTEMBER 17, 2004. DOMINION PEOPLES PERSONNEL ARRIVED AT THE SCENE, ASSESSED AND MONITORED THE SITUATION & SCHEDULED FOR A TEMPORARY RELOCATION OF THE PIPELINE TO BE PERFORMED ON SEPTEMBER 19, 2004. APPROXIMATELY 1,000' OF 3" TEMPORARY PIPELINE WAS INSTALLED ON SEPTEMBER 19, 2004. SERVICE TO CUSTOMERS WAS NEVER DISRUPTED. A PRELIMINARY DAMAGE ASSESSMENT AND MEETINGS WITH CONTRACTORS FOR AN EMERGENCY PIPELINE REPLACEMENT WAS CONDUCTED ON SEPTEMBER 20 AND 21, 2004. PRELIMINARY NOTIFICATION WAS MADE TO THE NRC AND THE PA-PUC BY TELEPHONE ON SEPTEMBER 21, 2004 WHEN IT WAS DETERMINED THAT THE ESTIMATED PIPELINE REPLACEMENT COSTS AND PROPERTY DAMAGE RELATED TO REPORTABLE INCIDENTS WOULD EXCEED THE REPORTABLE LEVEL. NRC #735861 WAS ASSIGNED TO THIS EVENT AT THAT TIME. THE PA-PUC PERFORMED AN ON-SITE INSPECTION OF THIS INCIDENT ON SEPTEMBER 30, 2004. PERMANENT REPAIRS ARE SCHEDULED FOR OCTOBER 2004. | 112159 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
72 | 2004-09-21 | PA | natural disasters | UNKNOWN (ALLEGHENY COUNTY) | DOMINION PEOPLES | ON SEPTEMBER 21, 2004, DOMINION PEOPLES DISCOVERED AN 8" BROKEN GAS PIPELINE CAUSED BY A LANDSLIDE FROM EARTH MOVEMENT DUE TO HEAVY RAINS ON SEPTEMBER 17, 2004. DOMINION PEOPLES PERSONNEL ARRIVED AT THE SCENE ASSESSED AND MONITORED THE SITUATION AND DISCONNECTED THE PIPELINE ON SEPTEMBER 21, 2004. PRELIMINARY DAMAGE ASSESSMENTS AND MEETINGS WITH THE LANDOWNER AND CONTRACTORS FOR AN EMERGENCY PIPELINE REPLACEMENT WERE CONDUCTED. ON OCTOBER 1, 2004, PRELIMINARY NOTIFICATION WAS MADE BY TELEPHONE TO THE NRC AND THE PA-PUC WHEN IT WAS DETERMINED THAT THE PIPELINE WOULD BE RELOCATED IN ANOTHER AREA CAUSING THE TOTAL PIPELINE RELOCATION & REPAIR COSTS RELATED TO REPORTABLE INCIDENTS TO EXCEED THE REPORTABLE LEVEL. NRC # 737022 WAS ASSIGNED TO THIS EVENT AT THAT TIME. PERMANENT REPAIRS ARE SCHEDULED FOR OCTOBER 2004. | 96164 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
73 | 2004-10-14 | AK | other | UNKNOWN (nan COUNTY) | ENSTAR NATURAL GAS CO | ON THURSDAY EVENING, OCTOBER 14, 2004 AT APPROXIMATELY 8:34PM ADT, ENSTAR NATURAL GAS COMPANY WAS NOTIFIED OF A STRUCTURE FIRE AT LOT 11, BLOCK 2 FREEMAN ANTHONY SUBDIVISION (6825 W BLONDELL DR) WASILLA, ALASKA. AN ENSTAR SERVICEMAN WAS DISPATCHED TO THE SCENE. UPON ARRIVAL THE SERVICEMAN FOUND A RESIDENTIAL STRUCTURE ON FIRE. HEAT FROM THE FIRE MELTED THE POLYETHYLENE SERVICE LINE RISER AND GAS METER, CAUSING A RELEASE OF NATURAL GAS. THE FIRE DEPARTMENT HAD SHUT OFF THE GAS FLOW BEFORE THE SERVICE TECH ARRIVED. THE LINE WAS DUG UP AND CAPPED. NATURAL GAS FROM ENSTAR'S FACILITIES DID NOT CAUSE OR CONTRIBUTE TO THE FIRE. | 51010 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
74 | 2004-09-16 | CA | other | UNKNOWN (ORANGE COUNTY) | SOUTHERN CALIFORNIA GAS CO | ELDERLY WOMAN INVOLVED IN AUTO ACCIDENT WITH ANOTHER VECHICLE LOST CONTROL, LEFT ROAD AND CAME TO REST ON TOP OF METERSET ASSEMBLY. DAMAGE TO METER SET RESULTED IN ESCAPING GAS WHICH DID NOT CONTRIBUTE TO DRIVER'S INJURIES. | 500 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
75 | 2004-07-08 | LA | sabotage | UNKNOWN (TERREBONNE COUNTY) | SOUTH COAST GAS CO INC |  | 396 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
76 | 2004-07-15 | LA | sabotage | UNKNOWN (LAFOURCHE COUNTY) | SOUTH COAST GAS CO INC |  | 187 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
77 | 2004-09-26 | IL | other | UNKNOWN (DEKALB COUNTY) | NORTHERN ILLINOIS GAS CO | SUPPLEMENTAL REPORT SUBMITTED WITH THE 3 PROPERTY DAMAGE SUBCATEGORIES SUMMING UP TO THE TOTAL VALUE. ***************************************************************************** MULCH/LANDSCAPING FIRE DAMAGED THE METER SET THUS CAUSING A RELEASE OF GAS. DAMAGED WIRING FOR LANDSCAPING LIGHTING WAS FOUND IN THE VICINITY OF THE METER SET. SOURCE OF IGNITION IS NOT POSITIVELY KNOWN. NOTE: THIS INCIDENT OCCURRED ON 9/26/04 BUT NOT REPORTED TO THE NRC UNTIL 9/28/04 BECAUSE INITIAL COMPANY AND FIRE DEPARTMENT PROPERTY DAMAGE ESTIMATES WERE WELL BELOW THE THREHOLD FOR REPORTING AND THUS NOT MEETING THE DEFINITION OF AN INCIDENT UNDER 49CFR191.3. ON 9/28/04 NICOR RECEIVED NOTIFICATION OF A THIRD VALUE FOR THE ESTIMATED PROPERTY THAT WOULD ELEVATE THIS EVENT TO AN "INCIDENT". ALTHOUGH THERE ARE 3 CONFLICTING ESTIMATES OF PROPERTY DAMAGE, IN AN ABUNDANCE OF CAUTION, NICOR DECIDED TO REPORT THIS EVENT AS AN INCIDENT. | 55000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
78 | 2004-09-20 | MD | other | UNKNOWN (BALTIMORE COUNTY) | BALTIMORE GAS & ELECTRIC CO | ACCORDING TO BATTALLION CHIEF MARK EWERS AND FIRE INVESTIGATOR #4 FOR THE BALTIMORE COUNTY FIRE DEPARTMENT, THE POINT OF FIRE ORIGINATED AT THE SOFFIT REAR OF BUILDING FROM THE SERVICE CABLES AFTER THE ELECTRICAL METER BOXES. THE HEAT AND/OR FIRE CAUSED THE GASKET OF THE REGULATOR TO MELT ALLOWING AN ESCAPE OF GAS THAT CAUGHT FIRE AROUND THE BODY OF THE REGULATOR. THE FIRE DEPARTMENT KEPT A SPRAY OF WATER TO KEEP THE FIRE UNDER CONTROL UNTIL WE OPERATED THE CURB VALVE AND TO STOP THE FLOW OF GAS. THE DAMAGE TO THE REGULATOR THAT ALLOWED GAS TO ESCAPE WAS SUBSEQUENT TO THE FIRE DAMAGE IT SUSTAINED. | 160000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
79 | 2004-08-16 | VA | sabotage | UNKNOWN (LOUDOUN COUNTY) | WASHINGTON GAS LIGHT CO | THE TOWN OF LEESBURG WAS PERFORMING MAINTENANCE ON A SEWER LINE WHEN THEY RUPTURED A 2" GAS MAIN. WHILE MOVING THE BACKHOE AFTER RUPTURING THE PLASTIC GAS LINE, THE LINE IGNITED CAUSING DAMAGE TO A DUMP TRUCK AND A BACKHOE. THE FIRE DEPARTMENT WAS ON THE SCENE AND IMMEDIATELY EXTINGUISHED THE FIRE. | 24611 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
80 | 2004-09-14 | NY | technical failure | UNKNOWN (SARATOGA COUNTY) | NIAGARA MOHAWK POWER CORP | OPERATING GAS CREW INCORRECTLY DISASSEMBLED MAIN VALVE WHILE IN SERVICE TO SUCH POINT WHERE THE VALVE CORE WAS EJECTED BY THE PRESSURE OUT OF THE HOUSING. BLOWING GAS FROM THE HOUSING EVENTUALLY IGNITED, SOURCE UNKNOWN. | 82429 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
81 | 2004-09-25 | WV | sabotage | UNKNOWN (PUTNAM COUNTY) | UNION OIL & GAS INC | ADELPHIA CABLE USING WALK BEHIND TRENCHER CUT INTO 2 INCH NATURAL GAS PIPELINE. PIPELINE WAS MARKED AND GAS COMPANY INVESTIGATION DETERMINES INCIDENT DUE TO ADELPHIA OPERATOR ERROR. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
82 | 2003-07-15 | MN | sabotage | UNKNOWN (nan COUNTY) | CENTENNIAL UTILITIES | EXCAVATION CONTRACTOR WAS WORKING AT THE ADJACENT ADDRESS TO THE ONE CALLED IN FOR LOCATES. | 75 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
83 | 2003-08-21 | MN | sabotage | UNKNOWN (ANOKA COUNTY) | CENTENNIAL UTILITIES | THE 4" LINE THAT WAS HIT MADE A HUGE CHANGE IN DEPTH BETWEEN THE POTHOLES ON EITHER SIDE OF EXCAVATION. THIS LINE WAS REPLACED AS PART OF THE ROAD REPLACEMENT PROJECT THAT WAS ONGOING. | 500 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
84 | 2004-05-10 | MN | other | UNKNOWN (HENNEPIN COUNTY) | CENTERPOINT ENERGY MINNEGASCO | HOMEOWNER DISCONNECTED GAS CONNECTION TO WATER HEATER DRIP LEG, PLUGGED WATER HEATER VENT WITH RAGS, ALLOWING GAS TO FILL THE HOUSE AND IGNITE WITH A CIGARETTE LIGHTER. HOUSE EXPLODED SERIOUSLY INJURING HOME OWNER. | 150000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
85 | 2004-07-13 | MI | sabotage | UNKNOWN (WAYNE COUNTY) | DTE ENERGY - MICHCON | RELEASE AND IGNITION OF NATURAL GAS FROM SERVICE LINE. MISS DIG WAS CALLED AND SITE WAS STAKED ACCURATELY. CONTRACTOR FAILED TO HAND EXPOSE NATURAL GAS FACILITY PRIOR TO USING POWER EQUIPMENT. THIS INCIDENT WAS CAUSED BY A CONTRACTOR WHEN THEY RUPTURED A MICHCON FACILITY. | 200000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
86 | 2004-10-07 | KS | other | UNKNOWN (JOHNSON COUNTY) | KANSAS GAS SERVICE | A DELIVERY TRUCK BACKED INTO THE METER SETTING AND CRACKED THE METER AROUND THE METER SPUD. APPARENTLY NATURAL GAS WAS DRAWN INTO THE BUILDING THROUGH A VENT AT THE SIDE OF THE BUILDING WHICH WAS APPARENTLY IGNITED BY SOME UNDETERMINED SOURCE LOCATED INSIDE OF THE BUILDING. 7/27/2006 - SUPPLEMENTAL CHANGES TO SECTION A 5 C - CHANGED PUBLIC/PRIVATE PROPERTY DAMAGE FROM 50,000.00 TO 500,000.00. BDK | 500040 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
87 | 2004-09-17 | TX | sabotage | UNKNOWN (HARRIS COUNTY) | CENTERPOINT ENERGY | CENTERPOINT ENERGY CONTRACTOR DAMAGED A 4" H.P. STEEL MAIN WITH A BORING TOOL WHILE INSTALLING A NEW GAS MAIN. | 28436 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
88 | 2004-10-11 | SD | other | UNKNOWN (nan COUNTY) | MONTANA - DAKOTA UTILITIES CO | FIRE OF UNKNOWN ORIGIN IN BASEMENT OF STORAGE AREA OF BUILDING SPREAD TO VICINITY OF METER SET, DESTROYING METER SET. GAS TO METER SET WAS TURNED OFF OUTSIDE OF BUILDING. FIRE DEPARTMENT DETERMINED THAT NATURAL GAS WAS NOT SOURCE OF FIRE. DAMAGE TO METER SET WAS RESULT OF FIRE. | 100800 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
89 | 2004-10-05 | AL | leaks and spills | UNKNOWN (MARSHALL COUNTY) | MARSHALL COUNTY GAS DISTRICT |  | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
90 | 2004-10-21 | LA | sabotage | UNKNOWN (ASSUMPTION COUNTY) | PIERRE PART NATURAL GAS INC |  | 125 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
91 | 2004-10-11 | WI | other | UNKNOWN (WASHINGTON COUNTY) | WISCONSIN GAS CO | ON THE MORNING OF OCTOBER 11, 2004, COMPANY'S CONTRACTOR CREW (ARBY CONSTRUCTION) PROCEEDED TO INSTALL A 6X6X6 TEE IN AN EXISTING 35#, 6", PE DISTRIBUTION MAIN. A 1&1/4" BY-PASS WAS CONSTRUCTED AROUND THE PROPOSED TEE CUT IN LOCATION TO AVOID CUSTOMER OUTAGES. INCLUDED WAS THE INSTALLATION OF A GROUNDING LINE FOR STATIC ELECTRICITY CONTROL. NEXT, TWO MANUAL SQUEEZE OFF TOOLS WERE INSTALLED TO CONTROL THE FLOW OF GAS IN PREPARATION FOR CUTTING OUT THE SEGMENT TO INSTALL THE NEW TEE USING TWO ELECTRO FUSION COUPLINGS FOR THE TIE-INS. GAS WORKER THAN PROCEEDED TO USE CUTTER TOOL TO SCORE THE LINE AND CREATE A SMALL BREAK ON THE TOP OF THE MAIN TO RELEASE THE ENTRAPPED GAS. UPON COMPLETION, HE NOTICED THAT MORE GAS WAS BEING RELEASED THAN EXPECTED. HE, AND AN ASSISTANT, PROCEEDED TO TIGHTEN DOWN THE SQUEEZE OFF TOOLS BELIEVING THAT A SMALL AMOUNT OF GAS WAS ESCAPING ONE OF THE CLAMPS. WHILE, TIGHTENING THE 2ND CLAMP, WORKERS STATED THEY HEARD WHAT THEY BELIEVED TO BE GAS ESCAPING FROM THE AREA OF THE FIRST CLAMP. RECOGNIZING THAT SOMETHING WAS WRONG, THEY EVACUATED THE DITCH, TURNED OFF ALL EQUIPMENT IN THE AREA AND CALLED THE COMPANY SUPERVISOR THAT THEY HAD AN UNCONTROLLED RELEASE OF GAS. COMPANY SUPERVISOR IMMEDIATELY CALLED COMPANY'S GAS DISPATCHER FOR ADDITIONAL ASSISTANCE AND NOTIFICATION OF A PROBLEM. CALL TO DISPATCH WAS MADE AT APPROXIMATELY 9:10 AM. COMPANY CREW'S ARRIVED APPROXIMATELY 20 MINUTES LATER. UPON ARRIVAL, GAS & DIRT WERE BLOWING OUT OF THE DITCH 15 TO 20 FEET IN THE AIR. WITHIN MINUTES AFTER THEIR ARRIVAL, AND BEFORE ANY EVALUATION OF THE CONDITION COULD BE MADE, THE GAS IGNITED. IT IS BELIEVED THAT THE DRY GAS COMBINED WITH DIRT RESULTED IN ENOUGH STATIC CONDITIONS TO CAUSE IGNITION. DESTROYED OR DAMAGED DURING THE PERIOD OF BURNING WAS A BACKHOE, TRUCK AND RELATED GAS EQUIPMENT & TOOLS. TO CONTROL THE FLOW OF GAS, THREE AREA VALVES, A 6", 4" AND A 2" WERE CLOSED. THE CLOSING OF VALVES RESULTED IN OUTAGES TO 10 CUSTOMERS. AFTER CONTROLLING THE GAS, CREWS PROCEEDED TO MAKE THE NECESSARY REPAIRS AND RELIGHTED THE CUSTOMERS AFFECTED. THE FIRE IN THE DITCH CONSUMED THE EXPOSED PE PIPE LEAVING LITTLE EVIDENCE OF ACTUAL CAUSE, CONDITION AND/OR PLACEMENT OF EQUIPMENT AND POST CONDITION OF PIPE. AS OF THE WRITING OF THIS PRELIMINARY REPORT, THE CAUSE AND FAILURE MODE HAS NOT BEEN DETERMINED. THE EQUIPMENT MANUFACTURE HAS BEEN CALLED IN TO VERIFY THE CONDITION OF THE TOOLS USED, AND PREPARATIONS FOR TESTING OF THE PE PIPE IS UNDERWAY. A POST INCIDENT REVIEW WAS HELD WITH ALL PERSONNEL INVOLVED TO COLLECT STATEMENTS AND TO REVIEW PROCEDURES USED. UPON COMPLETION OF TESTS AND FURTHER REVIEWS, A FOLLOW UP REPORT WILL BE MADE AS TO THE CONCLUSIONS DRAWN AND ANY PROCEDURAL CHANGES THAT SHOULD BE MADE. | 66000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
92 | 2004-10-12 | NJ | sabotage | UNKNOWN (MIDDLESEX COUNTY) | PUBLIC SERVICE ELECTRIC & GAS CO | AT 1500 HOURS ON TUESDAY, OCTOBER 12, 2004,A PSE&G SERVICE TECHNICIAN CALLED IN TO THE COMPANY TO REPORT THAT WHILE HE WAS WORKING AT A CUSTOMER'S HOME ON PROSPECT STREET, EDISON ON A SERVICE CALL, A NEIGHBOR INFORMED HIM THAT THERE WAS A SMELL OF NATURAL GAS IN THE NEIGHBORHOOD. AS THE TECHNICIAN WENT OUT TO INVESTIGATE, HE HEARD AN EXPLOSION. AFTER REPORTING THE EXPLOSION, HE IMMEDIATELY WENT TO THE SITE, ARRIVING AT 1502 HOURS, AND FOUND THAT A SINGLE STORY RESIDENCE AT 177 PLAINFIELD AVENUE, EDISON HAD EXPLODED AND THAT THE TWO ADJACENT HOMES #175 AND #179, WERE ON FIRE. THE TECHNICIAN CALLED IN TO THE COMPANY FOR ASSISTANCE AND PROCEEDED TO MAKE THE AREA SAFE. THE GAS SERVICES OT THE THREE BUILDINGS WERE SHUT OFF BY 1600 HOURS. INITIAL FINDINGS AT THE SCENE INDICATE THAT THE OWNER OF 177 PLAINFIELD AVENUE WAS HAVING A CONTRACTOR REMEDIATE THE CONTAMINATED SOIL FROM A PREVIOUSLY REMOVED OIL TANK THAT HAD LEAKAGE AND WHILE IN THE PROCESS OF REMEDIATION OF CONTAMINATED SOIL, THE 1 1/4 INCH, 60 PSIG DESIGN GAS SERVICE OPERATING AT 24 PSIG TO 177 PLAINFIELD AVENUE WAS DAMAMGED OR WAS DAMAGED SHORTLY THEREAFTER RESULTING IN A RELEASE OF NATURAL GAS THAT IGNITED FROM AN UNKNOWN SOURCE. THE CONTRACTOR WA AURORA ENVIRONMENTAL, 1102 UNION AVENUE, UNION BEACH, NJ 07735. RECORDS INDICATE THAT THE CONTRACTOR DID REQUEST A MARK-OUT (TICKET NUMBER 042581065) AND THAT THE SITE WAS MARKED ON SEPTEMBER 17, 2004. THE COMPANY HAS DETERMINED THAT THE GAS SERVICE WAS DAMAGED AS A RESULT OF THE TRENCH COLLAPSE. THERE WERE NO INJURIES. PRELIMINARY ESTIMATES INDICATE THAT THIS INCIDENT RESULTED IN PROPERTY OF APPROXIMATELY $500,000. ACCORDINGLY, THE NATIONAL RESPONSE CENTER WAS NOTIFIED WITHIN TWO HOURS OF THE INCIDENT (CASE NUMBER 738-137). | 505200 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
93 | 2004-10-23 | MD | natural disasters | UNKNOWN (BALTIMORE COUNTY) | BALTIMORE GAS & ELECTRIC CO | AT 11:15 ON 10/23/04, B/C/F/D CALLED TO REPORT A FURNACE EXPLOSION AT 4247 CARDWELL AVE. BGE'S FIRST RESPONDER ARRIVED TO FIND A LARGE WATER LEAK FROM AN APPARENT WATER MAIN BREAK AT THE INTERSECTION OF BELAIR RD & CARDWELL AVE. FOUND WATER IN CUSTOMER'S FUEL LINES AT 4247 & 4239 CARDWELL AVENUE. WATER FROM CITY WATER MAIN ENTERED THE GAS MAIN AT A BREAK IN VERY CLOSE PROXIMITY TO WATER MAIN RUPTURE. THE WATER PRESSURIZED AND FILLED A PORTION OF THE GAS DISTRIBUTION SYSTEM CAUSING AN OUTAGE THAT AFFECTED APPROXIMATELY 2000 CUSTOMERS. ALL METERS WERE OFF BY 12:00 MONDAY, 10/25/04. REPAIRS WERE MADE, APPROXIMATELY 56,000 GALS OF WATER WAS PUMPED FROM THE MAINS, 500 SERVICES WERE CLEARED OF WATER, 450 METERS WERE REPLACED AND SERVICE WAS RESTORED TO CUSTOMERS' METERS BY APPROXIMATELY 16:00 FRIDAY, 10/29/04. | 2750000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
94 | 2004-11-02 | OH | other | UNKNOWN (HAMILTON COUNTY) | CINCINNATI GAS & ELECTRIC CO | ATTEMPTIMG TO COMMIT SUICIDE, AN INDIVIDUAL USED A SAW TO CUT THROUGH THE OUTLET METER SWIVEL PIPING WHICH CAUSED GAS TO ESCAPE INSIDE A SINGLE FAMILY RESIDENCE RESULTING IN AN EXPLOSION. THERE WAS NO FIRE OR PERSONAL INJURY RESULTING FROM THE EXPLOSION. THE INDIVIDUAL TURNED THE GAS METER OFF HIMSELF AFTER THE EXPLOSION OCCURRED. | 110000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
95 | 2004-10-20 | IL | sabotage | UNKNOWN (DUPAGE COUNTY) | NORTHERN ILLINOIS GAS CO | THIRD PARTY CONTRACTOR WAS CONDUCTING DIRECTIONAL DRILLING OPERATIONS AND STRUCK A 4-INCH GAS LINE. GAS MIGRATED INTO THE STRUCTURE. EXPLOSION OCCURRED. | 812609 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
96 | 2004-10-30 | NM | other | UNKNOWN (DONA ANA COUNTY) | PUBLIC SERVICE COMPANY OF NEW MEXICO | ACCORDING TO THE DONA ANA COUNTY SHERIFF'S DEPARTMENT REPORT, ON OCTOBER 30, 2004, MARIO DELGADO, DRIVING A 2005 SUZUKI MOTORCYCLE, APPROACHED A CURVE AT OR AROUND 201 S ALVAREZ ST AND FAILED TO MAINTAIN HIS LANE OF TRAFFIC. MR. DELGADO LEFT THE ROADWAY AND ULTIMATELY COLLIDED WITH A BARRICADED RESIDENTIAL GAS METER. CONTRIBUTING FACTORS NOTED BY THE INVESTIGATING OFFICER ARE: EXCESSIVE SPEED, DRIVER INATTENTION AND OTHER IMPROPER DRIVING. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
97 | 2004-11-01 | AR | sabotage | UNKNOWN (PULASKI COUNTY) | CENTERPOINT ENERGY ARKLA | CONTRACTOR DAMAGED 4"STL MAIN WHILE BORING UNDER SHACKLEFORD RD TO INSTALL FIBER. THE COST ESTIMATE FOR PUBLIC/PRIVATE DAMAGE WAS ESTIMATED AT $40000 TO INCLUDE THE REPLACEMENT OF THE TRAFFIC SIGNAL AND PAVING REPAIR. | 72376 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
98 | 2004-10-23 | VA | other | UNKNOWN (LOUDON COUNTY) | WASHINGTON GAS LIGHT CO | DURING THE PROCESS OF REPLACING A WATER METER A TYLER MECHANCIAL EMPLOYEE WAS SOLDERING A COPPER WATER LINE WITH AN ACETYLENE TORCH. THE WORK WAS DONE IN THE AREA OF AN EXPOSED 2" - 55 PSI PLASTIC GAS SERVICE LINE IN AN OPEN EXCAVATION. THE METER AND REGULATOR WERE IN CLOSE PROXIMITY AND DAMAGED BY FIRE. | 100078 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
99 | 2004-11-01 | IA | technical failure | UNKNOWN (MONTGOMERY COUNTY) | MIDAMERICAN ENERGY COMPANY | GAS SERVICE TO MINSA CORPORATION WAS TURNED OFF AT THE METER SET AT THE CUSTOMER'S REQUEST SO THE CUSTOMER COULD WELD ON THE CUSTOMER'S PIPING. MINSA CORPORATION CALLED BACK BECAUSE GAS WAS LEAKING THROUGH. THE SERVICEMAN SHUTOFF THE OUTLET VALVE OF THE METER SET TO STOP THE GAS LEAKING INTO CUSTOMER PIPING. THE SERVICEMAN ALSO VALVED OFF THE OUT OF SERVICE METER SET RELIEF VALVE BECAUSE IT HAD BEEN LEAKING. MINSA CORPORATION REQUESTED THE GAS BE TURNED BACK ON ONE DAY AFTER IT WAS TURNED OFF. THE SERVICEMAN, WHO WAS ON A PRIORITY LOCATE, REQUESTED A QUALIFIED GAS CREW DO THE TURN ON AND TOLD THE CREW ABOUT THE RELIEF BEING LOCKED OFF. THE CREW SUSPECTED THE RELIEF TO HAVE SOMETHING IN THE SEAT AND SIMULTANEOUSLY TURNED ON THE RELIEF AND THE INLET VALVES WITH THE METER SET OUTLET VALVE CLOSED. THE REGULATOR SENSING LINE DOWNSTREAM OF THE OUTLET VALVE CAUSED THE REGULATOR TO OPEN UP TO 100%. THIS RESULTED IN THE PIPING DOWNSTREAN OF THE REGULATOR AND UPSTREAM OF THE OUTLET VALVE TO EXCEED THE METER'S MAOP AND THE METER FAILED WHEN IT WAS OVERPRESSURED. THE METER'S BELLOWS STRUCK A MINSA MANITENANCE MAN IN THE LOWER ABDOMINAL AND THIGH AREA. HE WAS TAKEN TO THE HOSPITAL WHERE HE WAS TREATED IN OUTPATIENTS. AT 4:00 P.M., HE STILL COMPLAINED OF PAIN AND WAS ADMITTED TO THE HOSPITAL. | 1000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
100 | 2004-11-08 | OK | sabotage | UNKNOWN (ROGERS COUNTY) | OKLAHOMA NATURAL GAS COMPANY | CONTRACTOR WORKING FOR DEVELOPER STRUCK ONG'S 4-INCH HIGH PRESSURE NATURAL GAS MAIN WITH A BACKHOE WHILE EXCAVATING FOR A SEWER LINE. THE EXCAVATOR DID NOT HAVE A LINE LOCATE REQUEST. THE BACKHOE RIPPED A 14"X4" GASH IN THE MAIN. THE SYSTEM HAD A TWO-WAY FEED AT THAT LOCATION, WHICH RESULTED IN SIGNIFICANT GAS LOSS. | 99000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
101 | 2004-11-15 | AZ | other | UNKNOWN (SANTA CRUZ COUNTY) | UNISOURCE ENERGY SERVICES | A VEHICLE HIT A SINGLE METER LOOP AS WELL AS A PHONE AND ELECTRIC METER PEDESTAL. THE BREAK OCCURRED AT THE METER BAR WHERE THE REGULATOR AND METER VALVE WAS STILL INTACT. THE ARCING ELECTRIC METER PEDESTAL IGNITED THE GAS, RESULTING IN DAMAGE TO VEHICLE. COMPANY FACILITIES AND MINOR DAMAGE TO A NEARBY RESIDENTIAL TRAILER HOME. THE POWER COMPANY SHUT OFF POWER IN THE IMMEDIATE AREA AND THE VEHICLE WAS TOWED AWAY. COMPANY CREWS THEN PROCEEDED TO VALVE OFF METER VALVE THUS SHUTTING THE GAS COMPLETELY OFF. | 12088 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
102 | 2004-11-29 | IN | sabotage | UNKNOWN (DEARBORN COUNTY) | LAWRENCEBURG GAS COMPANY | THE HIGHWAY CONTRACTOR WAS WORKING ON A ROAD PROJECT THAT HAS BEEN ONGOING FOR SEVERAL MONTHS. ONE-CALL LOCATES WERE PROPERLY MADE AT MANY DIFFERENT TIMES FOR THIS CONTRACTOR. IN THIS PARTICULAR AREA, CONTRACTOR WAS IN PROCESS OF DOING LIME STABLIZATION TO REMOVE MOISTURE FROM GROUND IN AREA TO PREPARE FOR PAVING FOR NEW ROAD SECTION. CONTRACTOR WAS USING RIPPER THAT EXTENDED INTO THE GROUND 16-20'. THE RIPPER ACTUALLY HOOKED A 1" STEEL MAIN-CURB SERVICE LINE THAT WAS NO LONGER SERVING A CUSTOMER, BUT WAS INACTIVE UNTIL THIS SEGMENT OF MAIN COULD BE ABANDONED. THE RIPPER PHYSICALLY PULLED THE SERVICE TEE OUT OF THE TOP OF THE MAIN, CAUSING A TRIANGULAR HOLE 0.5 INCHES WIDE ON ONE END AND 1.8 INCHES WIDE ON THE OTHER, AND 10 INCHES LONGITUDINALLY IN THE TOP OF THE MAIN. WE WERE NOT ABLE TO TAKE PICTURES OF THE LOCATE MARKINGS IN THIS AREA BECAUSE THE RIPPER OPERATION DESTOYRED ALL OF THE PAINTED MARKINGS. THE REASON THIS SEGMENT OF MAIN COULD NOT BE ABANDONED PRIOR TO THE ROAD CONSTRUCTION IS BECAUSE THE HIGHWAY DEPARTMENT HAS NOT BEEN ABLE TO SECURE RIGHT-OF-WAY IN ANOTHER PORTION OF THE PROJECT. ONCE WE ARE ABLE TO INSTALL APPROXIMATELY 1,000 FEET OF NEW 8" PIPELINE, THIS SEGMENT OF PIPING WILL BE ABANDONED. THE LAST REPORT GIVEN TO US BY THE STATE HIGHWAY DEPARTMENT IS THAT THE RIGHT-OF-WAY WILL BE AVAILABLE IN MARCH, 2005. THE AREA AROUND THE DAMAGE WAS SECURED IMMEDIATELY BY THE LOCAL FIRE DEPARTMENT, WHICH HAS A STATION NEAR THE INCIDENT. THE POLICE AND FIRE DEPARTMENT IMMEDIATLELY RESTRICTED PUBLIC TRAFFIC FROM ENTERING THE AREA. LAWRENCEBURG GAS PERSONNEL ARRIVED ON SITE WITHIN 15 MINUTES OF THE REPORT TO ASSESS THE DAMAGE AND BEGIN THE PROCESS FOR REPAIR. NO PERSONAL INJURIES OCCURRED, AND NO CUSTOMERS LOST SERVICE DURING THIS EVENT. WE WERE ABLE TO BACKFEED THIS AREA FROM ANOTHER PART OF OUR DISTRIBUTION SYSTEM. THE DAMAGED AREA WAS REPAIRED BY PLACING A STEEL BAND OVER THE HOLE, AND PERMANENTLY WELDING A DRESSER REPAIR SLEEVE OVER THE DAMAGED AREA. AS MENTIIONED, THIS SEGMENT OF PIPELINE WILL EVENTUALLY BE ABANDONED AFTER THE 1000 FOOT SEGMENT IS PLACED INTO SERVICE APPROXIMATELY ONE-HALF MILE FROM THE INCIDENT AREA. | 43031 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
103 | 2004-09-28 | CO | sabotage | UNKNOWN (nan COUNTY) | PUBLIC SERVICE CO OF COLORADO | ROAD EXCAVATION WORK HIT OLD BONNETED VALVE WHICH TORE PIPE CAUSING RUPTURE. | 85159 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
104 | 2004-11-19 | LA | sabotage | UNKNOWN (LAFOURCHE COUNTY) | SOUTH COAST GAS CO |  | 337 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
105 | 2004-11-05 | TX | leaks and spills | UNKNOWN (BEXAR COUNTY) | CITY PUBLIC SERVICE | GAS IGNITION OCCURRED WHEN THE CUSTOMER AT 4911 SWANN LANE FLIPPED A LIGHT SWITCH IN BATHROOM. AFTER INVESTIGATION, IT IS BELIEVED THAT THE SOURCE OF GAS ORIGINATED FROM A CRACKED POLYETHYLENE BUTT FUSION THAT MIGRATED UNDERGROUND TO THE HOUSE AND UNDER THE FOUNDATION WHERE IT ENTERED THROUGH THE TOILET DRAIN PENETRATION IN THE CONCRETE SLAB. THE CRACKED FUSION WAS LOCATED WHERE A 1" POLYETHYLENE SERVICE WAS CONNECTED TO A 1" TRANSITION FITTING. THIS TRANSITION FITTING WAS COMING DIRECTLY OFF OF THE SERVICE TEE TO 4915 SWANN LANE. | 61200 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
106 | 2004-12-03 | LA | sabotage | UNKNOWN (LAFOURCHE COUNTY) | SOUTH COAST GAS CO |  | 911 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
107 | 2004-11-27 | MN | natural disasters | UNKNOWN (GOODHUE COUNTY) | NORTHERN STATES POWER COMPANY DBA XCEL ENERGY | EARTH SETTLED UNDER STEEL-PE TRANSITION FITTING CAUSING LEAK IN PLASTIC SIDE OF COMPONENT. GAS MIGRATED ALONG THE SERVICE INTO THE HOUSE AND WAS IGNITED WHEN THE RENTER LIVING AT THE RESIDENCE LIT A LIGHTHER IN THE UTILITY ROOM. | 2000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
108 | 2004-11-16 | KY | sabotage | UNKNOWN (nan COUNTY) | BURKESVILLE GAS COMPANY INC |  | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
109 | 2004-10-26 | CA | leaks and spills | UNKNOWN (YOLO COUNTY) | PACIFIC GAS & ELECTRIC COMPANY | THE ROOT CAUSE OF THIS INCIDENT WAS THAT A LEAK ON A 4-INCH DIAMETER PLASTIC MAIN AT A PREVIOUS SQUEEZE POINT MIGRATED TO THE RESIDENCE AND IGNITED. THE SOURCE OF IGNITION HAS NOT BEEN DETERMINED. THE GAS LEAK WAS CAUSED BY A PLASTIC PIPE SLOW CRACK GROWTH FAILURE MOST LIKELY RESULTING FROM IMPROPER SQUEEZE PROCEDURES DURING INSTALLATION OF THE PIPE IN FEBRUARY 1977 AND/OR DURING A RECONSTRUCTION PROJECT IN OCTOBER 1992. IN ADDITION, THE LACK OF A SQUEEZE POINT SUPPORT CLAMP CONTRIBUTED TO THE FAILURE. ON DECEMBER 29, 1992, PG&E REVISED ITS PLASTIC INSTALLATION STANDARDS WITH TWO RELEVANT CHANGES. REQUIRED SUPPORT CLAMPS ON ALL EXPOSED SQUEEZE POINTS ON ALDYL "A" PIPE INSTALLED PROIR TO 1984. PREVIOUSLY, THE STANDARD IN EFFECT AT THE TIME OF THE OCTOBER 1992 INSTALLATION REQUIRED SUPPORT CLAMPS ON SQUEEZE POINTS ON ALDYL "A" PIPE INSTALLED PRIOR TO 1975. INSTITUTED A MAXIMUM RATE OF CLOSURE AND RELEASE FOR SQUEEZERS ON 1-INCH DIAMETER PER MINUTE. TAKEN TOGETHER, THESE TWO PROCEDURAL CHANGES MINIMIZE THE POSSIBLITY OF A REOCCURRENCE. | 514000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
110 | 2004-11-29 | MD | other | UNKNOWN (PRINCE GEORGES COUNTY) | WASHINGTON GAS | THE FIRE LOCATION, A RESTAURANT, AT 9128-30 BALTIMORE AVENUE IN COLLEGE PARK , MARYLAND CAUGHT FIRE AS A RESULT OF SUSPECTED ARSON. UPON ARRIVAL OF WASHINGTON GAS PERSONNEL, THE FIRE WAS BURNING AT THE BUILDING WHERE THE GAS SERVICE (METER BUILD-UP)WAS LOCATED AND FIRE FIGHTERS WERE EXTINGUISHING THE FIRE. THE INCIDENT COMMANDER WAS COLONEL JOY FROM THE PRINCE GEORGE'S FIRE DEPARTMENT. WASHINGTON GAS PERSONNEL EXCAVATED OVER THE 2-INCH PLASTIC SERVICE TO THE BUILDING AND SQUEEZED OFF THE SERVICE TO STOP THE FLOW OF GAS. THE GLASS FLOW WAS STOPPED AT 10:31AM. ACCORDING TO THE OWNER OF THE ESTABLISHMENT, JOSEPH LASICK, NO ONE WAS IN THE BUILDING AT THE TIME OF THE FIRE. THE ESTABLISHMENT HAD NOT OPENED FOR THE DAY. THE SPOKESMAN FOR THE PRINCE GEORGE'S COUNTY FIRE DEPARTMENT, MARK BRANDY, STATED THAT THE FIRE WAS IN THE AREA OF THE GAS METER. THE FIRE INVESTIGATOR, MR. LEAK, SAID THE PERSON WHO CALLED IN THE 911 EMERGENCY HAD BEEN INTERVIEWED AND SAID A FIRE WAS IN PROGRESS WHEN HE ARRIVED BUT THE GAS WAS NOT BLOWING AT THAT TIME. AFTER THE FIRE HAD BEEN EXTINGUISHED, THE METER AND REGULATOR WERE RECOVERED AND FOUND TO BE BURNED. THE METER WAS A "5 M ROTARY METER" THAT WAS INSTALLED ON APRIL 22, 2004. AS OF DECEMBER 28, 2004, THE PRINCE GEORGE'S COUNTY FIRE INVESTIGATORS HAVE NOT MADE ANY ARRESTS NOR HAVE THEY MADE ANY FINAL DETERMINATION PERTAINING TO THIS INCIDENT. THIS INVESTIGATION IS ONGOING. | 1000621 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
111 | 2004-12-04 | KS | maintenance | UNKNOWN (SEDGWICK COUNTY) | KANSAS GAS SERVICE | AN INVESTIGATION REVEALED NATURAL GAS WAS ESCAPING FROM A MAIN AND APPARENTLY MIGRATED TO A NEARBY STRUCTURE WHERE IGNITION OCCURRED. | 47000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
112 | 2004-12-10 | CA | sabotage | UNKNOWN (YOLO COUNTY) | PACIFIC GAS & ELECTRIC COMPANY | ON DECEMBER 10, 2004, A FOUR-INCH DIAMETER GAS DISTRIBUTION MAIN WAS STRUCK AND DAMAGED BY A THIRD PARTY EXCAVATOR, WHO WAS INSTALLING SANITARY SEWER MAIN, BY THE JACK AND BORE METHOD. THIS RESULTED IN A GAS LEAK. THE GAS MAIN IN QUESTION, WAS LOCATED APPROXIMATELY TWELVE FEET IN DEPTH, WHICH CONTRIBUTED TO THE EXTENSIVE AND COSTLY DAMAGE REPAIRS. LIQUEFIED NATURAL GAS (LNG) WAS USED TO SUPPORT LINE CAPACITY WHILE REPAIRS WERE IN PROGRESS. THE THIRD PARTY EXCAVATOR'S UNDERGROUND SERVICE ALERT (USA) TAG INDICATED EXCAVATION ONLY, WHICH DID NOT ACCURATELY DESCRIBE THE JACK AND BORE CONSTRUCTION METHOD BY WHICH THE SEWER MAIN WAS INSTALLED. DAYLIGHTING OF FACILITIES AT CROSSINGS WAS NOT PERFORMED BY THE THIRD PARTY. FURTHERMORE, THIRD PARTY CONSTRUCTION DRAWINGS APPEAR TO INDICATE INACCURATE DEPTHS OF PG&E GAS DISTRIBUTION MAINS AT THE FORCE MAIN CROSSINGS. INITALLY, PG&E ESTIMATED DAMAGES, INCLUDING REPAIR, LOSS OF GAS AND SUPPLEMENTAL LNG TO BE LESS THAN $50,000. ON THE AFTERNOON OF DECEMBER 12, 2004. PG&E DETERMINED THAT TOTAL COSTS WOULD EXCEED $50,000 AND THEREFORE, THE INCIDENT BECAME REPORTABLE. PG&E THEN PROMPTLY REPORT THE INCIDENT TO THE DOT AND CPUC AT THAT TIME. | 163100 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
113 | 2004-12-24 | AK | other | UNKNOWN (nan COUNTY) | ENSTAR NATURAL GAS COMPANY | ON FRIDAY EVENING, DECEMBER 24, 2004 AT APPROXIMATELY 9:37 PM AST, ENSTAR NATURAL GAS COMPANY WAS NOTIFIED OF A STRUCTURE FIRE AT LOT 25, BLOCK 2 TURNAGAIN VIEW SUBDIVISION (2710 CUTWATER CIRCLE) ANCHORAGE, ALASKA. AN ENSTAR SERVICEMAN WAS DISPATCHED TO THE SCENE. UPON ARRIVAL THE SERVICEMAN FOUND A RESIDENTIAL STRUCTURE ON FIRE. HEAT FROM THE FIRE MELTED THE POLYETHYLENE SERVICE LINE RISER AND GAS METER, CAUSING A RELEASE OF NATURAL GAS. THE SERVICE LINE WAS DUG UP AND CAPPED. THE FIRE WAS STARTED WHEN A PROPANE TURKEY COOKER BOILED COOKING OIL OVER ONTO A DECK. THE OIL IGNITED AND THE FIRE SPREAD TO THE STRUCTURE. NATURAL GAS FROM ENSTAR'S FACILITIES DID NOT CAUSE OR CONTRIBUTE TO THE FIRE. | 201010 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
114 | 2004-12-07 | MN | other | UNKNOWN (DOUGLAS COUNTY) | CENTERPOINT ENERGY | THE DAMAGE TO THE DISTRIBUTION SYSTEM THAT LEAD TO THE RUPTURE WAS NOT REPORTED TO CENTERPOINT ENERGY MINNESOTA GAS. THERE WERE EXCAVATORS WORKING FOR THE CITY OF ALEXANDRIA PERFORMING SEWER AND WATER CONSTRUCTION DURING THE DURING AND SUMMER OF 2004 NEAR THE GAS DISTRIBUTION SYSTEM. THERE WAS SEVERAL LINE LOCATING REQUESTS FOR THE AREA. ALL THE LINE LOCATING REQUESTS WERE PERFORMED ON TIME AND ACCURATELY. | 515000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
115 | 2004-12-24 | PA | other | UNKNOWN (CAMBRIA COUNTY) | DOMINION PEOPLES | ON DECEMBER 24, 2004 AT 4:20AM, DOMINION PEOPLES RECEIVED A REPORT FROM 911 THAT A VEHICLE HAD COLLIDED INTO A HOUSE AND CUSTOMER METER FACILITY LOCATED AT 106 FORREST HILLS DRIVE, JOHNSTOWN, ADAMS TOWNSHIP, CAMBRIA COUNTY, PA. DOMINION PEOPLES PERSONNEL ARRIVE AT THE SCENE, FOUND THE VEHICLE HAD HIT AND DAMAGED THE CUSTOMER METER SET, BREAKING OFF THE METER AND 1" RISER AND CAUSING A FIRE AT 106 FORREST HILLS DRIVE. LOCAL 911 RESPONDED AND EXTINGUISHED THE FIRE. DOMINION PEOPLES PERSONNEL RESPONDED AND SHUT OFF THE SERVICE LINE AT THE CURB. A PRELIMINARY DAMAGE ASSESSMENT WAS MADE ON DECEMBER 24, 2004 AND VERBAL NOTIFICATION WAS MADE AT THAT TIME TO THE NRC AND THE PA-PUC BY TELEPHONE WHEN IT WAS DETERMINED THAT THE ESTIMATED PROPERTY DAMAGE RELATED TO REPORTABLE INCIDENTS APPROACHED THE REPORTABLE LEVEL. NRC #745236 WAS ASSIGNED TO THIS EVENT AT THAT TIME. THE PA-PUC CONDUCTED AN ON-SITE INVESTIGATION OF THIS INCIDENT ON DECEMBER 28, 2004. | 70290 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
116 | 2004-12-20 | PA | natural disasters | UNKNOWN (WASHINGTON COUNTY) | COLUMBIA GAS OF PENNSYLVANIA INC | IN WASHINGTON COUNTY, FALLOWFIELD TOWNSHIP A 12-INCH LINE KNOWN AS D-7237 IN THE AREA OF FIFTH STREET AND KINDER AVE THERE WAS GROUND MOVEMENT, WHICH CAUSED A SEPARATION OF A COMPRESSION COUPLING ON A HILLSIDE. IT WAS A TWO WAY FEED AND COULD BE ISOLATED BY INSTALLING A BY-PASS. NO CUSTOMERS WERE AFFECTED. | 65000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
117 | 2004-12-17 | IL | other | UNKNOWN (COOK COUNTY) | NICOR GAS | AN UNKNOWN FLAMMABLE VAPOR INSIDE THE HOME CAUSED THE EXPLOSION. AS A RESULT OF THE IMPACT, THE NICOR GAS METERING FACILITIES, WHICH WERE LOCATED OUTDOORS, WERE DAMAGED THUS CAUSING A RELEASE OF NATURAL GAS WHICH WAS A SECONDARY FEED TO THE FIRE. NOTE: THIS EXPLOSION WAS ORIGINALLY REPORTED AS 20925 TORRENCE IN LYNNWOOD, IL. THE CORRECT ADDRESS IS 21060 TORRENCE, FORD HEIGHTS, IL. | 100900 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
118 | 2004-12-09 | VA | other | UNKNOWN (FAIRFAX COUNTY) | WASHINGTON GAS | THE CAUSE OF INCIDENT HAS BEEN DETERMINED TO BE ACCIDENTAL NATURE BY THE FAIRFAX COUNTY FIRE INVESTIGATIONS UNIT AND WAS CONTRIBUTED TO AN ELECTRICAL PROBLEM AT THE HOUSE PANEL. THE WASHINGTON GAS METER AND REGULATOR WERE DAMAGED DO TO HEAT EXPOSURE FROM THE FIRE. THE EFV FOR THIS SERVICE ACTIVATED AND NO DAMAGE WAS CAUSED BY THE RELEASE OF NATURAL GAS. | 405150 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
119 | 2004-11-14 | KS | other | UNKNOWN (nan COUNTY) | KANSAS GAS SERVICE | AN UNIDENTIFIED VEHICLE STRUCK THE METER SETTING DAMAGING THE METER SETTING AND CUSTOMER'S PIPING, THEN LEFT THE SCENE. APPARENTLY NATURAL GAS WAS IGNITED BY SOME UNDETERMINED SOURCE LOCATED INSIDE THE BUILDING. 7/27/2006 SUPPLEMENTAL REPORT CHANGED SECTION A 5 C - ADDED VALUES FOR COMPANY PROPERTY DAMAGE AND GAS LOSS ALONG WITH PRIVATE AND PUBLIC DAMAGE. BDK | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
120 | 2004-12-21 | PA | sabotage | UNKNOWN (JEFFERSON COUNTY) | NATIONAL FUEL GAS DISTRIBUTION CORPORATION | CONTRACTOR INSTALLING SEWER SYSTEM HIT AND SEVERED 3" PLASTIC 50 PSIG DISTRIBUTION MAIN WHICH NFG LOCATED WITHIN TOLERANCE. 609 CUSTOMERS LOST SERVICE AS A RESULT. | 75250 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
121 | 2005-01-07 | NH | sabotage | UNKNOWN (ROCKINGHAM COUNTY) | NORTHERN UTILITIES INC | WHILE GRINDING PAVEMENT/TRENCH FOR SEWER EXCAVATION, GRADING MACHINE HIT 6" PE IP GAS MAIN CAUSING IGNITION OF ESCAPING GAS AND ENVELOPING GRADING MACHINE. OPERATOR JUMPED TO ESCAPE INJURY. | 522400 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
122 | 2004-12-23 | CA | other | UNKNOWN (MONTEREY COUNTY) | PACIFIC GAS & ELECTRIC COMPANY | CAR STRUCK AN ELECTRIC POLE IN SEASIDE, CA @ 0853 CAUSING ELECTRIC OUTAGE. PG&E EMPLOYEES ATTEMPTED SWITCHING OPERATIONS AT THE SEASIDE SUBSTATION TO RESTORE POWER. A SWITCHING EQUIPMENT FAILURE CAUSED A GROUND FAULT TO APPLY ABNORMAL VOLTAGE TO THE GAS DISTRIBUTION SYSTEM, RESULTING IN GAS INCIDENTS AT TWO LOCATIONS THE RESIDENCE NEXT TO THE SUBSTATION (1940 SAN PABLO ST) AND A RUPTURE OF THE 2" 50 PSIG STEEL GAS MAIN A BLOCK AND A HALF AWAY (1717 HAVANA ST) THE ESCAPING GAS FROM THE GAS SERVICE AT 1940 SAN PABLO ST CONTRIBUTED TO THE SCOPE OF FIRE DAMAGE AT THAT LOCATION. THE 60 KV GROUND FAULT CAUSED THE INCIDENT AT THE SAN PABLO LOCATION. THE HAVANA STREET LOCATION OCCURRED DUE TO A CONTACT BETWEEN THE STEEL GAS MAIN AND A 3/4" COPPER WATER SERVICE. | 51000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
123 | 2004-12-08 | LA | sabotage | UNKNOWN (LAFOURCHE COUNTY) | SOUTH COAST GAS CO |  | 543 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
124 | 2004-12-17 | WA | sabotage | UNKNOWN (SPOKANE COUNTY) | AVISTA UTILITIES | ON DECEMBER 17TH 2004 AT APPROXIMATELY 3:35 PM PST, A RAILROAD CONTRACTOR DUG INTO AVISTA'S 8-INCH HIGH PRESSURE DISTRIBUTION FEEDER NEAR SULLIVAN ROAD AT THE UNION PACIFIC RAILROAD OVER CROSSING (RAILROAD TRACKS RUN UNDERNEATH), NORTH OF THE SPOKANE RIVER IN SPOKANE VALLEY, WA. THE GAS PIPELINE PARALLELS SULLIVAN RD, ON THE WEST SIDE OF THE STREET. THE INCIDENT WAS A SIGNIFICANT EVENT AND REQUIRED SOME INNOVATIVE PLANNING TO MAINTAIN BOTH RESIDENTIAL AND COMMERICAL CUSTOMERS (ONE BEING THE SPOKANE VALLEY MALL WHICH WAS FULL OF HOLIDAY SHOPPERS). THE LEAK WAS ISOLATED BETWEEN A VALVE AND AN 8-INCH STOPPER THAT WAS INSTALLED, TAPPED, AND PLUGGED. DOWNSTREAM CUSTOMERS WERE MAINTAINED BY BACK FEEDING DISTRIBUTION PRESSURE GAS INTO THE HIGH PRESSURE FEEDER. THE CONTRACTOR WAS DRIVING A ONE INCH THICK, 4 FT X 12 FT STEEL PLATE INTO THE GROUND WITH A TRACK HOE TO SEAL THE END OF A SHORING BOX, WHICH WAS LOCATED ALONGSIDE OUR GAS PIPELINE. THE CONTRACTOR HAD BEEN WORKING WITH AVISTA AND KNEW THAT THE PIPE WAS THERE. IN FACT, AN AVISTA INSPECTOR WAS ON SITE AT THE TIME OF THE INCIDENT. THE PLATE "TRAVELED" INTO THE PIPELINE AS IT WAS BEING DRIVEN INTO THE GROUND. THE PIPELINE HAD BEEN PREVIOUSLY EXPOSED THAT SAME DAY AND WAS BACKFILLED TO STABLIZE THE SHORING BOX. THE PLATE SHIFTED IN THE DIRECTION OF THE DISTRUBED SOIL. THE PIPELINE WAS CASED IN THIS LOCATION AND THE CORNER OF THE STEEL PLATE PIERCED THE CASING AND THE PIPELINE. OVERALL AVISTA'S RESPONSE TO THE EVENT WENT VERY WELL. THE REPAIR WAS PROBLEMATIC IN THAT THE LEAK WAS INSIDE A CASING AND IT TOOK EXTRA TIME TO EVACUATE THE GAS AIR MIXTURE FROM WITHIN THE CASING TO AFFECT A PERMANENT REPAIR. AN INNOVATIVE PLAN WAS DEVELOPED BETWEEN GAS ENGINEERING AND OPERATIONS TO MAINTAIN CUSTOMERS. WE WERE FORTUNATE THAT THIS OCCURRED ON A FRIDAY EVENING WHEN MUCH OF THE COMMERICAL LOAD HAD SHUT DOWN AND AT A TIME WHEN THE WEATHER WAS NOT EXTREMELY COLD. | 92173 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
125 | 2004-11-12 | MO | other | UNKNOWN (GREENE COUNTY) | SPRINGFIELD, MO MUNICIPAL GAS SYSTEM | CITY UTILITIES FILED A GAS INCIDENT REPORT WITH THE MISSOURI PUBLIC SERVICE COMMISION ON 12/08/04. SINCE THAT TIME, CITY UTILITIES RECEIVED NEW DAMAGE ESTIMATES FROM THE PROPERTY OWNER AT 1870 E PAGE. THE TOTAL ESTIMATED REPAIR COST IS $114,970.00. CITY UTILITIES OF SPRINGFIELD IS SUBMITTING THIS FEDERAL GAS INCIDENT REPORT TO REFLECT THIS NEWLY OBTAINED INFORMATION. FEDERAL GAS INCIDENT REPORT NUMBER IS 744101. ATTACHED IS A COPY OF THE PROPERTY OWNER DAMAGE ESTIMATE. | 119778 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
126 | 2004-12-31 | OH | other | UNKNOWN (CLARK COUNTY) | COLUMBIA GAS OF OHIO INC | THE CUSTOMER'S SERVICE LINE FAILED THE COH PRESSURE TEST, DROPPING FROM LINE PRESSURE TO ZERO IN APPROXIMATELY 3-4 SECONDS. COH EXCAVATED THE SERVICE LINE AND DISCOVERED LARGE ROCKS AND GRAVEL SURROUNDING IT IN THE TRENCH. CRACKS IN THE LINE WERE OBSERVED AT 2 LOCATIONS AND THESE WERE BELIEVED TO HAVE BEEN CAUSED BY ABRASION FROM THE ROCKY BACKFILL ABOVE AND BELOW. THE DAMAGED SECTIONS WERE REMOVED AND THE LINE PASSED PRESSURE TESTING FROM THAT POINT TO THE METER AND COMPANY CURB VALVE. NEIGHBORS AND FAMILY MEMBERS BOTH REPORTED TO INVESTIGATORS THAT THEY HAVE SMELLED GAS IN THE AREA PRIOR TO THE INCIDENT BUT DID NOT CALL THE GAS COMPANY. | 200000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
127 | 2005-01-01 | AZ | leaks and spills | UNKNOWN (MARICOPA COUNTY) | SOUTHWEST GAS CORPORATION | EXPLOSION AND FIRE AT COMMERICAL LAUNDRY COMPLEX LOCATED IN A STRIP MAILL AT 3918 N/W GRAND AVE. TWELVE APARTMENTS ON 39TH AVE/HAZLEWOOD AND SIX UNITS IN THE STRIP MALL WERE EVACUATED AFFECTING NINE PERSONS. THE CAUSE OF THE LEAK WAS DETERMINED TO BE DUE TO A CRACKED AND LEAKING ABS MAIN. ABS PIPE FAILED DUE TO A STRESS CONCENTRATION AT THE FLEXIBLE TO RIGID CONNECTION. LEAK DUE TO CIRCUMFERENTIAL CRACK, 2.5 INCHES IN LENGTH. THERE WERE NO INJURIES AS A RESULT OF THIS INCIDENT. | 200000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
128 | 2004-11-18 | WI | sabotage | UNKNOWN (ST CROIX COUNTY) | MIDWEST NATURAL GAS INC | EARTHMOVING EQUIPMENT OPERATED BY HOFFMAN CONSTRUCTION CO HIT AND SEVERED A 3 INCH PLASTIC MAIN (MEDIUM DENSITY PE) WITH AN MAOP OF 60 PSIG (OPERATING AT ABOUT 50 PSIG). THE GAS BEING RELEASED IGNITED WITHOUT DAMAGE TO THE EQUIPMENT OR OPERATOR (THE MACHINE HAD A FULL-ENCLOSURE CAB). THE FLOW OF GAS WAS STOPPED BY SHUTTING DOWN A REGULATOR STATION. APPROXIMATELY 32 MCF OF NATURAL GAS WAS LOST, ALONG WITH SERVICE TO 320 CUSTOMERS. THE FIRE DAMAGED CONCRETE BEAMS IN A NEARBY OVERPASS, AND THE ESTIMATE OF DAMAGE REPAIR IS $125,000. THIS HIT OCCURRED IN THE AREA OF AN ON-GOING CONSTRUCTION PROJECT. BASED ON MIDWEST NATURAL GAS INC'S AVAILABLE INFORMATION, HOFFMAN CONSTRUCTION WAS NOT EXCAVATING WITH A LEGITIMATE LOCATE REQUEST. | 125430 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
129 | 2005-01-06 | IN | natural disasters | UNKNOWN (HAMILTON COUNTY) | INDIANA GAS COMPANY INC | AFTER HEAVY RAINS, AN ICE LADEN TREE UPROOTED AND THE TREE ROOT BALL LIFTED METER SET BREAKING THE INLET TO THE METER BAR AND CAUSING A LEAK AT THE INLET TO THE RISER VALVE. ESCAPING GAS IGNITED CAUSING DAMAGE TO RESIDENTIAL STRUCTURE. IGNITION SOURCE UNKNOWN. | 700000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
130 | 2005-01-19 | NE | other | UNKNOWN (DOUGLAS COUNTY) | METROPOLITAN UTILITIES DISTRICT | THE HOUSE FIRE WAS STARTED FROM FUMES FROM THE FINISH PAINTERS WHOSE 5 GAL BUCKET OF LACQUER WAS IGNITED BY A HALOGEN LAMP. THE STRUCTURE CAUGHT FIRE AND THE HOUSE WAS ENGULFED BY FIRE. BETWEEN THE COLLAPSE OF THE STRUCTURE AND FIRE THE GAS SERVICE RISER/METER SET WAS DAMAGE AND THE RELEASE AND IGNITION OF GAS OCCURRED. | 700000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
131 | 2005-01-14 | IL | other | UNKNOWN (COOK COUNTY) | NICOR GAS | A VEHICLE HIT THE GAS METER SET, CAUSING THE METER TO BE SHEARED OFF AT THE RISER THUS CAUSING A RELEASE OF NATURAL GAS. DRIVER OF THE VEHICLE LEFT THE SCENE PRIOR TO ARRIVAL OF EMERGENCY RESPONSE PERSONNEL. NO INJURIES REPORTED. | 21367 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
132 | 2004-12-23 | IN | natural disasters | UNKNOWN (MARION COUNTY) | CITIZENS GAS & COKE UTILITY | FROST AND THAW CYCLE IS BELIEVED TO BE MAJOR CONTRIBUTING FACTOR TO THE FAILURE OF STEEL-TO-PLASTIC COMPRESSION TRANSITION FITTING FOR 1/2" HIGH DENSITY PLASTIC SERVICE. THE DEEP FROST CAP ALLOWED GAS TO MIGRATE FROM THE FAILURE THROUGH THE CASING PIPE TO THE FOUNDATION OF THE BUILDING LOCATED AT 2430 FOLTZ STREET. AT APPROXIMATELY 11:30 PM ON THE EVENING OF DECEMBER 23, 2004 GAS IGNITED AND EXPLODED INSIDE THE HOME. THE POINT OF IGNITION HAS NOT BEEN DETERMINED. | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
133 | 2004-12-28 | MN | natural disasters | UNKNOWN (ANOKA COUNTY) | CENTERPOINT ENERGY RESOURCES CORP DBA CENTERPOINT ENERGY MINNESOTA GAS | ANALYSIS OF THE FAILED PIPING INDICATES A DRESSER STYLE 90 COUPLER WAS USED TO JOIN THE ONE INCH IPS, DRISCOPIPE M7000 PE 3408 SERVICE LINE. THE ONE INCH PE ON THE OUTLET SIDE OF THE DRESSER COUPLING WAS FOUND TO HAVE INSUFFICIENT PENETRATION TO PROVIDE AND ADEQUATE SEAL. CIRCUMFERENTIAL MARKINGS ON THE PIPE INDICATE IT MAY HAVE GRADUALLY BEEN PULLED OUT FROM THE COUPLING IN STAGES, SUCH AS FROM THERMAL CONTRACTION DUE TO FROST CYCLES. | 300000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
134 | 2005-01-14 | CA | sabotage | UNKNOWN (KERN COUNTY) | PACIFIC GAS & ELECTRIC COMPANY | CONTRACTOR WAS EXCAVATING 24 FOOT DEEP TRENCH TO INSTALL SEWER MAIN, AND HAD EXPOSED THE 4" PG&E PLASTIC GAS LINE, BUT DURING THE INSTALLATION OF A TRENCH SHORING BOX THE EXCAVATOR CAUSED A PORTION OF THE ASPHALT TO BREAK AND FALL INTO THE EXCAVATION. THAT ACTION DIRECTLY CAUSED THE GAS LINE TO BREAK. 820 CUSTOMERS WERE EFFECTED WHEN THE "SINGLE-FEED" LINE WAS SHUTDOWN TO CONTROL THE GAS FLOW. REPAIRS WERE MADE AND SERVICE RESTORATION BEGAN AT 2030 HOURS. SERVICE TO 740 CUSTOMERS WAS RESTORED BY 0030 HOURS ON 01/15/2005. THE REMAINING 80 CUSTOMERS WERE NOT PRESENT AND DOOR HANGERS LEFT ASKING THAT THEY CALL PG&E FOR SERVICE RESTORATION WHEN AVAILABLE. | 59700 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
135 | 2004-09-22 | MT | sabotage | UNKNOWN (nan COUNTY) | NORTHWESTERN ENERGY | A CONTRACTOR, FOR THE CITY, REPLACING WATER MAINS, HIT AN UN-MARKED STEEL SERVICE. LOCATES WERE CALLED INTO THE ONE CALL SYSTEM, AND OTHER MAINS AND SERVICES WERE MARKED. THE HIT SERVICE PULLED APART AT A MECHANICAL COUPLING. THE LEAKING GAS MIGRATED ALONG A NEAR BY SERVICE INTO THE HOUSE AT 25 BENNETT ST. THE HOUSE LATER EXPLODED WITH ONE OCCUPANT INSIDE. THE HOUSE NEVER CAUGHT FIRE, BUT THE LEAKING GAS WAS BURNING NEAR THE SEPARATED JOINT. | 120000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
136 | 2005-02-22 | TX | sabotage | UNKNOWN (TARRENT COUNTY) | COSERV GAS | 2" LP GAS MAIN WAS DAMAGED BY EXCAVATOR INSTALLING WATER LINES. LP GAS TANKS WERE SHUT OFF TO ELIMINATE THE ESCAPING GAS. RESULTS OF DAMAGE CAUSED AN OUTAGE OF 50 CUSTOMERS. REPAIRES WERE MADE AND SERVICE RESTORED. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
137 | 2005-01-25 | IL | other | UNKNOWN (COOK COUNTY) | NICOR GAS | THE METER SET (REGULATOR AND METER) MELTED AS A RESULT OF A HOUSE FIRE. CAUSE OF THE FIRE IS UNKNOWN. | 228737 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
138 | 2005-01-17 | TX | sabotage | UNKNOWN (HARRIS COUNTY) | CENTERPOINT ENERGY | THIRD PARTY DAMAGED A 2" I.P. STEEL MAIN WITH A BACKHOE AND THE ESCAPING GAS WAS IGNITED. * ADDRESS WAS CORRECTED FROM 2615 CASON ST. TO 2612 WERLEIN ST. | 51928 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
139 | 2004-05-18 | TX | other | UNKNOWN (GALVESTON COUNTY) | CENTERPOINT ENERGY | TREE LIMB FELL ON AND DAMAGED SERVICE REGULATOR WHILE THIRD PARTY WAS TRIMMING TREE. RESULTING IN LINE PRESSURE DOWNSTREAM. IGNITION OCCURRED INSIDE AND HOME OWNER WAS INJURED AND HOSPITALIZED. 4-25-05 ADDITIONAL RELEVANT INFORMATION - HOME OWNER PASSED AWAY DUE TO THE SEVERITY OF HER INJURIES. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
140 | 2005-02-02 | NJ | other | UNKNOWN (CAMDEN COUNTY) | SOUTH JERSEY GAS COMPANY | BASED ON THE CONCLUSION FOUND IN THE CAMDEN COUNTY FIRE MARSHALL REPORT (SEE ATTACHED) WE BELIEVE THE SHUT OFF VALVE WAS DEFECTIVE AND THAT THE MOST LIKELY IGNITION SOURCE COULD HAVE BEEN THE STANDING PILOT ON THE PORTABLE NATURAL GAS APPLIANCE WHICH WAS SITTING JUST INSIDE THE WALL WHERE THE GAS METER WAS LOCATED. | 216000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
141 | 2005-01-27 | NJ | natural disasters | UNKNOWN (SALEM COUNTY) | SOUTH JERSEY GAS COMPANY | AN UNDERWATER 6" PIPELINE CROSSING OF THE SALEM RIVER CONSTRUCTED IN 1955 FAILED IN SERVICE ON 1/27/05 DUE TO SCOURING OF PROTECTIVE COVER AND SUPPORT OF THE PIPELINE ACROSS THE CHANNEL BOTTOM. THIS LOCATION IS SUBJECT TO STRONG TIDAL CURRENTS RESULTING IN THE EROSION OF THE CONTINUOUS SUPPORT FOR THE PIPELINE. AN INTERNAL VIDEO CAMERA WAS INSERTED INTO THE PIPELINE UP TO THE LOCATION OF THE BREAK WHERE A KINK IN THE PIPE WAS OBSERVED AT THE POINT OF RUPTURE. NO ATTEMPT WAS MADE TO REPAIR OR REPLACE THE PIPE UNDER THE WATER. A REPLACEMENT PIPE CROSSING OF THE SALEM RIVER WAS CONSTRUTED AND ATTACHED TO A NEW NJDOT ROUTE 49 STATE HIGHWAY BRIDGE CROSSING OF THE SALEM RIVER. THE REPLACEMENT COST FOR THIS BRIDGE CROSSING IS REFLECTED IN THE OPERATOR DAMAGE SHOWN IN PART A5C. THE EXISTING UNDERWATER CROSSING WAS RETIRED AND ABANDONED IN PLACE. | 546097 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
142 | 2005-02-04 | IL | other | UNKNOWN (MCHENRY COUNTY) | NICOR GAS | HOUSE FIRE CAUSED THE METER SET (REGULATOR AND METER) TO MELT THUS CAUSING THE RELEASE OF GAS. | 156187 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
143 | 2005-01-30 | NJ | other | UNKNOWN (UNION COUNTY) | ELIZABETHTOWN GAS COMPANY | ON JANUARY 30, 2005 ELIZABETHTOWN GAS RESPONDED TO A CALL RECEIVED AT 3:39 AM FROM THE UNION TOWNSHIP POLICE DEPARTMENT. UPON ARRIVAL AT 3:48 AM COMPANY EMPLOYEES FOUND THE FIRE DEPARTMENT PUTTING OUT FIRES AT #744 AND #748 LEHIGH AVE, UNION NJ. COMPANY PERSONNEL PERFORMED LEAK INVESTIGATION AND TOOK PROTECTIVE ACTION AT SURROUNDING HOMES. A CRACKED 8 INCH 25 PSI CAST IRON MAIN WAS LOCATED IN THE VICINITY AND REPAIRED USING AN ENCIRCLEMENT SLEEVE. REPAIRS WERE COMPLETE MY 6:57 AM. TWO HOMES WERE DESTORYED AND 3 PEOPLE HOSPITALIZED. TWO SUSPECTED APPARENT CAUSES: F3 EXCAVATION, #9 THIRD PARTY, EVIDENCE OF PRIOR NEARBY EXCAVATION ACTIVITY WAS OBSERVED AND IS UNDER INVESTIGATION. OR F2 - NATURAL FORCES #3 EARTH MOVEMENT - CAST IRON MAIN WAS CRACKED CIRCUMFERENTIALLY WHICH COULD HAVE BEEN CAUSED BY EARTH MOVEMENT. FINAL SUBMITTAL NOTE: INVESTIGATION IS COMPLETE: CAUSE CANNOT BE DEFINITIVELY IDENTIFIED DUE TO REFUSED ACCESS TO THIRD PARTY RECORDS. | 705100 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
144 | 2005-02-08 | LA | sabotage | UNKNOWN (LAFOURCHE COUNTY) | SOUTH COAST GAS CO |  | 177 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
145 | 2005-02-18 | LA | sabotage | UNKNOWN (LAFOURCHE COUNTY) | SOUTH COAST GAS CO |  | 868 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
146 | 2005-02-07 | PA | sabotage | UNKNOWN (BUCKS COUNTY) | PEO ENERGY COMPANY | A CONSTRUCTION COMPANY WAS EXCAVATING WITH A TRACK HOE TO INSTALL A WATER LINE FOR THE LOCAL SEWER AND WATER AUTHORITY WHEN THEY CONTACTED THE 3/4" STEEL GAS SERVICE WHICH FED 52 FERRY ST. WHEN THE TRACK HOE CAME IN CONTACT WITH THE GAS SERVICE, THE SERVICE WAS PULLED OUT OF THE CURB VALVE, WHICH CREATED A RELEASE OF GAS. THE GAS SERVICE TO 52 FERRY STREET WAS MARKED CORRECTLY PER PA ONE CALL GUIDELINES. | 500000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
147 | 2005-02-08 | PA | maintenance | UNKNOWN (nan COUNTY) | PECO ENERGY COMPANY | A 6 INCH STEEL MAIN ON THE HULMEVILLE ROAD BRIDGE OVER THE PENNSYLVANIA TURNPIKE HAD A SECTION FAILURE. THE GAS MAIN INCIDENT CAUSED THE SHUTDOWN OF THE PENNSYLVANIA TURNPIKE AND EVACUATION OF AREA RESIDENTS. | 114500 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
148 | 2005-02-08 | MI | other | UNKNOWN (EATON COUNTY) | CONSUMERS ENERGY | ON FEBRUARY 8, 2005, A RESIDENT AT 3930 HARTFORD RD, LANSING, MICHIGAN, WAVERLY PARK APARTMENTS DROVE HIS VEHICLE INTO THE FRONT OF A 35 UNIT APARTMENT BUILDING SEVERING THE ABOVE GROUND SERVICE VALVE AND DIRECTING THE FLOW OF GAS INTO TO THE BUILDING. THIS BUILDING WAS CENTRALLY METERED APPROXIMATELY 500 FEET FROM THE DAMAGED BUILDING. THE SERVICE ENTRANCE LOCATION CONSISTED OF A SERVICE RISER, METER STAND, SERVICE VALVE AND REGULATOR. THE VEHICLE CONTACTED THE REGULATOR INSTALLATION SEVERING THE TOP OF THE SERVICE VALVE COMPLETELY SEPARATING IT FROM THE REMAINDER OF THE SERVICE REGULATOR INSTALLATION. THIS DAMAGE RESULTED IN GAS ENTERING THE BUILDING AT APPROXIMATELY 52 PSIG SUBSEQUENTLY CAUSING AN EXPLOSION AND FIRE COMPLETELY DESTROYING THE BUILDING. THE DRIVER OF THE VEHICLE WAS REMOVED FROM HIS VEHICLE PRIOR TO THE EXPLOSION AND SUBSEQUENT FIRE AND TRANSPORTED TO THE HOSPITAL WITH NON-LIFE THREATENING INJURIES. APPROXIMATELY 15 TO 20 MINUTES AFTER THE DAMAGE, THE EXPLOSION AND SUBSEQUENT FIRE OCCURRED. ONE OTHER MINOR INJURY OCCURRED WHEN A RESIDENT JUMPED FROM THE SECOND FLOOR AND SUSTAINED AN ARM INJURY. THE OFFICIAL RESULTS OF THE INVESTIGATION DETERMINED THAT CURT GUILES 26, EXPERIENCED A MEDICAL SEIZURE AND ESSENTIALLY HAD ONE FOOT ON THE GAS AND THE OTHER ON THE BREAK UNTIL THE SEIZURE ENDED. AT THAT TIME MR. GUILES LEFT THE PARKING LOT AND DROVE INTO THE METER INSTALLATION ON THE APARTMENT BUILDING CAUSING THE GAS LEAK AND SUBSEQUENT FIRE. DUE TO THE MEDICAL SITUATION THE LANSING PROSECUTOR STATED THAT THERE WAS NO BASIS FOR CRIMINAL PROSECUTION. | 2004415 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
149 | 2005-02-09 | IN | leaks and spills | UNKNOWN (nan COUNTY) | NORTHERN INDIANA PUBLIC SERVICE COMPANY | ON FEBRUARY 9, 2005 NIPSCO'S CENTRAL OPERATIONS RECEIVED A CALL FROM THE JASFER COUNTY SHERIFF'S DEPARTMENT REPORTING A HOUSE EXPLOSION AND FIRE AT THE ABOVE ADDRESS. UPON ARRIVAL OF NIPSCO PERSONNEL, IT WAS DISCOVERED THAT GAS WAS ESCAPING FORM AND UNDERGROUND VALVE LOCATED IN THE PUBLIC RIGHT-OF-WAY IN THE VICINITY OF THE INCIDENT. THE LOCAL FIRE DEPARTMENT AND POLICE WERE IN THE PROCESS OF EVACUATING RESIDENTS WITHIN A TWO-BLOCK RADIUS. THE GAS WAS SHUT OFF AT 13:39 (CST). THE FAILED VALVE WAS SUBSEQUENTLY REMOVED, AND SERVICE WAS RESTORED TO THE AREA. RESIDENTS THEN RETURNED TO THEIR HOMES. THERE WERE NO INJURIES REPORTED. | 150056 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
150 | 2005-02-24 | TN | technical failure | UNKNOWN (COFFEE COUNTY) | ELK RIVER PUBLIC UTILITY DISTRICT | EMPLOYEE WHILE IN THE PROCESS OF ABANDONING AN OLD 3/4" STEEL SERVICE WAS INVOLVED IN AN INCIDENT. AN IGNITION OCCURED IGNITING THE NATURAL GAS IN THE BELL HOLE. | 1037 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
151 | 2005-02-06 | CA | natural disasters | UNKNOWN (EL DORADO COUNTY) | AVISTA UTILITIES | AT APPROXIMATELY 09:30 A NATURAL GAS EXPLOSION OCCURRED AT THE ABOVE ADDRESS. THE LAKE VALLEY FIRE DEPARTMENT RESPONDED AND CONTACTED AVISTA UTILITIES AT 09:53. THE FIRE PERSONNEL SHUT OFF THE GAS AT THE SERVICE LOCKCOCK AT 10:30. AVISTA PERSONNEL ARRIVED BY 10:58 AND VERIFIED THAT THE GAS WAS SHUT OFF AND THEN HE SEALED THE LOCKCOCK. HE THEN CHECKED FOR ANY OTHER POSSIBLE LEAKS AND FOUND NONE. THE CAUSE, DETERMINED BY BOTH FIRE AND AVISTA UTILITIES PERSONNEL, WAS ICE AND SNOW BUILDUP ON THE METER SET ASSEMBLY CAUSING FAILURE OF THE METER SET PIPING BETWEEN THE SERVICE LOCKCOCK AND SERVICE REGULATOR. THE RESULTING LEAKING GAS MIGRATED UNDER THE UNOCCUPIED CABIN, IGNITED, AND EXPLODED. THE RESULTING DAMAGE WAS IN EXCESS OF $50,000. ONE INJURY WAS REPORTED BY THE MEDIA, BUT NOT TO AVISTA UTILITIES. A LOCAL NEWSPAPER ARTICLE NOTED THAT A VISITOR TO THE CAMPGROUND WAS THROWN AGAINST AN OUTSIDE WALL OF A CABIN SOME DISTANCE FROM THE ACTUAL DAMAGED CABIN, AND SENT TO HOSPITAL. AVISTA LOOKED INTO THIS AND FOUND THAT THE PERSON WAS RELEASED THE SAME DAY AND LEFT THE AREA. NO FURTHER INFORMATION ON THIS INDIVIDUAL IS AVAILABLE TO AVISTA AT THIS TIME. ON FEBRUARY 7, FURTHER INVESTIGATION BY BOTH FIRE AND AVISTA PERSONNEL DETERMINED THAT THE FORCED AIR FURNACE WAS THE CAUSE OF IGNITION. ALSO, DURING THE INVESTIGATION THE SERVICE PIPING WAS PRESSURE TESTED TO 90 PSIG AND FOUND TO HAVE NO LEAKS. BECAUSE THE SERVICE WAS NO LONGER NEEDED, IT WAS DISCONNECTED AT THE MAIN AND RETIRED. GAS ODORANT READS WERE TAKEN AT THE SITE AND FOUND WELL WITHIN APPROPRIATE LEVELS AT 0.04% AND 0.05% GAS IN AIR. RECORDS REQUESTED FROM THE MANUFACTURER OF THE METER SET ASSEMBLY PROVIDED AVISTA WITH DOCUMENTATION VERIFYING THE PRESSURE TEST OF THE ASSEMBLY. DAMAGE FROM THIS EXPLOSION WAS FOUND ONLY AT THIS ONE BUILDING. NO FIRE RESULTED FROM THE EXPLOSION. MEDIA, POLICE, FIRE AND AMBULANCE SERVICES RESPONDED TO THE INCIDENT. NO OTHER OUTAGES OCCURRED. | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
152 | 2005-02-02 | MA | natural disasters | UNKNOWN (SUFFOLK COUNTY) | BOSTON GAS COMPANY DBA KEYSPAN ENERGY DELIVERY NEW ENGLAND | COLD TEMPERATURE WITH FROST CAUSED A BREAK IN THE NATURAL GAS MAIN. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
153 | 2005-02-23 | IN | other | UNKNOWN (MARION COUNTY) | CITIZENS GAS & COKE UTILITY | ON FEBRUARY 23RD, 2005, AT APPROXIMATELY 1:56 PM, CITIZENS GAS & COKE UTILITY RECEIVED A CALL FROM WARREN TOWNSHIP FIRE DEPARTMENT INFORMING US OF A GAS METER THAT HAD BEEN STRUCK BY A VEHICLE AND RESULTED IN A FIRE. AT APPROXIMATELY 2:05 P.M., CITIZEN GAS PERSONNEL ARRIVED ON THE SCENE AND DETERMINED THAT THE METER RISER HAD BEEN SHEARED OFF AND THAT THE VEHICLE AND THE HOUSE LOCATED AT 9346 MERCURY DRIVE WERE ENGULFED IN A FIRE. A MAINTENANCE CREW WAS SENT TO THE SCENE AND ARRIVED AT APPROXIMATELY 2:20 P.M. THE SERVICE WAS CUT AND PLUG AND THE GAS WAS OFF AT APPROXIMATELY 3:05 P.M. THE FIRE COMPLETELY DESTROYED WHAT REMAINED OF THE HOME, ITS CONTENTS AND THE VEHICLE. | 250220 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
154 | 2005-02-27 | IL | other | UNKNOWN (COOK COUNTY) | NICOR GAS | METER SET LOCATED IN UTILITY/LAUDRY ROOM MELTED AS A RESULT OF THE INTENSE HEAT OF THE FIRE. CAUSE OF FIRE WAS DUE TO ELECTRICAL SHORT. | 100600 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
155 | 2005-02-23 | NJ | other | UNKNOWN (HUNTERDON COUNTY) | ELIZABETHTOWN GAS COMPANY | DISPATCH RECEIVED CALL FROM HUNTERDON COUNTY COMMUNICATIONS AT 17:23. RESPONDER ARRIVED AT 17:43. LAMBERTVILLE FIRE DEPT CLOSED CURB VALVE AT APPROXIMATELY 18:00. BASEMENT FIRE HAD BEEN EXTINGUISHED. METER WAS NOT IN PLACE. NOTE: FIRE INVESTIGATOR DID NOT INDICATE GAS INVOLVEMENT UNTIL MORNING OF 2/24/05. DOT WAS THEN NOTIFIED. CUSTOMER HAD OXYGEN TANK USED FOR TORCH IN JEWELRY BUSINESS INTERCONNECTED WITH NATURAL GAS HOUSE LINE. THERE ARE INDICATIONS THAT THE PRESSURIZED OXYGEN FLOWED BACK THROUGH HOUSE LINE INTO METER CREATING A CHEMICAL REACTION IN THE BODY OF THE METER, WHICH RUPTURED. THE RESULT WAS A RELEASE OF GAS THAT IGNITED FROM AN UNKNOWN SOURCE IN THE BASEMENT. INVESTIGATION OF CUSTOMER HOUSE LINE REVEALED THE INTERCONNECTION AND LACK OF BACKPRESSURE DEVISE TO PREVENT OXYGEN FROM FLOWING BACK. (NATIONAL FUEL GAS CODE 5.10 REQUIRES SUCH A BACK PRESSURE DEVISE) THE METER WAS COMPLETELY DESTROYED AND FOUND IN JAGGED PIECES UP TO TEN FEET AWAY WHICH IS INDICATIVE OF A RUPTURE. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
156 | 2005-03-03 | CT | other | UNKNOWN (nan COUNTY) | YANKEE GAS SERVICES COMPANY | A TRACTOR TRAILER HAD CRASHED INTO A BUILDING LOCATED AT 39-41 MAPLE AVE AND THERE WAS DAMAGE TO OUR FACILITIES. ON THURSDAY MARCH 3, 2005 AT 12:40, A YANKEE GAS DISPATCHER RECEIVED A CALL FROM THE ENFIELD FIRE DEPARTMENT A YANKEE GAS METER & SERVICE MECHANIC ARRIVED ON SITE AT 12:50 AND FOUND GAS BLOWING INSIDE THE TWO FAMILY STRUCTURE. A YANKEE GAS DISTRIBUTION CREW ARRIVED SHORTLY AFTER THE M&S MECHANIC. A DECISION WAS MADE TO WAIT FOR THE ELECTRIC COMPANY TO SHUT OFF THE POWER PRIOR TO LOCATING AND SHUTTING OFF A CURB VALVE OUTSIDE THE STRUCTURE. THE HOUSE PIPING, REGULATOR, AND TWO METERS LOCATED IN THE BASEMENT WERE DAMAGED IN THE ACCIDENT. NATURAL GAS ESCAPED INTO THE STRUCTURE FOR APPROXIMATELY AN HOUR BEFORE GAS WAS SHUT OFF. ALL PROPERTY DAMAGE, INCLUDING DAMAGE TO COMPANY FACILITIES, WAS CAUSED BY THE VEHICLE. TWO PEOPLE WERE IN THE HOUSE WHEN THE CRASH OCCURRED, BUT WERE NOT INJURED. THE DRIVER OF THE VEHICLE WAS OUTSIDE THE VEHICLE WHEN IT STRUCK THE HOUSE AND WAS NOT INJURED. THE HOUSE WAS A TOTAL LOSS WAS DEMOLISHED LATER THAT NIGHT. | 200449 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
157 | 2005-03-21 | NY | other | UNKNOWN (nan COUNTY) | CONSOLIDATED EDISON COMPANY OF NEW YORK INC | THIS IS THE FOLLOW-UP TO THE VERBAL REPORT OF AN INCIDENT ON MARCH 21, 2005 07:52 HOURS AT 938 EAST 163RD STREET IN BRONX, NEW YORK. COMPANY FORCES RESPONDED TO A REPORT (FROM THE NYPD) OF A POSSIBLE GAS EXPLOSION INSIDE A SUPERMARKET AND FOUND THE FDNY ON LOCATION. AT THEIR REQUEST, WE TURNED OFF THE GAS SERVICE AT THE CURB VALVE. WE ALSO LEARNED FROM THE FDNY THAT THE STOREOWNER OF THE ASSOCIATED DELI SUPERMARKET HAD SMELLED GAS WHEN OPENING THE STORE. WHEN THE LIGHT SWITCH WAS TURNED ON, AN EXPLOSION OCCURRED AND A FIRE ENSUED. THE FDNY EXTINGUISHED THE FIRE. A THOROUGH OUTSIDE LEAK INVESTIGATION WAS PERFORMED AND NO GAS READINGS WERE FOUND. WHILE INVESTIGATING INSIDE, WE FOUND WHAT APPEARED TO BE GAS PIPING PULLED AWAY FROM AN OLD SPACE HEATER. AN INTEGRITY TEST WAS PERFORMED WHICH WAS WITNESSED BY THE NY STATE PUBLIC SERVICE COMMISSION & FDNY ON THE OUTSIDE GAS SERVICE FROM THE HOS VALVE TO THE CURB VALVE, AND THE TEST PASSED. THE FIRE MARSHALL CONDUCTED AN INVESTIGATION, AND THE CAUSE OF THE EXPLOSION/FIRE WAS DETERMINED TO BE THE RESULT OF FAULTY WORKMANSHIP ON THE SPACE HEATER AND THE ASSOCIATED GAS PIPING BY THE STOREOWNER'S PLUMBER. THE STOREOWNER INDICATED THAT WORK HAD BEEN PERFORMED ON THE SPACE HEATER AND ASSOCIATED GAS PIPING AT LEAST 3 PREVIOUS TIMES IN THE VICINITY OF THE EXPLOSION/FIRE. THE GAS PIPING AND GAS METER WERE REMOVED BY CON EDISON AT THE REQUEST OF THE LAW DEPARTMENT, AND THE HOS VALVE & CURB VALVE WERE LEFT OFF, LOCKED, AND A WARNING TAG WAS ISSUED. THERE WERE 6 CIVILIANS (2 TAKEN TO JACOBI HOSPITAL FOR BURNS & 4 TREATED ON SITE) & 3 FIRE FIGHTERS INJURED (2 TAKEN TO JACOBI HOSPITAL, 1 TREATED ON SITE AND RELEASED). THERE IS MAJOR INSIDE/OUTSIDE PROPERTY DAMAGE ESTIMATED TO BE GREATER THAN $50,000. EMS, FDNY, NYPD, PSC, DEP HAZMAT, NYC DEPARTMENT OF BUILDINGS, CE LAW DEPARTMENT, CE PHOTOGRAPHER, CE ENVIRONMENTAL RESPONSE TEAM, CE GAS QUALITY ASSURANCE, AND NEWS MEDIA CHANNELS 2, 4, 7 & 12 WERE ALL ON LOCATION. THIS WAS A SERIOUS LEVEL INCIDENT. IT WAS RULED BY THE FDNY THAT FAULTY WORKMANSHIP ON THE SPACE HEATER AND THE ASSOCIATED CUSTOMER OWNED GAS PIPING BY THE STOREOWNER'S PLUMBER WAS THE CAUSE OF THE EXPLOSION/FIRE. THIS INCIDENT DID NOT MEET CRITERIA FOR NOTIFICATION AND WE ARE CANCELING THIS VERBAL NOTICATION. THEREFORE, NO FURTHER COMPANY ACTION IS REQUIRED. PLEASE NOTE: THE OPERATOR 5 DIGIT IDENTIFICATION PERTAINS TO OUR HEADQUARTERS LOCATED AT 4 IRVING PLACE, NEW YORK, NY 10003 ALTHOUGH THE ADMINSTRATIVE SITE WHERE THIS FORM WAS COMPLETED IS THE GAS EMERGENCY RESPONSE CENTER LOCATED AT 1615 BRONXDALE AVE, BLDG 21A, BRONX, NY 10462. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
158 | 2005-03-27 | IL | other | UNKNOWN (WILL COUNTY) | NICOR GAS | STRUCTURE FIRE AT A VACANT FARM HOUSE. PART OF THE WALL FELL ONTO THE METER SET, DAMAGING IT AND CAUSING A RELEASE OF NATURAL GAS. INCIDENT WAS ORIGINALLY REPORTED AT 17040 OAK AVENUE. ACTUAL ADDRESS IS 17024 OAK AVENUE. | 78520 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
159 | 2005-02-15 | LA | sabotage | UNKNOWN (TERREBONNE COUNTY) | SOUTH COAST GAS CO |  | 72 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
160 | 2005-03-23 | PA | other | UNKNOWN (MONROE COUNTY) | PPL GAS UTILITIES CORPORATION | A CAR LOST CONTROL ON BLUE VALLEY DRIVE (S R 512) AS ROAD CONDITIONS BEGAN TO DETERIORATE DURING A SNOWSTORM. THE VEHICLE SLID OFF THE ROAD AND RUPTURED A NATURAL GAS SERVICE. THE IMPACT RESULTED IN A FIRE THAT BURNED THE SIDE OF A HOUSE. | 104882 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
161 | 2005-04-01 | TX | sabotage | UNKNOWN (MEDINA COUNTY) | CITY OF LYTLE | IRBY CONTRACTOR FOR CITY PUBLIC SERVICE RUPTURE 3" DISTRIBUTION GAS MAIN THAT SERVICE THE CITY OF LYTLE. SYSTEM WAS SHUT DOWN FOR REMOVAL OF BACK BUCKET AND REPAIR OF MAIN. HAVING THE CITY OF LYTLE WITHOUT GAS SERVICE. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
162 | 2005-03-16 | PA | sabotage | UNKNOWN (ALLEGHENY COUNTY) | COLUMBIA GAS OF PENNSYLVANIA INC | CONTRACTOR INSTALLING CABLE IN ALLEGHENY COUNTY USING A DIRECTIONAL BORE MACHINE, HIT A 50 PSIG 2" PLASTIC NATURAL GAS MAIN CAUSING LEAKAGE. THE NATURAL GAS MIGRATED TO NEARBY RESIDENTS, 107 BERTLEY RIDGE DRIVE, WHICH IS APPROXIMATELY 50 FEET AWAY FROM THE DAMAGE LOCATION WHERE THE GAS APPARENTLY CONTACTED AN IGNITION SOURCE. SECTION 5 C (GAS LOSS) IS A PRELIMINARY ESTIMATE AND IS SUBJECT TO CHANGE. | 165440 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
163 | 2005-03-30 | LA | sabotage | UNKNOWN (ASSUMPTION COUNTY) | PIERRE PART NATURAL GAS COMPANY |  | 315 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
164 | 2005-04-12 | NC | other | UNKNOWN (GASTON COUNTY) | PUBLIC SERVICE OF NORTH CAROLINA INCORPORATED (DBA PSNC ENERGY) | VEHICLE WAS TRAVELING WEST ON WILKINSON BLVD. OCCUPANT LOST CONTROL OF VEHICLE STRIKING POWER POLE AND 1" RELIEF VALVE AT STATION #RS01118 AT THE INTERSECTION OF CHURCH AND WILKINSON BLVD. VEHICLE CAME TO REST ON TOP OF RELIEF VALVE WITH NOSE OF VEHICLE AGAINST BROKEN POWER POLE. INJURIES SUSTAINED IN VEHICLE ACCIDENT WERE NOT RELATED TO NATURAL GAS. WEATHER CONDITIONS - HEAVY TO MODERATE RAIN. INCIDENT REPORTED AT 21:30 ON 4/12/05 AND FIRST RESPONDER WAS ON THE SCENE AT 21:40. PSNC WAS WORKING THROUGH EMS AND OTHER UTILITIES TO DE-ENERGIZE POWER LINES TO EVALUATE AND MAKE SAFE THE DAMAGED PRESSURE LIMITING AND REGULATING FACILITY. | 13700 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
165 | 2005-03-23 | IL | maintenance | UNKNOWN (nan COUNTY) | THE PEOPLES GAS LIGHT AND COKE COMPANY | ON MARCH 23, 2005, SOMETIME BEFORE 7:04 PM, A FIRE OCCURRED AT A BOILER LOCATED IN THE BASEMENT OF 7117 S EUCLID STREET, CHICAGO. ILLINOIS, A 24-UNIT APARTMENT BUILDING. AT APPROXIMATELY 7:04 PM, THE FIRE DEPARTMENT (CFD) NOTIFIED PEOPLES GAS OF A FIRE/EXPLOSION AT THE BUILDING. PEOPLES GAS DISPATCHED A SERVICEPERSON TO THE SCENE, WHO ARRIVED AT 7:31 PM. HIS INVESTIGATION DETERMINED THAT A FIRE OCCURRED AND NOT AN EXPLOSION. THE CFD HAD SHUT THE NATURAL GAS SUPPLY VALVE TO THE BOILER PRIOR TO THE SERVICE PERSON'S ARRIVAL. NO COMPLAINTS OF GAS LEAKS WERE REPORTED PRIOR TO THE INCIDENT. A 1" CTS (1-1/8" OD) POLYETHYLENE (PE) SERVICE SUPPLIED THE BUILDING WITH PRESSURE, REDUCED BY A CONTROL/MONITOR REGULATOR SET FROM 22 PSI TO 6" WATER COLUMN IN A ROOM SEPARATE FROM THE BOILER ROOM. THE CONTROL AND MONITOR REGULATORS FAILED DUE TO BROKEN PUSHER POSTS INSIDE THE REGULATORS. | 250000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
166 | 2005-04-06 | MA | other | UNKNOWN (SUFFOLK COUNTY) | BOSTON GAS COMPANY DBA KEYSPAN ENERGY DELIVERY NEW ENGLAND |  | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
167 | 2005-04-15 | AZ | other | UNKNOWN (PIMA COUNTY) | SOUTHWEST GAS CORPORATION | A TWO VEHICLE CAR ACCIDENT RESULTED IN THE METER SET ASSEMBLY AT THIS ADDRESS BEING HIT. FACILITY DAMAGE WAS ISOLATED TO METER SET ASSEMBLY RESULTING IN AN OUTAGE OF ONE CUSTOMER. TWO FIREFIGHTERS REQUIRED HOSPITALIZATION AS A RESULT OF INHALATION OF BOTH GASOLINE FUMES AND NATURAL GAS. THE FIREFIGHTERS WERE RELEASED AFTER TREATMENT. | 440 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
168 | 2005-01-10 | MD | other | UNKNOWN (MONTGOMERY COUNTY) | WASHINGTON GAS LIGHT | MONTGOMERY COUNTY FIRE AND RESCUE RECEIVED AN ALARM FOR AN ELECTRIC CLOTHES DRYER ON FIRE AT 17610 LONGVIEW LANE IN THE OLNEY MARYLAND AREA. UPON THE FIRE DEPARTMENT'S ARRIVAL, THEY FOUND THE ENTIRE HOUSE ENGULFED, INCLUDING THE REAR BUILDING WALL ON THE EXTERIOR OF THE BUILDING. THE FIRE IN THE REAR CAME FROM THE INSIDE OF THE STRUCTURE TO THE OUTSIDE OF THE STRUCTURE ENGULFING THE GAS METER AND REGULATOR TO THE BUILDING. DURING THE FIRE, THE METER AND REGULATOR WERE COMPLETELY DESTROYED. UPON ARRIVAL OF WASHINGTION GAS, THE FIRE DEPARTMENT HAD SHUT OFF THE GAS AT THE METER RISER STOPCOCK. DURING THE REMAINDER OF THE EXTINGUISHMENT OPERATIONS, THE REAR WALL PARTIALLY COLLAPSED AND THE REMAINING FIRE DESTROYED THE METER AND REGULATOR COMPLETELY. THE GAS DID NOT CAUSE ANY DELAY IN EXTINGUISHMENT EFFORTS PER THE FIRE CHIEF IN CHARGE OF THE INCIDENT. WASHINGTON GAS WAS CALLED TO THE SCENE TO DO A PHYSICAL DISCONNECT TO THE SERVICE AT THE BUILDING. 10/24/2007 PER INVESTIGATOR OFFICER CAPT. SAM HSU, THE FIRE WAS RULED ACCIDENTAL IN ORIGIN. IT WAS CAUSED BY A FAILED/FAULTY ELECTRICAL CLOTHING DRYER. THE FIRE CONSUMED MULTIPLE UNITS CAUSING SIGNIFICANT DAMAGE. DAMAGES WERE ESTIMATED TO BE APPROXIMATELY $140,000.000 | 300000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
169 | 2005-03-29 | VA | sabotage | UNKNOWN (nan COUNTY) | WASHINGTON GAS | LINEAL INDUSTRIES CO WAS INSTALLING FIBER-OPTIC LINES USING A DIRECTIONAL DRILL MACHINE. WHILE ATTEMPTING TO PULL THE LINES THE DRILL HEAD DAMAGED A 4" PLASTIC MAIN. THE HOLE WAS 14' 10" LONG ON THE UNDERSIDE OF THE MAIN. THIS SYSTEM WAS A ONE WAY FEED AND HAD TO BE SHUT DOWN. THIS CAUSED AN 800 CUSTOMER OUTAGE FOR APPROX 24 HOURS. | 35543 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
170 | 2005-03-28 | MD | other | UNKNOWN (nan COUNTY) | WASHINGTON GAS | INCIDENT UPDATE: PER THE REPORT OF INVESTIGATION COMPLETED BY LT. DALE EDNOCK, IT WAS CONCLUDED THAT THE CAUSE OF THE EXPLOSION AND ENSUING HOUSE FIRE WAS A NATURAL GAS LEAK. ALTHOUGH THE CAUSE OF THE EXPLOSION/FIRE IS NATURAL GAS, THE EXACT CAUSE FOR THE LEAK WAS NOT DETERMINED. | 250000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
171 | 2005-04-16 | UT | natural disasters | UNKNOWN (IRON COUNTY) | QUESTAR GAS COMPANY | EXCESSIVE SNOW LOAD AGAINST THE METER CREATED A "GLACIER" EFFECT (I.E. WHERE THE SNOW MELTS AND FREEZES, MELTS AND FREEZES). DUE TO EXCESSIVE STRESS AGAINST THE SERVICE LINE RISER, THE THREADS, JUST BELOW THE SERVICE REGULATOR, CRACKED. THE LEAKING GAS MIGRATED INTO THE STRUCTURE AND WAS IGNITED. WHEN FIRE FIGHTERS ARRIVED, THEY APPLIED FOAM TO THE METER SET AND PUT OUT THE FIRE. THE FIRE FIGHTERS THEN FILLED THE STRUCTURE WITH FOAM THROUGH THE FIRE PLACE VENT AND THEN ENTERED TO ASSESS THE SITUATION INSIDE. WHILE THE FIRE FIGHTERS WERE INSIDE, THE CRAWL SPACE FILLED WITH GAS (OR WAS FILLED WITH GAS PRIOR TO ENTRY) AND THE GAS WAS IGNITED BY AN UNKNOWN IGNITION SOURCE AND EXPLODED. NO PERSONS, (PUBLIC, FIRE FIGHTERS, COMPANY EMPLOYEES) WERE INJURED IN THIS INCIDENT. THE GAS WAS THEN SHUT OFF AT THE SERVICE VALVE BELOW THE CRACKED THREADS. AT THIS TIME THE PROPERTY DAMAGE AND GAS LOSS IS A ROUGH ESTIMATE. PROPERTY LOSS IS ESTIMATED TO BE LESS THAN $20,000.00 BASED ON THE SIZE AND THE EXTENT OF THE DAMAGE TO THE STRUCTURE. | 21115 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
172 | 2005-04-15 | LA | other | UNKNOWN (nan COUNTY) | SOUTH COAST GAS CO |  | 238 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
173 | 2005-04-18 | IL | other | UNKNOWN (COOK COUNTY) | NICOR GAS | FIRE AT MULTIPLE STRUCTURES. METER SET RISER TO 5807 ROOSEVELT ROAD MELTED AS A RESULT OF THE STRUCTURE FIRE. | 51354 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
174 | 2005-04-18 | IL | other | UNKNOWN (OGLE COUNTY) | NICOR GAS | VEHICLE ACCIDENT BETWEEN SEMI AND FARM TRACTOR. SEMI LEFT THE ROAD AND STRUCK THE 1ST STAGE REGULATOR, SHEARING OFF A PIPE NIPPLE ON THE DOWNSTREAM SIDE OF THE REGULATOR. THE 2 REPORTED INJURIES WERE A RESULT OF THE VEHICLE ACCIDENT. | 150850 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
175 | 2005-04-09 | TX | other | UNKNOWN (ANGELINA COUNTY) | CENTERPOINT ENERGY | VEHICLE RAN INTO THE METER INSTALLATION, DAMAGED THE SERVICE REGULATOR, CAUSING THE PRESSURE TO INCREASE ON THE HOUSELINE. | 200200 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
176 | 2004-09-24 | TX | sabotage | UNKNOWN (DALLAS COUNTY) | ATMOS ENERGY CORPORATION LONE STAR DIVISION | A THIRD PARTY EXCAVATOR DRILLING TO INSTALL ELECTRIC POLES DRILLED INTO A POLY GAS MAIN. | 49000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
177 | 2005-03-11 | TX | other | UNKNOWN (DALLAS COUNTY) | ATMOS ENERGY CORP MID-TEX DIVISION | A VEHICLE RAN OFF THE ROAD, OVER THE RISER, AND INTO THE RESIDENCE. THE ESCAPING GAS IGNITED AND CAUGHT THE VEHICLE AND HOUSE ON FIRE. | 145000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
178 | 2005-04-12 | MI | other | UNKNOWN (INGHAM COUNTY) | CONSUMERS ENERGY COMPANY | THE FINAL INVESTIGATION DETERMINED THAT THE CAUSE OF THE INCIDENT WAS CARELESS SMOKING AROUND THE METER INSTALLATION. THE AREA SURROUNDING THE RISER LOCATION WAAS COVERED WITH DRY WOOD CHIPS AND IT APPEARS THAT SOMEONE THREW A LIT CIGARETTE BUTT ONTO THE WOOD CHIPS. THE WOOD CHIPS EVENTUALLY CAUGHT FIRE AND CAUSED DAMAGE TO THE PLAASTIC RISER PROTECTOR AND THE CARRIER PIPE INSIDE THE RISER ASSEMBLY RESULTING IN A RELEASE OF GAS TO THE ATMOSPHERE. THE ESCAPING GAS SUBSEQUENTLY CAUGHT FIRE AND CONTRIBUTED TO THE STRUCTURE FIRE. ON MAY 8, 2006, CONSUMERS ENERGY'S INVESTIGATION TEAM REVIEWED THE PHYSICAL EVIDENCE FROM THE FIRE WITH THE APARTMENT BUILDING OWNER'S INVESTIGATION TEAM AND TOGETHER THEY DETERMINED THAT THE ORIGINAL CAUSE OF THE INCIDENT WAS STATE CORRECTLY. THE RESULTS OF THIS INVESTIGATION ENDED ALL SUBSEQUENT INVESTIGATIONS AND THE ISSUE OF CAUSE HAS BEEN RESOLVED. | 302100 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
179 | 2005-04-24 | CT | other | UNKNOWN (HARTFORD COUNTY) | CONNECTICUT NATURAL GAS CORP | HOMEOWNER WAS PERFORMING MECHANICAL WORK ON OWNERS MOTORCYCLE. OWNER WAS IN THE BASEMENT COMPLETING THIS WORK. WHILE WORKING ON THE MOTORCYCLE THE MOTORCYLE TIPPED OVER SPILLING GASOLINE FROM ITS GAS TANK ONTO THE FLOOR OF THE BASEMENT. NEARBY WAS A KEROSENE HEATER WHICH WAS IN OPERATION AND IGNITED THE GASOLINE VAPORS WHICH THEN SPREAD TO THE MOTORCYCLE ITSELF AND THAN CAUGHT THE HOUSE STRUCTURE ON FIRE. APPROXIMATELY FIVE FEET AWAY ON THE BASEMENT WALL EXISTED 2 (250 AL) METERS. THE HEAT FROM THE FIRE MELTED THE FACE OF THE METERS, WHICH THEN RELEASED THE NATURAL GAS AND SUBSEQUENTLY IGNITED THE ESCAPING GAS. FIRE DEPARTMENT PERSONNEL WERE ABLE TO EXTINGUISH THE FLAMES NEAR THE GAS METERS AND STOP THE ESCAPING GAS BY TURNING OFF THE VALVES AT THE METER SET. THE STRUCTURE WAS CONSIDERED A TOTAL LOSS. | 250180 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
180 | 2005-05-25 | AK | other | UNKNOWN (nan COUNTY) | ENSTAR NATURAL GAS COMPANY | ENSTAR WAS NOTIFIED BY ANCHORAGE FIRE DEPARTMENT (AFD) OF A STRUCTURE FIRE AT 4521 PARSONS AVE, ANCHORAGE, AK AT 0507, ON 5/29/05. THE FIRE HAD BURNED THROUGHT ENSTAR'S HDPE RISER AND CAUSED A RELEASE OF NATURAL GAS. AFD CREWS PINCHED OFF THE RISER TO SHUT OFF THE FLOW OF NATURAL GAS. ENSTAR CREWS DUG UP THE RISER AND CAPPED IT OFF. NATURAL GAS IS NOT BELEIVED TO HAVE CAUSED OR CONTRIBUTED TO THE FIRE. | 101050 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
181 | 2005-06-01 | AK | other | UNKNOWN (ANCHORAGE COUNTY) | ENSTAR NATURAL GAS COMPANY | ENSTAR WAS NOTIFIED BY THE ANCHORAGE FIRE DEPARTMENT (AFD) OF A STRUCTURE FIRE AT 3324 AND 3230 ORION CIRCLE, ANCHORAGE, AK AT 0212, JUNE 1, 2005. ENSTAR CREWS RESPONDED TO FIND A 2-UNIT TOWNHOME FULLY ENGULFED IN FIRE. EACH UNIT WAS SERVED BY A SEPARATE NATURAL GAS SERVICE LINE AND METER. THE FIRE MELTED BOTH NATURAL GAS RISERS AND METERS. ENSTAR CREWS DUG UP BOTH NATURAL GAS SERVICE LINES AND PINCHED THEM OFF AND CAPPED THEM. NATURAL GAS DID NOT CAUSE OR CONTRIBUTE TO THE FIRE. | 352100 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
182 | 2005-04-28 | PA | sabotage | UNKNOWN (ALLEGHENY COUNTY) | DOMINION PEOPLES | ON APRIL 28, 2005, AT APPROXIMATELY 11:30 AM DOMINION PEOPLES RECEIVED A REPORT FROM 911 THAT A PIPELINE WAS HIT AND DAMAGED BY A CONTRACTOR BORING THE ROAD AT RT.8 AND SAXONBURG BOULEVARD, SHALER TOWNSHIP, ALLEGHENY COUNTY, PA. DOMINION PEOPLES PERSONNEL RESPONDED, ARRIVED AT THE SCENE AT 11:50 AM AND FOUND A 10" PIPELINE WAS DAMAGED AND LEAKING. THE PIPELINE WAS THEN SHUTDOWN AT THE MAINLINE VALVE. NOTIFICATION OF THE EVENT WAS MADE BY TELEPHONE TO THE PA-PUC. A PRELIMINARY DAMAGE ASSESSMENT WAS THEN CONDUCTED, WHEN IT WAS DETERMINED THAT THE ESTIMATED PROPERTY DAMAGE RELATED TO REPORTABLE INCIDENTS MAY REACH THE REPORTABLE LEVEL, VERBAL NOTIFICATION WAS MADE ON APRIL 28, 2005 AT APPROXIMATELY 1:20 PM TO THE NRC AND AGAIN TO THE PA-PUC BY TELEPHONE. NRC #757091 WAS ASSIGNED TO THIS EVENT AT THIS TIME. THE PA-PUC RESPONDED AND CONDUCTED AN ON-SITE INVESTIGATION OF THIS INCIDENT ON APRIL 28, 2005. A FOLLOW-UP REVIEW WITH THE PUC WAS ALSO CONDUCTED ON MAY 9, 2005. PRELIMINARY INVESTIGATIONS REVEALED THAT THE PIPELINE WAS MISMARKED BY APPROXIMATELY 6 FEET AND THE EXCAVATOR FAILED TO DIG TEST HOLES AS REQUIRED IN ORDER TO ACCURATELY DETERMINE THE DEPTH AND LOCATION OF THE PIPELINE. | 64891 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
183 | 2005-05-23 | CO | sabotage | UNKNOWN (DOUGLAS COUNTY) | PUBLIC SERVICE CO OF COLORADO | CONTRACTOR EXCAVATING IN AREA NOT LOCATED FOR PIPELINE. BACKHOE RUPTURED FOUR INCH PE GAS MAIN. BLOWING GAS IGNITED. FIRE DESTORYED BACKHOE. | 70000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
184 | 2005-05-18 | NJ | sabotage | UNKNOWN (BERGEN COUNTY) | PUBLIC SERVICE ELECTRIC AND GAS | ON WEDNESDAY, MAY 18, 2005, AN EXTERMINATOR FROM HORIZON TERMITE AND PEST CONTROL CORPORATION WAS DRILLING HOLES FOR HOME TERMITE TREATMENT AT 80 W PROSPECT STREET IN WALDWICK, NEW JERSEY AND DRILLED INTO A 1/2" PS, 60 PSIG GAS SERVICE. THE TECHNICIAN INSTRUCTED THE HOMEOWNER TO EVACUATE AND THEN CALLED 911. THE CALL WAS RECEIVED BY PSE&G'S CLIFTON DISPATCH AT 12:49, WAS IMMEDIATELY DISPATCHED, AND THE TECHNICIAN ARRIVED AT 1:11 PM WHERE THE POLICE AND FIRE WERE FOUND TO BE ON THE SCENE. THE EXPLOSION OCCURRED FOUR MINUTES LATER. A REVIEW OF THE RECORDS SHOWS THAT THE CONTRACTOR HAD NOT CALLED FOR A MARKOUT. | 800000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
185 | 2005-06-13 | AK | other | UNKNOWN (ANCHORAGE COUNTY) | ENSTAR NATURAL GAS COMPANY | ENSTAR WAS NOTIFIED BY ANCHORAGE FIRE DEPARTMENT OF A STRUCTURE FIRE AT 4141 E. 66TH AVE AT 0153 ON JUNE 13, 2005. A SERVICEMAN AND CREW WERE DISPATCHED. THE STRUCTURE FIRE CAUSED ENSTAR'S HDPE RISER AND METER SET ASSEMBLEY TO LEAK GAS AND IGNITE. THE SERVICE LINE WAS DUG UP AND PINCHED OFF TO STOP THE BLOWING GAS. GAS FROM ENSTAR'S FACILITIES DID NOT CAUSE OR CONTRIBUTE TO THE FIRE. | 201050 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
186 | 2005-06-06 | LA | sabotage | UNKNOWN (LAFOURCHE COUNTY) | SOUTH COAST GAS CO |  | 898 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
187 | 2005-06-01 | CA | natural disasters | UNKNOWN (ORANGE COUNTY) | SOUTHERN CALIFORNIA GAS COMPANY | ON JUNE 1, 2005 NUMEROUS GAS FACILITIES WERE DAMAGED WHEN A MAJOR LANDSLIDE OCCURRED IN THE CITY OF LAGUNA BEACH. A NUMBER OF HOMES SLIPPED OFF OF A HILLSIDE IN THE AREA OF FLAMINGO AND BLUEBIRD ROADS. GAS FACILITIES DAMAGED FROM THE LANDSLIDE INCLUDE 43 SERVICES, THREE 2" STEEL MAINS AND NUMEROUS METER SET ASSEMBLIES. IT WAS QUICKLY DETERMINED THAT THE AFFECTED SYSTEM WAS A ONE WAY FEED AREA AND THAT OUTAGES WOULD BE EXPERIENCED AS A RESULT OF EMERGENCY RESPONSE. A PLAN WAS DEVELOPED TO STOP THE GAS FLOW INTO THIS AREA FROM A SAFE LOCATION, RESULTING IN APPROXIMATELY 360 RESIDENCES BEING SHUT DOWN TEMPORARILY. SERVICE TO ALL HABITABLE HOMES HAS BEEN RESTORED. APPROXIMATELY 2 DOZEN HOMES WERE SEVERELY DAMAGED OR DESTORYED. THIS INCIDENT BECAME REPORTABLE TO THE DOT AND BASED UPON ESTIMATED DAMAGES TO GAS FACILITIES EXCEEDING $50,000. FOR ANY FURTHER QUESTIONS, CONTACT JEFF KOSKIE AT 213-244-3283. | 200000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
188 | 2005-06-05 | IL | natural disasters | UNKNOWN (MCHENRY COUNTY) | NICOR GAS | LIGHTNING STRUCK THE HOUSE ON LOT 427 (9100 DURHAM DRIVE). HOUSE FIRE MELTED THE METER SET AND RISER, THUSE CAUSING A RELEASE OF GAS. FIRE DAMAGE ALSO SUSTAINED BY LOTS 425 AND 427. GAS FACILITIES HAD NOT YET BEEN INSTALLED AT LOT 425 AND LOT 426. | 401100 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
189 | 2005-06-11 | CA | sabotage | UNKNOWN (SANTA BARBARA COUNTY) | SOUTHERN CALIFORNIA GAS COMPANY | ON JUNE 11, 2005 AN 8" HIGH PRESSURE DISTRIBUTION SERVICE WAS DAMAGED BY CUSTOMER, CELITE CORPORATION. EMPLOYEE OF CELITE CORPORATION WAS GRADING FIRE ROAD WHEN HE STRUCK AND PUNCTURED THE SERVICE FOR CELITE CORPORATION, RESULTING IN ONE OUTAGE. INVESTIGATION OF THE INCIDENT SHOWED THAT CELITE CORPORATION DID NOT HAVE A USA TICKET, BUT THAT LINE MARKERS INDENTIFIED PATH OF THE DAMAGED SERVICE. NO FIRE OR INJURIES RESULTED FROM THE ESCAPING GAS. REPAIRS AND RESTORES WERE COMPLETED ON JUNE 13TH. THIS INCIDENT BECAME REPORTABE TO THE CPUC AND DOT BASED UPON THE CUSTOMER'S ESTIMATE OF PRODUCT LOST AND LOSS OF PRODUCTION. THE CUSTOMER PROVIDED THIS ESTIMATE AT APPROXIMATELY 20:00. THIS FACILITY MAKES/PROCESSES DIATOMACEOUS EARTH, AND THE ESTIMATED LOSS TO THE CUSTOMER IS APPROXIMATELY $300,000. FOR ANY FURTHER QUESTIONS, CONTACT JEFF KOSKIE AT 213-244-3283. | 320000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
190 | 2005-06-20 | LA | sabotage | UNKNOWN (LAFOURCHE COUNTY) | SOUTH COAST GAS CO |  | 1170 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
191 | 2005-04-21 | TX | technical failure | UNKNOWN (HOUSTON COUNTY) | CENTERPOINT ENERGY | GULF SOUTH PIPELINE LOST GAS SUPPLY TO THE CITY OF CROCKETT. FAILURE WAS DUE TO A CONTROL VALVE BEING LEFT IN THE CLOSED POSITION. | 66970 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
192 | 2005-06-14 | CT | other | UNKNOWN (NEW HAVEN COUNTY) | YANKEE GAS SERVICES | THE ONGOING STRUCTURE FIRE AT 49 EAST STREET CAUSED THE OUTSIDE METERSET ASSEMBLY (METER & REGULATOR) TO MELT RESULTING IN THE RELEASE OF NATURAL GAS AT A PRESSURE OF APPROXIMATELY 24 PSI. THE GAS IGNITED AND CONTRIBUTED TO THE EXISTING STRUCTURE FIRE UNTIL THE GAS SERVICE WAS CUTOFF STOPPING THE FLOW OF GAS. THE 10 PEOPLE EVACUATED FROM THE 2 STRUCTURES WERE EVACUATED BY FIRE PERSONNEL PRIOR TO THE FAILURE OF THE METERSET ASSEMBLY AND THE IGNITED OF THE GAS RELEASED. AN APPROSIMATE TIME LINE OF THE EVENTS IS ATTACHED. | 230535 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
193 | 2005-05-27 | AZ | leaks and spills | UNKNOWN (PIMA COUNTY) | SOUTHWEST GAS | BRIEF DESCRIPTION AT 1552 HOURS ON MAY 27, 2005, SOUTHWEST GAS WAS NOTIFIED OF A FIRE AT 1841 SOUTH CAMPBELL AVENUE. UPON ARRIVAL AT 1614 HOURS, TWO APARTMENT UNITS WERE FOUND TO BE DAMAGED BY THE REPORTED FIRE. A LEAK INVESTIGATION WAS INITIATED AND THE PRESENCE OF GAS WAS DETECTED BELOW GROUND. GAS CONTROL OF THE MAIN AND SERVICES IN THE VICINITY OF THE FIRE WAS ACHIEVED AT 1822 HOURS BY DIGGING AND SQUEEZING, WHICH RESULTED IN AN OUTAGE OF 28 SERVICES. ONE PERSON REQUIRED INPATIENT HOSPITALIZATION. FURTHER INVESTIGATION DETERMINED THAT THE LEAK WAS ON A 2" POLYETHYLENE MAIN. THE LEAK WAS DUE TO ROCK IMPINGEMENT. THERE IS A POSSIBILITY THAT PREVIOUS THIRD PARTY EXCAVATION IN THE IMMEDIATE AREA WAS A CONTRIBUTING FACTOR TO THE INCIDENT. AN INVESTIGATION IS ONGOING. RESULTS OF AN ANALYSIS CONDUCTED ON THE POLYETHYLENE MAIN DETERMINED THE PROBABLE CAUSE OF THE CRACK IN THE PIPE WAS THE RESULT OF ROCK IMPINGEMENT. WHILE THIRD PARTY EXCAVATION WAS KNOW TO HAVE TAKEN PLACE IN THE VICINITY OF THE FAILED PIPE SECTION, FINDINGS WERE INCONCLUSIVE SO TO WHETHER THIS WORK CONTRIBUTED TO THE INCIDENT. | 225000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
194 | 2005-06-17 | MD | other | UNKNOWN (ANNE ARUNDEL COUNTY) | BALTIMORE GAS & ELECTRIC COMPANY | ANNE ARUNDEL COUNTY FIRE INVESTIGATION BUREAU (FIB) OFFICER DOUG WILSON REPORTS THAT AN OUTSIDE FIRE IMPINGED ON THE GAS METER AND REGULATOR INSTALLATION CAUSING DAMAGE TO THE REGULATOR BODY, RELEASE AND THEN IGNITION OF NATURAL GAS. JUVENILES WERE WITNESSED IN TEH REAR OF THE BUILDING BEFORE THE FIRE WAS DISCOVERED. OTHER WITNESS STATEMENTS COLLABORATED THE FIB FINDINGS THAT THERE WAS A TRASH FIRE IN THE REAR OF THE BUILDING IN THE ARE LOCATED BETWEEN THE GAS AND ELECTRIC METERING EQUIPMENT AND A REFRIGERATED COOL BOX. THE FIRE WAS ORIGINALLY CONFINED TO THAT TRASH; THE GAS EQUIPMENT WAS NOT INVOLVED UNTIL IT WAS DAMAGED BUY THE HEAT OF THE FIRE. | 500000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
195 | 2005-05-25 | MO | other | UNKNOWN (CLAY COUNTY) | MISSOURI GAS ENERGY | AN OUT OF CONTROL VEHICLE, WHICH APPEARED TO BE TRAVELING AT A HIGH RATE OF SPEED, WENT THROUGH TWO FENCES, TRAVERSED A DITCH AND IMPACTED A REGULATOR STATION. A FOUR (4) INCH ELBOW WAS BROKEN OFF BELOW GROUND ON THE OUTLET SIDE OF THE REGULATOR STATION. BOTH THE REGULATORS AND STATION PIPING WERE DEMOLISHED IN THE ACCIDENT. SERVICE TO 919 CUSTOMERS WAS INTERRUPTED UNTIL THE STATION COULD BE REBUILT AND THE LINES PUTGED OF ALL AIR. ALL CUSTOMERS WERE PUT BACK IN SERVICE. | 49969 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
196 | 2005-03-24 | MD | other | UNKNOWN (PRINCE GEORGE'S COUNTY) | WASHINGTON GAS | THE PRINCE GEORGES COUNTY FIRE DEPARTMENT'S INVESTIGATION IS UNDERWAY. THE METER WAS MISSING AT THE FIRE BOARDS ARRIVAL AS ADVISED. THE FIRE DEPARTMENT ALSO ADVISED THAT THEIR PERSONNEL TURNED THE GAS OFF AT THE HIGH PRESSURE STOPCOCK JUST INSIDE THE BUILDING WALL. NO EVIDENCE OF HEAT EFFECTS IN THE IMMEDIATE AREA OF THE METER BUILDUP. THE EQUIPMENT IN THE ARE OF WHERE THE METER SHOULD HAVE BEEN, REMAINED INTACT. THE METER HAS NOT BEEN LOCATED AT THIS TIME. UNUSUAL ADAPTATIONS WERE IN PLACE AT THE METER CONNECTION. FOUL PLAY IS UNDER CONSIDERATION. PER WASHINGTON GAS RECORDS THE METER WAS IN PLACE ON 3-21-05. THE INVESTIGATION CONTINUES. 10-24-2007 OUR CONTACT WITH THE PRINCE GEORGE'S COUNTY FIRE/EMS DEPARTMENT HAS REVEALED THAT THE INVESTIGATIVE OFFICER ASSIGNED THIS CASE HAS SINCE RETIRED. NO CAUSE HAS YET TO BE DETERMINED, THE CASE REMAINS IN A PENDING STATUS. FROM WHAT WE'RE TOLD IT WILL REMAIN IN THIS STATE INDEFINITELY. | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
197 | 2005-06-16 | CT | leaks and spills | UNKNOWN (NEW HAVEN COUNTY) | SOUTHERN CONNECTICUT GAS COMPANY | FROM F5-14 SHEAR FAILURE AT CONNECTION TO SERVICE TEE. THE INCIDENT OCCURRED WHEN A PLASTIC SERVICE FAILED AT THE CONNECTION TO A STEEL MAIN. THE PLASTIC PROTECTIVE SLEEVE APPARENTLY SLIPPED OUT OF POSITION DURING THE BACKFILLING OPERATION AND ALLOWED THE PLASTIC SERVICE PIPE TO FAIL IN SHEAR AT THE CONNECTION TO THE STEEL SERVICE TEE. THE GAS THEN MIGRATED INTO THE SANITARY SEWER SYSTEM AND INTO THE SINGLE FAMILY HOME AT 551 WOODIN ST. IT APPARENTLY LEAKED INTO THE WALLS AND WAS IGNITED BY THE OPERATION OF A LIGHT SWITCH. THERE WAS NO FIRE OR INJURIES, BUT THERE WAS APPROXIMATELY $75,000.00 OF DAMAGE TO THE HOUSE. | 75000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
198 | 2005-06-27 | TN | other | UNKNOWN (HAYWOOD COUNTY) | BROWNSVILLE UTILITIES DEPARTMENT | ON JUNE 27, 2005 A 1995 PONYIAC GRAN AM CARRYING DONNA MANN (APPROX. AGE 60), TAYLOR KILLEN (AGE 10), AND KATIE LADEWELL (AGE 11) WAS TRAVELING NORTH ON STATE ROUTE 76. THE VEHICLE VEERED OFF THE WEST SIDE OF THE ROAD AND TRAVELED 165' ON THE SHOULDER OF THE RAOD. THEN THE VEHICLE TRAVELED DOWN THE EMBARKMENT AND STRUCK A DISTRICT REGULATOR STATION (HWY 76@KOKO). AFTER IMPACT THE VEHICLE TRAVELED 30¿ AND HIT A TREE AND CAME TO REST. APPROXIMATELY 75 CUSTOMERS GAS SERVICES WERE DISRUPTED DUE TO THE CAR WRECK. WE CLOSED ALL VALVES NECESSARY AHEAD OF THE METER SETS BEFORE REPRESSURIZING THE SYSTEM. THE BROWNSVILLE UTILITY DEPARTMENT RESTORED SERVICE TO MOST OF THE CUSTOMERS THE NIGHT OF 6/27/05. CUSTOMERS THAT USED THE GAS FOR HEATING HAD THEIR SERVICED RESTORED LATER. THE MORNING OF 6/28/05 WE FOUND OUT THAT MRS DONNA MANN HAD BEEN HOSPITALIZED. WE THEN CONTACTED THE TENNESSEE REGULATORY AUTHORITY AND THE US DEPARTMENT OF TRANSPORTATION. MRS. DONNA MANN WAS RELEASED FROM THE HOSPITAL THE AFTERNOON OF 6/29/05. ALSO FIND ATTACHED PHOTO'S OF TH WRECK OF AND THE ACCIDENT REPORT FROM THE TENNESSEE HIGHWAY PATROL. | 14700 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
199 | 2005-06-27 | IN | sabotage | UNKNOWN (VANDERBURGH COUNTY) | SOUTHERN INDIANA GAS AND ELECTRIC COMPANY | EXCAVATOR WORKING ON ROADS PULLED A 1 1/4" STEEL SERVICE FROM A COMPRESSION COUPLING AT THE SERVICE TEE. GAS ESCAPING TO ATMOSPHERE WAS IGNITED BY AN UNDETERMINED IGNITION SOURCE. TWO INDIVIDUALS WERE BURNED. ONE OF THE INDIVIDUALS WAS ADMITTED TO THE HOSPITAL FOR TREATMENT OF HIS BURNS. EVANSVILLE FIRE DEPARTMENT EVACUATED A 2 BLOCK AREA AS A PRECAUTION. GAS WAS SHUT-OFF BY SQUEEZING THE PIPE IN AN AREA AWAY FROM THE LEAKAGE AND IGNITED GAS. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
200 | 2005-06-23 | OK | sabotage | UNKNOWN (HASKELL COUNTY) | OKLAHOMA NATURAL GAS COMPANY | EXCAVATOR DAMAGED ONG'S 4 INCH HIGH PRESSURE DISTRIBUTION LINE THAT SERVES THE TOWN OF STIGLER, OKLAHOMA. 1623 ACCOUNTS WERE LOST DUE TO THIS INCIDENT. | 82420 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
201 | 2005-06-28 | TN | sabotage | UNKNOWN (nan COUNTY) | MEMPHIS LIGHT GAS & WATER DIVISION | ON JUNE 28, 2005, STABILIZATION INC., WAS WORKING APPROXIMATELY 100' NORTH OF GEORGE R JAMES RD. ON REED HOOKER RD WHEN THEIR 55-250 PULVIMIXER PUNCTURED A 8" PE GAS LINE. THE RELEASE OF GAS WAS FOLLOWED BY IGNITION RESULTING IN DAMAGE TO THE PULVIMIXER AND THEIR EMPLOYEE, MR. DERRICK MOORE, BEING TRANSPORTED TO THE HOSPITAL WHERE HE WAS TREATED AND RELEASED APPROXIMATELY ONE AND ONE HALF HOURS AFTER BEING SEEN BY THE DOCTOR. | 104309 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
202 | 2005-06-28 | IL | technical failure | UNKNOWN (COOK COUNTY) | NICOR GAS | EMPLOYEE WAS CONDUCTING A SCHEDULED ROUTINE LEAK REPAIR. WHILE IN THE PROCESS OF REMOVING THE TAP CONNECTION FROM THE MAIN TO THE SERVICE LINE, AN UNAPPROVED NON-INTRINSICALLY SAFE TOOL WAS USED TO REMOVE BOLTS FROM THE TEE CONNECTION, CAUSING IGNITION OF THE GAS. EMPLOYEE WAS HOSPITALIZED WITH BURNS TO FOREARMS AND FACE. NOTE: PRESSURE AT TIME OF INCIDENT WAS APPROX. 7" W.C. (.25 PSIG). MAOP OF .3 PSIG. ONLINE ENTRY DOES NOT ALLOW .25 PSIG OR .3 PSIG AS VALID ENTRY. ONLY WHOLE INTEGERS ALLOWED, THEREFORE 1 PSIG WAS ENTERED TO SUBMIT REPORT. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
203 | 2005-06-17 | WV | other | UNKNOWN (MCDOWELL COUNTY) | WELCH GAS COOPERATIVE ASSOCIATION | STATEMENT BY RONNIE CLEMINS, OPERATIONS MANAGER OF WELCH GAS CO-OP, FIRE AT AMBULANCE AUTHORITY 6/17/05 - 1:10 PM WELCH CITY DISPATCHER CALLS FOR GAS TRUCK #3 OR #4 TO GO TO THE AMBULANCE AUTHORITY AT MAITLAND AND CUT GAS OFF. THE BUILDING WAS ON FIRE AT ABOUT 1:12PM. GAS TRUCK #3 WAS IN HEMPHILL GETTING GAS READINGS. SO HE CALLED GAS TRUCK #4 TO RESPOND TO THE SCENE; HE WAS CLOSER. IN THE MEANTIME, GAS TRUCKS #2 AND #6 WERE AT THE BANTAM MARKET WHICH IS ABOUT 200 FEET AWAY FROM THE SCENE. GAS TRUCK #6 WENT BEHIND THE BUILDING TO CUT GASS OFF AT THE METER. HE DID NOT KNOW THE GAS LINE WAS ON FIRE AT THE CORNER OF THE BUILDING. THE FLAMES WERE TO HOT FOR HIM TO CUT THE METER OFF SO HE WENT BACK AROUND TO THE FRONT OF THE BUILDING. BOBBY BOWMAN, WELCH CHIEF OF POLICE SHOWED UP STOPPING ALL TRAFFIC. THEN THE FIRE DEPARTMENT CAME AND STARTED SPRAYING WATER ON THE BUILDING. GAS TRUCK #4 ARRIVES ON THE SCENE. HE SEES THAT SPRAYING WATER DOESN'T HELP SO HE REALIZES THE GAS LINE IS ON FIRE. HE THEN PUTS A SQUEEZE OFF ON THE 3/4" GAS LINE TO SHUT IT OFF. HE ESTIMATES THE GAS HAD BEEN BLOWINGFOR AN ESTIMATED 7-10 MINUTES. GAS TRUCK #3 ARRIVES ON THE SCENE AND TALKS TO BOBBY BOWMAN AND GAS TRUCK #4 ABOUT THE NATURE OF THE FIRE. WHILE STANDING THERE WE SEE MR. THOMAS, WORKER FOR GLEM CORPORATION CARRYING A PROPANE TANK AND TORCH AROUND BEHIND THE BUILDING AND LATER HE PUT IT IN HIS OWN TRUCK. I ASKED WHAT HAPPENED. HE SAID HE JUST GOT BACK FROM LUNCH AND FIRED HIS TORCH UP AND THAT'S ALL HE KNOWS. HE SAID THERE WAS A GAS LEAK OR SOMETHING. I TOLD HIM THERE WAS NO GAS LEAK THAT HE LAID HIS TORCH ON THE GAS LINE. HE REPLIED, "I DON'T KNOW WHAT HAPPENED." THE OWNER OF THE NEW BUILDING THAT WAS UNDER CONSTRUCTION HAD MADE A REQUEST TO HAVE THE GAS LINE LOCATED AND MARKED SO HIS CONTRACTORS WOULD KNOW WHERE THE GAS LINE WAS AND COULD AVOID IT. THIS REQUEST WAS ANSWERED AND THE GAS LINE WAS UNCOVERED AND MAKED BY SIGNS READING "GAS LINE - DANGER". THE REQUEST TO LOCATE AND THE ACTUAL LOCATING AND MARKING OF GAS LINES IN THE STATE OF WEST VIRGINIA ARE MANDATED BY STATE LAW. THE LAWS WERE FOLLOWED BY BOTH THE PROPERTY OWNER AND THE GAS CO-OP. SEVERAL OTHER THINGS WERE SAID AND DONE TO MAKE ME BELIEVE THAT'S WHAT HAPPENED. HUMAN MISTAKE; IT HAPPENS TO EVERYONE SOMETIME. | 200000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
204 | 2005-06-06 | TX | sabotage | UNKNOWN (HARRIS COUNTY) | CENTERPOINT ENERGY | THIRD PARTY DAMAGED A 12" H.P. STEEL MAIN WITH A BORING TOOL WHILE INSTALLING A WATER MAIN. | 63232 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
205 | 2005-07-05 | NM | other | UNKNOWN (DONA ANA COUNTY) | PUBLIC SERVICE COMPANY OF NEW MEXICO | A MOTORIST LOST CONTROL OF THE VEHICLE THEY WERE DRIVING, WENT OFF THE ROADWAY AND ROLLED OVER STRIKING GAS METER SET WHICH RESULTED IN TEH DRIVER BEING HOSPITALIZED. SUPPLEMENTAL: NATURAL GAS WAS NOT THE CAUSE OF THE INJURY RESULTING IN HOSPITALIZATION. | 5400 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
206 | 2005-07-09 | IL | other | UNKNOWN (WILL COUNTY) | NICOR GAS | PEOPLE CUTTING DOWN A TREE DROPPED A LARGE BRANCH ON AN OVERHEAD POWER LINE. THE POWER LINE FELL TO THE GROUND AND ARCED ONTO AN UNDERGROUND STEEL MAIN LOCATED UNDER THE POWER LINE. NATURAL GAS IGNITED. | 40500 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
207 | 2005-07-10 | IL | other | UNKNOWN (WILL COUNTY) | NICOR GAS | MULCH FIRE DAMAGED THE REGULATOR AND METER CAUSING A RELEASE OF NATURAL GAS WHICH THEN FUELED THE ON-GOING FIRE. | 101000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
208 | 2005-07-02 | LA | sabotage | UNKNOWN (TERREBONNE COUNTY) | SOUTH COAST GAS CO |  | 1293 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
209 | 2005-07-11 | MD | sabotage | UNKNOWN (nan COUNTY) | BALTIMORE GAS AND ELECTRIC COMPANY | ON JULY 11, 2005 AT APPROXIMATELY 11:50 AM, A CONTRACTOR WORKING TO INSTALL A NEW 48 INCH SEWER LINE AT BELAIR RD. AND HAMILTON AVE. IN BALTIMORE CITY, STRUCK THE BGE 20" NATURAL GAS MAIN WITH A HIGHHOE TARMAC. THE STROKE PRODUCED A HOLE 10" BY 12" AND ALSO CAUSED MAIN TO SPLIT APPROXIMATELY 3 FT., RESULTING IN THE RELEASE OF NATURAL GAS. THE INCIDENT RESULTED IN THE EVACUATION OF 4 BUILDING SHUTTING DOWN BUSINESS FOR THE DAY. ALSO BELAIR RD. WAS SHUT DOWN FROM 11:50 AM UNTIL 5:00 AM THE NEXT DAY. | 175000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
210 | 2005-01-27 | AZ | leaks and spills | UNKNOWN (MARICOPA COUNTY) | SOUTHWEST GAS CORPORATION | PL# 2005-5601 ODOR COMPLAINT CALLED IN. CONSTRUCTION CREW RESPONDED, IDENTIFIED AND ISOLATED LEAK AREA AND SHUT DOWN A SEGMENT OF 4" MAIN. LEAK WAS DUE TO A CRACK ON 4" NORDSTROM LUBE VALVE. OUTAGE OF 11,017 CUSTOMERS CONTRIBUTED TO PROPERTY DAMAGE TOTAL. | 550000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
211 | 2005-07-21 | NJ | other | UNKNOWN (CUMBERLAND COUNTY) | SOUTH JERSEY GAS COMPANY | ON JANUARY 24, 1994, R&T CASTELLINI COMPANY, THE COMPANY'S QUALIFIED DISTRIBUTION CONTRACTOR FOR THE CUMBERLAND DIVISION, CONSTRUCTED A NEW 3/4" POLYETHYLENE RESIDENCIAL SERVICE LATERAL EXTENSION FOR A PROPERTY AT 708 SHAR LANE BOULEVARD, IN MILLVILLE, NEW JERSEY. A SERVICE LATERAL FOR THIS CORNER PROPERTY WAS INSTALLED FROM THE SIDE OF THE HOME FACING WHITALL AVENUE, AS THERE WAS NO EXISTING GAS MAIN ON SHAR LANE BOULEVARD. (A FORMER 2" BARE STEEL GAS DISTRIBUTION MAIN ALONG SHAR LAN BOULEVARD HAD BEEN PREVIOUSLY RETIRED AND ABANDONED FROM SERVICE IN 1975. THIS RETIREMENT WAS EFFECTED BY CUTTING AND CAPPING THE EXISTING 2" MAIN ON WHITALL AVENUE NEAR IT'S INTERSECTION WITH SHAR LANE BOULEVARD.) IN THE COURSE OF ATTEMPTING TO ENERGIZE THE CONNECTION OF THE NEW SERVICE LATERAL TO THE DISTRIBUTION MAIN ON WHITALL AVENUE TO PROVIDE SERVICE TO 708 SHAR LANE BOULEVARD, IT WAS DETERMINED THAT THE PROPOSED CONNECTION POINT ON THE DISTRIBUTION MAIN WAS NOT ALONG A SECTION OF ACTIVE MAIN, BUT RATHER WAS LOCATED ON THE PREVIOUSLY RETIRED ADJACENT SECTION WHICH EXISTED ALONG WHITALL AVENUE. THEREFORE THE 1994 INSTALLATION CREW INSERTED THE 3/4" POLYETHYLENE SERVICE INTO THE ABANDONED 2" BARE STEEL MAIN ALONG WHITALL AVENUE FOR A DISTANCE OF 48', WHICH REPRESENTED THE DEAD-END LOCATION OF THE EXISTING ACTIVE MAIN ON WHITALL AVENUE. AT THIS POINT THEY EXCAVATED AND RE-CONNECTED THE END OF THE INSERTED SERVICE LINE TO THE TERMINUS OF THE EXISTING MAIN. THIS SERVICE LINE INSERTION TECHNIQUE WHITHIN THE ABANDONED 2" DISTRIBUTION MAIN ON WHITALL AVENUE WAS RECORDED ON THE AS-BUILT SERVICE RECORD CARD DOCUMENT ASSOCIATED WITH THE SERVICE INSTALLATION FOR 708 SHAR LANE BOULEVARD. THIS SAME SERVICE LINE INSERTION WAS NOT RECORDED ON THE DISTRIBUTION MAIN RETIREMENT RECORD FROM 1975. IN 2005, TWO NEW REQUESTS FOR GAS SERVICE WERE RECEIVED FOR ADDITIONAL PROPERTIES ALONG SHARE LANE BOULEVARD WHICH NECESSITATED AS DISTRIBUTION MAIN EXTENSION FROM THE TERMINUS OF THE EXISTING MAIN ON WHITALL AVENUE TO SHAR LANE BOULEVARD, AND THENCE ALONG SHAR LANE BOULEVARD FOR A TOTAL DISTANCE OF APPROXIMATELY 307'. THE LAYOUT AND DESIGN OF THIS PROPOSED DISTRIBUTION MAIN EXTENSION WAS PERFORMED IN THE FIELD BY AN EXPERIENCED COMPANY CONSTRUCTION INSPECTOR, WHO ROUTINELY PERFORMES THIS TYPE OF WORK, ALONG WITH THE ASSOCIATED INSPECTION ACTIVITIES OF SUB-CONTRACTOR INSTALLATION CREWS TO ASSURE COMPLIANCE WITH COMPANY CONSTRUCTION STANDARDS. AS PART OF HIS PROPOSED DISTRIBUTION MAIN EXTENSION LAYOUT AND DESIGN DUTIES, THE INSPECTOR OBSERVED THE LOCATIONS OF THE EXISTING METERS SUPPLYING SERVICE TO THE TWO CORNER PROPERTIES KNOWN AS 708 AND 800 SHAR LANE BOULEVARD. THE INSPECTOR ALSO OBSERVED FIELD LOCATION MARKOUTS DEPICTING THE LOCATIONS OF THE EXISTING SUB-SURFACE GAS MAIN AND SERVICES, AND INCORPORATED THESE OBSERVATIONS INTO HIS PROPOSED MAIN EXTENTION LAYOUT DESIGN. THE INSPECTOR DID NOT CROSS-CHECK THE SERVICE RECORD CARDS ON FILE IN THE DIVISIONAL OFFICE DEPICTING THE AS-BUILT INSTALLATION DETAILS FOR EITHER OF THE CORNER PROPERTIES, INSTEAD RELYING ON HIS EXPERIENCE AND THE FIELD LOCATION MARKOUTS WHICH ACCURATELY DEPICTED THE UNDERGROUND LOCATIONS OF THE SUB-SURFACE GAS FACILITIES. ON JULY 21, 2005, UTILITY LINE SERVICE (ULS), THE COMPANY'S QUALIFIED DISTRIBUTION CONTRACTOR FOR THE CUMBERLAND DIVISION WAS COMPLETING THE CONSTRUCTION OF THE 2" POLYETHYLENE DISTRUBUTION MAIN EXTENSION ON SHAR LANE BOULEVARD AND WAS PREPARING TO MAKE A TIE-IN INTO THE 2" BARE STEEL MAIN ON WHITEALL AVENUE. THE ULS CREW EXCAVATED AND PREPARED THE 2" BARE STEEL MAIN FOR A WELDED TIE-IN AND WAS IN THE PROCESS OF WELDING ON A 2" MUELLER NO-BLOW TEE PIECE WHEN THE INSERTED PLYETHYLENE SERVICE LINE FAILED, AND GAS ESCAPED THROUGH AREAS OF CORROSION OF THE STEEL MAIN WHICH WAS ACTING AS A CASING FOR THE INSERTED SERVICE LINE. THE ESCAPING GAS IGNITED WITHIN THE TIE-IN EXCAVATION AREA, AND THE CONTRACTOR EMPLOYEE PERFORMING THE WELDING SUFFERED FIRST A ND SECOND DEGREE BURNS. A CREW MEMBER PROVIDING EVACUATION ASSISTANCE TO THE WELDER OUT OF THE EXCAVATION AREA SUFFERED FIRST DEGREE BURNS.SOUTH JERSEY GAS COMPANY WAS NOTIFIED IMMEDIATELY OF THE IGNITION AT 1100 HOURS AND ARRIVED ON SITE AT APPROXIMATELY 1100 HOURS. THE CONTROLLING VALVE WAS LOCATED AND SHUT DOWN AT 1135 HOURS TERMINATING GAS FLOW TO THE IGNITION SITE. LOCAL EMERGENCY MANAGEMENT PERSONNEL RESPONDED TO THE SCENE AND PROVIDED FIRE SUPRESSION, TRAFFIC CONTROL AND MEDICAL EVACUATION SERVICES FOR THE TWO INJURED CONTRACTOR EMPLOYEES. ONE EMPLOYEE WAS TREATED AND RELEASED. THE OTHER EMPLOYEE WAS ADMITTED AND RETAINED OVERNIGHT FOR OBSERVATION PURPOSES, AND WAS RELEASED THE NEXT MORNING. | 700 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
212 | 2005-07-19 | MN | sabotage | UNKNOWN (BETRAMI COUNTY) | AQUILA | CONTRACTOR WAS EXCAVATING FOR INSTALLATION OF A SEWER LINE. THE 6" GAS MAIN AND A TELEPHONE CONDUIT WERE IN THE EXCAVATION. IN THE PROCESS OF EXPOSING AND SUPPORTING THE TELEPHONE CONDUIT THE CONTRACTOR PUNCTURED THE GAS MAIN. THE LINE HAD BEEN ACCURATELY LOCATED AND MARKED WITH YELLOW PAINT. | 35400 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
213 | 2005-07-30 | WA | sabotage | UNKNOWN (PIERCE COUNTY) | PUGET SOUND ENERGY | PSE RESPONDED TO A REPORT FROM THE CITY OF PUYALLUP FIRE DEPARTMENT OF A DAMAGED GAS MAIN. THE CONTRACTOR HAD PUNCTURED A 6" PE GAS MAIN WHILE EXCAVATING IN A STATE HIGHWAY. CITY OF PUYALLUP POLICE AND FIRE DEPARTMENTS CLOSED THE HIGHWAY. PSE DETERMINED THE SITE WAS A 4-WAY FEED AND PROCEEDED TO CONTROL THE GLOW OF GAS BY SHUTTING DOWN 3 VALVES AND SQUEEZING THE MAIN. A LEAK CLAMP WAS INSTALLED FOR TEMPORARY REPAIR. PSE'S SERVICE PROVIDER IS SCHEDULE TO HAVE FINAL REPAIRS COMPLETED BY THE END OF AUGUST. NOVEMBER 8, 2005 THIS FINAL REPORT REFLECTS ACTUAL COSTS. NO FURTHER CHANGES. | 60191 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
214 | 2005-07-07 | TX | maintenance | UNKNOWN (GALVESTON COUNTY) | TEXAS GAS SERVICE COMPANY | THE REGULATORAND MONITOR PILOT LINES WERE FILLED WITH A FOREIGN LIQUID FROM THE GAS SUPPLY CAUSING THE REGULATOR AND MONITOR TO FAIL OPEN. THE 14" LINE EXPERIENCED A LEAK LOCATED AT A JOINT WELD FROM THE OVERPRESSURIZATION. TWO SECTIONS OF THE LINE, TOTALING 124 FT. WERE REPLACED. THE LINE PRESSURE WAS INCREASED AND LEAK SURVEYED INCREMENTALLY. THE REGULATOR BOOTS WERE REPLACED AND THE REGULATOR AND MONITORS WERE CLEANED AND INSPECTED. | 128585 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
215 | 2005-07-26 | TX | other | UNKNOWN (YOUNG COUNTY) | TEXAS GAS SERVICE | A FREIGHTLINER WAS PARKED ON THE SIDE OF THE ROADWAY IN THE 1300 BLK OF HWY 16 SOUTH ON TOP OF A HILL. THE UNATTENDED VEHICLE ROLLED SOUTH DOWN A HILL STRIKING A GAS RISER AND AN ELECTRICAL POLE. THE ESCAPING GAS IGNITED AND ENGULFED THE CAB OF THE TRUCK AND A PORTION OF THE TRAILER. | 108044 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
216 | 2005-07-22 | LA | sabotage | UNKNOWN (ASSUMPTION COUNTY) | PIERRE PART NATURAL GAS CO. |  | 124 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
217 | 2005-09-01 | AK | other | UNKNOWN (nan COUNTY) | ENSTAR NATURAL GAS COMPANY | ANCHORAGE FIRE DEPARTMENT CALLED ENSTAR NATURAL GAS TO REPORT A STRUCTURE FIRE AT 2621 LYVONA LANE, ANCHORAGE AK, AT 0054 ON 9/1/05. THE STRUCTURE FIRE CAUSED THE GAS METER, REGULATOR AND HDPE RISER TO MELT, CAUSING A RELEASE OF NATURAL GAS. ENSTAR RESPONDED BY SENDING A SERVICE TECH, DUTY SUPERVISOR AND DISTRIBUTION CREW TO EXCAVATE AND PINCH OFF THE 1/2" CTS HDPE SRVICE LINE. THE LINE WAS PINCHED OFF AT 0305. THE FIRE STARTED IN A WOOD BURNING FIREPLACE. THE STRUCTURE SUFFERED EXTENSIVE DAMAGE. NATURAL GAS DID NOT CAUSE OR CONTRIBUTE TO THE FIRE. | 201050 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
218 | 2005-08-03 | IL | other | UNKNOWN (JO DAVIES COUNTY) | NICOR GAS | STRUCTURE FIRE AT THIS ADDRESS. METER SET WAS OFF AND LOCKED PRIOR TO STRUCTURE FIRE. RISER, REGULATOR AND METER WERE DAMAGED AS A RESULT OF THE FIRE, THUS CAUSING A RELEASE OF NATURAL GAS. | 51000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
219 | 2005-08-10 | IL | other | UNKNOWN (HENDERSON COUNTY) | NICOR GAS | STRUCTURE FIRE ORIGINATED AT NEIGHBORING HOUSE AND SPREAD TO THIS (WS 1ST 3S CLAY)ADDRESS. THE METER SET WAS DAMAGED AS A RESULT OF THE INTENSE HEAT AND FLAMES THUS CAUSING A RELEASE OF NATURAL GAS. | 51000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
220 | 2005-08-25 | CO | sabotage | UNKNOWN (JEFFERSON COUNTY) | COLORADO NATURAL GAS INC. | HOMEOWNDER BEGAN INSTALLING A RETAINING WALL THE PRIOR DAY OF THE EXPLOSION, 8-24-05 AT 13:00. HOMEOWNDER AND FRIEND WERE USING 1/2 INCH DIAMETER BY 3 FEET LONG REBAR TO ANCOR WALL TO GROUND. THE WALL ULTIMATELY CONSISTED OF 4 TIERS OF RAIL ROAD TIES. THE GROUND LEVEL OR 1ST TIER REBAR ANCOR PIERCED THE 3/4 INCH IPS NATURAL GAS SERVICE LINE APPROXIMATELY 8 FEET FROM THE FOUNDATION WALL. HOMEOWNDER STATED IN THE PRESENCE OF MYSELF, SEVERAL COLORADO NATURAL GAS EMPLOYEES AND THE JEFFERSON COUNTY SHERRIF REPRESENTATIVE THAT HE DID NOT CALL IN FOR A UTILITY LOCATE AND THAT HE ASSUMED THAT THE LINE ANGLED TOWARD HIS GAS METER ADJACENT TO THE FOUNDATION WALL AND DID NOT REMEMBER THAT THE LINE TOOK 90 DEGREE ANGLES. THE HOME OWNDER WAS PRESENT WHEN THE LINE WAS REROUTED DUE TO HOME EXPANSION IN 2004. HOMEOWNER ALSO STATED THAT HE THOUGHT HE SMELLED NATURAL GAS ON THE EVENING OF 8-24 BUT HE AND FRIEND DECIDED THAT IT WAS THE CRESOTE IN THE NEWLY SAWN RAILROAD TIES AND NOT THE SMELL OF NATURAL GAS. AT APPROXIMATELY 1:50PM MDST THE HOME EXPLODED FROM WHAT APPEARS INITIALLY A BUILD UP OF GAS IN THE CRAWL SPACE OF THE NEW ADDITION. THE GAS MIGRATED TO AN IGNITION SOURCE, MOST LIKELY THE HOT WATER HEATER OR FURNACE AND EXPLODED. COLORADO NATURAL GAS EMPLOYEES REPONDED AT 2:11PM TO A ELK CREEK FIRE DEPARTMENT REQUEST. THE HOME WAS ON FIRE AT THE SOUTH END. THE END OPPOSITE OF THE NATURAL GAS METER AND SERVICE LINE. ELK CREED FIRE DEPARTMENT HAD THE FIRE EXTINGUISHED BY THE TIME COLORADO NATURAL GAS EMPLYEES ARRIVED AT 2:18PM. THE STRUCTURE WAS STILL UPRIGHT HOWEVER THE NEW ADDITION WAS SEPERATED FROM THE OLDER EXISTING HOME BY 2 FEET 4 INCHES. THE ENTIRE HOME WAS CONDEMNED BY THE JEFFERSON COUNTY BUILDING DEPARTMENT AND WILL HAVE TO BE DEMOLISHED. I HAVE SEVERAL PHOTOS OF THIS IF YOU WOULD LIKE COPIES, PLEASE LET ME KNOW. DAVE MOODY | 250180 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
221 | 2005-08-12 | WY | natural disasters | UNKNOWN (CAMPBELL COUNTY) | KINDER MORGAN RETAIL | THERE WERE ADDITIONAL COSTS THAT WERE NOT INCLUDED WITH THE FIRST REPORT WHICH WAS LABLED "ORIGINAL" AND "FINAL". SEE SECTION 5C. A TORNADO HIT THE TOWN OF WRIGHT WY. (SPECIFICALLY THE COTTONWOOD MOBILE HOME PARK OF 112 HOMES) CAUSING DAMAGE TO THE GAS DISTRIBUTION FACILITIES FROM UPROOTED MOBILE HOMES AND FLYING DEBRIS. DUE TO LEAKING GAS WITHIN THE AFFECTED MOBILE HOME COURT, TO PROTECT THE SAFETY OF EMERGENCY RESPONDERS AND CITIZENDS IN THE AREA OF DAMAGE THE GAS WAS SHUT OFF TO THE TOWN OF WRIGHT APPROXIMATELY 1 HOUR AND 20 MINUTES AFTER THE TORNADO HIT. THERE WAS NO IGNITION OF LEAKING NATURAL GAS. THE SHUT DOWN AFFECTED 498 CUSTOMERS/METERS. TWO DEATHS AND THIRTEEN INJURIES (INPATIENT HOSPITALIZATION) RESUTED FROM THE TORNADO. THE DEATHS AND INJURIES WERE NOT NATURAL GAS RELATED. AFTER ISOLATING THE DAMAGED SECTION OF THE DISTRIBUTION SYSTEM WHICH CONSISTED OF 112 CUSTOMERS/METERS, THE GAS WAS TURNED BACK ON TO THE REMAINDER OF THE TOWN THE DAY AFTER THE INCIDENT, AND SERVICE WAS RESTORED PER OUR EMERGENCY PLAN. AFTER CLEANUP OF DEBRIS, ETC. IN THE AREA OF DAMAGE, REPAIRS WERE MADE TO THE AFFECTED SECTION OF THE DISTRIBUTION SYSTEM AND IT WAS PRESSURE TESTED AT 60 PSIG. THERE WERE APPROXIMATELY 49 HOMES DEEMED "LIVABLE" THAT HAVE BEEN RECONNECTED TO GAS SERVICE. NOTE PART C - ORIGIN OF INCIDENT: ANODELESS SERVICE RISERS (ASTM D2513) BROKEN AT THREADS ABOVE GROUND AT STOP COCK - SOME DAMAGED/BENT OVER HAD TO BE REPLACED - NO BROKEN POLYETHELENE PLASTIC BELOW GROUND. NOMINAL PIPE SIZE = 3/4" ANODELESS RISERS & METER SET ASSEMBLY FITTINGS 3/4" & 1" STEEL BROKEN AT THREADED JOINTS. YEAR MANUFACTURED AND YEAR INSTALLED 1970'S DECADE. | 68659 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
222 | 2005-08-06 | CT | other | UNKNOWN (NEW HAVEN COUNTY) | YANKEE GAS SERVICES | THE ONGOING STRUCTURE FIRE AT 2104 NORTH BROAD STREET CAUSED THE 2 INCH OUTSIDE SERVICE RISER TO MELT RESULTING IN THE RELEASE OF NATURAL GAS AT A PRESSURE OF APPROXIMATELY 55 PSIG. THE GAS IGNITED AND CONTRIBUTED TO THE EXISTING STRUCTURE FIRE UNTIL THE GAS SERVICE WAS SHUT OFF STOPPING THE FLOW OF GAS. THIS SITE WAS AN ACTIVE CONSTRUCTION SITE. THERE WERE NOT PERSONNEL ONSITE AT THE TIME OF THE FIRE. AN APPROXIMATE TIMELINE OF EVENTS IS LISTED BELOW: 1. 03:48 YANKEE DISPATCH (YG) RECEIVED A CALL FROM THE MERIDEN FIRE DEPT REGARDING A STRUCTURE FIRE AT 2104 NORTH BROAD STREET 2. 03:52 YG DISPATCHED STRUCTURE FIRE CALL TO METER & SERVICE (M&S) MECHANIC 3. 04:28 YG M&S MECANIC ARRIVED ON SCENE AND CONTACTED ON CALL SUPERVISION 4. 04:30 YG DISTRIBUTION (DIST) ARRIVED ON SCENE 5. 04:45 YG DIST LOCATED CURB VALVE 6. 05:10 YG DIST SHUTOFF CURB VALVE 7. 05:10 - 05:35 YG DIST TOOK BARHOLE READINGS AND CREATED SURVEY 8. 05:15 YG SYSTEM ON CALL SUPERVISOR CONTACTED THE DPUC 9. 06:00 MERIDEN FIRE DEPT. RELEASED YG | 500435 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
223 | 2005-09-13 | NE | other | UNKNOWN (DOUGLAS COUNTY) | METROPOLITAN UTILITIES DISTRICT | METROPOLITAN UTILITIES DISTRICT ID# 12390 SUPPLEMENTAL REPORT REPORT FROM: MICHAEL G. CONRAD, CLAIMS ADJUSTER ADDRESS OF INCIDENT: 7003 N. 113TH PLZ., LOT 494, OMAHA NE 68142 DATE/TIME OF INCIDENT: SEPTEMBER 13, 2005, 2140 HOURS NRC REPORT#: 772398 OUR CLAIM#: 17416 NARRATIVE: ON SEPTEMBER 13, 2005 AT APPROXIMATELY 2208 HOURS METROPOLITAN UTILITIES DISTRICT (MUD) DISPATCH SUPERVISOR LINDA HERNANDEZ NOTIFIED ME THAT THERE WAS AN EXPLOSION AND WORKING FIRE AT 7003 N. 113TH PLZ., LOT 494. UPON ARRIVAL ON SEPTEMBER 13, 2005 AT ABOUT 2220 HOURS I OBSERVED THAT THE MOBILE HOME DWELLING APPEARD TO HAVE BEEN INVOLVED IN AN EXPLOSION AND THE REMAINING STRUCTURE INDICATED THAT NATURAL GAS WAS LIKELY INVOLVED. AT THIS TIME AN INVESTIGATION WAS CONDUCTED. IN MY INVESTIGATION IT WAS DISCOVERED THAT THE 5/8" COPPER SERVICE LINE THAT LIES BETWEEN THE GAS METER AND THE MOBILE HOME HAD BEEN CUT WITH A PIPE CUTTER AND INSERTED INTO A DRILLED HOLE IN THE REAR OF THE MOBILE HOME. THE DRILLED HOLE WENT THROUGH THE ENTIRE WIDTH OF THE MOBILE HOME WALL JUST ABOVE FLOOR LEVEL. THIS OBSERVATION WAS REPORTED TO THE NEBRASKA STATE FIRE MARSHAL'S OFFICE TO INVESTIGATOR JACK MALICKY. SHORTLY AFTER THE DISCOVERY I INTERVIEWED IRVINGTON FIRE CHIEF NOLAN PAULSEN WHO WAS THE FIRST RESPONDER ON THE SCENE. ACCORDING TO FIRE CHIEF NOLAN PAULSEN HE WAS INVESTIGATING A GAS LEAK AROUND THE AREA OF THIS MOBILE HOME. AT 2135 HOURS HE HAD A 911 OPERATOR CONTACT MUD DISPATCHERS AND REQUEST ASSISTANCE FROM MUD IN LOCATING AND ELIMINATING THIS LEAK. AT 2140 HOURS CHIEF PAULSEN NOTIFIED A 911 OPERATOR HE NEEDED FIRE AND RESCUE PERSONNEL BECAUSE THE MOBILE HOME HAD SUFFERED AN EXPLOSION AND WAS ENGULFED IN FLAMES. FROM THE INFORMATION GATHERED AT THE SCENE AND STATEMENTS FROM THE POLICE AND FIRE DEPARTMENT PERSONNEL, IT IS APPARENT THAT THERE IS NO LIABILITY ON BEHALF OF MUD AND OUR INVESTIGATION IN REGARD TO THIS MATTER IS CLOSED. SEPTEMBER 27, 2005 SUPPLEMENTAL ADDITION: THE TWO OCCUPANTS, LINDA AND KEN TOPPING, HAVE BOTH DECEASED FROM THEIR INJURIES FROM THIS INCIDENT. THESE CIRCUMSTANCES DO NOT AFFECT OR CHANGE THE OUTCOME OF OUR INVESTIGATION. OUR INVESTIGATION AGAIN REVEALS THAT THERE IS NOT RESPONSIBILITY OR LIABILITY ON BEHALF OF THE METROPOLITAN UTITLITIES DISTRICT. | 70000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
224 | 2005-08-02 | TN | sabotage | UNKNOWN (RUTHERFORD COUNTY) | ATMOS ENERGY | ON AUGUST 2, 2005, ATMOS ENERGY CORPORTATION, IN MURFREESBORO, TENNESSEE EXPERIENCED A RUPTURE OF A TWO-INCH NATURAL GAS PIPELINE RESULTING IN IGNITION OF GAS HOSPITALIZATION OF ONE ATMOS EMPLOYEE. | 124317 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
225 | 2005-08-27 | MI | other | UNKNOWN (KENT COUNTY) | MICHIGAN CONSOLIDATED GAS COMPANY/DTE ENERGY | A CAR SPED THROUGH THE SOUTH PARKING LOT OF 2720 28TH STREET SE,, ACROSS LANDSCAPED AREA, AND STRUCK THE WEST SIDE OF THE BUILDING THE METER ASSEMBLY AT 2730 28TH STREET SE, COMING TO REST AGAINST THE WEST WALL OF THE BUILDING AND ATOP THE SERVICE LINE RISER AND SERVICE VALVE. THE METER ASSEMBLY WAS SHEARED AT THE 3" THREADS OF A 3" X 2" SWAGED NIPPLE CONNECTING A 3" THREADED COMPANION FLANGE AND THE 2" SERVICE REGULATOR. BLOWING GAS EXPLODED AND IGNITED APPROX. 23 MINUTES LATER, DESTROYING THE NORTH THIRD OF THE BUILDING AND BLOWING OUT WINDOWS AT THE BUILDINGS ON EITHER SIDE AND ACROSS TEH STREET. GAS WAS SHUT OFF BY DIGING AND PINCHING THE 3" PLASTIC SERVICE LINE APPROXIMATELY 100 FEEL FROM THE BUILDING. THE FIRE WAS ALMOST IMMEDIATELY CONTROLLED. THE RESPONDING EMPLOYEE WAS INJURED BY FLYING GLASS AND DEBRIS, AND WAS TREATED AT A HOSPITAL EMERGENCY ROOM AND RELEASED THE NEXT MORNING. THE SOURCE OF IGNITION REMAINS UNKNOWN. | 500000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
226 | 2005-08-26 | CA | sabotage | UNKNOWN (LOS ANGELES COUNTY) | SOUTHERN CALIFORNIA GAS COMPANY | CPUC?DOT REPORTABLE INCIDENT 58TH & WEST J14, LANCASTER NARRATIVE ON AUGUST 26, 2005, A 2" PLASTIC MEDIUM PRESSURE MAIN WAS PUNCTURED BY A CONTRACTOR USING A BACKHOE TO EXCAVATE FOR UTILITY CONDUITS. THERE WAS A USA REQUEST FOR THIS AREA, AND FACILITIES WERE PROPERLY MARKED. IN ADDITION TO STRIKING THE GAS MAIN, THE CONTRACTOR STRUCK THE UNDERGROUND ELECTIC FACILITIES, CAUSING AN ARC THAT IGNITED GAS ESCAPING FROM THE DAMAGED GAS MAIN. THE RESULTING FIRE DESTROYED ONE HOME THAT WAS PARTIALLY COMPLETED, AND DAMAGED TWO OTHERS. THE MAIN WAS REPAIRED, AND CUSTOMERS WERE PUT BACK INTO SERVICE. THE LIKELY CAUSE OF THIS INCIDENT WAS FAILURE OF THE CONTRACTOR TO HAND EXCAVATE IN THE VICINITY OF THE PIPELINE. THIS INCIDENT BECAME REPORTABLE TO THE CPUC AND DOT WHEN THE TOTAL VALUE OF DAMAGE AND REPAIRS WAS DETERMINED TO EXCEED $50,000. FOR ANY FURTHER QUESTIONS, CONTACT JEFF KOSKIE AT 213-244-3283 | 202000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
227 | 2005-09-15 | NC | other | UNKNOWN (NEW HANOVER COUNTY) | PIEDMONT NATURAL GAS (DBA NCNG) | A PERSON DRIVING A CAR STRUCK A METER SET AND CAUSED A GAS LEAK IN THE PIPING ON THE 60 PSIG SIDE OF THE SERVICE REGULATOR. THE GAS IGNITED AND A FIRE RESULTED. THE TWELVE PEOPLE IN THE BUILDING EVACUATED AFTER THE INCIDENT OCCURRED AND THERE WERE NOT REPORTED INJURIES. WE RECEIVED NOTIFICATION OF THE INCIDENT AT 12:02 PM AND HAD THE GAS TO THE BUILDING OFF AT 12:39PM. THE FULL EXTENT OF THE DAMAGE TO THE BUILDING IS UNKNOWN AT THIS TIME. | 505200 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
228 | 2005-08-16 | GA | other | UNKNOWN (WHITEFIELD COUNTY) | WATER LIGHT & SINKING FUN DBA DALTON UTILITIES | ON AUGUST 16, 2005, DALTON UTILITIES PERSONNEL WERE CALLED TO THE SCENE OF A FIRE AT THE COUNTRY INN'S & SUITES LOCATED AT 903 WEST BRIDGE RD. THE DALTON FIRE DEPARTMENT WAS IN TEH PROCESS OF EXTINGUISHING A FIRE NEAR THE GAS METER WHEN DALTON UTILITIES PERSONNEL ARRIVED. IT WAS DETERMINED THAT GAS FROM THE METER WET WAS FUELING THE FIRE, SO DALTON UTILITIES PERSONNEL LOCATED THE NEAREST SHUT OFF VALVE AND SHUT THE GAS OFF TO THE LOCATION. THE NEXT MORNING, AN INVESTIGATION INTO THE CAUSE OF THE FIRE WAS INITIATED. THE PRIMARY CAUSE APPEARED TO BE A GROUND FIRE WHICH IS BELIEVED TO HAVE STARTED AT A GROUND MOUNTED HALOGEN SPOTLIGHT THAT WAS PLUGGED INTO AN OUTLET LOCATED ON THE OUTSIDE OF THE BUILDING NEAR THE METER. IT APPEARS THE PINE BARK MULCH IGNITED AND HEATED THE PLASTIC SPRING CAP ON THE REGULATOR, CAUSING IT TO FAIL AND RELEASE LINE PRESSURE TO THE ATMOSPHERE, WHICH FURTHER FUELED THE FIRE AND HEATED THE ALUMINUM METER CASING CAUSING IT TO FAIL AS WELL. BASED ON THE INVESTIGATION CONDUCTED BY DALTON UTILITIES IN CONJUNCTION WITH THE DALTON FIRE DEPARTMENT, IT IS OUR DETERMINATION THAT THE GAS RELEASE ONLY FUELED THE EXISTING FIRE. | 135559 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
229 | 2005-08-22 | MO | sabotage | UNKNOWN (CASS COUNTY) | MISSOURI GAS ENERGY | CONTRACTOR, CALLED TEAM EXCAVATING, WHILE DIGGING WITH A TRACK HOE TO INSTALL SEWER MAIN LINE HIT A GAS SERVICE LINE THAT WAS 1 1/4 INCH PE MATERIAL. THE SERVICE WAS CUT IN TWO AND GAS WAS BLOWING. THE OPERATOR LEFT HIS TRACK HOE IN PLACE AND WHILE CALLING FOR ASSISTANCE THE ESCAPING GAS IGNITED. SEVERE DAMAGE TO TRACK HOE. | 150845 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
230 | 2005-09-20 | LA | sabotage | UNKNOWN (LAFOURCHE COUNTY) | SOUTH COAST GAS |  | 449 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
231 | 2005-09-19 | LA | sabotage | UNKNOWN (LAFOURCHE COUNTY) | SOUTH COAST GAS CO |  | 295 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
232 | 2005-09-22 | LA | sabotage | UNKNOWN (LAFOURCHE COUNTY) | SOUTH COAST GAS CO |  | 756 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
233 | 2005-09-07 | MA | other | UNKNOWN (nan COUNTY) | BOSTON GAS COMPANY DBA KEYSPAN ENERGY DELIVERY NEW ENGLAND | A KEYSPAN SERVICEMAN RESPONDING TO AN ODOR CALL FOUND FIRE DEPARTMENT AND POLICE DEPARTMENT PERSONNEL AT THE SCENE INVESTIGATING A SUSPECTED SUICIDE. THE POLICE REPORTEDLY FOUND GAS LEAKING FROM A DISCONNECTED CUSTOMER-OWNED PIPE. THE CASE OF DEATH IS BELIEVED TO BE ASPHYXIATION. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
234 | 2005-09-07 | IL | other | UNKNOWN (DUPAGE COUNTY) | NICOR GAS | STRUCTURE FIRE CAUSED WALL TO COLLAPSE ONTO METER SET THUS DAMAGING IT AND CAUSING A RELEASE OF GAS. HOUSE WAS UNDER RENOVATION. GAS HAD BEEN TURNED OFF AT THE METER SET PRIOR TO THE STRUCTURE FIRE. NOTE: THIS INCIDENT WAS REPORTED AS 29W560 POINT OAK DRIVE. THE ACTUAL ADDRESS IS 29W516 TOWNLINE ROAD. | 201000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
235 | 2005-09-16 | OK | other | UNKNOWN (OKLAHOMA COUNTY) | OKLAHOMA NATURAL GAS COMPANY | MOTORCYCLE DRIVER TRAVELING AT A HIGH RATE OF SPEED LOST CONTROL AND VEERED OFF THE ROAD INTO ONG'S DISTRICT REGULATOR STATION. THE DRIVER WAS DEAD AT THE SCENE. THE IMPACT BENT THE GUARD RAIL SURROUNDING THE DISTRICT REGULATOR STATION AND PUSHED THE GUARD RAIL INTO THE REGULATOR BREAKING OR PULLING OUT THE PIPE THREADS BELOW THE REGULATOR. THE FIRE DEPARTMENT ARRIVED ON THE SCENE BEFORE ONG'S PERSONNEL AND TURNED OFF THE INLET VALVE TO THE DISTRICT REGULATOR STATION TO ISOLATE THE BLOWING GAS. ELEVEN ACCOUNTS WERE LOST WHEN THE VALVE WAS TURNED OFF. THE REGULATOR ITSELF WAS NOT DAMAGED. PERMANENT REPAIRS WERE NADE TO THE DISTRICT REGULATOR STATION THE NEXT DAY. | 6711 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
236 | 2005-09-14 | CA | other | UNKNOWN (FRESNO COUNTY) | PACIFIC GAS & ELECTRIC COMPANY | THE FIRE IS SUSPECTED TO HAVE STARTED AT UNIT 122, AND DUE TO THE WOOD SIDING AND SHAKE ROOFS, THE FIRE CARRIED OVER TO UNIT 123. BOTH STRUCTURES WERE APPROXIMATELY 15 FEET APART WITH THE GAS METER SETS LOCATED ON ADJACENT WALLS. THE GAS METER SET LOCATED AT UNIT 122 WAS LOCATED WITHIN A SMALL FENCED OFF AREA THAT INCLUDED THE GAS AND ELECTRIC METERS, COMMUNICATIONS INTERFACE AND TRASH CONTAINERS. OUR INVESTIGATION DETERMINED THAT GAS DID NOT CONTRIBUTE TO THE STRUCTURE FIRE AND THE GAS METER SETS WERE DAMAGED (MELTED) BY THE FIRE FROM THE STRUCTURES. | 870000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
237 | 2005-09-15 | MT | sabotage | UNKNOWN (PARK COUNTY) | NORTHWESTERN ENERGY | 5/4/09 - THIS WILL BE THE FINAL REPORT FOR THIS INCIDENT. A THIRD PARTY CONTRACTOR THAT WAS EXCAVATING FOR A SEWER PROJECT FOR THE CITY OF LIVINGSTON DAMAGED A SERVICE LINE THAT CAUSED THE INCIDENT. THIS INCIDENT REPORT SHOULD NOW BE CONSIDERED CLOSED WITH NO FURTHER INVESTIGATION REQUIRED. FORM PHMSA F 7100.1, PART G (NARRATIVE) THE CITY OF LIVINGSTON HAS A SEWER LINE REPLACEMENT PROJECT ON-GOING IN TEH CITY. THE ALLEY BEHIND 100 SOUTH L STREET WAS PART OF THIS PROJECT. THE GAS LINE LOCATE REQUEST WAS RECEIVED ON 8/31/2005. LOCATES WERE MADE WITHING 2 DAYS. THE REQUEST START DATE WAS 9/3/2005. THE EXCAVATOR ONLY EXPOSED THE GAS SERVICE LINES WHERE THEY CROSSED THE SEWER PROJECT AT THE SITE OF THE INCIDENT. ON 9/14/05, THE SEWER DITCH WAS BACKFILLED WITHOUT COMPACTION BECAUSE THE SEWER CONTRACTOR'S COMPACTION DEVICE WAS INOPERABLE. BEFORE 0800 HOURS ON 9/15/2005 NORTHWESTERN ENERGY (NWE) RECEIVED A CALL ON A LOCAL CELL PHONE, NOT THE ONE CALL SYSTEM, ASKING FOR RE-LOCATES IN THIS ALLEY. THE SEWER CONTRACTOR WAS RE-EXCAVATING THE SEWER MAIN TO PROPERLY COMPACT THE DITCH. AT 0834 HOURS, THE CONTRACTOR MADE A SECOND CALL AND LEFT A VOICE MAIL MESSAGE ON THE SAME LOCAL CELL NUMBER STATING THAT A GAS LINE HAD BEEN HIT. THE SERVICEMAN WAS ON THE PHONE WITH BOZEMAN DISPATCH WHEN THE SECOND CALL CAME IN, AND WAS ON SITE WITH THE CONTRACTOR BEFORE HE COULD RETURN THE CALL MADE AT 0834 HOURS, 3 TO 4 MINUTES HE REMAINED ON SITE UNTIL THE EXPLOSION. THE SEWER CONTRACTOR EXPOSED THE HIT SERVICE LINE BEFORE THE SERVICEMAN ARRIVED, BUT THE BREAK WAS NOT EXPOSED (~24" AWAY). OTHER CREW MEMBERS ARRIVED, ASSESSED THE SITUATION AND LEFT TO GATHER EQUIPMENT AND MATERIAL OVER THE NEXT HOUR. AT THE TIME OF THE EXPLOSION, 1010 HOURS, THE CREW WAS STASRTING TO EXPOSE THE BREAK. A BYSTANDER, WHO IS ALSO A MEMEBER OF THE FIRE DEPARTMENT, NOTIFIED THE FIRE DEPARTMENT BY RADIOI OF THE INCIDENT. BURNING DEBRIS IGNITED THE GAS AT THE SITE OF EXCAVATION. THE STSRUCTURE THAT EXPLODED WAS BURNING, AS WELL. TWO OTHER STRUCTURES WERE DAMAGED IN THE EXPLOSION. FOUR NWE EMPLOYEES WERE INJURED IN THE BLAST, BUT NOT HOSPITALIZED. ONE MEMBER OF THE GENERAL PUBLIC WAS INJURED IN THE STRUCTURE THAT EXPLODED AND HOSPITALIZED. AFTER THE AREA WAS RELEASED BY THE FIRE DEPARTMENT, THE BREAK IN THE SERVICE LINE WAS FOUND TO BE THE ONLY SOURCE OF GAS. THE SERVICE LINE SHOWS SEVERAL POINTS OF CONTACT FROM EXCAVATION AND WAS BENT WITH THE DIRECTION OF THE SEWER MAIN DITCH BEING EXCAVATED, INDICATING HAVING BEEN PULLED OR PUSHED DURING EXCAVATION. THE SERVICE BROKE CIRCUMFERENTIALLY MORE THAN HALF WAY AROUND THE PIPE AT THE THREADS ENTERING A FITTING. THIS SERVICE LINE DID NOT SERVE THE STRUCTURE THAT EXPLODED, BUT A HOUSE ON THE OPPOSITE SIDE OF THE ALLEY. THE GAS MAY HAVE MIGRATED ALONG A SEWER SERVICE. THOUGH NO GAS WAS FOUND ALONG THIS ROUTE DURING INVESTIGATION. THE SOIL ALONG THIS SEWER LINE SERVING THE DAMAGED STRUCTURE WAS DRY AND LOOSELY COMPACTED (GRAVEL) COMPARED TO THE SURROUNDING SOIL. IF THE GAS MIGRATED ALONG THE SEWER SERVICE, IT THEN MAY HAVE MIGRATED THROUGH THE FOUNDATION WALL, COLLECTED AND FOUND A SOURCE OF IGNITION. | 501000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
238 | 2005-10-18 | IL | other | UNKNOWN (COOK COUNTY) | NICOR GAS | A STRUCTURE FIRE AT THE RESIDENCE DESTROYED THE HOME AND ALSO MELTED THE METER SET WHICH WAS LOCATED IN THE BASEMENT. | 151000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
239 | 2005-10-13 | LA | sabotage | UNKNOWN (TERREBONNE COUNTY) | SOUTH COAST GAS |  | 336 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
240 | 2005-10-20 | PA | technical failure | UNKNOWN (ALLEGHENY COUNTY) | EQUITABLE GAS COMPANY | AN EQUITABLE GAS CREW WAS IN THE PROCESS OF PURGING A NEWLY INSTALLED 4" PLASTIC MAIN LINE BEFORE PLACING IT INTO SERVICE. AN EQUITABLE GAS EMPLOYEE WAS IN THE EXCAVATION MONITORING GAS FLOW AT TEH PURGE SITE, WHEN A FLASH FIRE OCCURRED. THE EQUITABLE GAS EMPLOYEE RECEIVED 2ND DEGREE BURNS ON HIS FACE. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
241 | 2005-10-10 | AL | other | UNKNOWN (JEFFERSON COUNTY) | ALABAMA GAS CORPORATION | THERE HAVE BEEN PUBLIC REPORTS BY THE INVESTIGATING FIRE DEPARTMENT THAT THE SERVICE LINE RUPTURED BY EXTERNAL FORCES FROM FALLING DEBRIS AFTER RESIDENCE CAUGHT FIRE. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
242 | 2005-09-28 | LA | sabotage | UNKNOWN (LAFOURCHE COUNTY) | SOUTH COAST GAS |  | 155 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
243 | 2005-10-12 | LA | sabotage | UNKNOWN (TERREBONNE COUNTY) | SOUTH COAST GAS |  | 655 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
244 | 2005-08-29 | MD | other | UNKNOWN (PRINCE GEORGE'S COUNTY) | WASHINGTON GAS | THE BOWIE FIRE DEPARTMENT RESPONDED TO A HOUSE FIRE. WASHINGTON GAS WAS NOTIFIED AT 6:38AM, AND ARRIVED AT 7:09AM TO FIND GAS OFF AND THE FIRE EXTINGUISHED. THE FIRE DEPARTMENT DETERMINED THAT THE FIRE WAS DUE TO A MALFUNCTION IN THE ELECTRICAL AIR CONDITIONING UNIT. THE UNIT WAS LOCATED APPROXIMATELY THREE FEET AWAY FROM THE GAS METER SET. THE FIRE ENGULFED THE HOUSE AND MELTED THE METER AND REGULATOR, CAUSING GAS TO BE RELEASED AND IGNITE DURING THE COURSE OF THE FIRE. WGL EMPLOYEES REMOVED THE METER AND CAPPED THE GAS SERVICE OFF IN THE YARD. | 41000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
245 | 2005-09-30 | LA | natural disasters | UNKNOWN (WASHINGTON COUNTY) | WASHINGTON PARISH GAS UTILITY DISTRICT #2 | EMERGENCY RESPONDER DID NOT FOLLOW PROCEDURE AS DESCRIBED WITHIN OPERATIONS, MAINTENANCE & EMERGENCY MANUAL IN ACCORDANCE WITH 193.605(B)(9). RESPONDER WAS CALLED AT 8:30PM ON 9/30/2005 WITH REPORT OF GAS SMELL. HE WAS FOUND AT 12:00AM ON 10/1/05. THE INVESTIGATION CONCLUDED THE ABOVE FINDINGS AND IS COMPLETE. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
246 | 2005-10-14 | IN | sabotage | UNKNOWN (JOHNSON COUNTY) | INDIANA GAS COMPANY, INC. | THIRD PARTY CONTRACTOR PERFORMING ROADWORK FOR ROADWAY APPROACH TO SUBDIVISION DAMAGED A 6" PE MAIN. CONTRACTOR HAD PREVIOUSLY REMOVED 31" OF COVER PRIOR TO DAMAGING THE PIPE. OPERATOR OF MACHINERY WAS ADMITTED TO HOPSITAL FOR 2ND AND 3RD DEGREE BURNS TO HIS BODY. FACILITY LOCATES WERE REQUESTED. MARKINGS WERE MADE WITHIN THE REQUIRED TIME FRAME AND WERE ACCURATE. | 172000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
247 | 2005-09-27 | NY | sabotage | UNKNOWN (NASSAU COUNTY) | KEYSPAN ENERGY DELIVERY LONG ISLAND (KEYSPAN GAS EAST CORP, DBA) | ON SEPTEMBER 27, 2005, A THIRD PARTY CONTRACTOR DAMAGED A 2" 60# PLASTIC GAS MAIN WHILE TRENCHING ON THE NORTH SIDE OF JERICHO TURNPIKE IN NEW HYDE PARK, NY. THE MACHINE THAT HIT THE GAS MAIN WAS A SMALL MAN OPERATED TRENCHING MACHINE. NATURAL GAS ESCAPTED FROM THE DAMAGED GAS MAIN AND IGNITED, CAUSING A FIRE AT SEVERAL ADDRESSES: #617, #619, AND #621 JERICHO TURNPIKE. KEYSPAN WAS NOTIFIED OF THE DAMAGED FACILITY AT 10:14 AM. A RESPONDER WAS DISPATCHED AT 10:15 AM, AND ARRIVED ON SITE AT 10:21 AM. VALVE 015-04-3989, WHICH FED THE DAMAGED GAS MAIN, WAS CLOSED AT 10:56 AM. THE GAS FIRE FROM THE DAMAGED GAS MAIN WAS IMMEDIATELY EXTINGUISHED. FIRE DEPARTMENT PERSONNEL CONTINUED TO FIGHT THE STRUCTURAL FIRES. AFTER REPAIRS, THE GAS MAIN WAS PLACED BACK IN SERVICE ON SEPTEMBER 28, 2005 AT 8:21 PM. | 1000000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
248 | 2005-10-10 | MD | sabotage | UNKNOWN (nan COUNTY) | BALTIMORE GAS & ELECTRIC COMPANY | ON OCTOBER 10TH AT APPROXIMATELY 7:45 AM, A CONTRACTOR WORKING TO MAKE PROACTIVE REPAIRS TO OUT 16" NATURAL GAS MAIN PUNCTURED THE TOP OF THE MAIN WITH A HIGHHOE. THE STRIKE PRODUCED A HOLE APPROXIMATELY 9" BY 5" AND ALSO CAUSED THE MAIN TO CRACK ABOUT 3' LONGITUDINALLY RESULTING IN THE RELEASE OF NATURAL GAS. THERE WERE NO INJURIES OR EVACUATIONS. IT TOOK 9 HOURS TO STOP THE FLOW OF GAS BECAUSE THE MAIN WAS LOCATED AT THE BASE OF A SLOPE ANDUNDER 114 FEET OF COVER. ADDITIONALLY, THE DEPTH OF THE MAIN DROVE THE COST OF REPAIRS BEYOND $50,000, WHICH BECAUSE KNOWN ON OCTOBER 19TH. | 84000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
249 | 2005-10-04 | MN | natural disasters | UNKNOWN (WASHINGTON COUNTY) | NORTHERN STATES POWER COMPANY D/B/A XCEL ENERGY | ROCKING IMPINGING ON A 1-1/2" CENTURY PLASTIC MAIN CAUSED A BRITTLE CRACK FAILURE OF THE PIPE WALL. GAS LEAKED FROM THE FAILURE, MIGRATED TO THE BUILDING, AND WAS IGNITED BY AN UNKNOWN SOURCE OF IGNITION. | 260000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
250 | 2005-10-20 | TX | sabotage | UNKNOWN (WARD COUNTY) | TEXAS GAS SERVICE COMPANY | 5" GAS MAIN HIT AND DAMAGED BY GRADER, REPLACED 27 FT. OF GAS MAIN. NO LINE LOCATES REQUESTED. | 58291 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
251 | 2005-08-30 | LA | sabotage | UNKNOWN (LAFOURCHE COUNTY) | SOUTH COAST GAS CO |  | 375 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
252 | 2005-09-05 | LA | sabotage | UNKNOWN (LAFOURCHE COUNTY) | SOUTH COAST GAS CO |  | 760 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
253 | 2005-09-05 | LA | sabotage | UNKNOWN (LAFOURCHE COUNTY) | SOUTH COAST GAS CO |  | 1106 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
254 | 2005-07-21 | LA | sabotage | UNKNOWN (LAFOURCHE COUNTY) | SOUTH COAST GAS CO |  | 446 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
255 | 2005-09-03 | LA | sabotage | UNKNOWN (LAFOURCHE COUNTY) | SOUTH COAST GAS CO |  | 491 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
256 | 2005-09-02 | LA | sabotage | UNKNOWN (LAFOURCHE COUNTY) | SOUTH COAST GAS CO |  | 1183 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
257 | 2005-07-05 | LA | sabotage | UNKNOWN (THREBORNE COUNTY) | SOUTH COAST GAS CO |  | 743 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
258 | 2005-07-20 | LA | sabotage | UNKNOWN (LAFOURCHE COUNTY) | SOUTH COAST GAS CO |  | 347 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
259 | 2005-10-25 | CO | technical failure | UNKNOWN (ADAMS COUNTY) | PUBLIC SERVICE COMPANY OF COLORADO | CREW WAS GOING TO CONNECT A 1 1/4" PIECE OF POLYETHYLENE INTO A PVC TAPPING TEE WITH GAS BLOWING. WHEN THE CREW WENT TO REMOVE THE CAP ON THE BRANCH OF THE PVC TAPPING TEE, A STATIC CHARGE JUMPED FROM THE CAP TO THE BODY OF THE TEE CAUSING THE ESCAPING GAS TO IGNITE. | 100 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
260 | 2005-10-24 | NC | sabotage | UNKNOWN (ROWAN COUNTY COUNTY) | PUBLIC SERVICE OF NORTH CAROLINA, INCORPORATED (DBA PSNC ENERGY) | GAS SERVICE WAS DAMAGED BY CONTRACTOR RECLAIMING THE ROAD. SEE ATTACHED REPORT. 11/09/2005 FINAL REPORT: NORTH FRANKLIN STREET, CHINA GROVE NORTH CAROLINA TIME LINE OF EVENTS MONDAY, OCTOBER 24,2005 1:26 P.M. PROPST CONSTRUCTION COMPANY HIT AND SEVERED A 3/4" PLASTIC NATURAL GAS SERVICE IN THE CENTER OF NORTH FRANKLIN STREET APPROXIMATELY 72 FEET NORTH OF THE CENTER LINE OF SWINK STREET. THE 3/4" PLASTIC SERVICE FED NATURAL GAS TO THE RESIDENTS AT 204 NORTH FRANKLIN STREET. THE UNCONTROLLED ESCAPE OF NATURAL GAS IGNITED IMMEDIATELY AND THE RECLAIMER MACHINE THAT SEVERED THE NATURAL GAS LINE STARTED BURNING. 1:27 P.M. THE CHINA GROVE FIRE DEPARTMENT WAS ALARMED TO RESPOND TO FIRE AT THE INTERSECTION OF SWINK STREET AND NORTH FRANKLIN STREET. 1:30 P.M. THE CHINA GROVE FIRE DEPARTMENT ARRIVED ON THE SCENE AND STARTED TO FIGHT THE FIRE. 1:45 P.M. THE EMPLOYEE OPERATING THE RECLAIMER MACHINE FOR PROPST CONSTRUCTION COMPANY INFORMED THE CHINA GROVE FIRE CHIEF THAT HE THOUGHT HE MAY HAVE HIT A NATURAL GAS LINE AND THAT MAY BE THE REASON THE FIRE DEPARTMENT WAS HAVING A HARD TIME PUTTING OUT THE FIRE. 1:46 P.M. THE CHINA GROVE FIRE DEPARTMENT EVACUATED FOUR HOMES IN THE 200 BLOCK OF NORTH FRANKLIN STREET. 1:47 P.M. PSNC EMPLOYEE DALE BROCK HEARD OVER A SCANNER THAT THERE WAS A GAS FIRE ON NORTH FRANKLIN STREET IN CHINA GROVE. DALE CALLED THE CONCORD OPERATION CENTER AND INFORMED AN OPERATIONS ASSISTANT THAT HE WAS ON HIS WAY TO THE FIRE. 1:54 P.M. DAVID WITH THE CITY OF CHINA GROVE NOTIFIED THE CALL CENTER THAT A MILLING MACHINE HIT A NATURAL GAS LINE AND IT WAS ON FIRE. DAVID WAS NOT SURE IF GAS WAS BLOWING BUT THE FIRE DEPARTMENTS FROM KANNAPOLIS AND LANDIS WERE ALSO BEING DISPATCHED TO HELP. 1:58 P.M. PSNC EMPLOYEE DALE BROCK ARRIVED ON THE SCENE AND INFORMED THE OPERATIONS CENTER AS TO THE CURRENT STATUS OF EVENTS ON NORTH FRANKLIN STREET. 2:00 P.M. THE CONSTRUCTION SUPERVISOR WAS INFORMED OF THE INCIDENT. A LOCATOR/FIRST RESPONDER AND TWO CONSTRUCTION CREWS WERE DISPATCHED TO THE SCENE. A THIRD CONSTRUCTION CREW WAS DISPATCHED TO THE OPERATIONS CENTER AND PUT ON STAND-BY TO BRING ANY EQUIPMENT OR MATERIALS NEEDED TO ASSIST IN THE INCIDENT. 2:25 P.M. THE LOCATOR/FIRST RESPONDER AND ONE OF THE CONSTRUCTION CREWS ARRIVED ON THE SCENE AND BEGAN ACCESSING THE SITUATION. THREE FIRE TRUCKS WERE SPRAYING WATER ON THE BURNING RECLAIMER MACHINE IN ORDER TO KEEP IT COOL WHILE THE NATURAL GAS RUPTURE WAS STILL BURNING. 2:40 P.M. THE CONSTRUCTION SUPERVISOR AND THE SECOND CONSTRUCTION CREW ARRIVED ON THE SCENE. IT WAS DETERMINED THAT THE FLOW OF NATURAL GAS COULD BE STOPPED BY EXCAVATING WITH SHOVELS THE TAP-N-TEE ON THE MAIN AND SQUEEZING OFF THE PLASTIC 3/4" SERVICE LINE. 2:50 P.M. THE 3/4" PLASTIC SERVICE WAS SQUEEZED OFF PREVENTING THE UNCONTROLLED ESCAPE OF NATURAL GAS. 2:54 P.M. THE FIRE WAS EXTINGUISHED AND THE SCENE WAS DECLARED SAFE. THE FIRE DEPARTMENT ALLOWED THE FOUR EVACUATED HOMES TO BE RE-ENTERED. 3:10 P.M. THE REPLACEMENT OF THE DAMAGED 3/4" PLASTIC SERVICE BEGAN. IT WAS DETERMINED THAT ALL OF THE PLASTIC PIPE CWENTLY UNDER THE ROAD BED WOULD BE REPLACED. 5:10 P.M. THE REPLACEMENT AND REPAIR OF THE 3/4" PLASTIC SERVICE FOR 204 N. FRANKLIN STREET WAS COMPLETED AND PSNC PERSONNEL LEFT THE SCENE. 10:03 P.M. THE METER AT 204 NORTH FRANKLIN STREET WAS TURNED ON AND ALL GAS APPLIANCES WERE WORKING. DESCRIPTION OF GAS FACILITIES THE 3/4" PLASTIC NATURAL GAS SERVICE WAS INSTALLED AT 204 NORTH FRANKLIN STREET ON NOVEMBER 22, 1989, BY A PSNC CONSTRUCTION CREW. IT IS OPERATED AT 60 PSI. EVALUATION OF DAMAGE THE 3/4" PLASTIC SERVICE WAS SEVERED AND IGNITED BY A RECLAIMING MACHINE WHILE THE CONTRACTOR WAS REMOVING COVER AND FILL FROM THE ROAD RIGHT OF WAY. THE COST TO MAKE REPAIRS ON THE 3/4" PLASTIC SERVICE AND RE-LIGHT THE RESIDENCE AT 204 NORTH FRANKLIN STREET WAS APPROXIMATELY $1,717.87 THE DAMAGE TO THE RECLAIM ING MACHINE MAY BE $100,000. EVALUATION OF CAUSE THE CONTRACTOR WAS GRADING IN THE ROAD RIGHT-OF-WAY WITH A RECLAIMING MACHINE WHEN THEY SEVERED THE PLASTIC NATURAL GAS SERVICE LINE. NO LOCATES WERE CALLED IN TO THE NORTH CAROLINA ONE CALL CENTER OR TO PSNC PRIOR TO THE WORK BEGINNING. INCIDENT COORDINATION COORDINATION BETWEEN PSNC ENERGY AND EMERGENCY RESPONSE PERSONNEL WAS VERY GOOD. THE CHINA GROVE FIRE DEPARTMENT CONTROLLED TRAFFIC AND MONITORED THE AREA UNTIL IT WAS MADE SAFE. ASSESSMENT OF PSNC ENERGY PERFORMANCE PSNC ENERGY RESPONDED TO THE INCIDENT, ACCURATELY IDENTIFIED THE PROBLEM, AND WORKED WITH EMERGENCY RESPONDERS TO MAKE THE AREA SAFE IN A TIMELY MANNER. COORDINATION BETWEEN COMPANY PERSONNEL AND NON-PSNC RESPONDERS WAS GOOD. PSNC EMPLOYEES ON THE SCENE NAME, JOB TITLE DONALD L. BOYIAS, CREW LEADER RONNIE P. GREGORY, SENIOR EQUIPMENT OPERATOR BRYAN D. MILLS, PIPE LAYER I DALE F. BROCK, FIELD SERVICE SPECIALIST ROBERT E. HAMMONDS, LOCATOR FIRST RESPONDER KEVIN L. JOHNSON, LOCATOR FIRST RESPONDER OSCAR D. BOST, SENIOR CREW LEADER DOUGLAS N. DONALDSON, SENIOR PIPE LAYER RICHARD P. HALE, WELDER BRIAN E. SMITH, EQUIPMENT OPERATOR TERRY M. OVERCASH, CREW LEADER MARK E. CRAFT, SENIOR EQUIPMENT OPERATOR RONALD D. HARRINGTON, EQUIPMENT OPERATOR WILBUR J. NORRIS, SUPERVISOR | 101717 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
261 | 2006-01-03 | AK | other | UNKNOWN (KENAI PENINSULA COUNTY) | ENSTAR NATURAL GAS COMPANY | ENSTAR WAS NOTIFEID OF A MOBILE HOME FIRE AT 3:45AM ON 1/3/06 AT TRACT 12A ECHO LAKE SUBDIVISION, LAKESIDE AVENUE, NEAR SOLDOTNA ALASKA. A SERVICE MAN WAS DISPATCHED TO FIND THE GAS METER AT THIS LOCATION SHUT OFF UPON ARRIVAL. A FIRE AT THE MOBILE HOME BURNED THE GAS METER. FIRE DEPARTMENT PERSONNEL CLOSED THE SERVICE LINE SHUT OFF VALVE TO STOP THE FLOW OF GAS. NATURAL GAS DID NOT CAUSE OR CONTRIBUTE TO THE FIRE. | 50260 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
262 | 2005-10-23 | CA | maintenance | UNKNOWN (SANTA CLARA COUNTY) | PACIFIC GAS & ELECTRIC COMPANY | REGULATOR MALFUNCTION AND IRV DID NOT APPEAR TO PERFORM AS REQUIRED AND CAUSE PRESSURE TO BUILD UP DOWNSTREAM AND EVENTUALLY CAUSE THE TOP OF THE METER TO RUPTURE, RELEASING GAS TO ATMOSPHERE AND THE SUBSEQUENT FIRE. | 200000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
263 | 2005-11-10 | LA | sabotage | UNKNOWN (LAFOURCHE COUNTY) | SOUTH COAST GAS CO INC |  | 587 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
264 | 2005-11-10 | LA | sabotage | UNKNOWN (LAFOURCHE COUNTY) | SOUTH COAST GAS CO INC |  | 361 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
265 | 2005-12-05 | IL | other | UNKNOWN (WILL COUNTY) | NICOR GAS | STRUCTURE FIRE ORIGINATED INSIDE THE GARAGE. THE METER SET, WHICH WAS ATTACHED TO THE OUTSIDE GARAGE WALL, WAS MELTED AS A RESULT OF THE FIRE. | 351000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
266 | 2005-12-14 | LA | sabotage | UNKNOWN (TERREBONNE COUNTY) | SOUTH COAST GAS CO. |  | 926 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
267 | 2005-11-03 | TX | sabotage | UNKNOWN (NACOGDOCHES COUNTY) | CHIRENO NATURAL GAS | TEXAS DEPARTMENT OF TRANSPORATION DID NOT CALL IN A LOCATE NOR DID WE RECIEVE ANY NOTIFICATION OF THEIR ACTIVITIES ON LOOP 34. | 186912 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
268 | 2005-11-11 | MD | other | UNKNOWN (nan COUNTY) | BALTIMORE GAS & ELECTRIC COMPANY | BALTIMORE CITY FIRE DEPT. (BCFD) REQUESTED OUR ASSISTANCE TO TURN OFF NATURAL GAS SERVICE TO 3852 QUARRY ST. A GAS MECHANIC WAS DISPATCHED AT 13:34 AND ARRIVEDAT 13:58. THE 1" INSULOCK LEAADING TOTHE INLET SIDE OF THE METER HAD BEEN DAMAGED BY THE HEAT OF THE FIRE CRATING A RESTRICTED LOW PRESSURE GAS FIRE WITH ABOUT A 4" TO 6" LAZY FLAME. BCFD HASED DOWN THE GAS SERVICE AND THE GAS MECHANIC APPLIED FITTERS CLAY AND ELECTIC TAPE TO THE 1" INSULOCK STOPPING THE FLOW OF THE INSIDE FRONT WALL UNDER TH HAS SERVICE. THE GAS DRYER HAD NO VENT TO THE OUTSIDE OF THE BUILDING AND CLOTHES WERE ON THE FLOOR ALL AROUND THE DRYER. SURFACE AND SUB-SURFACE SURVEYS WERE CONDUCTED AT THE BUILDING FOUNDATION, SERVICE NAD OVER THE TAP AT THE MAIN; NO INDICATIONS OF NATURAL GAS. ALSO STRUCTURES WERE CHECKED FRONT OF BUILDINGS; NO INDICATIONS OF NATURAL GAS. | 300000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
269 | 2005-11-11 | TX | sabotage | UNKNOWN (HARRIS COUNTY) | CENTERPOINT ENERGY | THIRD PARTY DAMAGED A 4" I.P. STEEL SERVICE RISER, WHILE CLEARING A LOT WITH A BULLDOZER. THE HOUSTON FIRE DEPARTMETN BLOCKED LIBERTY ROAD FROM LOCKWWOD DRIVE TO KASHMERE STREET. *ORGINALLY REPORTED AS LOCKWOOD AT LIBERTY, BUT LATER CORRECTED TO 5200 BLK. OF LIBERTY ROAD. | 250935 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
270 | 2005-11-09 | MA | other | UNKNOWN (nan COUNTY) | BOSTON GAS COMPANY D/B/A KEYSPAN ENERGY DELIVERY NEW ENGLAND |  | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
271 | 2005-12-11 | TX | other | UNKNOWN (HARRIS COUNTY) | CENTERPOINT ENERGY | RADIANT HEAT FROM A VEHICLE FIRE MELTED METER SET ASSEMBLY AND THE ESCAPING GAS WAS IGNITED. DRIVER OF VEHICLE WAS KILLED WHILE STILL INSIDE VEHICLE. *ORIGINALLY REPORTED AS 530 E. CANINO, BUT WAS LATER CORRECTED TO 613 E. CANINO. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
272 | 2005-12-13 | NJ | sabotage | UNKNOWN (BERGEN COUNTY) | PUBLIC SERVICE ELECTRIC & GAS COMPANY | ON TUESDAY, DECEMBER 13, 2005, WORKERS FROM THE AMERICAN TANK COMPANY WERE IN THE PROCESS OF REMOVING AN UNDERGROUND OIL TANK THAT SERVED A THREE STORY 24 UNIT APARTMENT BUILDING WHEN THE GROUND SURROUNDING A 1-1/4 INCH 15 PSI DESIGN PRESSURE STEEL GAS SERVICE REPORTEDLY COLLAPSED AND CAUSED A GAS LEAK. PSE&G RECEIVED A CALL FROM MR.COLUMBO, AT 8:54 AND FROM THE BERGENFIELD POLICE DEPARTMENT AT 8:58. AT 9:01,BOTH CALLS WERE DISPATCHED TO A TECHNICIAN, WHO ARRIVED ON SITE AT 09:22. THE TECHNICIAN ATTEMPTED TO CLOSE THE GAS VALVE AT THE CURB, BUT WAS UNABLE TO TURN THE VALVE. AN INSPECTOR ARRIVED ON SITE AT 09:30. AFTER MEETING THE TECHNICIAN, THE INSPECTOR CALLED HEADQUARTERS AND REQUESTED ADDITIONAL ASSISTANCE. THE TECHNICIAN THEN WALKED TOWARD THE BUILDING WITH HIS GAS DETECTOR TO ASCERTAIN GAS LEVEL READINGS. AS THE TECHNICIAN WAS OBTAINING A GAS READING OF 0.2% IN OPEN AIR NEAR THE BOILER ROOM DOOR, THE EXPLOSION OCCURRED. A PORTION OF THE 24 UNIT THREE STORY BUILDING WAS DESTROYED IN THE EXPLOSION AND OTHER PORTIONS OF THE BUILDING CAUGHT FIRE. AFTER THE EXPLOSION, BOTH THE TECHNICIAN AND THE INSPECTOR ASSISTED THE INJURED AND SUPPORTED EMERGENCY PERSONNEL. THE CURB GAS VALVE WAS CLOSED AT 10:00 AFTER ADDITIONAL PERSONNEL ARRIVED. PRIOR TO THE COMMENCEMENT OF THE EXCAVATION WORK, THE GAS SERVICE HAD BEEN ACCURATELY MARKED BY PSE&G IN ACCORDANCE WITH NEW JERSEY'S UNDERGROUND FACILITY PROTECTION ACT. IN ADDITION, THE DAY BEFORE THE ACCIDENT, THE GAS SERVICE HAD BEEN LOCATED AND IDENTIFIED BY THE PSE&G INSPECTOR IN THE PRESENCE OF THE CONTRACTOR EMPLOYEES. AN INVESTIGATION IS ONGOING TO DETERMINE THE CAUSE AND RELATED FACTORS. | 2760000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
273 | 2005-09-25 | PA | other | UNKNOWN (PHILADELPHIA COUNTY) | PHILADELPHIA GAS WORKS | PGW WAS CALLED TO THE SCENE OF A FIRE/EXPLOSION BY THE PHILADELPHIA FIRE DEPARTMENT. UPON ARRIVAL WE FOUND A FIRE WITH EXTENSIVE STRUCTURAL DAMAGE TO 3304 AND 3306 N. HOPE STREET, ALSO DAMAGED WERE 3302 AND 3308. THERE WAS A GAS FIRE APPROXIMATELY 12 FEET WEST OF THE WEST BUILDING LINE AND ALONG THE SOUTH BUILDING WALL OF 3304 COMING FROM THE BASEMENT. BRICKS, DOORS AND WINDOWS WERE BOWN OUTWARD INTO THE STREET. ADDITIONALLY, WE FOUND A SLIGHT ODOR OF GAS AND A 60 LEL READING COMING FROM THE RUBBLE INSIDE OF THE PROPERTY NEAR WHERETHE HEAD OF SERVICE WOULD HAVE BEEN (THE AREA OF THE HEAD OF SERVICE WAS NOT ACCESSIBLE). PHILADELPHIA FIRE DEPARTMENT ASSISTED IN MOVING DEBRIS FROM IN FRONT OF 3304. PGW RECORDS INDICATED THAT THE 1" PLASTIC CURB VALVE WAS TURNED OFF ON JULY 15,2005. PGW PERSONNEL FOUND THIS VALVE IN THE ON POSITION. AT THAT TIME WE TURNED THE VALVE OFF AND THE FIRE ON THE SOUTH WALL DECREASED IN INTENSITY AND THE LEL READING DISSIPATED. PGW CREWS MADE MIGRATION CHECKS, EXCAVATED AND PROBED ALONG THE MAIN AND THE SERVICES AND FOUND NO INDICATION OF AN UNDERGROUND LEAK IN THE AREA OF THIS INCIDENT. THE SERVICE LINES AT THE MAIN CONNECTION TO 3302, 3304 AND 3306 WERE THEN ABANDONED. ALL SERVIE LINES WERE INSTALLED IN 1989 AND WERE CONNECTED TO A 4" CATHODICALLY PROTECTED STEEL MAIN ALSO INSTALLED AT THAT TIME. ALL SERVICE CONNECTIONS AT THE MAIN WERE IN GOOD CONDITION AND WE FOUND NO INDICATION OF LEAKS IN THE AREA OF THIS INCIDENT. THE SERVICE LINE TO 3302 WAS TESTED AND HELD AN AIR TEST AT OPERATING PRESSURE. THE PROPERTIES AT 3304 AND 3306 WERE STRUCTURALLY UNSAFE CONDITION AT THIS TIME TO ALLOW ACCESS TOTHE HEAD OF THE SERVICE CONNECTION. THIS WORK WAS CONDUCTED IN THE PRESENCE OF PUC GAS SAFETY INSPECTORS CLYDE W. STANLEY, AND NGHI NGUYEN. DURING THE INVESTIGATION PGW CREWS FOUND IN INDICATION OF LEAKING GAS ON THE NORTH END OF THE STREET. THESE READING WERE INVESTIGATED THE MIGRATION PATTERN INDICATED THAT THE READING WERE NOT ASSOCIATED WITH THIS INCIDENT. REPAIRS WERE MADE TO TWO 8" CAST IRON JOINTS A 6" CAST IRON JOINT ON THE FAR NORTH END OF THE STREET AND THE SERVICE LINE TO 3353 AND 3332. ON SEPTEMBER 30, 20005, PGW CREWS GAINED ACCESS TOT HE HEAD OF SERVICE LINES TO 3304 AND 3306. IN THE PRESENCE OF PUC GAS SAFETY INSPECTORS CLYDE W. STANLEY, AND NGHI NGUYEN WE CONDUCTED TESTS ON BOTH PLASTIC SERVICE LINES. THE SERVICE LINE 3304 FAILED THE TEST. WE FOUND THE HEAD OF SERVICE MELTED DUE TO THE INTENSE FIRE. THE SERVICE LINE TO 3306 HELD 12" W.C. FOR FIFTEEN MINUTES. THIS INCIDENT IS UNDER INVESTIGATION BY THE PHILADELPHIA FIRE MARSHALS OFFICE | 35650 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
274 | 2005-11-01 | VA | sabotage | UNKNOWN (nan COUNTY) | WASHINGTON GAS | NATELCO ELECTRICAL CONTRACTOR TRENCHING FOR VERIZON TO INSTALL PHONE CONDUIT STRUCK A 2" PLASTIC GAS MAIN IN THE ECONOMY PARKING LOT AT REAGAN NATIONAL AIRPORT. THE ESCAPING GAS IGNITED AND DESTROYED THE CONTRACTOR'S RENTAL TRENCHER AND CAUSED MINOR DAMAGE TO SEVERAL PRIVATELY OWNED VEHICLES IN THE AREA. | 118030 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
275 | 2005-12-12 | AR | natural disasters | UNKNOWN (PULASKI COUNTY) | CENTERPOINT ENERGY | A STRESS FRACTURE CAUSED A 2" CAST IRON MAIN TO RUPTURE THAT WAS LOCATED BETWEEN 2008 AND 2016 DURWOOD, LITTLE ROCK,AR APPROXIMATELY 11' FROM THE REAR (NORTHWEST CORNER) OF 2016. AT APPROXIMATELY 1:00 AM ON 12/12/05, THERE WAS A REPORTED SMALL EXPLOSION IN AN UPSTAIRS APARTMENT AT 2016 DURWOOD CAUSING A FIRE AND SOME WINDOWS TO BE BLOWN OUT. THE RESIDENT AND HER TWO CHILDREN EVACUATED THE HOME AT 2016 DURWOOD WITHOUT SUSTAINING ANY INJURIES.THE RESIDENCE WAS A TOTAL LOSS. ACCORDING TO THE ASSISTANT LITTLE ROCK FIRE MARSHALL, THE RESIDENTS AT 2008 DURWOOD STATED THEY SMELL GAS IN THE AREA AROUND MIDNIGHT BUT DID NOT MAKE A REPORT. THE RESIDENTS OF 2008 DURWOOD WERE ALSO EVACUATED DURING THE INCIDENT WITHOUT INJURY. BAR TESTING RESULTS SHOWED CONCENTRATIONS OF GAS AROUND THE FOUNDATION OF BOTH HOMES. GAS FLOW WAS STOPPED AT 8:30AM BY TAPPING AND PLUGGING THE MAIN AT TWO REMOTE LOCATIONS. | 149650 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
276 | 2005-12-10 | TX | leaks and spills | UNKNOWN (HARRIS COUNTY) | CENTERPOINT ENERGY | THIRD PARTY DAMAGED A 2" I.P. STEEL SERVICE LINE WITH A BORING TOOL WHILE INSTALLING FIBER OPTIC CABLES. HOUSTON FIRE DEPARTMENT BLOCKED THE EAST BOUND TRAFFIC LANES OF WESTHEIMER. | 77429 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
277 | 2005-11-17 | LA | sabotage | UNKNOWN (TERREBONNE COUNTY) | SOUTH COAST GAS CO. |  | 408 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
278 | 2005-12-11 | KS | natural disasters | UNKNOWN (JOHNSON COUNTY) | KANSAS GAS SERVICE | ON DECEMBER 11, 2005 AT 0810 HRS KANSAS GAS SERVICE WAS NOTIFIED BY THE SHAWNEE, KANSAS FIRE DEPARTMENT OF AN EXPLOSION AND FIRE AT 6513 HALSEY, SHAWNEE, JOHNSON COUNTY, KANSAS. COMPANY PERSONNEL WERE DISPATCHED TO THE SITE AND THE FIRST RESPONDER ARRIVED AT APPROXIMATELY 0823 HRS. A COMPANY CONSTRUCTION CREW WAS ALSO DISPATCHED TO THE AREA. THE FIRE DEPARTMENT REPORTED AT THE TIME OF COMPANY PERSONNEL ARRIVAL THAT THE HOUSE AFFECTED BY THE FIRE AND EXPLOSION, AND SURROUNDING RESIDENCES HAD BEEN EVACUATED. THERE WERE NO INJURIES OR FATALITIES. AT 1010 HRS THE PE MAIN WAS PINCHED OFF AND THERE WAS NO GAS FLOWING TO THE AFFECTED AREA. THE SERVICE LINE WAS EXCAVATED TO DETERMINE A POSSIBLE CAUSE FOR THE EXPLOSION AND FIRE. THERE WAS A BRASS COUPLING WITH METAL STIFFENERS IN THE LINE THAT HAD THE SERVICE LINE PULLED OUT OF ONE SIDE. THOUGH IT IS SUSPECTED THAT THIS FITTING MIGHT HAVE BEEN THE CAUSE OF THE LEAK, AND IT IS POSSIBLE THAT THE FITTING HAD BEEN LOOSENED BY RECENT FREEZING AND EXPANSION OF THE SOIL AROUND AN ADJACENT STORM SEWER MANHOLE, THE SERVICE WAS ALSO ACCIDENTALLY PULLED COMPLETELY IN TWO BY THE BACKHOE THAT WAS DOING THE EXPLORATORY EXCAVATION. IT IS NOT THEREFORE CONCLUSIVE AS TO HOW MUCH IF ANY THE BRASS COUPLING WAS LEAKING. ONCE THE AREA WAS MADE SAFE AND THE EXCAVATION PROCESS WAS COMPLETE THE GAS WAS RESTORED AND THE OTHER HOUSES THAT WERE SHUT OFF WERE RELIT AND ADDITIONAL LEAK SURVEYS OF THE MAIN AND SERVICES IN THE AREA WERE CONDUCTED. ONCE THE AREA WAS MADE SAFE AND THE EXCAVATION PROCESS WAS COMPLETE THE GAS WAS RESTORED AND THE OTHER HOUSES THAT WERE SHUT OFF WERE RELIT AND ADDITIONAL LEAK SURVEYS OF THE MAIN AND SERVICES IN THE AREA WERE CONDUCTED. | 200000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
279 | 2005-11-09 | AL | sabotage | UNKNOWN (TALLAPOOSA COUNTY) | DADEVILLE WATER SUPPLY AND GAS BOARD | TRACKHOE OPERATOR HIT 4" HP MAIN.LINE LOCATION WAS NOT CALLED IN. THE OPERATOR WHO HIT THE LINE IS HEATH MCADAMS. EMPLOYER IS RACON, FROM TUSCALOOSA,ALABAMA. REPAIRS MAID, LINE IS BACK IN OPERATION. COST - $12,818.99 GAS LOST - $1,783.22 | 21780 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
280 | 2005-11-04 | LA | sabotage | UNKNOWN (LAFOURCHE COUNTY) | SOUTH COAST GAS CO. |  | 196 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
281 | 2005-10-10 | MO | technical failure | UNKNOWN (COOPER COUNTY) | UNION ELECTRIC COMPANY D/B/A AS AMERENUE | PRE-INCIDENT INFORMATION: A CAST IRON REPLACEMENT PROJECT WAS UNDERWAY WHICH INVOLVED REPLACING VARIOUS SIZES OF LOW PRESSURE (INCHES OF WATER COLUMN) CAST IRON MAINS AND STEEL SERVICES, AND CONVERTING ALL OF THESE NEW FACILITIES AND SOME EXISTING LOW PRESSURE POLYETHYLENE MAINS AND SERVICES TO AN OPERATING PRESSURE OF 10 PSIG. THE AMERENUE CONTRACTOR COMPLETED THE FIRST PHASE OF THE PROJECT BY REPLACING THE EXISTING CAST IRON MAINS AND STEEL SERVICES. THE SECOND PHASE OF THE PROJECT INVOLVED CONVERTING A LOW PRESSURE AREA WHICH HAD EXISTING POLYETHYLENE MAINS AND SERVICES TO 10 PSIG. THE EXISTING POLYETHYLENE MAINS AND SERVICES HAD AN ESTABLISHED MAOP OF 60 PSIG. THIS REQUIRED SEPARATING A SECTION OF THE EXISTING POLYETHYLENE MAINS FROM THE LOW PRESSURE SYSTEM, ADDING REGULATORS TO EACH METER IN THE SECTION, AND CONNECTING THE SECTION TO AN ADJACENT 10 PSIG GAS SOURCE. THE SECTION TO BE CONVERTED WAS SIZED TO ALLOW FOR THE COMPLETION OF WORK BY THE AMERENUE CONTRACTOR WITHIN A SINGLE DAY TO MINIMIZE GAS SERVICE INTERRUPTION. INCIDENT INFORMATION: THE CONTRACTOR BEGAN THE MORNING BY PERFORMING WORK TO ISOLATE THE SYSTEM TO BE CONVERTED TO 10 PSIG FROM THE LOW PRESSURE SYSTEM. DURING THIS TIME ADDITIONAL CONTRACTOR CREW MEMBERS WENT TO EACH OF THE THIRTEEN METER LOCATIONS DESIGNATED BY AMERENUE AS PART OF CONVERSION TO SHUT OFF SERVICE AND TO REMOVE THE METER FROM THE INLET PIPING. AN AMERENUE INSPECTOR WAS WITNESSING THIS ACTIVITY AND CHECKED EACH SERVICE OFF OF A LIST ONCE THE WORK WAS COMPLETED. THE CONTRACTOR COMPLETED THE WORK TO ISOLATE THE SYSTEM AT APPROXIMATELY 11:00 AM. THE AMERENUE SUPERVISOR, AMERENUE INSPECTOR, AND THE CONTRACTOR FOREMAN MET AGAIN AT APPROXIMATELY 11:30AM TO REVIEW THE WORK COMPLETED TO THIS POINT AND TO REVIEW THE PLANS TO MAKE SURE EVERYTHING WAS READY FOR THE INTRODUCTION OF 10 PSIG INTO THE SYSTEM. THEY REVIEWED THE CONSTRUCTION PRINTS AND DISCUSSED THE MAIN SEPARATION LOCATIONS, TIE-IN LOCATIONS, AND THE THIRTEEN SERVICE LOCATIONS THAT WERE SEPARATED. ALL WERE IN AGREEMENT THAT THEY WERE READY TO PROCEED WITH THE NEXT STEP OF INTRODUCING 10 PSIG INTO THE SYSTEM. AT APPROXIMATELY 11:35 AM, A VALVE WAS OPENED TO INTRODUCE THE 10 PSIG INTO THE SYSTEM. AT APPROXIMATELY 11:53 AM, THE AMERENUE SUPERVISOR OVERHEARD THE AMERENUE DISPATCHER CALLING AN AMERENUE SERVICEMAN TO RESPOND TO A GAS PRESSURE PROBLEM AT A RESTAURANT AT 415 ASHLEY ROAD IN BOONVILLE. THE AMERENUE SUPERVISOR RECOGNIZED THE RESTAURANT WAS LOCATED ON THE LOW PRESSURE SYSTEM JUST NORTH OF THE AREA THAT WAS BEING CONVERTED TO 10 PSIG. HE SUSPECTED THERE MUST BE A PROBLEM RESULTING FROM THE SYSTEM CONVERSION SO HE CALLED THE AMERENUE INSPECTOR AND INSTRUCTED HIM TO CLOSE THE VALVE THAT WAS PREVIOUSLY OPENED. THE INSPECTOR HAD LEFT THE JOB SITE TO OBTAIN ADDITIONAL MATERIALS SO HE CONTACTED THE CONTRACTOR BY CELL PHONE AND INSTRUCTED TO IMMEDIATELY CLOSE THE VALVE. THE AMERENUE SUPERVISOR RETURNED TO THE JOB SITE AND INSTRUCTED THE CONTRACTOR TO OPEN METER SERVICE VALVES IN THE AREA AND CUT A CAP OFF OF AN EXPOSED POLYETHYLENE MAIN TO RELIEVE THE 10 PSIG OF PRESSURE FROM THE SYSTEM. THE AMERENUE SUPERVISOR CONTACTED THE AMERENUE SUPERINTENDENT, ENGINEERING AND OPERATIONS AND NOTIFIED HIM OF THE SITUATION AT APPROXIMATELY 12:10 PM. THE SUPERINTENDENT INSTRUCTED AMERENUE SUPERVISOR TO SEND AMERENUE GAS PERSONNEL TO THE LOW PRESSURE REGULATOR STATIONS TO BLEED THE PRESSURE OFF OF THE LOW PRESSURE SYSTEM THAT WAS AFFECTED. IT WAS DETERMINED THAT THE LOW PRESSURE SYSTEM WAS PRESSURIZED TO 10 PSIG SO THE SUPERINTENDENT INSTRUCTED THE SUPERVISOR TO SHUT DOWN AND ISOLATE THE ENTIRE LOW PRESSURE SYSTEM. THE SUPERINTENDENT ARRIVED AT BOONVILLE AT APPROXIMATELY 12:50PM. AT THAT TIME THE AFFECTED LOW PRESSURE SYSTEM WAS DEPRESSURIZING AND WAS AT A PRESSURE OF 0-1 PSIG. AT APPROXIMATELY 1:30 PM AMERENUE GAS PERSONNEL BEGAN SHUTTING OFF THE METERS THAT SERVED THE LOW PRESSURE SYSTEM THAT WAS ISOLATED. ADDITIONAL A MERENUE GAS PERSONNEL FROM OTHER LOCATIONS WERE CALLED TO ASSIST. THERE WERE APPROXIMATELY 750 CUSTOMERS AFFECTED BY ISOLATING THE LOW PRESSURE SYSTEM. AMERENUE INVESTIGATED AND DISCUSSED THE SITUATION TO DETERMINE THE CAUSE OF THE OVER PRESSURIZATION. IT WAS IDENTIFIED THAT A 4¿ MAIN CONNECTING THE LOW PRESSURE SYSTEM AND THE SYSTEM TO BE CONVERTED TO 10 PSIG WAS OVERLOOKED AND WAS NOT SEPARATED PRIOR TO INTRODUCING THE 10 PSIG. THIS ALLOWED THE 10 PSIG TO FLOW INTO THE LOW PRESSURE SYSTEM, WHICH IS SUPPLIED BY REGULATOR STATIONS THAT ARE IN A MONITOR CONFIGURATION, CAUSING THE SYSTEM OVER PRESSURIZATION. | 600000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
282 | 2005-12-06 | LA | sabotage | UNKNOWN (LAFOURCHE COUNTY) | SOUTH COAST GAS CO. |  | 2680 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
283 | 2005-12-20 | LA | sabotage | UNKNOWN (LAFOURCHE COUNTY) | SOUTH COAST GAS CO. |  | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
284 | 2005-12-10 | NY | sabotage | UNKNOWN (nan COUNTY) | NEW YORK STATE ELECTRIC & GAS | THE INVESTIGATION OF THE ORIGIN AND CAUSE OF THE INCIDENT IS CURRENTLY UNDER INVESTIGATION. AT THIS TIME, WE DO NOT KNOW WHAT CAUSED THE INCIDENT OR WHY IT OCCURRED. A PARTIALLY CIRCUMFRENTIAL CRACK WAS FOUND ON THE UPPER SIDE OF THE THREAD ROOT OF A SERVICE LINE AFTER THE INCIDENT BUT IT IS NOT NOW KNOWN WHETHER THIS WAS A CONSEQUENCE OF THE INCIDENT OR ONE OF THE FACTORS LEADING TO ITS CAUSE. WE DO NOT KNOW WHETHER NATURAL GAS WAS THE FIRST FUEL IGNITED OR WHETHER SOME OTHER FUEL WAS THE CAUSE OF THE INCIDENT. A COOPERATIVE, COMPREHENSIVE EVALUATION,OF THE INCIDENT SCENE HAS BEEN CONDUCTED BY THE COMPANY AND VARIOUS AGENCIES REPRESENTING AFFECTED PARTIES. CLAIMS HAVE BEEN FILED BY THE COMPANY AND AFFECTED PARTIES, BASED UPON THE INFORMATION CURRENTLY KNOWN AND ARE SUBJECT TO FURTHER MODIFICATION OR ELABORATION. PROTOCOL FOR METALLURGICAL EVALUATION OF THE CRACKED GAS SERVICE HAS BEEN DEVELOPED BY THE COMPANY AND HAS BEEN CIRCULATED TO ALL POTENTIALLY AFFECTED PARTIES FOR FINAL APPROVAL. WHEN PROTOCOL CONCURRENCE HAS BEEN REACHED BY ALL AFFECTED PARTIES, TESTS WILL BE CONDUCTED TO AID IN DETERMINING THE CAUSE OF THE FAILURE. UPDATED BY PHMSA ON 12/16/2015 PER OPERATOR'S MARK UP (PART A, QUESTION 4 – TYPE OF LEAK OR RUPTURE; PART C, QUESTION 1 – INCIDENT OCCURRED ON; PART C, QUESTION 2 – FAILURE OCCURRED ON; PART F – APPARENT CAUSE; AND PART G - NARRATIVE). THE INVESTIGATION OF THE CAUSE AND ORIGIN OF THE INCIDENT RESULTED IN THE FOLLOWING FINDINGS: THE GAS LEAK OCCURRED FROM A FRACTURE AT THE THREADED JOINT OF A SERVICE VALVE ON THE BARE STEEL PORTION OF THE GAS SERVICE. NYSEG DETERMINED THE FRACTURE WAS CAUSED BY A UNIQUE CONFLUENCE OF EVENTS. FIRST, THE WATER DEPARTMENT STRUCK AND DAMAGED THE GAS SERVICE WHILE INSTALLING A DRYWELL ADJACENT TO THE GAS SERVICE. THE FORCE FROM THE BACKHOE, BOTH DURING THE DIGGING AND BACKFILL PROCESS, CREATED A DOWNWARD FORCE THAT CONTRIBUTED TO THE GAS PIPELINE FAILURE. SECOND, REPEATED BREAKS IN THE WATER MAIN IN DIRECT PROXIMITY OF THE HOME CONTRIBUTED TO SOIL SUBSIDENCE UNDERNEATH THE GAS SERVICE, DUE TO FLOODING WATER WASHING AWAY FINE PARTICLES WHICH ERODED THE SOIL SUPPORT UNDERNEATH THE GAS PIPE. THIRD, ADDITIONAL UNDERMINING OF THE GAS SERVICE WAS CAUSED BY WATER FLOW INTO AND OUT OF THE SEWER MAIN THROUGH CRACKS AND LEAKY JOINTS, WHICH WASHED AWAY THE DIRT THAT SUPPORTED THE GAS SERVICE. THE DAMAGE CAUSED BY THE COMBINATION OF THESE EVENTS EVENTUALLY LED TO THE FAILURE OF THE GAS SERVICE. | 513000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
285 | 2005-11-22 | LA | sabotage | UNKNOWN (LAFOURCHE COUNTY) | SOUTH COAST GAS CO. |  | 1004 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
286 | 2005-12-20 | MI | sabotage | UNKNOWN (WAYNE COUNTY) | MICHIGAN CONSOLIDATED GAS COMPANY / DTE ENERGY |  | 500000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
287 | 2005-12-08 | TX | other | UNKNOWN (WILLIAMSON COUNTY) | ATMOS ENERGY CORPORATION | A RELIEF VALVE OPERATED PROPERLY. | 112000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
288 | 2005-12-10 | TX | other | UNKNOWN (WILLIAMSON COUNTY) | ATMOS ENERGY CORPORATION., MID TEX DIVISION | A RELIEF VALVE OPERATED PROPERLY. | 53000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
289 | 2006-01-06 | IL | other | UNKNOWN (nan COUNTY) | NICOR GAS | STRUCTURE FIRE ORIGINATING IN A BEDROOM SPREAD TO THE EXTERIOR WALL DAMAGING THE METER SET, THUS CAUSING A RELASE OF NATURAL GAS. | 144750 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
290 | 2006-01-05 | SC | sabotage | UNKNOWN (SPARTANBURG COUNTY) | PIEDMONT NATURAL GAS | HIGHWAY CONTRACTOR INSTALLING DRAINAGE FACILITIES FOR ROAD WIDENING PROJECT STRUCK GAS MAIN. LINE WAS MARKED BUT CONTRACTOR ASSUMED LINE WAS ABANDONED BECAUSE OF PREVIOUS EXPERIENCE WITH ABANDONED MAIN IN ADJACENT AREAS. | 95923 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
291 | 2005-12-14 | TX | other | UNKNOWN (HARRIS COUNTY) | CENTERPOINT ENERGY | A LEAK OCCURRED ON A 6' NATURAL GAS DISTRIBUTION LINE, WITH THE BANKS OF GREENS BAYOU. THE LEAKING NATURAL GAS CAUSED THE COAST GUARD TO TAKE PRECAUTIONARY MEASURES AND TEMPORARILY RESTRICT BOAT TRAFFIC IN THE AREA. THE LINE WAS SHUT DOWN AND TAKEN OUT OF SERVICE PENDING REPAIR OR REPLACEMENT. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
292 | 2005-12-30 | WI | technical failure | UNKNOWN (MILWAUKEE COUNTY) | WISCONSIN GAS COMPANY, D/B/A WE-ENERGIES | ON DECEMBER 30TH, 2005 A CONTRACT EMPLOYEE FROM SOUTHERN CROSS CORPORATION, PERFORMED A GAS SERVICE SURVEY INVOLVING AN INSIDE METER SET AT 3491 N. BARLETT AVENUE, MILWAUKEE, WISCONSIN. WHILE COMPLETING THE LEAK SURVEY ON THE INSIDE METER SET, HE FOUND A SMALL LEAK IN THE AREA OF A PIPE ON THE END OF A 2 INCH TEE LOCATED BETWEEN THE END OF THE GAS SERVICE PIPE ENTRY POINT AND THE SERVICE REGULATOR (GAS IN AIR READING TAKEN WAS 0.65 OF 1% AT THE THREADED REGION OF THE PLUG). IN ACCORDANCE WITH PROCEDURES, HE CALLED IN THE LEAK TO GAS DISPATCH AT 2:15PM AND GRADED IT AS A GRADE 2 LEAK (THE COMPANY DEFINES A GRADE 2 LEAK AS "A LEAK THAT IS RECOGNIZED AS BEING NON-HAZARDOUS AT THE TIME OF DETECTION, BUT REQUIRES SCHEDULED REPAIR BASED ON POSSIBLE FUTURE HAZARD"). GAS DISPATCH, IMMEDIATELY SCHEDULED A FIELD WORK ORDER TO REPAIR THE LEAK. AT 4:38PM THAT SAME AFTERNOON, GAS DISPATCHRECEIVED A CALL FROM THE SERVICE FITTER WHO TOOK THE WORK ORDER TO FIX THE LEAK THAT HE HAD A SERIOUS PROBLEM. HE INFORMED DISPATCH THAT THE HUSE BLEW UPAND WAS ON FIRE. IN ADDITION, HE REQUESTED THAT A CONSTRUCTIONAND REPAIR (C & R) CREW BE SENT TO ASSIST IN TURNING OFF THE GAS SUPPLY TO THE BUILDING. AT APPROXIMATELY 5:15PM, GAS DISPATCH RECEIVED A CALL FROM THE C & R CREW THAT THE GAS SUPPLY TOT HE BUILDING HAD BEEN SHUT OFF AT THE CURB VALVE TO THE BUILDING AND THAT THE FIRE DEPARTMENT NOW HAD CONTROL OF THE FIRE WHICH HAD BEEN THREATENING THE REMAINING 4 ADJACENT UNITES OF THE 6 UNITS APARTMENT COMPLEX. DRUING THE FOLLOWING WEEK OF JANUARY 1, 2006, THE COMPANY CONDUCTED A FORMAL INCIDENT REVIEW PROCESS. AS PART OF THAT REVIEW, A SERIES OF INTERVIEWS WERE CONDUCTED WITH THE EMPLOYEE INVOLVED IN THE INCIDENT AS WELL AS OTHERS WHO ARRIVED AT THE SCENE TO ASSIST THE EMPLOYEE AND/OR THE EMERGENCY CREWS. BASED ON THE RESULTS OF THE REVIEWS, AND STATEMENTS MADE BY THE COMPANY'S SERVICE FITTER INVOLVED IN THE INCIDENT, THE FOLLOWING RECONSTRUCTION OF ACTIONS TAKEN AFTER THE EMPLOYEE ARRIVED TO REMEDIAATE THE LEAK WAS MADE: AFTER ARRIVING AT THE APARTMENT COMPLEX AND VERIFING THE LOCATIONAND PRESENCE OF THE LEAK REPORTED, THE EMPLOYEE MADE SEVERAL ATTEMPTS TO TIGHTEN THE PIPE PLUG, BUT FAILED TO STOP THE LEAK. HE THEN ATTEMPTED TO BACK OFF THE PLUG AND APPLY PIPE DOPE TOT HE THREADED AREA TO CREATE A BETTER LEAK SEAL. HIS FIRST ATTEMPT FAILED TO STOP THE LEAK AND DURING THE SECOND ATTEMPT TO RE-DOPE THE THREADS, THE PIPE PLUG FELL FREE. WITH GAS NOW ESCAPING, HE ATTEMPTED TO RE-THREAD THE PIPE PLUG BACK INTO THE TEE WHILE SIMULTANEOUSLY OPEINING AN ADJACENT WINDOW TO VENTILATE THE ESCAPING GAS. UNABLE TO COMPLETE EITHER TASK, THE BASEMENT ROOM QUICKLY FILLED WITH AN EXPLOSIVE MIXTURE OF GAS. IT IS NOT KNOWN WHAT IGNITED THE MIXTURE, BUT SOURCES OF POTENTIAL IGNITION WERE PRESENT SUCH AS FURNACES AND WATER HEATERS. THE SUBSEQUENT EXPLOSION APPARENTLY KNOCKED HIM TO THE FLOOR AND HIS NEXT RECOLLECTION WAS FINDING HIMSELF LYING ON THE FLOOR LOOKING UP AND SEEING FLAMES ACROSS THE BASEMENT CEILING JOISTS. HE IMMEDIATELY MADE HIS WAY UP THE STAIRS WHERE HE WAS MET BY ONE OF THE RESIDENTS ALREADY EXITING THE BUILDING. EVEN THOUGH EH SUFFERED 2ND DEGREE BURNES PRIMARILY TO HIS FACIAL AREA, HE CONTINUED TO MAKE SURE ALL THE RESIDENCES WERE EVACUATED WHILE MAKING HIS EMERGENCY CALL BACK TO GAS DISPATCH SEEKING HELP. THE FIRE DEPARTMENT, EVENTUALLY RECOGNIZING THE MAN WAS INJURED, LED HIM TO AN EMERGENCY VEHICLE WHERE HE WAS TRASPORTED TO A NEARBY HOSPITAL AND WAS TREATED AND RELEASED THAT SAME EVENING FOR BURN INJURIES. COMPANY ACTONS TAKEN FOLOWING THE INCIDENT TWO SAFETY RELATED INITIATIVES HAVE ALREADY BEEN PUT INTO PLACE: (1) A COMPANY WIDE NOTIFICATION WAS SENT OUT TO ALL GAS OPERATING PERSONNEL ON WEDNESDAY, JANUARY 4TH, 2006 THAT GAS FIELD PERSONNEL WORKING ON INSIDE GAS FACILITIES SHALL NOT DISTURB ANY PIPING THAT DOES NOT HAVE A READILY ACCESSIBLE CONTROL VALVE. MORE SPECIFICALLY: REPAIRS UPSTREAM OF THE REGULATOR-THE U PSTEAM VALVE MUST BE SHUT OFF. FOR REPAIRS DOWNSTEAM OF THE REGULATOR, THE UPSTEAM VALVE MUST BE READILY ACCESSIBLE AND OPERABLE. (2) A SERVICE FITTER REFRESHER TRAINING HAS BEEN IMPLEMENTED. THE TRAINING WILL REVIEW SAFETY PROCEDURES, INCLUDE SCENARIO DISCUSSIONS TO DETERMINE APPROPRIATE FOLLOW-UP ACTIONS, AND INCLUDE A TEST AT THE END AND THE SCORES REVIEWED. ALL TRAINING SESSIONS ARE TO BE COMPLETED BY JANUARY 31, 2006. | 325425 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
293 | 2006-01-23 | CA | other | UNKNOWN (LOS ANGELES COUNTY) | SOUTHERN CALIFORNIA GAS COMPANY | ON JANUARY 23, 2006 A DAMAGED METER SET CAUGHT FIRE AND GAS IGNITED AT THE LOCATION OF 17325 HALSTED STREET, NORTHRIDGE. THE INCIDENT WAS REPORTED TO THE DOT AND CPUC BRANCH DUE TO TOTAL FIRE DAMAGE EXPECTED TO EXCEED $50,000. INVESTIGATIONS BY BOTH THE FIRE DEPARTMENT AND A FIRE INVESTIGATOR HIRED BY SOUTHERN CALIFORNIA GAS COMPANY HAVE BEEN COMPLETED. BOTH OF THESE INVESTIGATIONS DETERMINED THAT THE FIRE LIKELY STARTED AT THE RISER /MSA LOCATION. UPON THE FIRE DEPARTMENT'S ARRIVAL, THE REGULATOR AND MSA WERE NOT ATTACHED TO THE RISER, AND THE RISER WAS BLOWING FULL OPEN. THE FIRE DEPT CLOSED THE RISER AND THEN WORKED ON EXTINGUISHING THE FIRE WHICH HAD SPREAD THROUGHOUT THE HOUSE, LIKELY VIA THE ATTIC. UPON THE GAS COMPANY'S ARRIVAL, THE GAS WAS ALREADY SHUT OFF, AND WE WERE NOT GRANTED ACCESS TO THE PROPERTY UNTIL FIREFIGHTING EFFORTS WERE COMPLETED. IT IS STILL UNKNOWN HOW THE MSA AND REGULATOR WERE KNOCKED OFF THE RISER, ALLOWING GAS TO ESCAPE AT DISTRICT PRESSURE (APPROX 40 TO 50 PSI.) THE MSA WAS IN A LOCATION THAT WOULD NOT ALLOW A STRIKE BY VEHICULAR TRAFFIC . THERE IS SPECULATION THAT HIGH WINDS MAY HAVE BLOWN SOMETHING AGAINST THE MSA, BUT THIS COULD NOT BE SUBSTANTIATED. IT IS ALSO UNDETERMINED AS TO WHAT WAS THE SOURCE OF IGNITION. ALL GAS COMPANY FACILITIES HAVE BEEN REPAIRED. FOR ANY FURTHER QUESTIONS, CONTACT JEFF KOSKIE AT 213-244-3283 | 200500 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
294 | 2006-01-25 | MN | other | UNKNOWN (RAMSEY COUNTY) | NORTHERN STATES POWER COMPANY DBA XCEL ENERGY | VEHICLE STRUCK DUAL METER SET, SHEARING OFF ANODELESS RISERS AT GRADE LEVEL AND ALLOWING GAS TO ESCAPE IN TO RESIDENCE. ESCAPING GAS IGNITED CAUSING FIRE AND SECONDARY EXPLOSION. | 180000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
295 | 2006-01-31 | MI | other | UNKNOWN (MACOMB COUNTY COUNTY) | SEMCO ENERGY GAS COMPANY |  | 904050 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
296 | 2005-04-11 | CA | other | UNKNOWN (ORANGE COUNTY COUNTY) | SOUTHERN CALIFORNIA GAS COMPANY | ON APRIL 11, 2005 A METER SET ASSEMBLY WAS DAMAGED WHEN A DRIVER LOST CONTROL OF HIS VEHICLE ON THE ROADWAY, COMING TO REST ON A METER SET ASSEMBLY. THIS METER SET ASSEMBLY IS LOCATED 45¿ OFF THE ROADWAY. ESCAPING GAS FROM THE DAMAGED METER SET ASSEMBLY IGNITED, CAUSING APPROXIMATELY $100K DAMAGE TO THE HOME. NO INJURIES WERE ATTRIBUTED IN ANY WAY TO THE ESCAPING GAS OR RESULTING FIRE.. THIS INCIDENT BECAME REPORTABLE TO THE DOT AND CPUC BASED UPON THE DOLLAR VALUE OF THE FIRE. NOTE: DURING INTERNAL AUDIT, THIS REPORT WAS FOUND TO BE MISSING FROM OPS DATABASE. THE REPORT WAS PROVIDED TO CALIFORNIA PUBLIC UTILITIES COMMISION ON MAY 9, 2005, BUT SOCAL RECORDS DO NOT INDICATE A COPY WAS FORWARDED TO OPS AS WELL. | 101000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
297 | 2003-04-26 | CA | other | UNKNOWN (FRESNO COUNTY COUNTY) | SOUTHERN CALIFORNIA GAS COMPANY | ¿ ON APRIL 26, 2003, A VEHICLE ACCIDENT OCCURRED AT THE INTERSECTION OF NEBRASKA AVE. AND ACADEMY AVE. IN THE CITY OF SELMA. THE COLLISION CAUSED ONE VEHICLE TO CAREEN OFF THE ROAD AND STRIKE A BARRICADED METER SET ASSEMBLY, BREAKING PIPING ABOVE THE LOW PRESSURE SIDE OF THE DOMESTIC REGULATOR. THE ESCAPING GAS IGNITED, BURNING AN INDIVIDUAL IN THE VEHICLE. ¿ SOCALGAS RESPONDED, CONTROLLING THE GAS AND REPAIRING THE DAMAGED METER SET ASSEMBLY, AND REPLACING DAMAGED BARRICADES. SERVICE TO CUSTOMER WAS RESTORED. ¿ INTERNAL INVESTIGATION CONCLUDED THAT THIS INCIDENT WAS RESULT OF AUTOMOBILE ACCIDENT THAT SENT 2 VEHICLES OFF-ROAD AND INTO AN ADJACENT GRAPE VINEYARD. ONE VEHICLE DROVE THROUGH STOP SIGN AND THROUGH GUARD RAILS TO STRIKE METER SET ASSEMBLY THAT WAS PLACED OFF THE ROADWAY ADJACENT TO ROWS OF GRAPEVINES. ¿ THE CALIFORNIA PUBLIC UTILITIES COMMISSION SAFETY AND RELIABILITY SECTION IS SCHEDULED TO PERFORM AN ON-SITE INVESTIGATION ON OR ABOUT JANUARY 6TH, USING PHOTOS AND POLICE REPORT MEASUREMENTS. THE METER SET ASSEMBLY WAS SUBSEQUENTLY REMOVED IN THE YEAR FOLLOWING THE INCIDENT, WHEN, UNRELATED TO THE INCIDENT, THE PROPERTY OWNER ELECTED TO DISCONTINUE SERVICE RATHER THAN MAKE REPAIRS TO A LEAKING YARD LINE. THIS INCIDENT WAS REPORTED LATE TO THE DOT AND CPUC AS A RESULT OF ERRORS IN COMMUNICATING INCIDENT SPECIFICS. OUR INVESTIGATION INDICATES THAT ONE OR MORE EMPLOYEE ERRORS COMBINED TO RESULT IN FAILURE TO REPORT BACK WHEN THE INCIDENT OCCURRED, AND WHEN THE INCIDENT WAS BROUGHT TO SAFETY DEPARTMENT¿S ATTENTION AS THE RESULT OF A LAWSUIT PRODUCTION OF DOCUMENTS REQUEST LAST MONTH, A REPORT WAS IMMEDIATELY FILED. ISSUES SURROUNDING THE LATE REPORT HAVE BEEN REVIEWED, AND CORRECTIVE ACTION TAKEN. A FULL REPORT OF CIRCUMSTANCES AND CORRECTIVE ACTIONS HAS BEEN PROVIDED TO THE CPUC SAFETY AND RELIABILITY SECTION. NOTE: DURING INTERNAL AUDIT, THIS REPORT WAS FOUND TO BE MISSING FROM OPS DATABASE. THE REPORT WAS PROVIDED TO CALIFORNIA PUBLIC UTILITIES COMMISION ON JANUARY 5, 2006, BUT SOCAL RECORDS DO NOT INDICATE A COPY WAS FORWARDED TO OPS AS WELL. | 3000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
298 | 2006-01-26 | OH | sabotage | UNKNOWN (FRANKLIN COUNTY) | COLUMBIA GAS OF OHIO INC. | A THIRD PARTY EXCAVATOR INSTALLING CONDUIT, DIRECTIONAL BORED INTO A COLUMBIA GAS OF OHIO,INC. 4-INCH PLASTIC GAS MAIN. THE EXTENT OF THE DAMAGE REQUIRED COLUMBIA GAS OF OHIO,INC. TO SHUT DOWN AND ISOLATE THE DAMAGED PORTION OF THE MAIN TO SAFELY MAKE THE REPAIR TO OUR FACILITY. THE ISOLATION OF THE DAMAGED PORTION OF THE MAIN RESULTED IN A GAS DISRUPTION TO 797 CUSTOMERS. | 55383 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
299 | 2005-11-15 | IN | other | UNKNOWN (MONROE COUNTY) | COMMUNITY NATURAL GAS CO. INC. | FIRE STAARTED NEAR ELECTRICAL SERVICE BOX IN GARAGE AT APPROX. 1:10AM. RESIDENCE WAS APPROX. 40 YRS OLD AND UNOCUPIED AT TIME OF FIRE. ROOF COLLAPSE CAUSED DAMAGE TO 1" BLACK STEEL PIPE CAUSING SOME GAS TO ESCAPE. FIRE WAS PUT OUT IN APPROX. 1HR. METER ON OUTSIDE WAS ALSO DAMAGED BY FIRE. METER WAS PULLED AT 2:30AM. SERVICE LINE WAS DISCONNECTED AND CAPPED | 60450 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
300 | 2004-12-01 | NY | maintenance | UNKNOWN (SUFFOLK COUNTY) | KEYSPAN ENERGY DELIVERY LONG ISLAND | WORKING FIRE REPORTED BY SUFFOLK COUNTY CENTRAL FIRE DISPATCH #6. UPON KEYSPAN ENERGY ARRIVAL GAS READINGS WERE OBTAINED AT THE FOUNDATION AND MIDPOINT OF THE SERVICE. IN ADDITION, SEVERE DAMAGE WAS DISCOVERED AT THE REAR OF THE BUILDING. THERE WERE 16 INDIVIDUALS IN THE HOUSE AT THE TIME OF THE INCIDENT, AND 1 MINOR INJURY WAS REPORTED. LUCIUS PITKIN,INC..,CONSULTING ENGINEERS, CONDUCTED AN EVALUATION OF THE PIPE AT THIS INCIDENT. THEIR FINDINGS CONCLUDED THAT THE CAUSE OF FAILURE WAS CLASSIC STRAY CURRENT ADJACENT RAILROADTRACKS WITH ROCK IMPINGEMENT. | 150000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
301 | 2004-10-12 | NY | leaks and spills | UNKNOWN (SUFFOLK COUNTY) | KEYSPAN ENERGY DELIVERY LONG ISLAND (KEYSPAN GAS EAST CORP, DBA) | ONE 1 BUILDING AND NUMEROUS AUTOMOBILES SUSTAINED DAMAGE FROM A DISTURBANCE AND ENSUING FIRE. THERE WERE 9 NINE INDIVIDUALS IN THE BUILDING AT THE TIME OF THE INCIDENT,WITH ONE REPORTED INJURY. GAS TECHNOLOGY INST. CONDUCTED THE EVALUATION OF THE PIPE REMOVED AT THIS INCIDENT. LAB ANALYSIS DETERMINED THE ROOT CAUSE OF THE FAILURE WAS THE QUALITY OF BUTT FUSION JOINT AND EXTERNAL LOADING COULD HAVE CONTRIBUTED TO THE SLOW CRACK GROWTH RATE. | 550000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
302 | 2004-12-03 | NY | sabotage | UNKNOWN (SUFFOLK COUNTY) | KEYSPAN ENERGY DELIVERY LONG ISLAND | LAURELWOOD LANDSCAPING CONSTRUCTION INC. ( SUBCONTRACTOR TO NEWBORN CONSTRUCTION ) DAMAGED AN 8¿ HIGH PRESSURE PLASTIC GAS MAIN ON ROUTE 25 IN CUTCHOGUE. AS A RESULT OF THIS DAMAGE, GAS SERVICE WAS INTERRUPTED TO OVER 1,800 CUSTOMERS. THE OPERATOR DAMAGE ESTIMATE INCLUDES COST FOR RESPONSE,RECOVERY AND RESTORATION. NYS PSC ISSUED A CITATION TO THE SUBCONTRACTOR, LAURELWOOD LANDSCAPING CONSTRUCTION INC FOR VIOLATION OF CODE SECTION 16 NYCRR PART 753-3.1A AND 753-3.6 | 1002720 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
303 | 2006-01-21 | TX | sabotage | UNKNOWN (HARRIS COUNTY) | CENTERPOINT ENERGY | THIRD PARTY DAMAGED A 4" I.P. POLY GAS MAIN WITH A BORING TOOL WHILE INSTALLING CONDUIT FOR WATER LINE. HOUSTON FIRE DEPARTMENT AND POLICE DEPARTMENT BLOCKED HOUSTON CENTER BLVD. FROM RICHMOND AVE. SOUTH TO WEST PARK DR. *ORIGINALLY TELEPHONICALLY REPORTED AS 12606 OLD WESTHEIMER RD., BUT WAS LATER CORRECTED TO 12606 HOUSTON CENTER BLVD. | 85485 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
304 | 2006-01-18 | TX | leaks and spills | UNKNOWN (DALLAS COUNTY) | ATMOS ENERGY CORPORATION., MID TEX DIVISION | A CUSTOMER SERVICE TECHNICIAN INVESTIGATING A REPORTED LEAK WAS BAR TESTING NEAR A METER. THE BAR TEST HOLE PROVIDED AN ENHANCED AVENUE FOR THE GAS ESCAPING FROM THE EXISTING LEAK TO VENT THE ATMOSPHERE. THE ESCAPING GAS WAS IGNITED BY A SPARK FROM AN OVERHEAD ELECTRIC METER, WHICH RESULTED IN A FIRE AT A RESIDENCE. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
305 | 2006-02-14 | NV | sabotage | UNKNOWN (CLARK COUNTY) | SOUTHWEST GAS CORP. | WHILE DIGGING WITH A BACKHOE TO INSTALL POWER CONDUIT, AN OPERATOR FOR ACME ELECTRIC HIT AND DAMAGED A 2" PE DISTRIBUTION MAIN WITH TWO-WAY FEED. SEVERAL SOURCES OF IGNITION WHERE PRESENT AND IGNITION OCCURRED PRIOR TO SWG CREWS ARRIVING ON THE SCENE. AVALENO CHAVEZ, THE OPERATOR OF THE BACKHOE, WAS INJURED AND TRANSPORTED TO A LOCAL HOSPITAL. HE WAS TREATED FOR 2ND DEGREE BURNS TO HIS HANDS AND NECK AREA AND RELEASED FEB. 16 2006. THE EXCAVATOR DID HAVE A VALID LOCATE TICKET. THERE WERE 3,931 THERMS OF GAS LOSS. THERE WERE NO FATALITIES AS A RESULT OF THIS INCIDENT. UPDATE 02/20/2009 - FINAL REPORT THE TYPE OF LEAK HAS BEEN UPDATED FROM A FOUR INCH DIAMETER PUNCTURE TO A FIVE INCH LONGITUDINAL TEAR UNDER ITEM NUMBER FOUR, TYPE OF LEAK OR RUPTURE, UNDER PART A. | 9432 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
306 | 2006-02-20 | CA | leaks and spills | UNKNOWN (IMPERIAL COUNTY) | SOUTHERN CALIFORNIA GAS COMPANY | ON FEBRUARY 20, 2006, GAS FROM A LEAKING 2¿ PLASTIC MEDIUM PRESSURE MAIN AT THE INTERSECTION OF CROSS ROAD AND ATEN, CITY OF IMPERIAL WAS IGNITED BY A CATERING TRUCK PASSING OVER THE LOCATION. THE RESULTING FIRE DESTROYED THE CATERING TRUCK AND CONTENTS. NO INJURIES RESULTED FROM THIS INCIDENT. THE LEAK OCCURRED WHEN A BUTT FUSION FROM THE 2¿ PIPING TO A 2¿ X 4¿ REDUCER FITTING FAILED. THE MAIN WAS REPAIRED, AND NO CUSTOMERS WERE PUT OUT OF SERVICE. THIS INCIDENT BECAME REPORTABLE TO THE CPUC AND DOT WHEN THE TOTAL VALUE OF DAMAGE AND REPAIRS WAS DETERMINED TO EXCEED $50,000. AN INVESTIGATION OF THE FAILURE DETERMINED THAT THE FUSION¿S THERMAL TRANSFER WAS IMPACTED BY SOME FOREIGN MATERIAL (DUST OR HAND NATURAL OIL). THIS WAS BY VISUAL EXAMINATION AND A CONSENSUS OF OPERATIONAL EXPERTS. THE EMPLOYEE WHO PERFORMED THIS FUSION HAD RETIRED FROM THE GAS COMPANY PRIOR TO THIS INCIDENT. SUBSEQUENT TO THIS INCIDENT, MEETINGS WITH EMPLOYEES WERE CONDUCTED TO REINFORCE THE IMPORTANCE OF VERIFYING IRON TEMPERATURE, AND PROPER HANDLING AND CLEANING OF FUSION MATERIAL. ADDITIONALLY, 400' OF THE PIPE ON BOTH SIDES OF DAMAGE WAS LEAK SURVEYED, AND ALL EXPOSED FUSIONS WERE VISUALLY INSPECTED. NO LEAKAGE OR VISUAL INSPECTION ANOMALIES WERE OBSERVED. FOR ANY FURTHER QUESTIONS, CONTACT JEFF KOSKIE AT 213-244-3283. | 55000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
307 | 2006-03-01 | LA | sabotage | UNKNOWN (LAFOURCHE COUNTY) | SOUTH COAST GAS CO. |  | 2926 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
308 | 2006-02-22 | LA | sabotage | UNKNOWN (LAFOURCHE COUNTY) | SOUTH COAST GAS CO. |  | 567 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
309 | 2006-02-27 | LA | sabotage | UNKNOWN (LAFOURCHE COUNTY) | SOUTH COAST GAS CO. |  | 222 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
310 | 2005-12-19 | KS | sabotage | UNKNOWN (NEOSHO COUNTY) | KANSAS GAS SERVICE | ALLEN CONSTRUCTION WAS IN THE PROCESS OF INSTALLING PIPE USING A LARGE TRACK ROCK TRENCHER FOR THE EXCAVATION WHEN THEY HIT OUR GAS LINE. ACCORDING TO THE KANSAS ONE CALL LOCATE TICKET #5458642 AND OUR GPLS LOCATOR THE REQUEST WAS FROM HWY 59 AND HWY 39, GO EAST FOR 5 OR 6 MILES ON HWY 39 TO 20TH ROAD, THEN GO NORTH FOR 1 MILE ON 20TH ROAD TO EAGLE ROAD.MARK FROM THE SW CORNER OF THE INTERSECTION GOING NE FOR 300 FT. TO THE NE CORNER OF INTERSECTION. THE PROBLEM WAS OUR GAS LINE WAS HIT 25' SOUTH AND WEST OF THE SW CORNER OF THE INTERSECTION AND THE LOCATE WOULD NOT HAVE COVERED THE AREA WHERE OUR PIPE WAS HIT. | 85672 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
311 | 2006-03-05 | NY | sabotage | UNKNOWN (ULSTER COUNTY) | CENTRAL HUDSON GAS & ELECTRIC CORPORATION | THE PORT EWEN WATER DEPARTMENT WAS EXCAVATING TO REPAIR A WATER MAIN LEAK IN FRONT OF 150 WEST MAIN STREET IN PORT EWEN ON MARCH 5, 2006. THE WATER DEPARTMENT, UTILIZING AN EXCAVATOR, STRUCK THE 3/4" STEEL NATURAL GAS SERVICE LINE OPERATING AT 30 PSIG. THE SERVICE LINE SEPARATED AT A JOINT INSIDE THE BUILDING WALL AND IT WAS PULLED THROUGH THE BUILDING WALL. A MARK-OUT REQUEST HAD BEEN CALLED IN BY THE PORT EWEN WATER DEPARTMENT SUPERINTENDENT FOR A WATER MAIN LEAK ON WEST MAIN STREET BETWEEN BROADWAY (RT. 9W) AND GREEN AND A CENTRAL HUDSON GAS MECHANIC RESPONDED TO MARK-OUT GAS FACILITIES AT THE SITE. PRELIMINARY RESULTS OF THE COMPANY'S INVESTIGATION HAVE REVEALED THAT THE WATER DEPARTMENT PREMATURELY PROCEEDED WITH THE EXCAVATION PRIOR TO COMPLETION OF THE MARK-OUT. CENTRAL HUDSON PERSONNEL WERE ATTEMPTING TO CLOSE THE CURB VALVE SERVING 150 WEST MAIN STREET AND SUBSEQUENT TO POWER DISCONNECTION BY CENTRAL HUDSON PERSONNEL ON SITE, THE HOUSE EXPLODED. CENTRAL HUDSON AND PSC STAFF PERSONNEL ARE CURRENTLY INVESTIGATING THIS INCIDENT. | 300000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
312 | 2006-02-21 | FL | maintenance | UNKNOWN (BREVARD COUNTY) | FLORIDA CITY GAS | FCG WAS NOTIFIED OF A LEAK ON A 6'' STEEL LINE OPERATING AT APPROX 57 PSI CROSSING UNDER INDIAN RIVER. THE LEAK WAS FOUND TO BE LOCATED APPROX 500'SOUTH OF THE SR 520 BRIDGE AND APPROX 2000' FROM EITHER SHORE. A COURTESY CALL WAS MADE TO THE NATIONAL RESPONSE CENTER AS THE EXACT NATURE OF THE SITUATION WAS NOT KNOWN. DIVERS WERE BROUGHT IN TO DIRECTLY EXAMINE THE LINE AND FOUND THE LEAK SOURCE TO BE A COUPLING FROM THE ORIGINALINSTALLATION. THE LEAK WAS JUDGED TO BE NON-HAZARDOUS. ENGINEERING MODELS SHOWED THAT CUSTOMER OUTAGES COULD OCCUR IF THIS LINE WERE SHUT DOWN UNDER THE CURRENT COOL WETHER CONDITIONS. DUE TO THE LOCATION AND CLASSIFICATION OF THE LEAK, AND THE MODEL RESULTS, FCG DECIDED TO WAIT SEVERAL WEEKS FOR WARMER WEATHER TO ALLOW A PERMANENT REPAIR TO BE MADE WITHOUT CAUSING INTERRUPTIONS TO CUSTOMERS. A SUPPLEMENTAL REPORT WILL BE SENT WHEN MORE INFORMATION IS AVAILABLE FOLLOWING THE REPAIR. THE FOLLOWING PRECAUTIONARY ACTIONS ARE BEING TAKEN UNTIL REPAIRS ARE MADE:.MARK SITE WITH WARNING BUOYS.VISUALLY INSPECT THE SITE TWICE DAILY .MONITOR PRESSURE AND FLOW 24/HOUR DAY.FULLY DEVELOP REPAIR SCENARIOS AND SECURE MATERIALS FOR MULTIPLE REPAIR TECHNIQUES..FULLY DEVELOP ALTERNATIVE NEW CONSTRUCTION OPTIONS AS CONTIGENCY TO THE REPAIR BEING UNFEASIBLE..SCHEDULE ADDITIONAL UNDERWATER ASSESSMENT WHEN LONG RANGE WEATHER FORECASTS INDICATES LOW LIKELIHOOD OF COLD WEATHER SCENARIOS..COMPLETELY EXPOSE PIPE IN AREA TO FURTHER ASSESS REPAIR OPTIONS.. UPDATE U.S. COAST GUARD IF SITUATION CHANGES OR AT LEAST WEEKLY.KEEP FWC UP-TO -DATE ON THE SITUATION. | 60000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
313 | 2006-04-02 | AK | other | UNKNOWN (MATANUSKA SUSITNA BOROUGH COUNTY) | ENSTAR NATURAL GAS COMPANY | ENSTAR NATURAL GAS COMPANY WAS NOTIFIED OF A RESIDENTIAL STRUCTURE FIRE AT 2850 S. TEELAND STREET, WASILLA AK AT 10:07PM AST ON 4/2/06. THE FIRE CAUSED ENSTAR'S HDPE SERVICE LINE TO MELT INSIDE THE STEEL RISER, RELEASING NATURAL GAS. THE SERVICE LINE WAS DUG UP AND PINCHED OFF TO STOP THE FLOW OF GAS. NATURAL GAS DID NOT CAUSE OR CONTRIBUTE TO THE FIRE. | 50550 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
314 | 2006-03-21 | OK | other | UNKNOWN (KAY COUNTY) | CENTERPOINT ENERGY | AT APPROX 2:41AM ON MARCH 21ST 2006, CENTERPOINT ENERGY WAS NOTIFIED OF ZERO GAS PRESSURE AT THE BLACKWELL AND TONKAWA OKLAHOMA TOWN BORDER STATIONS. CENTERPOINT ENERGY PIPELINE SERVICES, THE SUPPLIER FOR CENTERPOINT ENERGY, OK ADVISED THAT A METERING STATION LOCATED AT THE OKLAHOMA/KANSAS STATE LINE MALFUNCTIONED, CAUSING TOTAL PRESSURE LOSS TO TONKAWA/BLACKWELL BORDER STATIONS. GAS SERVICES WERE DISCONTINUED AT BLACKWELL AND TONKAWA,OK STARTING AT 3 PM ON MARCH 21ST 2006. TOTAL CUSTOMERS AFFECTED IN BLACKWELL WERE 3,205 AND IN TONKAWA WERE 1371. AL METERS WERE TURNED OFF BY 230 AM ON MARCH 22,2006. PRESSURIZATION AND PURGING WAS COMPLETED BY 3:30 AM ON MARCH 22,2006. RESTORATION OF SERVICES BEGAN AT 3:30 AM ON MARCH 22,2006 AND THE MAJORITY OF SERVICES WERE RESTORED BY 10:00 PM ON MARCH 24,2006. | 55000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
315 | 2006-04-07 | AK | other | UNKNOWN (MATANUSKA SUSITNA BOROUGH COUNTY) | ENSTAR NATURAL GAS COMPANY | ON FRIDAY, APRIL 7, 2006 AT 1:01 PM ADT, ENSTAR NATURAL GS COMPANY WAS NOTIFIED OF A RESIDENTIAL STRUCTURE FIRE AT LOT 7, BLOCK 5 EAGLE ESTATES IN PALMER, ALASKA. HEAT FROM THE FIRE CAUSED ENSTAR'S HDPE SERVICE LINE RISER TO MELT, RELEASING NATURAL GAS. THE SERVICE LINE WAS DUG UP AND PINCHED OFF TO STOP THE FLOW OF NATURAL GAS. NATURAL GAS DID NOT CAUSE OR CONTRIBUTE TO THE FIRE. | 226050 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
316 | 2006-03-10 | IL | other | UNKNOWN (COOK COUNTY) | PEOPLES GAS LIGHT & COKE CO | DATA COLLECTION TEAM - 06/30/2014 THE PEOPLES GAS LIGHT AND COKE COMPANY HAS COMPLETED ITS INVESTIGATION OF THE INCIDENT AT 3211 SOUTH WOOD STREET, CHICAGO, IL. AT APPROX. 1:10P.M. ON MARCH 10,2006, AN EXPLOSION OCCURRED AT 3211 S.WOOD IN CHICAGO, IL ("PREMISES"), A SITE WITH TWO SEPARATE BUILDINGS HOUSING A COMPANY ENGAGED IN PRODUCING ROOFING COATINGS AND MASTICS AND WATERPROOFING COATINGS AND CHEMICAL TREATMENTS. THE EXPLOSION DESTROYED ONE BUILDING AND DAMAGED THE OTHER. PEOPLES GAS RECEIVED A CALL COMPLAINING OF A NATURAL GAS LEAK AT THE PREMISES AT 1233PM MARCH 10,2006, AND A SERVICE PERSON DISPATCHED TO THE SCENE BY PEOPLES GAS REPORTED BEING PRESENT WHEN THE EXPLOSION OCCURRED. AN INVESTIGATION INTO THE CAUSE OF THE OCCURRENCE IS UNDERWAY. AFTER THE OCCURENCE AND DURING THE COURSE OF THE INVESTIGATION TO DATE , PEOPLES GAS FOUND THAT THE PLASTIC SERVICE WAS SEPARATED FROM THE SERVICE HEAD ADAPTER ON THE SERVICE LINE INSIDE THE BUILDING. THE INVESTIGATION IS CONTINUING. AT THIS POINT, THERE HAS BEEN NO FINAL DETERMINATION OF THE CAUSE AND ORIGIN OF THE EXPLOSION AND THE SOURCE OF IGNITION. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
317 | 2006-03-13 | OH | sabotage | UNKNOWN (BUTLER COUNTY) | DUKE ENERGY,OHIO | A PLUMBING CONTRACTOR AUGERING A SEWER LATERAL STRUCK A GAS SERVICE CAUSING GAS TO MIGRATE INTO THE HOME, RESULTING IN AN EXPLOSION. | 150000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
318 | 2006-03-09 | IN | natural disasters | UNKNOWN (JACKSON COUNTY) | INDIANA GAS CO INC | A VECTREN SIX INCH STEEL DISTRIBUTION LINE THAT CROSSES UNDER THE WHITE RIVER NORTH OF SEYMOUR, INDIANA DEVELPOED A LEAK AND RELEASED GAS THROUGH THE WATER INTO THE ATMOSPHERE REQUIRING IT TO BE SHUT DOWN. WHEN HIGH WATERS RECEDED ENOUGH TO SAFELY ALLOW FOR AN INVESTIGATION, IT WAS DISCOVERED THE PIPELINE WAS DAMAGED AND SEVERED APPARENTLY DUE TO DEBRIS BEING FORCED DOWN THE RIVER AS A RESULT OF SEVERE FLOODING IN THE AREA. | 2017130 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
319 | 2006-03-08 | TX | sabotage | UNKNOWN (HARRIS COUNTY) | CENTERPOINT ENERGY | THIRD PARTY DAMAGE TO 16" HP STEEL MAIN WITH TRACKHOE PACE SERVICE LP 281 256-2201. | 149568 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
320 | 2005-08-29 | LA | natural disasters | UNKNOWN (ORLEANS COUNTY) | ENTERGY NEW ORLEANS, INC - GAS DISTRIBUTION BUSINESS | EXPLANATION OF 5.C ABOVE RESTORATION (COST TO GET CURRENT SYSTEM OPERATIONAL) $107,263,900 LOSS PRODUCT (NATURAL GAS) $4,000,000 REPLACEMENT OF PIPE/INFRASTRUCTURE $355,254,217 GAS SERVICE HAS BEEN RESTORED AND IS AVAILABLE TO ALL FLOODED AREAS WITHIN OUR SYSTEM EXCEPT WHERE THE LEVEE BREECHES OF THE 17TH STREET CANAL AND THE INDUSTRIAL CANAL FLOODED LAKEVIEW AND THE LOWER 9TH WARD, RESPECTIVELY; AND WHERE STORM SURGE RAZED THE LAKE CATHERINE COMMUNITY. THESE AREAS WILL REQUIRE EXTENSIVE REPAIR AND RECONSTRUCTION BEFORE THEY CAN BE REPOPULATED. ENTERGY NEW ORLEANS GAS IS COMPLETING TURN-ONS AS SOON AS RETURNING CUSTOMERS REPAIR, RESTORE, AND REMODEL THEIR HOMES, AND REQUEST SERVICE. THE REPLACEMENT OF PIPE AND INFRASTRUCTURE MENTIONED ABOVE IS BEING PLANNED AND WILL HAPPEN OVER THE NEXT SEVERAL YEARS. | 466518117 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
321 | 2005-11-22 | GA | natural disasters | UNKNOWN (FULTON COUNTY) | ATLANTA GAS LIGHT COMPANY | A POWER LINE FELL IN WINDY CONDITIONS AND ENERGIZED A WATER DEPARTMENT VAULT WHICH IN TURN CAUSED ARCING BETWEEN THE WATER LINE AND A 2" STEEL GAS LINE SERVING THE GREENBRIAR COMMONS APARTMENT COMPLEX. THE ARCING BURNED 3 HOLES IN THE GAS SERVICE AT A POINT OF CLOSE CONTACT BETWEEN THE TWO FACILITIES. GAS FLOWED BACK INTO THE WATER DEPARTMENT VAULT AND WAS IGNITED. THE ELECTRIFIED GAS SERVICE ALSO CREATED A SECOND FIRE AT GAS METERS ON THE OUTSIDE OF ONE OF THE APARTMENT BUILDINGS. THE GAS LINE WAS INSTALLED IN 1987 AND THE WATER LINE WAS INSTALLED IN 2004. THE WATER FACILITY WAS NOT INSTALLED WITH ADEQUATE SEPARATION FROM THE GAS LINE WHICH CONTRIBUTED TO THE INCIDENT. | 18750 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
322 | 2004-09-17 | PA | natural disasters | UNKNOWN (ALLEGHENY COUNTY) | EQUITABLE GAS CO | AN 10 INCH STEEL GAS MAIN FAILED AS A RESULT OF HEAVY RAINS. PIPELINE SECTION IS PHYSICALLY SEPARATED AND ABANDONED. | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
323 | 2004-09-17 | PA | natural disasters | UNKNOWN (ALLEGHENY COUNTY) | EQUITABLE GAS CO | AN 8 INCH STEEL GAS MAIN FAILED AS A RESULT OF HEAVY RAINS. PIPELINE SECTION IS PHYSICALLY SEPARATED AND ABANDONED. | 240000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
324 | 2006-03-24 | UT | natural disasters | UNKNOWN (SUMMIT COUNTY) | QUESTAR GAS COMPANY | A 3/4¿ NIPPLE FITTING (LOCATED BENEATH THE SERVICE REGULATOR) ON A METER SET CRACKED ON THE THREADS DUE TO HEAVY SNOW ACCUMULATION ON QUESTAR GAS COMPANY¿S NATURAL GAS METER AT 6871 SADDLE CT, PARK CITY, UTAH. THE ESCAPING GAS FROM THE CRACKED NIPPLE FITTING MIGRATED INTO THE RESIDENCE AND WAS IGNITED. IT IS POSSIBLE THAT THE GAS MIGRATED INTO THE RESIDENCE BY A COMBUSTION AIR INTAKE OR A DRYER VENT THAT WAS IN CLOSE PROXIMITY TO WHERE THE METER WAS LOCATED. THE RESULTING IGNITION CAUSED AN EXPLOSION WHICH CAUSED DAMAGE TO THE RESIDENCE. THE PARK CITY FIRE DEPARTMENT RESPONDED TO THIS LOCATION AND PUT OUT THE FIRE. QUESTAR GAS PERSONNEL WERE DISPATCHED IMMEDIATELY TO THE SCENE AFTER RECEIVING THE INITIAL PHONE CALL FROM THE PARK CITY FIRE DEPARTMENT. UPON ARRIVAL, QUESTAR¿S FIRST RESPONDER SHUT OFF GAS AT THE SERVICE VALVE TO SECURE THE SCENE. | 101210 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
325 | 2006-04-21 | FL | natural disasters | UNKNOWN (ALACHUA COUNTY) | GAINESVILLE REGIONAL UTILITIES - GAS | AT 1752, ON 04/21/06, GRU SYSTEM CONTROL DISPATCHED THE ON CALL GAS WORKER TO A REPORTED LEAK AT 3455 NW 50TH AVE. IN GAINESVILLE FLORIDA. THE GAINESVILLE FIRE DEPARTMENT WAS ON THE SCENE AND HAD EXTINGUISHED A SMALL FIRE AT THE BASE OF A TREE THAT HAD BEEN STRUCK BY LIGHTNING. THE CURRENT TRACKED DOWN THE TREE AND ONTO THE TRACER WIRE. WHERE THE WIRE WAS CLOSE TO THE 1/2" CTS POLY SERVICE, IT BURNED A SMALL HOLE IN THE SERVICE. AT 1852, OUR GAS WORKER HAD DUG THE SERVICE IN A REMOTE LOCATION AND SQUEEZED IT OFF. THEY THEN DUG UP THE LEAK AREA AND MADE REPAIRS. GAS WORKER DEPARTED THE SCENE AT 2007 ON 4/21/06. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
326 | 2006-04-04 | TX | other | UNKNOWN (BOWIE COUNTY) | CENTERPOINT ENERGY | THE HOME LOCATED AT 23 SARAH LANE,RED LICK, TEXAS, CAUGHT FIRE AND WAS BELIEVED TO BE A COMPLETE LOSS. THE INCIDENT WAS REPORTED BASED ON THE ESTIMATED PROPERTY DAMAGE OF APPROXIMATELY $100,000. GAS SERVICE TO THE RESIDENCE WAS ACTIVE AT THE TIME OF THE INCIDENT BUT IS NOT BELIEVED TO HAVE BEEN A FACTOR IN THE CAUSE OF THE FIRE. | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
327 | 2006-04-11 | PA | other | UNKNOWN (nan COUNTY) | PECO ENERGY CO | A VEHICLE WAS TRAVELING NORTH ON ROUTE 152 (LIMEKILN PIKE ) FAILED TO TURN LEFT AT THE TRAFFIC SIGNAL AT ROUTE 202 (BUTLER AVE.) AND PROCEEDED INTO THE EXIT AREA OF THE PROPERTY IMPACTING THE SOUTH SIDE OF THE BUILDING, BALLARD AND GAS ROTARY METER SET. GAS ESCAPING FROM THE DAMAGED METER SET IGNITED. | 75000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
328 | 2006-03-21 | NY | sabotage | UNKNOWN (nan COUNTY) | ROCHESTER GAS & ELECTRIC | ON 3-21-2006 AT 11:38 AM A CALL WAS RECEIVED BY RG&E FROM THE ROCHESTER FIRE DEPT INDICATING AN INCIDENT HAD OCCURRED AT 68 AKRON ST IN THE CITY OF ROCHESTER. THE CONTRACTOR (R.P. MYERS) WAS DIGGING ADJACENT TO THE MAIN AS PART OF THE CAST IRON MAIN REPLACEMENT PROJECT ON AKRON ST WHEN THE SERVICE FOR THIS ADDRESS WAS DAMAGED, RESULTING IN A BREAK AT THE SERVICE TEE. THE CONTRACTOR CREW ATTEMPTED TO REPAIR THIS BREAK BY UNDERCUTTING THE SIDEWALK TO GAIN ACCESS AND WHILE THE JOB FOREMAN WAS UNDER THE SIDEWALK ATTEMPTING THIS REPAIR, HE APPARENTLY BECAME ASPHYXIATED. A MEMBER OF HIS CREW FOUND THAT HE WAS NON-RESPONSIVE, REMOVED HIM FROM THE AREA AND CALLED 911. ON SCENE PERSONNEL FOUND HIM AND HE APPEARED TO BE NOT BREATHING AND WITHOUT PULSE. CPR WAS PERFORMED BY CONTRACTOR CREW MEMBERS ON SCENE UNTIL THE AMBULANCE CREW ARRIVED. THE INDIVIDUAL WAS REVIVED AND THEN TAKEN TO STRONG MEMORIAL HOSPITAL. | 1250 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
329 | 2006-05-02 | TN | natural disasters | UNKNOWN (DICKSON COUNTY) | GREATER DICKSON GAS AUTHORITY | LIGHTING HIT GAS METER CAUSING THE GAS TO IGNITE WHICH SET HOUSE ON FIRE. | 60480 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
330 | 2006-04-06 | CA | other | UNKNOWN (MERCED COUNTY) | PACIFIC GAS & ELECTRIC CO | OUT OF CONTROL VEHICLE RAN THROUGH A FENCE AND STRUCK A RESIDENTIAL GAS METER AT 1181 W. CHILDS AVE., MERCED, CA, SHEARING THE METER OFF AT THE RISER. ESCAPING GAS WAS IGNITED, CAUSING A FIRE WHICH CAUSED DAMAGE IN EXCESS OF $50,000. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
331 | 2006-04-11 | IL | other | UNKNOWN (COOK COUNTY) | NICOR GAS | GARAGE FIRE AT THIS ADDRESS. HEAT FROM DIRECT FLAME CAUSED DAMAGE TO THE METER SET CAUSING A RELEASE OF NATURAL GAS. CAUSE OF THE FIRE IN UNKNOWN. NOTE: THIS WAS ORIGINALLY REPORTED AS A A VEHICLE HITTING THE METER SET. AFTER FURTHER INVESTIGATION IT WAS DETERMINED THAT THE VEHICLE WAS NOT INVOLVED. | 60750 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
332 | 2006-04-11 | TX | other | UNKNOWN (POLK COUNTY) | CENTERPOINT ENERGY | A HOUSE FIRE AT 314 MORRISON, LIVINGSTON, POLK COUNTY, TEXAS RESULTED IN ONE (1) DEATH AND ONE (1) INJURY REQUIRING HOSPITALIZATION FOR WHAT WAS REPORTED AS 3RD DEGREE BURNES. THE HOME WAS OCCUPIED BY AN ELDERLY COUPLE. THE WOMAN IS REPORTED TO HAVE SMOKING CIGARETTE WHILE USING OXYGEN. THE INCIDENT WAS REPORTED BASED ON THE FATATITY AND INJURY. NATURAL GAS DOES NOT APPEAR TO HAVE BEEN A FACTOR IN THE CAUSE OF THE FIRE. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
333 | 2006-04-17 | WV | natural disasters | UNKNOWN (TUCKER COUNTY) | CANAAN VALLEY GAS COMPANY | ON FRIDAY, APRIL 14, 2006 AT APPROXIMATELY 9:00 P.M., A SEVERE THUNDERSTORM PASSED THROUGH THE AREA. LIGHTNING APPARENTLY HIT IN THE VICINITY OF OUR PIPELINE. THE LIGHTNING IS BELIEVED TO HAVE TRAVELED THE TRACER WIRE TO A 1" TAP ON A 4" MAIN, CAUSING THE TAP TO SEPARATE FROM THE MAIN AND THE 1" TO PARTIALLY SPLIT AT THE CONNECTION TO THE TAP. GAS ESCAPED UNDERGROUND. WEATHER CONDITIONS FROM THE TIME OF THE LIGHTNING STRIKE TO THE TIME OF THE INCIDENT WERE COLD TEMPERATURES, RAIN, AND FOG. AT APPROXIMATELY 10:15 A.M. ON MONDAY, APRIL 17, 2006 THE INCIDENT STRUCTURE EXPLODED, BLOWING OUT ONE WALL AND CAUSING INJURY TO 5 HOUSING CONSTRUCTION WORKERS INSIDE. ALL 5 WERE HOSPITALIZED. FOUR OF THE FIVE ARE SINCE DECEASED. ONE HAS RETURNED HOME. DURING THE STORM, A NEIGHBORING HOUSE WAS STRUCK BY LIGHTNING WITH RESULTANT DAMAGE TO INSIDE WIRING AND GAS PLUMBING, CAUSING A GAS LEAK ON FLEX PIPING INSIDE THE HOME. THIS WAS UNKNOWN TO THE OPERATOR UNTIL AFTER THE INCIDENT. IT IS UNKNOWN AT THIS TIME WHETHER THERE WAS SIMILAR DAMAGE INSIDE THE INCIDENT STRUCTURE. ESTIMATES OF DAMAGE ARE UNDETERMINED AT THIS TIME, BUT WILL BE PROVIDED AT A LATER DATE. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
334 | 2006-04-16 | OH | other | UNKNOWN (FRANKLIN COUNTY) | COLUMBIA GAS OF OHIO, INC. | ON APRIL 16,2006 COLUMBIA GAS OF OHIO CONTACTED DOT AND REPORTED THE INCIDENT REFERENCED ABOVE. AT THE TIME OF THE OCCURRENCE THE CITY OF COLUMBUS FIRE DEPARTMENT REPORTED THAT THE CAUSE OF THE EXPLOSION WAS LIKELY A RELEASE OF NATURAL GAS. SINCE THE TIME OF THAT REPORT, IT HAS BEEN DETERMINED BY AN INDEPENDENT INVESTIGATOR THAT THE ORIGIN OF THE EXPLOSION AND SUBSEQUENT FIRE WAS DOWN STREAM OF THE GAS METER. THEREFORE, COLUMBIA BELIEVES THE INCIDENT IS NOT REPORTABLE. PLEASE CLOSE YOUR FILE IN THIS MATTER. | 150000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
335 | 2006-05-08 | VA | other | UNKNOWN (nan COUNTY) | CITY OF RICHMOND DEPARTMENT OF PUBLIC UTILITIES | ON MAY 8, 2006 AT APPROXIMATELY 3:40 P.M., A VEHICLE BACKED INTO AND DAMAGED THE NATURAL GAS METER AT THE OUTBACK RESTAURANT (7917 WEST BROAD STREET, RICHMOND, VIRGINIA 23226). THE METER IS A 10,000 ROCKEWELL SERIES METER AND WAS LOCATED THIRTY-SIX (36) INCHES FROM THE CURB AND SIDEWALK. THE ENSUING GAS LEAK APPARENTLY CONTRIBUTED TO A FIRE IN THE REAR OF THE RESTAURANT. AT THIS TIME, VEHICLE IDENTIFICATION HAS NOT BEEN DETERMINED. (THE HENRICO COUNTY POLICE DEPARTMENT CLASSIFIED THIS AS A "HIT-AND-RUN"). THE RICHMOND DEPARTMENT OF PUBLIC UTILITIES IS WAITING THE RESULTS OF HENRICO COUNTY FIRE DEPARTMENT'S INVESTIGATION. | 138490 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
336 | 2006-04-25 | IL | other | UNKNOWN (KANE COUNTY) | NICOR GAS | REVISED REPORT WITH UPDATES PROPERTY DAMAGE AMOUNT. ___________________________________________________________________________ HIGH WINDS KNOCKED CHARCOAL FROM GRILL AND STARTED FIRE ON THE BALCONY. DEBRIS FROM THE BALCONY FELL ONTO THE METER SET, CAUSING DAMAGE TO THE METER SET AND THUS A RELEASE OF NATURAL GAS. | 71000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
337 | 2006-04-24 | LA | sabotage | UNKNOWN (HARRIS COUNTY) | CENTERPOINT ENERGY | THIRD PARTY DAMAGED 8" STEEL MAIN WHILE DRIVING PILINGS IN CANAL. (NON-REPORTABLE) | 23669 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
338 | 2006-04-23 | NM | other | UNKNOWN (TORRANCE COUNTY) | E. M. W. GAS ASSOCIATION | THE GAS SERVICE TO THIS ADDRESS WAS INSTALLED AS PART OF THE ORIGINAL SYSTEM IN 1964.AND AT SOME POINT THROUGH THE YEARS THE HOMEOWNER BUILT A ROOM OVER THE RISER.NOBODY FROM E.M.W. KNEW THE RISER WAS THEIR.ON APRIL 23, 2006 THE HOMEOWNER WAS ATTEMPTING TO CUT THE PIPE OFF AT FLOOR LEVEL. AN EMPLOYEE WITH 20 YEARS EXPERIENCE.WENT INTO THE ROOM TO ASSESS THE SITUATION AND THE STRUCTURE EXPLODED. | 101651 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
339 | 2006-03-30 | MO | other | UNKNOWN (ST.CHARLES COUNTY) | LACLEDE GAS COMPANY | THE INCIDENT RESULTED FROM A HOUSE FIRE WHICH ORIGINATED OUTSIDE THE HOUSE IN A WOOD MULCH BED NEAR THE NATURAL GAS METER SET SERVING THE RESIDENCE. VISUAL OBSERVATION AT THE SCENE INDICATED THAT THE MULCH IGNITED AND EVENTUALLY ENGULFED THE SERVICE LINE RISER AND METER SET. THE METER SET AND RISER ASSEMBLY LEAKED AFTER BEING SUBJECTED TO EXTREME HEAT. THE RELEASED NATURAL GAS WAS IGNITED BY THE MULCH FIRE. | 151000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
340 | 2006-04-19 | KY | sabotage | UNKNOWN (HENRY COUNTY) | LOUISVILLE GAS AND ELECTRIC COMPANY | ON APRIL 19, 2006, MR. BILLY GRIGSBY WAS ATTEMPTING TO REPAIR A WATERLINE LEAK AT 8016 MAIN STREET IN CAMPBELLSBURG, KENTUCKY. MR. GRIGSBY INDICATED HE WAS DIGGING BY HAND AND COULD NOT GET A DEEP ENOUGH HOLE TO FIND THE WATERLINE. MR. GRIGSBY SAW A BACK-HOE DOWN THE STREET FROM WHERE HE WAS WORKING. MR. CHARLES MOORE WAS THE OWNER/OPERATOR OF THE BACK-HOE. MR. GRIGSBY ASKED MR. MOORE IF HE WOULD DIG THE WATERLINE UP SO HE COULD MAKE THE NECESSARY REPAIRS. MR. MOORE SAID YES AND DROVE THE BACK-HOE TO THE JOB SITE. AS MR. MOORE WAS DIGGING, THE BUCKET OF THE BACK-HOE STRUCK AND PULLED IN TWO, THE NATURAL GAS SERVICE FEEDING 8016 MAIN STREET. MR. GRIGSBY STATED THAT AT THAT TIME HE CALLED TO AN OFFICE IN TOWN AND ASKED WHAT THE NUMBER FOR LG&E WAS. MR. GRIGSBY STATED THAT ONCE HE RECEIVED THE NUMBER HE CALLED LG&E TO REPORT THE DIG-IN. MR. GRIGSBY AND MR. MOORE BOTH STATED THAT THEY COULD SMELL A SLIGHT ODOR OF NATURAL GAS BUT, COULD NOT HEAR IT BLOWING. MR. MOORE STATED THAT WHEN HE STRUCK THE NATURAL GAS SERVICE HE STOPPED DIGGING AND SHUT THE BACK-HOE OFF AND LEFT IT IN PLACE. HE ALSO STATED THAT AFTER THE DIG-IN, HE RETURNED TO A SHOP DOWN THE STREET. MR. GRIGSBY STATED THAT AFTER THE DIG-IN, HE RETURNED TO A SECOND HOLE THAT HE HAD ALREADY DUG. MR. GRIGSBY STATED THAT HE WAS ATTEMPTING TO INSTALL A WATER VALVE ON A CHURCH¿S WATERLINE IN THE SECOND HOLE, WHEN THE EXPLOSION OCCURRED DESTROYING THE CHURCH. THERE WERE NO INJURIES ASSOCIATED WITH THE EXPLOSION. THE HENRY COUNTY 911 DISPATCH RECEIVED A CALL REPORTING THE EXPLOSION AT 2:37PM. THE CAMPBELLSBURG FIRE AND RESCUE WAS DISPATCHED AT 2:38PM. THE LG&E CREW ARRIVED ON SCENE AT 2:47PM. THE LG&E CREW IMMEDIATELY SHUT THE NATURAL GAS SERVICE OFF TO 8016 MAIN STREET. THE CREW THEN SHUT THE NATURAL GAS SERVICE OFF TO THE CHURCH AND THE HOUSE NEXT DOOR. THE PRELIMINARY INVESTIGATIONS DID POINT TO NATURAL GAS AS THE CAUSE OF THE EXPLOSION. A JOINT INVESTIGATION WAS HELD THE NEXT DAY, APRIL 20, 2006 WITH LG&E, INDIANA INSURANCE COMPANY, THE KENTUCKY STATE POLICE, THE KENTUCKY STATE FIRE MARSHALL¿S OFFICE AND FEDERAL ALCOHOL TOBACCO AND FIREARMS. INVESTIGATORS FROM THE KENTUCKY PUBLIC SERVICE COMMISSION WERE ALSO ON SCENE. THE JOINT INVESTIGATION FOUND THAT THE NATURAL HAS SERVICE GOING TO 8016 MAIN STREET HAD BEEN RE-LINED AND WAS ½ INCH PLASTIC SERVICE INSIDE OF A 1 ¼ INCH BARE STEEL LINE. INVESTIGATION FOUND THAT THE PLASTIC SERVICE HAD BEEN PULLED IN TWO BY THE BACK-HOE. THERE WAS A 6 INCH TERRACOTTA TILE DRAIN PIPE RUNNING FROM THE CHURCH TO THE MAIN SEWER LINE THAT RAN PERPENDICULAR TO THE NATURAL GAS SERVICE. NEAR THE POINT WHERE THE NATURAL GAS SERVICE WAS PULLED APART, THE DRAIN PIPE WAS ALSO CRACKED. THE INVESTIGATION FOUND THAT THERE WERE TREE ROOTS ON, AROUND AND INSIDE OF THE DRAIN PIPE. THE DRAIN PIPE HAD SEVERAL CRACKS AND AN APPROXIMATELY 1 INCH HOLE ON THE BOTTOM OF THE DRAIN PIPE. THE END OF THE PLASTIC NATURAL GAS SERVICE WAS 14 INCHES AWAY FROM THE DAMAGED SECTION OF THE DRAINPIPE AND WAS NEARLY IN-LINE WITH THE DAMAGED AREA AND HOLE. THE ESCAPING 30PSI NATURAL GAS WAS BLOWING INTO THE DRAINPIPE AND FILLING THE CHURCH¿S BASEMENT WITH NATURAL GAS. THERE WERE TWO FURNACES LOCATED IN THE BASEMENT THAT WERE PILOT LIGHT OPERATED. ONCE THE NATURAL GAS FILLED THE BASEMENT AREA IT REACHED THE PILOT LIGHTS AND IGNITED. THIS WAS A HIGH ORDINANCE EXPLOSION. THE INVESTIGATION FOUND THAT MR. MOORE HAD NOT CONTACTED THE KENTUCKY ONE CALL CENTER FOR A BUD REQUEST LOCATED OF THE UTILITIES IN THE AREA. THE INVESTIGATION ALSO FOUND THROUGH INTERVIEWS WITH JOHN DAVENPORT, PASTOR CAMPBELLSBURG UNITED METHODIST CHURCH AND HIS WIFE SIRI, THAT THEY HAD NOT NOTICED OR DETECTED ANY NATURAL GAS ODORS PRIOR TO THIS INCIDENT. SERVICE RELINED ¿ MARCH 17, 1987 GRADE TO SERVICE ¿ 26 ½ INCHES GRADE TO VALVE ¿ 20 ½ INCHES STOP BOX WAS VISIBLE AND OPERABLE | 341592 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
341 | 2006-05-07 | KS | other | UNKNOWN (nan COUNTY) | KANSAS GAS SERVICE | AT APPROXIMATELY 0730HRS ON MAY 7, 2006 A CAR TRAVELING THROUGH THE INTERSECTION AT 7TH AND KANSAS AVE, KANSAS CITY, KANSAS HIT A CAR IN THAT INTERSECTION AND THEN VERED OFF THE ROAD AND HIT THE REGULATOR STATION LOCATED ON THE NE CORNER OF THE INTERSECTION. AS A RESULT OF THIS ACCIDENT THERE WAS ONE FATALITY AND 2 IN-HOSPITAL INJURIES. THE STATION ALSO SUSTAINED DAMEGED THAT TORE OPEN THE OUTLET SIDE OF THE STATION AND CREATED A RELEASE OF GAS. THERE WAS NO FIRE OR EXPLOSION AND THE RELEASE OF GAS WAS NOT A FACTOR OF EITHER THE FATALITY OR THE INJURIES. THERE WERE NO CUSTOMERS LOST AS GAS TO THE SYSTEM WAS MAINTAINED BY ALTERNATE FEEDS. | 23425 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
342 | 2006-04-19 | FL | sabotage | UNKNOWN (ESCAMBIA COUNTY) | CITY OF PENSACOLA - ENERGY SERVICE OF PENSACOLA (ESP) | PRELIMINARY INVESTIGATION REVEALED FRACTURES ON SERICE LINE COMPONENTS APPARENTLY DUE TO ACTIVITY OF EXCAVATOR CONTRACTOR. THE VALVE CONNECTION OF THE SERVICE LINE FRACTURED, APPARENTLY DUE TO IMPROPER SUPPORT AND BACKFILL BY THE EXCAVATOR AND TO EXCESSIVE OVERHEAD FORCE OF A ROLLER BY THE EXCAVATOR CONTRACTOR. | 3426 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
343 | 2006-04-02 | MO | natural disasters | UNKNOWN (PEMISCOT COUNTY) | ATMOS ENERGY | TORNADO DAMAGE IN TOWN ONE STATION HAD TO BE TURNED OFF. A BLOW DOWN VALVE WAS SHEARED OFF AT GROUND LEVEL BY FLYING DEBRIS AND APPROX. 425 CUSTOMERS HAD TO BE TURNED OFF. AT THIS TIME THE NUMBER OF RETURNING CUSTOMERS IS UNDETERMINED. | 98000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
344 | 2006-05-18 | LA | sabotage | UNKNOWN (LA FOURCHE COUNTY) | SOUTH COAST GAS CO |  | 331 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
345 | 2006-05-09 | LA | sabotage | UNKNOWN (LA FOURCHE COUNTY) | SOUTH COAST GAS CO |  | 357 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
346 | 2006-05-10 | IL | other | UNKNOWN (WINNEBAGO COUNTY) | NICOR GAS | VOLUNTEER FIREFIGHTER AND FORMER EMPLOYEE OF THE BUSINESS AT 2758 ALWORTH WAS ACCUSED OF SETTING THE FIRE THAT DESTROYED THE STRUCTURE AND DAMAGED THE METER SET WHICH WAS ATTACHED TO THE STRUCTURE. | 551500 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
347 | 2006-05-12 | IL | other | UNKNOWN (KENDALL COUNTY) | NICOR GAS | FIRE AND/OR EXPLOSION IN UTILITY/BOILER ROOM OF SINGLE FAMILY HOME. CAUSE OF THE FIRE/EXPLOSION IS UNKNOWN AFTER INVESTIGATIONS. | 100002 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
348 | 2006-05-15 | UT | other | UNKNOWN (SALT LAKE COUNTY) | QUESTAR GAS COMPANY | THE FIRE ORIGINATED INSIDE THE RESIDENCE AND WAS NOT RELATED TO NATURAL GAS. THE FIRE MOVED OUT OF A WINDOW AND THE HEAT OF THE FIRE CAUSED THE REGULATOR TO MELT AND A RELEASE OF NATURAL GAS. THE PUBLIC/PRIVATE PROPERTY DAMAGES OF $100,000.00 IS A DIRECT RESULT OF THE FIRE AND NOT RELATED TO THE RELEASE OF NATURAL GAS. | 100770 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
349 | 2005-11-08 | CA | leaks and spills | UNKNOWN (RIVERSIDE COUNTY) | SOUTHERN CALIFORNIA GAS COMPANY | ON NOVEMBER 8, 2005 AN EXPLOSION AND FIRE OCCURRED AT THE ADDRESS OF 5760 LUCRETIA, MIRA LOMA. UNDERGROUND NATURAL GAS WAS DISCOVERED AT THE FOUNDATION OF THE DAMAGED BUILDING. THE INCIDENT WAS REPORTED TO THE CPUC AS A RESULT OF MAJOR MEDIA BEING PRESENT. THIS INCIDENT WAS INITIALLY REPORTED TO CALIFONIA PUBLIC UTILITIES COMMISSION ONLY. UPON FURTHER INVESTIGATION, IT WAS DETERMINED THAT NATURAL GAS FOUND AT FOUNDATION ORIGINATED AT A CRACKED 4¿ PE COUPLING. THE COUPLING AND 4¿ OF GAS MAIN WERE REMOVED AND REPLACED. ALL GAS COMPANY FACILITIES HAVE BEEN REPAIRED, AND SERVICES RESTORED. THIS INCIDENT WAS INITIALLY ESTIMATED TO BE LESS THAN $50K TO COSTS, BASED UPON THE HOMEOWNER'S CLAIM ADJUSTER ESTIMATE. HOWEVER, MONTHS LATER THE ESTIMATE WAS REVISED, DUE TO DISCOVERY OF STRUCTURAL DAMAGE, AND HAZARDOUS MATERIAL MITIGATION INSIDE THE RESIDENCE. UPON THIS NOTIFICATION, A REPORT WAS IMMEDIATELY FILED. | 102000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
350 | 2006-06-02 | VA | other | UNKNOWN (nan COUNTY) | CITY OF RICHMOND PUBLIC UTILITIES | ON JUNE 2, 2006 AT APPROXIMATELY 3:52 P.M., OPERATOR RESPONDED TO A HOUSE FIRE AT 3701 GRANDEL DRIVE. THE ENSUING FIRE EVENTUALLY CONSUMED THE METER AND REGULATOR SET CAUSING GAS RELEASE. THE FIRE, THEN BEING GAS FED, ESCALATED IN INTENSITY UNTIL EXTINGUISED BY FIRE PERSONNEL. UPON ARRIVAL, GAS PERSONNEL SHUT THE GAS OFF AT THE CURB COCK AND CHECKED THE NEARBY AREAS FOR GAS LEAKS (FOUND NONE). PRESSURE TESTED THE GAS SERVICE FOR INTEGRITY (WITH AIR HELD TO 40 PSI FOR 30 MINUTES). ODORIZATION WAS READILY DETECTIBLE. | 168800 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
351 | 2006-05-27 | LA | sabotage | UNKNOWN (TERREBONNE COUNTY) | SOUTH COAST GAS CO |  | 181 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
352 | 2006-05-06 | TX | natural disasters | UNKNOWN (HARRIS COUNTY) | CENTERPOINT ENERGY | LIGHTNING STRIKE TO LIGHTPOLE, WHICH HIT FENCE CAUSING ARC TO 2" STEEL MAIN AND ESCAPING GAS IGNITED. | 54685 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
353 | 2006-05-19 | IL | other | UNKNOWN (MCHENRY COUNTY) | NICOR GAS | FULLY INVOLVED STRUCTURE FIRE. WALL COLLAPSED ONTO THE METER SET CAUSING A RELEASE OF GAS. | 551000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
354 | 2006-03-30 | CO | other | UNKNOWN (nan COUNTY) | PUBLIC SERVICE CO OF COLORADO | HEAVY SNOW IN THE REGION THIS YEAR CAUSED SNOW TO BE PILED IN ABNORMAL LOCATIONS. WHEN THE SNOW WAS CLEARED FROM THE PAVED ACCESS ROAD RUNNING THROUGH THE ANTLERS COMPLEX, IT WAS PUSHED OFF AN EMBANKMENT TO AN AREA WHERE XCEL ENERGY'S METERS WERE LOCATED, AT AN ELEVATION APPROXIMATELY 10 FEET BELOW THE ACCESS ROAD SURFACE. THE SNOW WAS PUSHED, PILED AND COMPACTED ON TOP OF THE METERS, APPARENTLY CAUSING THE RISER TO BREAK UPSTREAM OF THE REGULATOR. | 1500000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
355 | 2006-06-05 | CA | sabotage | UNKNOWN (ORANGE COUNTY COUNTY) | SOUTHERN CALIFORNIA GAS COMPANY | ON JUNE 5 2006 A 3¿ NATURAL GAS DISTRIBUTION PIPELINE OPERATING AT APPROXIMATELY 45 POUNDS WAS DAMAGED BY A CONTRACTOR INSTALLING NATURAL GAS PIPELINES FOR THE OPERATOR (SOUTHERN CALIFORNIA GAS COMPANY). NO INJURIES OR PUBLIC PROPERTY DAMAGE RESULTED FROM THIS INCIDENT. ALL REPAIRS HAVE BEEN COMPLETED, AND FIVE CUSTOMERS WHO WERE OUT OF GAS HAVE BEEN RESTORED. INVESTIGATION OF THE INCIDENT SHOWED THAT THE EXCAVATOR KNEW THE LOCATION OF THE NATURAL GAS PIPELINE, BUT FAILED TO HAND EXPOSE PRIOR TO MACHINE EXCAVATION. THIS INCIDENT WAS REPORTED TO DOT UNDER INCIDENT # 799554, BASED UPON DAMAGE TO COMPANY FACILITIES AND POTENTIAL DOWNTIME / LOSS OF BUSINESS CLAIMS EXCEEDING $50K. | 50500 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
356 | 2006-05-30 | CA | other | UNKNOWN (STANISLAUS COUNTY) | PACIFIC GAS AND ELECTRIC COMPANY | AT 1312 HOURS THE DUPLEX AT 106/108 OAK STREET EXPLODED AND BURNED. NATURAL GAS WAS SUSPECTED TO HAVE BEEN INVOLVED. AT 1730 HOURS WE WERE INFORMED THAT A PASSERBY HAD BEEN INJURED IN THE EXPLOSION AND HAD BEEN TAKEN TO THE UC DAVIS MEDICAL CENTER IN SACRAMENTO. BASED ON THIS INFORMATION, THIS INCIDENT WAS REPORTED. ON THE DAY OF THE INCIDENT, THE MODESTO FIRE DEPARTMENT DEEMED THAT THE STRUCTURE WAS TOO HOT AND DANGEROUS TO ENTER FOR INVESTIGATION AND THAT AN INVESTIGATION COULD BE PERFORMED THE FOLLOWING DAY. WHEN COMPANY PERSONNEL RETURNED THE FOLLOWING DAY, THE STRUCTURE HAD BEEN DEMOLISHED AND ALL MATERIALS HAD BEEN REMOVED THUS ELIMINATING THE ABILITY TO INVESTIGATE THE STRUCTURE ITSELF. A POST INCIDENT LEAK SURVEY SHOWED NO LEAKAGE ON THE GAS COMPANY FACILITIES. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
357 | 2006-06-19 | NC | sabotage | UNKNOWN (nan COUNTY) | PIEDMONT NATUAL GAS CO. | A 3RD PARTY CONTRACTOR, PIKE ELECTRIC, WAS DIGGING UNDERGROUND IN THE PROCESS OF INSTALLING LIGHTING IN THE RUNAWAY BAY APARTMENTS IN CHARLOTTE, NC. AT AROUND 10:30 AM (6.19.06)THE PIKE CREW CUT A 1 1/4 PLASTIC GAS LINE COSE TO ONE OF THE APARMENT BUILDINGS WHICH IMMEDIATELY BEGAN TO BLOW NATURAL GAS AT 65 PSIG IN THE DIRECTION OF THE BUILDING. THE OPERATOR OF THE BACKHOE SHUT THE ENGINE OFF AND ESCAPED. THE LEAKING GAS IGNITED A SHORT TIME LATER WHICH FUELED A FLAME DIRECTLY TO THE OUTSIDE OF THE BUILDING. THIS STARTED A FIRE WHICH EVENTUALLY WORKED THROUGH ALL 12 UNITS IN THE BUILDING. THERE WAS ALSO DAMAGE TO SOME SURROUNDING BUILDINGS. THE DAMAGE TOTAL WAS ESTIMATED AT $500,000. THERE WERE NO INJURIES. 29 PEOPLE WERE DISPLACED FROM THEIR HOMES. THE CONTRACTOR WAS DIGGING WITHOUT A VALID LOCATE TICKET (ORIGINAL LOCATE TICKET VALID PERIOD HAD EXPIRED). | 770614 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
358 | 2006-06-03 | PA | other | UNKNOWN (CRAWFORD COUNTY COUNTY) | NATIONAL FUEL GAS DISTRIBUTION CORPORATION | A PASSENGER VEHICLE TRAVELLING WEST BOUND ON PA SR 408 LEFT THE ROADWAY, TRAVELLING THROUGH LIVESTOCK FENCE, AND APPROXIMATELY 350' BEFORE CRASHING THROUGH STATION CHAIN LINK SECURITY FENCE. THE VEHICLE STRUCK PRESSURE RELIEF AND REGULATION FACILITIES, SPUN 180 DEGREES, FINALLY STOPPING INSIDE AND AGAINST THE STATION SECURITY FENCE. 294 LOCAL DISTRIBUTION CUSTOMERS LOST SERVICE AS A RESULT. | 160000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
359 | 2006-07-02 | AK | other | UNKNOWN (KENAI PENINSULA BOROUGH COUNTY) | ENSTAR NATURAL GAS COMPANY |  | 76050 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
360 | 2006-06-16 | MN | natural disasters | UNKNOWN (HENNEPIN COUNTY) | CENETERPOINT ENERGY RESOURCES GROUP D/B/A CENTERPOINT ENERGY MINNESOTA GAS | METER SET AND OR HOUSE WAS STRUCK BY LIGHTING CAUSING A FIRE. | 71000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
361 | 2006-05-31 | MN | technical failure | UNKNOWN (HENNEPIN COUNTY) | CENTERPOINT ENERGY RESOURCES GROUP D/B/A CENTERPOINT ENERGY MINNESOTA GAS | CONTRACT EMPLOYEE USED A SAZALL TO CUT THROUGH A SERVICE LINE. A GASOUS ATMOSPHERE WAS CREATED AND A FLASH FIRE FOLLOWED. | 1000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
362 | 2006-04-28 | MA | technical failure | UNKNOWN (MIDDLESEX COUNTY) | NSTAR GAS COMPANY | THE INJURED EMPLOYEE WAS TAPPING THE 2 INCH HIGH VOLUME TAPPING TEE INSTALLED ON AN EXISTING 2INCH INTERMEDIATE PRESSURE PLASTIC MAIN. THE ELECTROFUSION TAPPING TEE WAS ONE OF FOUR TAPS PLANNED ON A DOUBLE BYPASS TO FACILITATE A MAIN CUTOUT IN CONJUNCTION WITH A LEAK REPAIR. THE TAPPING TOOL CAP WAS NOT PROPERLY TIGHTENED ON THE FITTING, THEREFORE THE CAP LOOSENED AS THE CUTTER WAS RETRACTED CAUSING THE LEAK. UPDATED BY PHMSA ON 1/15/2016 PER OPERATOR'S MARK UP. (PART F - APPARENT CAUSE - F6 EQUIPMENT OR OPERATIONS, QUESTION 23 INCORRECT OPERATION; AND PART I NARRATIVE). | 21000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
363 | 2006-05-02 | TX | sabotage | UNKNOWN (BRAZORIA COUNTY) | CENTERPOINT ENERGY | THIRD PARTY DAMAGE TO 3/4" POLY SERVICE LINE WHILE HEAT SHRINKING PHONE CABLE AN ESCAPING GAS IGNITED. | 43919 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
364 | 2006-05-14 | TX | other | UNKNOWN (HARRIS COUNTY) | CENTERPOINT ENERGY | STOLEN VEHICLE HIT METER SET ASSEMBLY AND ESCAPING GAS IGNITED. | 52079 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
365 | 2005-12-17 | AL | other | UNKNOWN (JEFFERSON COUNTY) | ALABAMA GAS CORPORATION | COMPANY RESPONDED TO RESIDENCE FIRE AT REQUEST OF MIDFIELD FIRE DEPARTMENT. CAUSE OF FIRE WAS NOT DETERMINED DURING THE INVESTIGATION ASSOCIATED WITH THIS INCIDENT. THE HOMEOWNER ALLEGED IN LITIGATION THAT THERE WAS AN EXPLOSION AT THE RESIDENCE PRECEDING THE FIRE, BUT THE OPERATOR HAS NOT BEEN ABLE TO MAKE THAT SAME DETERMINATION. THERE WAS A BREAK IN THE 2" CAST IRON MAIN INSTALLED IN 1951, AND THE GAS DID MIGRATE FROM THE BREAK TO THE RESIDENCE, BUT THE INVESTIGATION WAS INCONCLUSIVE AS TO WHETHER THIS WAS A FACTOR IN THE INCIDENT. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
366 | 2006-05-31 | CA | other | UNKNOWN (SHASTA COUNTY) | PACIFIC GAS AND ELECTRIC COMPANY | LINSEED OIL SOAKED RAGS IN THE GARAGE SPONTANEOUSLY COMBUSTED AND CAUSED THE STRUCTURE FIRE TO SPREAD TO THE GAS METER SET. THE DAMAGE TO THE GAS METER SET CAUSED NATURAL GAS TO ESCAPE AND IGNITE. THE FIRE DEPARTMENT SHUT THE GAS SERVICE VALVE PRIOR TO THE ARRIVAL OF COMPANY PERSONNEL. THE FIRE CAUSED SUBSTANTIAL DAMAGE TO THE STRUCTURE. | 50100 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
367 | 2006-06-18 | IL | other | UNKNOWN (COOK COUNTY) | NICOR GAS | SUSPICIOUS FIRE SPREAD THROUGHOUT THE VACANT STRUCTURE WHICH THEN DAMAGED THE METER SET AND CAUSED A RELEASE OF GAS. | 77000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
368 | 2006-04-16 | VA | other | UNKNOWN (FAIRFAX COUNTY) | COLUMBIA GAS OF VIRGINIA | VEHICLE JUMPED PARKING LOT CURBING TRAVELING APPROXIMATELY 25¿ ACROSS GRASS AREA AND SIDEWALK STRIKING FOUR METER MANIFOLD SETTING. THE FAIRFAX COUNTY FIRE DEPT. TURNED OFF THE METER SETTING EXTINGUISHING THE FIRE. VEHICLE WAS APPARENT IGNITION SOURCE. | 250000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
369 | 2006-06-19 | CA | sabotage | UNKNOWN (CONTRA COSTA COUNTY) | PACIFIC GAS & ELECTRIC COMPANY | ON MONDAY, JUNE 19, 2006, AT APPROXIMATELY 1245 HOURS, A CONSTRUCTION CREW FROM PERFORMANCE MECHANICAL INC. (PMI) DUG INTO A 4-INCH PLASTIC MAIN AT STONEMAN AVENUE AND BRIAR CLIFF DRIVE IN PITTSBURG CAUSING GAS TO ESCAPE WHILE EXCAVATING TO EXPOSE A WATER LINE. THERE WAS NO FIRE OR EXPLOSION AS A RESULT OF THIS INCIDENT. THERE WAS A VALID USA TICKET (201217 CALLED IN ON 6/8/06) FOR THIS CONSTRUCTION ACTIVITY, AND THE MAIN WAS MARKED CORRECTLY BY PG&E. PG&E RESPONDED TO THE SITE OF THE DIG-IN AND INITIATED EXCAVATIONS AND SQUEEZING OPERATIONS TO STOP THE FLOW OF GAS. SQUEEZING OPERATIONS PROVIDED AN INDICATION THAT THE MAIN WAS A ONE-WAY FEED AND SQUEEZERS WERE RAISED. PG&E BEGAN RECEIVING CALLS OF ¿NO GAS¿ FORM CUSTOMERS. UPON REVIEW OF THE PLATS, IT WAS DISCOVERED THAT THE 4¿ MAIN IS A ONE-WAY FEED SUPPORTING 429 SERVICES, WHICH SERVE APPROXIMATELY 900 CUSTOMERS (MANIFOLDS). THE REPAIR OF THE LINE WAS COMPLETED AT 2200 HOURS, AND GSRS WERE DISPATCHED TO BEGIN RELIGHTS AT 2230. DUE TO THE LATE HOUR, APPROXIMATELY 80% OF CUSTOMERS WERE CGIS AND THE RESTORATION PROCESS CONTINUED THE FOLLOWING DAY. GAS SERVICE TO ALL CUSTOMERS WAS REESTABLISHED BY 2130 HOURS ON 6/20/06. THIS INCIDENT WAS REPORTED TO THE DOT DUE TO COSTS IN EXCESS OF $50,000. | 65200 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
370 | 2006-06-28 | NY | natural disasters | UNKNOWN (BROOME COUNTY) | NEW YORK STATE ELECTRIC & GAS CORPORATION | ON JUNE 27TH 2006 FLOOD WATERS IN BROOME COUNTY NEW YORK REACHED RECORD LEVELS ESPECIALLY IN THE CONKLIN NEW YORK AREA. DURING AN INVESTIGATION OF 14 VICTORY STREET IT WAS MOTED THAT THE GAS DRYER IN THE BASEMENT WAS MOVED AWAY FROM THE WALL PULLING ON THE INTERIOR GAS PIPING ABOVE THE GAS DRYER. THE NIPPLE OUT OF THE ELBOW ABOVE THE DRYER WAS LEAKING AIR PRESSURE WHEN THE AIR TEST AT HOUSE LINE PRESSURE OF 7 INCHES OF WATER COLUM WAS APPLIED. WATER LEVEL MARKS INT THE SURROUNDING AREA INDICATED THAT THE WATER LEVEL HAD RISEN NOT ONLY IN THE BASEMENT BUT INTO THE FIRST FLOOR OF THE HOME. NEW YORK STATE ELECTRIC & GAS CORPORATION PERFORMED SOAP AND PRESSURE TESTING TO ITS FACILITIES FROM THE MAIN TO THE METER SET. ALSO THE PRESSURE REGULATOR WAS TESTED FOR LOCKUP AND DELIVERY. ALL TESTS PASSED. IN ADDITION TO THOSE TESTS, A LEAK SURVEY WAS PERFORMED IN THE VICINITY OF THIS STRUCTURE WITH NO INDICATIONS OF UNDERGROUND LEAKS. THESE TESTS WERE PERFORMED ON JULY 24TH 2006 IN THE PRESENCE OF THE NEW YORK STATE DEPARTMENT OF PUBLIC SERVICE AND THE HOMEOWNER'S INSURANCE COMPANY INVESTIGATOR. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
371 | 2006-06-16 | CA | other | UNKNOWN (nan COUNTY) | PACIFIC GAS & ELECTRIC COMPANY | ON JUNE 16, 2005 A SUSPECT FLEEING FROM POLICE CRASHED INTO AN APPLIANCE STORE AND DAMAGED THE GAS METER AT 1048 W 8TH STREET IN CHICO, CALIFORNIA. FIREFIGHTERS EXTINGUISHED THE RESULTING STRUCTURAL FIRE AND VALVED OFF THE GAS RISER FOR SAFETY. THERE WERE NO INJURIES OR DEATHS. THE GAS METER WAS LOCATED ON THE SIDE OF THE BUILDING AND TWO, FOUR-INCH METER PORTECTION POSTS HAD BEEN INSTALLED AT THE METER LOCATION. THE METER POSTS COULD NOT BE EFFECTIVE IN PREVENTING THIS INCIDENT DUE TO THE SPEED OF TRAVEL OF THE VEHICLE. THIS INCIDENT IS REPORTABLE TO THE DOT DUE TO DAMAGE IN EXCESS OF $50,000. | 750000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
372 | 2006-06-24 | VA | other | UNKNOWN (PRINCE WILLIAM COUNTY) | WASHINGTON GAS | THE FIRE/DAMAGE LOCATION, A HOUSE AT 3217 BERKLEY LANE - DALE CITY, VIRGINIA WAS THE RESULT OF A VEHICLE STRIKING THE SIDE OF THE HOUSE AND METER BUILD UP (DRIVER FLED SCENE) CAUSING IT TO RUPTURE AND A FIRE ENSUED THERBY DAMAGING THE STRUCTURE AND DISPLACING THE OCCUPANTS. | 409157 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
373 | 2006-06-19 | OH | sabotage | UNKNOWN (SUMMIT COUNTY) | DOMINION EAST OHIO GAS | ON JUNE 19,2006 AT APPOROXIMATELY 1:28 PM DOMINION EAST OHIO GAS CALL CENTER RECEIVED A REPORT FROM CABLING PROFESSIONALS THAT A PIPELINE WAS HIT AND DAMAGED BY A CONTRACTOR DIRECTIONAL BORING THE ROAD AT ILLINOIS PLAXE AND IOWA PLACE, BARBERTON, SUMMIT COUNTY, OH. AT APPROXIMATELY 1:59 PM DOMINION EAST OHIO GAS DISPATCH CENTER RECEIVED A REPORT OF AN EXPLOSION AT 212 ILLINOIS PLACE, BARBERTON, SUMMIT COUNTY, OH. DOMINION EAST OHIO GAS PERSONNEL ARRIVED AT THE SCENE AT 2:08 PM AND FOUND A 2" PIPELINE HAD BEEN DAMAGED, RESULTING IN A FIRE AND EXPLOSION OF A TWO-STORY DUPLEX. AT APPROXIMATELY 2:45 PM, THE PIPELINE WAS SHUTDOWN AT THE MAINLINE VALVE AND STOPPING THE FLOW OF GAS TO 37 APARTMENTS. A PRELIMINARY DAMAGE ASSESSMENT WAS THEN CONDUCTED, WHEN IT WAS DETERMINED THAT THE ESTIMATED PROPERTY DAMAGE RELATED TO REPORTABLE INCIDENTS MAY REACH THE REPORTABLE LEVEL, VERBAL NOTIFICATION WAS MADE ON JUNE 19, 2006 AT APPROXIMATELY 6:30 PM TO THE NATIONAL RESPONSE CENTER AND TO THE PUBLIC UTILITIES COMMISSION OF OHIO BY TELEPHONE. NRC# 801280 WAS ASSIGNED TO THIS EVENT AT THAT TIME. THE PUBLIC UTILITIES COMMISSION OF OHIO RESPONDED AND CONDUCTED AN ON-SITE INVESTIGATION OF THIS INCIDENT ON JUNE 20, 2006. PRELIMINARY INVESTIGATIONS REVEALED THAT THE PIPELINE WAS MISMARKED BY APPROXIMATELY 12 FEET. THE EXCAVATOR PERFORMING THE DIRECTIONAL BORE FAILED TO PLACE A ONE-CALL TICKET FOR THE EXCAVATION, SUB-CONTRACTOR WAS WORKING OFF CONTRACTORS ONE-CALL TICKET. SUB-CONTRACTOR ALSO FAILED TO DIG TEST HOLES AT THE MAIN AS REQUIRED IN ORDER TO ACCURATELY DETERMINE THE DEPTH AND LOCATION OF THE PIPELINE. TEST HOLES WERE LOCATED ON THE SERVICE LINE WHICH HAD A DIFFERENT DEPTH THAN THE MAINLINE. | 181300 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
374 | 2006-07-15 | WY | other | UNKNOWN (PARK COUNTY) | MONTANA-DAKOTA UTILITIES CO. | HOME OWNER WAS SIPHONING GASOLINE NEAR HOME. GASOLINE CAUGHT FIRE, MIGRATEED TO HOME AND IGNITED STRUCTURE. TOP OF NATURAL GAS METER WAS DESTROYED BY FIRE, RESULTING IN THE RELEASE OF NATURAL GAS. ONCE FIRE WAS EXTINGUISHED, SERVICEMAN WAS ABLE TO CLOSE RISER STOP VALVE AND STOP FLOW OF NATURAL GAS. THE RELEASE OF NATURAL GAS WAS THE RESULT OF THE FIRE DESTROYING T HE NATURL GAS METER. | 200000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
375 | 2006-06-20 | KY | sabotage | UNKNOWN (HAZARD COUNTY) | CITY OF HAZARD KENTUCKY/ HAZARD GAS COMPANY |  | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
376 | 2006-07-14 | CA | sabotage | UNKNOWN (LOS ANGELES COUNTY) | SOUTHERN CALIFORNIA GAS COMPANY | ON JULY 14, 2006, A 16¿ STEEL MEDIUM PRESSURE MAIN WAS DAMAGED BY A CONTRACTOR USING POWER AUGERING EQUIPMENT DURING A ROAD WIDENING PROJECT. THERE WAS A USA REQUEST FOR THIS AREA, AND FACILITIES WERE PROPERLY MARKED. NO FIRE OR INJURIES RESULTED FROM THE ESCAPING GAS. THE MAIN WAS REPAIRED, AND NO CUSTOMERS WERE OUT OF SERVICE. THE LIKELY CAUSE OF THIS INCIDENT WAS FAILURE OF THE CONTRACTOR TO HAND EXCAVATE IN THE VICINITY OF THE PIPELINE. THIS INCIDENT BECAME REPORTABLE TO THE DOT AND CPUC WHEN ESTIMATED ASSOCIATED COSTS EXCEEDED $50K. THIS FIGURE WAS NOT MET UNTIL AUGER WAS REMOVED FROM EXCAVATION, ALLOWING VISUAL ACCESS TO DETERMINE OPENING SIZE AND CALCULATE GAS LOSS VOLUME. | 52000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
377 | 2006-07-26 | MN | other | UNKNOWN (ANOKA COUNTY) | CENTERPOINT ENERGY RESOURCES GROUP D/B/A CENTERPOINT ENERGY MINNESOTA GAS | A CAR BAUSING A FIRE STRUCK THE RESIDENTIAL HOME AND OUR METER SET. | 400000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
378 | 2006-06-28 | NY | natural disasters | UNKNOWN (BROOME COUNTY) | NEW YORK STATE ELECTRIC & GAS CORPORATION | ON JUNE 27TH FLOOD WATERS IN BROOME COUNTY NEW YORK REACHED RECORD LEVELS ESPECIALLY IN THE CONKLIN NEW YORK AREA. DURING AN INVESTIGATION OF 21 MORRIS BLVD, IT WAS NOTED THAT THE BACK WALL OF THE STRUCTURE FACING THE RIVER HAD CAVED IN, NEGATIVELY AFFECTING THE PHYSICAL INTEGRITY OF THE CUSTOMER¿S EQUIPMENT, INCLUDING THE NATURAL GAS APPLIANCES AND PIPING. WATER LEVEL MARKS IN THE SURROUNDING AREA INDICATED THAT THE WATER LEVEL HAD RISEN NOT ONLY IN THE BASEMENT BUT INTO THE FIRS FLOOR OF THE HOME. NEW YORK STATE ELECTRIC & GAS CORPORATION PERFORMED SOAP AND PRESSURE TESTING TO ITS FACILITIES FROM THE MAIN TO THE METER SET. ALSO THE PRESSURE REGULATOR WAS TESTED FOR LOCKUP AND DELIVERY. ALL TESTS PASSED. IN ADDITION TO THOSE TESTS, WERE PERFORMED ON JULY 10TH 2006 IN THE PRESENCE OF THE NEW YORK STATE DEPARTMENT OF PUBLIC SERVICE AND THE HOMEOWNER¿S INSURANCE COMPANY INVESTIGATORS. | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
379 | 2006-07-20 | CA | sabotage | UNKNOWN (LOS ANGELES COUNTY) | SOUTHERN CALIFORNIA GAS COMPANY | ON JULY 20, 2006, A 6¿ PLASTIC MEDIUM PRESSURE MAIN WAS PUNCTURED BY A CONTRACTOR WORKING FOR SOUTHERN CALIFORNIA GAS COMPANY¿S TRANSMISSION DEPARTMENT. THE CONTRACTOR WAS PERFORMING PIPELINE INTEGRITY WORK, USING A BACKHOE WHEN HE STRUCK THE DISTRIBUTION MAIN. THERE WAS A USA REQUEST FOR THIS AREA, AND FACILITIES WERE PROPERLY MARKED. NO FIRE OR INJURIES RESULTED FROM THE ESCAPING GAS. APPROXIMATELY 20 SMALL BUSINESSES INSIDE THE MAGIC MOUNTAIN AMUSEMENT PARK LOST SERVICE, BUT WERE QUICKLY RESTORED. THE LIKELY CAUSE OF THIS INCIDENT WAS FAILURE FOR THE CONTRACTOR TO HAND EXCAVATE IN THE VICINITY OF THE DAMAGE. THIS INCIDENT BECAME REPORTABLE TO THE CPUC AND DOT WHEN IT WAS DETERMINED THAT THE VALUE OF REPAIRS AND POTENTIAL BUSINESS LOSS CLAIMS COULD EXCEED $50K. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
380 | 2006-07-13 | MD | other | UNKNOWN (PRINCE GEORGES COUNTY) | WASHINGTON GAS | THE SERVICE RISER THAT FEEDS THIS LOCATION WAS ALTERED BY AN UNKNOWN INDIVIDUAL WITHOUT APPROVAL FROM WASHINGTON GAS. THE ALTERED LINE APPEARED TO BE BENT AND SUBSEQUENTLY DAMAGED CONTRIBUTING TO THE HOUSE EXPLOSION. UPDATED BY PHMSA ON 1/25/2016 PER OPERATOR'S MARK UP.(PART A, QUESTION 3 LOCATION OF INCIDENT; PART C, QUESTION 2 - FAILURE OCCURRED ON; PART F APPARENT CAUSE; AND PART G NARRATIVE). WASHINGTON GAS (WG) PERSONNEL RESPONDED TO A REPORT OF AN EXPLOSION AT 911 NOVA AVENUE, CAPITOL HEIGHTS, MD ON 7/13/2006. THE INSIDE GAS METER WAS REMOVED FROM THIS LOCATION BY WG ON 05/25/2006 AND THE SERVICE WAS SHUT OFF AT THE STOPCOCK AT THE CURB. THE GAS SERVICE HAD BEEN ILLEGALLY RECONNECTED AND TURNED BACK ON PRIOR TO THE FIRE BY UNKNOWN PERSON(S). THE GAS SERVICE LINE, LOCATED INSIDE THE HOUSE WHERE IT CONNECTS TO THE METER, WAS DISCOVERED IN A BENT OVER POSITION. A PRESSURE TEST PERFORMED BY WG PERSONNEL ON THE GAS SERVICE LINE INDICATED A LEAK IN THE AREA OF THIS BEND. THE PRINCE GEORGES FIRE MARSHALL’S REPORT INDICATES THAT THE EXPLOSION WAS ACCIDENTAL IN NATURE, THE RESULT OF THE NATURAL GAS LEAKING INTO THE STRUCTURE FROM THE DAMAGED GAS LINE LOCATED INSIDE THE HOUSE AND MIGRATING TO AN IGNITION SOURCE RESULTED IN THE EXPLOSION. WASHINGTON GAS CONSIDERS THE INVESTIGATION OF THIS INCIDENT CLOSED. | 200000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
381 | 2006-07-06 | WI | sabotage | UNKNOWN (WAUKESHA COUNTY) | WISCONSIN GAS COMPANY, D/BA WE-ENERGIES | ON JULY 6, 2006, AT APPROXIMATELY 1:56PM, HOFFMAN CONSTRUCTION COMPANY OF BLACK RIVER FALLS, WI., WAS EXCAVATING SOIL AS PART OF A ROAD RECONSTRUCTION PROJECT WITH A TRACK MOUNTED BACKHOE IN THE VICINITY OF WISCONSIN GAS COMPANY¿S 3¿ ¿ 35# DISTRIBUTION MAIN WHEN IT STRUCK AND SEVERELY DAMAGED THE MAIN ALLOWING GAS TO ESCAPE TO THE ATMOSPHERE. THE BACKHOE OPERATOR, AND THE OPERATOR OF A NEARBY BULLDOZER, IMMEDIATELY CUT THE POWER TO THEIR EQUIPMENT AND ABANDONED THEM IN PLACE AND CALLED FOR ASSISTANCE. THE GAS CONTINUED TO VENT FROM THE DAMAGED PIPE FOR ABOUT 20 MINUTES, AT WHICH TIME IT IGNITED. (IGNITION, BECAUSE THERE WAS NO OTHER KNOWN SOURCE, IS ASSUMED TO HAVE BEEN CAUSED BY THE BUILD UP OF STATIC ELECTRICITY.) THE IGNITED GAS RAPIDLY CONSUMED THE D5 BULLDOZER AND CAUSED DAMAGE TO THE ARM OF THE TRACK MOUNTED BACKHOE. DUE TO THE FIRE, AND THE FACT THAT THE DAMAGE TO THE 3¿ GAS MAIN WAS TO CLOSE TO THE TEE AT THE 6¿ STEEL GAS MAIN FEEDER TO ALLOW SHUT OFF, IT BECAME NECESSARY TO SHUT DOWN THE 6¿ STEEL MAIN FEEDING THE 3¿ PE MAIN. UTILIZING THE MAPPING SYSTEM, THE NECESSARY VALVES WERE IDENTIFIED TO CONTROL THE FLOW OF GAS TO THE 3¿ MAIN. HOWEVER, DUE TO THE FAT THAT THE BURNING GAS WAS NOT THREATENING LIFE OR ANY ADDITIONAL PROPERTY AT THAT TIME, AND AFTER CONSULTING WITH THE LOCAL FIRE DEPARTMENT AND TOWN OFFICIALS, A DECISION WAS MADE TO LOCATE AND UTILIZE TWO EXISTING LINE STOPPER FITTINGS SHOWN ON THE WISCONSIN GAS COMPANY¿S MAPS AND WOULD RESULT IN SIGNIFICANTLY REDUCING THE NUMBER OF POTENTIAL CUSTOMER OUTAGES. THE FIRST STOPPER FITTING WAS LOCATED AND ACTIVATED. THE SECOND FITTING WAS NOT LOCATED DESPITE EXTENSIVE DIGGING BECAUSE THE WRONG REFERENCE MARK WAS BEING UTILIZED IN THE FIELD. WITH THE BLOWING GAS STILL UNDER CONTROL FROM CAUSING ANY ADDITIONAL DAMAGE, A DECISION WAS MADE TO INSTALL A NEW 6¿ LINE STOPPER FITTING TO AGAIN MINIMIZE THE LOSS OF CUSTOMERS. UPON COMPLETION, THE SECOND STOPPER WAS ACTIVATED, THE FLOW OF GAS SHUT OFF AND EXTINGUISHED AT APPROXIMATELY 9:10PM. AS SOON AS ACCESS TO THE DAMAGED AREA WAS AVAILABLE, THE EXISTING TEE WAS RETIRED AND A NEW 3¿ TEE AND ASSOCIATED MAIN INSTALLED. GAS WAS THEN RESTORED TO THE AREA AND 39 GAS METER LOCATIONS WERE RE-LIT. | 182399 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
382 | 2006-07-16 | TX | other | UNKNOWN (PECOS COUNTY) | CITY OF FORT STOCKTON | AN 11 YEAR OLD GIRL GOT IN A VEHICLE AND BACKED UP IN HER YARD HITTING THE GAS METER. THE VEHICLE BECAME HIGH CENTERED ON TOP OF THE GAS METER SET AND COULD NOT BE MOVED. | 2970 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
383 | 2006-07-20 | IL | other | UNKNOWN (COOK COUNTY) | NICOR GAS | INVESTIGATION FOUND THAT A BOX OF CLOTHES WAS STORED ON THE FLOOR IN FRONT OF ONE OF TWO WATER HEATERS IN THE UTILITY ROOM. THE BOX WAS STORED TOO CLOSE TO THE WATER HEATER AND WAS IGNITED FROM THE WATER HEATER BURNER. THERE WERE TWO GAS METERS LOCATED ON THE OPPOSITE SIDE OF THE THE UTILITY ROOM. ONE METER WAS DAMAGED AS A RESULT OF THE FIRE, CAUSING A RELEASE OF GAS. THE SECOND METER WAS REMOVED BY AN UNAUTHORIZED PARTY PRIOR TO THE FIRE. NOTE: THE ESTIMATED PRESSURE AT THE TIME OF THE RELEASE WAS APPROXIMATELY 1/4-PSIG BUT THE DATABASE DOES NOT ACCEPT NUMBERS OTHER THAN WHOLE INTEGERS THEREFORE 1-PSIG WAS ENTERED TO PROCESS THE REPORT. | 50500 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
384 | 2006-07-18 | TX | sabotage | UNKNOWN (HARRIS COUNTY) | CENTERPOINT ENERGY | THIRD PARTY COLT UTILITIES DAMAGED 4" PLASTIC MAIN WHILE INSTALLING STORM SEWER WITH A TRACKHOE. | 75424 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
385 | 2006-07-18 | MS | maintenance | UNKNOWN (LAUDERDALE COUNTY) | ATMOS ENERGY CORPORATION | <P>RECORDS REFLECT THAT THE INITIAL SERVICE TAP TO THE MAIN WAS INSTALLED IN 1962, AFTER WHICH THE STEEL SERVICE LINE IN QUESTION WAS INSTALLED. THE INVESTIGATION REVEALED A HOLE IN A SERVICE LINE APPARENTLY DUE TO LOCALIZED CORROSION. THE CAUSE OF THE LOCALIZED CORROSION WAS INVESTIGATED. SOIL SAMPLES WERE OBTAINED. THE SOIL SAMPLES WERE ANALYZED AND DID NOT REVEAL A REASON FOR THE LOCALIZED CORROSION. AN EXCAVATION OF A NEARBY WATER LINE ALSO DID NOT REVEAL A REASON FOR THE LOCALIZED CORROSION. THE CONNECTION OF THE SERVICE LINE TO THE CATHODICALLY PROTECTED GAS MAIN WAS INVESTIGATED. THE COMPRESSION COUPLING AT THE CONNECTION OF THE SERVICE TO THE MAIN SHOWED A CONTINUITY OF THE CATHODIC PROTECTION. THE FIRST NINE (9) FEET OF SERVICE LINE WERE CATHODICALLY PROTECTED. FURTHER EXCAVATION REVEALED A DISRUPTION OF THE CATHODIC PROTECTION ON THE SERVICE LINE DOWNSTREAM FROM ANOTHER COMPRESSION COUPLING, LOCATED APPROXIMATELY NINE (9) FEET FROM THE CONNECTION TO THE MAIN, WHICH ACCOUNTED FOR THE ACCELERATED CORROSION IN THAT SECTION OF THE SERVICE LINE.</P> | 200000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
386 | 2006-08-02 | LA | sabotage | UNKNOWN (LAFOURCHE COUNTY) | SOUTH COAST GAS CO. |  | 315 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
387 | 2006-02-27 | TX | other | UNKNOWN (LUBBOCK COUNTY COUNTY) | ATMOS ENERGY CORPORATION | AT APPROXIMATELY 4:30 P.M. A PROPANE TANK AT WYLIE LP GAS INC. IGNITED, RESULTING IN A LARGE FIRE AT 8205 AVENUE F. THE LUBBOCK FIRE AND POLICE DEPARTMENT RESPONDED TO THE AREA AND SET UP A 1/2 MILE RADIUS PERIMETER AROUND THE PROPANE FIRE. BUSINESSES AND HOMES WERE EVACUATED INSIDE THE PERIMETER. AT 7:10 P.M. , THE FIRE DEPARTMENT REPORTED SEEING NATURAL GAS METER SETTINGS ON FIRE WITH THE PERIMETER, HOWEVER ATMOS CREWS WERE RESTRICTED FROM THE AREA UNTIL THE FIRE WAS CONTAINED. AN INCIDENT REPORT WAS MADE TO THE TEXAS RAILROAD COMMISSION AT 8:45 P.M. REGARDING THE NATURAL IGNITION. AT APPROXIMATELY 10:30 P.M. THE FIRE DEPARTMENT ESCORTED TWO ATMOS SERVICE TECHNICIANS TO ASSESS AND REPAIR THE SERVICES. THE TECHNICIANS VALVED OFF THREE RISERS AND REPLACED A FOURTH RISER THAT WAS LEAKING UNDERGROUND. A DETERMINATION WAS MADE THAT THE IMPACT OF THE PROPANE FIRE DAMAGED SEVERAL METER SETTINGS RESULTING IN THE RELEASE AND IGNITION OF NATURAL GAS. | 9429 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
388 | 2006-08-02 | IL | other | UNKNOWN (COOK COUNTY) | NICOR GAS | FIRE DEPARTMENT INVESTIGATION REVEALED THIS WAS AN ARSON FIRE WHICH DAMAGED THE GAS METER WHICH WAS LOCATED INSIDE THE GARAGE. DAMAGE FROM THE FIRE CAUSED THE RELEASE OF GAS FROM THE METER. REGULATOR WAS LOCATED OUTSIDE AND SUSTAINED NO DAMAGE. NOTE: ESTIMATED DELIVERY PRESSURE AT TIME OF RELEASE WAS 1/4-PSIG. DATABASE ONLY ALLOWS FULL INTEGERS TO BE ENTERED. THEREFORE, TO PROCESS THE REPORT, 1-PSIG WAS ENTERED. | 60500 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
389 | 2006-08-07 | SC | other | UNKNOWN (SOUTH CAROLINA COUNTY) | SOUTH CAROLINA ELECTRIC & GAS COMPANY |  | 78936 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
390 | 2006-08-21 | LA | sabotage | UNKNOWN (TERREBONNE COUNTY) | SOUTH COAST GAS CO. |  | 400 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
391 | 2005-09-08 | LA | natural disasters | UNKNOWN (ST. BERNARD PARISH COUNTY) | ATMOS ENERGY - LOUISIANA DIVISION | THIS INCIDENT OCCURRED AS A RESULT OF THE AFTERMATH OF HURRICANE KATRINA WHICH INCLUDED RECEIVING FLOOD WATERS WITH THE RESULTS OF MOST OF OUR SYSTEM BEING SUBMERGED. THE RESULTING RELEASE OF NATURAL GAS WS DUE MAINLY FROM HOUSES AND DEBRIS BEING PUSHED BY THE FLOOD WATERS THUS DAMAGING METERS CAUSING A RELEASE OF GAS TO THE ATMOSPHERE. SINCE THE AREA WAS FLOODED FROM THE HURRICANE, THESE LEAKS WERE UNREACHABLE TO STOP. CONCERN OCCURED WHEN A NEAR-BY OIL REFINERY CRUDE OIL TANK RUPTURED FROM THE FLOODING CONDITIONS AND THE OIL MIGRATED OUTSIDE OF THE REFINERY PROPERTY AND INTO THE RESIDENTIAL COMMUNITY. BEING A PRUDENT OPERATOR WE FELT OBLIGED TO SHUT-IN THE NATURAL GAS DISTRIBUTION SYSTEM AT THE NEAREST OPPORTUNITY TO STOP THE FLOW OF GAS INTO THE ATMOSPHERE THUS PREVENTING THE POSSIBILITY OF ACCIDENTAL IGNITION FROM NATURAL GAS. WHEN FLOOD WATERS SUBSIDED, NO MAJOR SYSTEM WASHOUTS AND/OR EXPOSED MAINS OCCURED AS THE RESULT OF THE RUSHING FLOOD WATERS. THE DISTRIBUTION SYSTEM WAS INITIALLY RESTORED AND IS STILL BEING RESTORED IN REMOTE AREAS WITHIN THE FRAMEWORK OF OUR EXISTING O&M PROCEDURES MANUAL AND IN COORDINATION WITH FEDERAL, STATE, AND LOCAL OFFICIALS. | 2000000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
392 | 2006-08-02 | MO | sabotage | UNKNOWN (WARREN COUNTY) | UNION ELECTRIC COMPANY D/B/A AS AMERENUE | RALPH JONES GRADING AND CONTRACTING WAS PERFORMING EXCAVATION FOR THE INSTALLATION OF A NEW ROAD FOR A RESIDENTIAL SUBDIVISION NEAR THE INTERSECTION OF STUERMANN ROAD AND HIGHWAY H NEAR WRIGHT CITY, MO. THE CONTRACTOR WAS OPERATING EXCAVATING EQUIPMENT AND DAMAGED THE 6-INCH STEEL GAS MAIN. THE DAMAGE RESULTED IN THE LOSS OF GAS SERVICE TO APPROXIMATELY 1000 CUSTOMERS IN WARRENTON, MO AND TRUESDALE, MO. | 299457 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
393 | 2006-08-13 | CA | other | UNKNOWN (ALAMEDA COUNTY) | PACIFIC GAS AND ELECTRIC COMPANY | ON 8/13/2006 AT 1602 HOUR, A STRUCTURAL FIRE OCCURED AT 2126 35TH AVENUE IN OAKLAND, CALIFORNIA TO A 4-UNIT APARTMENT BUILDING CAUSING DAMAGE TO 1 UNIT AND THE BASEMENT. GAS METER WAS MELTED DOWN DUE TO FIRE, BURNING GAS THROUGH SERVICE RISER WAS A RESULT OF METER MELT DOWN. THE 1-1/4" RISER WAS PLUGGED AT SERVICE VALVE. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
394 | 2006-08-24 | OH | other | UNKNOWN (GUERNSEY COUNTY) | COLUMBIA GAS OF OHIO | PROPERTY OWNER AT 1439 ELM STREET, CAMBRIDGE, OH WAS USING AN AUGER DEVICE TO CLEAN OUT THE SEWER LATERAL FROM HIS PROPERTY WHEN THE DEVICE PUCTURED A PLASTIC MEDIUM PRESSURE MAIN GAS LINE RESULTING IN A LEAK. WITHIN A SHORT TIME THE LEAK CAUSED AN EXPLOSION TO OCCUR DAMAGING THREE RESIDENTIAL PROPERTIES (INCLUDING THE ONE WHERE THE PROPERTY OWNER USING THE AUGER WAS LOCATEDP AND INJURING TWO PEOPLE (INCLUDING THE PROPERTY OWNER) PRELIMINARY INVESTIGATION REVEALED THAT THE PLASTIC GAS MAIN WHICH HAD BEEN INSTALLED BY A CONTRACTOR IN ELM STREET IN 2001 HAD CROSSED THROUGH THE AREA OF THE SEWER LATERAL UNDER A DRIVEWAY AREA THAT EXTENDED INTO PUBLIC RIGHT OF WAY. ALTHOUGH MOST OF THE INSTALLATION IN 2001 WAS PERFORMED USING THE TRENCH METHOD, THE PORTIONS OF THE INSTALLATION THAT TRAVERSED DRIVEWAYS AND PAVEMENT WERE BORED USING A HOLE HOG DEVICE. A PROPER LOCATE REQUEST HAD BEEN MADE TO THE CITY OF CAMBRIDGE FOR LOCATION OF THE SEWER LINE, BUT APPARENTLY THE LATERALS ARE NOT LOCATED AS THEY ARE DEEMED CUSTOMER PROPERTY BY THE CITY. THERE WAS NO INDICATION AT TIME OF INSTALLATION THAT IT HAD INTERFERED WITH THE SEWER LATERAL. MOREOVER, SINCE THE SEWER MAIN IS ESTIMATED TO BE 9 FEET DEEP, IT WAS NOT CONTEMPLATED THAT A SEWER LATERAL WOULD BE ENCOUNTERED AND ONLY BE AT A DEPTH OF ABOUT 30 TO 31 INCHES, WHICH WAS THE DEPTH THE PLASTIC GAS MAIN WAS INSTALLED AT. | 307224 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
395 | 2006-08-24 | IA | sabotage | UNKNOWN (POLK COUNTY) | MIDAMERICAN ENERGY COMPANY | PROPERTY MANAGEMENT COMPANY EMPLOYEES HIT A 2" 60 PSIG GAS MAIN AT 6944 HEMINGWAY ST. WHILE ADDRESSING A PROBLEM WITH SURFACE WATER DRAINAGE. THE PROPERTY MANAGEMENT COMPANY HAD NOT REQUESTED LOCATES. | 66500 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
396 | 2006-08-30 | OR | sabotage | UNKNOWN (JACKSON COUNTY COUNTY) | AVISTA UTILITIES | A THIRD PARTY CONTRACTOR WAS GRADING AND CLEARING A RESIDENTIAL BUILDING LOT WITH A TRACKHOE TO PREPARE IT FOR BUILDING CONSTRUCTION AT 173 EVENBROOK. HE STRUCK BOTH THE 2" PE GAS MAIN AND THE POWERLINE THAT WERE INSTALLED IN A JOINT DITCH IN THE PUBLIC UTILITY EASEMENT. THE GAS MAIN WAS COMPLETELY SEVERED. NO LOCATES WERE REQUESTED AND THE GAS MAIN WAS NOT MARKED. THE GAS WAS IGNITED BY THE POWERLINE. THE TRACKHOE CAUGHT ON FIRE AND WAS CONSUMED. NO ONE WAS INJURED IN THE INCIDENT. SERVICE WAS INTERRUPTED TO ONE CUSTOMER FOR APPROXIMATELY 1 1/2 HOURS. | 91700 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
397 | 2006-09-09 | CA | sabotage | UNKNOWN (LOS ANGELES COUNTY) | SOUTHERN CALIFORNIA GAS COMPANY | HOMEOWNER REMOVING STREE STUMP WITH POWERED EXCAVATING EQUIPMENT PULLED SERVICE, EXERTING PRESSURE ON METER SET ASSEMBLY THAT ULTIMATELY BROKE, RELEASING NATURAL GAS AT HOUSELINE PRESSURE (1/3 PSI.) ESCAPING GAS WAS INGINITED BY NEARBY WATER HEATER, CATCHING HOME ON FIRE. BECAME REPORTABLE WHEN FIRE DAMAGE EXCEEDED $50K. NO INJURIES. FOR MORE INFORMATION, CONTACT JEFF KOSKIE AT 213 244-3283. | 100520 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
398 | 2006-09-18 | CA | sabotage | UNKNOWN (LOS ANGELES COUNTY) | SOUTHERN CALIFORNIA GAS COMPANY | CONTRACTOR WAS AUGERING HOLES 10' TO 15' WHEN HE STRUCK 8" STEEL MAIN. AUGER BECAME STUCK IN MAIN, AND LARGE SHORED EXCAVATION HAD TO BE DUG TO RETRIEVE EQUIPMENT. ADJACENT FREEWAY WAS CLOSED AS A RESULT. BECAME REPORTABLE WHEN IT WAS EVIDENT THAT CONTRACTOR WOULD NOT BE ABLE TO READILY REMOVE AUGER, AND RESULTING POTENTIAL DOWNTIME CLAIMS, AS WELL AS SIGNIFICANT EXCAVATING AND SHORING PUSHED ASSOCIATED COST ESTIMATE OVER $50K. INVOLVED VICINITY HAD A REGULATOR STATION AND FOUR SEPARATE MAINS: 30¿ HIGH PRESSURE, 24¿ MEDIUM PRESSURE, 16¿ MEDIUM PRESSURE AND 8¿ MEDIUM PRESSURE, INVOLVING EXTENSIVE LOCATE AND MARK ACTIVITIES. THE LOCATOR DID NOT REALIZE THAT THE 8¿ MEDIUM PRESSURE CONTINUED SOUTH OF THE REGULATOR STATION, AND AS A RESULT FAILED TO LOCATE THE FACILITY. THE LOCATOR RELIED UPON THE APERTURE CARD VS. AN ATLAS PRINT. THE APERTURE CARD DID NOT SHOW THIS FACILITY AS CLEARLY AS THE ATLAS PRINT. COUNSELED EMPLOYEE IN UTILIZING ALL AVAILABLE RESOURCES TO ASSURE ACCURATE LOCATING OF ALL GAS FACILITIES, INCLUDING PRINTS OF THE ENTIRE WORK LOCATION AND UPDATES FROM TECHNICAL SERVICES REGARDING RECENT INSTALLATIONS. DISCUSSED THIS INCIDENT AND LESSONS LEARNED WITH DISTRICT PERSONNEL. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
399 | 2006-09-03 | MD | sabotage | UNKNOWN (WORCESTER COUNTY) | EASTERN SHORE GAS COMPANY |  | 200000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
400 | 2006-09-01 | TX | other | UNKNOWN (WILLIAMSON COUNTY) | ATMOS ENERGY CORPORATION - MID TEXAS DIVISION | A VEHICLE STRUCK A TWO METER MANIFOLD CAUSING A GAS LEAK AND THE ESCAPING GAS IGNITED. | 37000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
401 | 2006-09-02 | PA | leaks and spills | UNKNOWN (LANCASTER COUNTY) | UGI UTILITIES, INC. | 04/28/2015: AN INVESTIGATION INTO THE FAILURE INDICATED THAT TWO OF THE FOUR NYLON BOLTS USED TO ATTACH THE TEE TO THE MAIN CRACKED AND ALLOWED GAS TO LEAK. A REMEDIATION PROGRAM WAS LAUNCHED TO INVESTIGATE AND REPAIR SIMILIAR TEES. THIS FINAL REPORT IS BEING SUBMITTED TO UPDATE COSTS FAILURE CAUSE AND TO CLOSE THE INCIDENT REPORT. GAS MIGRATED FROM AN UNDERGROUND LEAKING MECHANICAL SERVICE TEE INTO A RESIDENTIAL STRUCTURE. THE GAS WAS IGNITED CAUSING AN EXPLOSION. THE BUILDING COLLAPSED BREAKING THE METER SET BELOW THE METER VALVE, ACTIVATING THE EXCESS FLOW VALVE. | 381300 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
402 | 2006-07-22 | MS | other | UNKNOWN (WARREN COUNTY) | MISSISSIPPI RIVER GAS | RAINING ALL DAY, VERY WET CONDITION, CAR LOST CONTROL HIT GAS REGULATOR. | 10978 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
403 | 2006-10-07 | OH | other | UNKNOWN (WOOD COUNTY COUNTY) | COLUMBIA GAS OF OHIO | THE CAUSE OF THIS FIRE IS UNDETERMINABLE AND THIS REPORT SHOULD BE CONSIDERED FINAL. THE FIRE WAS INVESTIGATED BY COLUMBIA INVESTIGATORS WHO WERE NOT ABLE TO ASCERTAIN, WITH REASONABLE CERTAINTY, THE CAUSE OR ORIGIN. A NON-JUISDICTIONAL POOL HEATER WITH A BRASS APPLIANCE VALVE LOCATED NEAR THE OUTSIDE METER SETTING WAS FRACTURED FROM AN OVERLOAD CONDITION. IT COULD NOT BE DETERMINED WITH REASONABLE CERTAINTY IF THE FRACTURE OCCURRED BEFORE THE FIRE OR AS A RESULT OF THE FIRE. THE PREMISE CONTAINED A CUSTOMER OWNED NORMAC RISER, AND LABORATORY EVALUATION OF THIS RISER ALSO DETERMINED THAT IT WAS INCORRECTLY ASSEMBLED. RADIOGRAPHIC EXAMINATION OF THE RISER REVEALED THAT THE METAL RING WAS INSTALLED UPSIDE DOWN.. THERE IS NO INDICATION THAT THE MISASSEMBLY CONTRIBUTED TO THE FIRE. AS WITH THE BRASS APPLIANCE VALVE, IT CAN NOT BE NOT BE ASCERTAINED TO A REASONABLE DEGREE OF CERTAINTY IF THE RISER FAILURE OCCURRED BEFORE THE FIRE OR AS A RESULT OF THE FIRE. AS A RESULT OF THE PUCO’S INVESTIGATION OF PRONE TO FAIL RISERS, COLUMBIA GAS OF OHIO INC. HAS TAKEN CORRECTIVE ACTIONS. A PROGRAM IS WELL UNDERWAY TO REPLACE ALL RISERS IDENTIFIED BY THE PUCO AS PRONE TO FAIL. THE PROGRAM IS 90% COMPLETE WITH AN EXPECTED COMPLETION DATE OF JUNE 20, 2011. | 95355 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
404 | 2006-09-12 | MO | sabotage | UNKNOWN (SAINT LOUIS COUNTY) | LACLEDE GAS COMPANY | ADB UTILITY CONTRACTING, A SUBCONTRACTOR FOR AMEREN UE IN PREPARATION FOR INSTALLING AN ELECRIC LINE, WAS BORING FROM 1387 PREMIO DRIVE UNDERNEATH AND ACROSS PREMIO DRIVE TO A PEDESTAL LOCATION IN FRONT OF 1394 PREMIO DRIVE. DURING THE BORING OPERATION, A 2-INCH GAS MAIN IN FRONT OF 1390 PREMIO DRIVE WAS STRUCK AT A DEPTH OF APPROXIMATELY 36 INCHES. GAS MIGRATED INTO THE RESIDENCE AT 1390 PREMIO DRIVE RESULTING IN AN EXPLOSION AND FIRE. | 318804 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
405 | 2006-09-28 | CA | sabotage | UNKNOWN (SACRAMENTO COUNTY) | PACIFIC GAS & ELECTRIC COMPANY | AT 0734 HOURS TEICHERT CONSTRUCTION WAS USING AN EARTHMOVER IN ITS QUARRY WHEN IT STRUCK A 12 INCH GAS DISTRIBUTION MAIN CAUSING GAS TO ESCAPE THROUGH A 3 INCH BY 36 INCH RIP. THE DECREASE IN LINE PRESSURE CAUSED LOSS OF SERVICE TO TWO CUSTOMERS, ONE OF WHICH WAS A RESALE CUSTOMER (WEST COAST GAS) THAT IN TURN LOST APPROXIMATELY 1200 CUSTOMERS. THE ESCAPE OF GAS WAS STOPPED AT 1435 HOURS AFTER FITTINGS WERE INSTALLED ON THE LINE AND LINE STOPPERS WERE INSTALLED. THE DAMAGED SECTION OF THE PIPE WAS REPLACED AND SERVICE WAS RESTORED AT 1625 HOURS. THE EXCAVATOR PROPERLY CALLED THE ONE CALL CENTER AND THE LINE WAS ACCURATELY MARKED. THE INCIDENT WAS IN AN ISOLATED LOCATION. | 59987 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
406 | 2006-10-09 | GA | maintenance | UNKNOWN (PEACH COUNTY) | FORT VALLEY UTILITY COMMISSION | IN ORDER TO INSTALL A REPAIR CLAMP ON A LEAKING MAIN, TWO EMPLOYEES ENTERED AN EXCAVATED AREA AT THE LEAK SITE AND WORKED THROUGH BLOWING GAS AND DIRT WHILE TWO MORE EMPLOYEES STOOD BY. AFTER COMPLETION OF THE REPAIR, BOTH EMPLOYEES THAT HAD ENTERED THE EXCAVATION COMPLAINED OF BREATHING DIFFICULTIES. THESE TWO EMPLOYEES WERE TAKEN TO THE LOCAL HOSPITAL EMERGENCY ROOM, WHERE THEY WERE TREATED AND RELEASED. ONE EMPLOYEE DID NOT REST WELL DURING THE NIGHT AND RETURNED TO THE HOSPITAL THE NEXT MORNING, OCTOBER 10, 2006, COMPLAINING OF DISCOMFORT IN HIS CHEST. THE LOCAL HOSPITAL SENT HIM TO A REGIONAL HOSPITAL WHERE HE WAS ADMITTED AND TREATED FOR A HEART CONDITION BY INSTALLING A STINT IN AN ARTERY. EMPLOYEE WAS DISCHARGED FROM HOSPITAL A FEW DAYS LATER AND RETURNED TO LIGHT-DUTY WORK ON NOVEMBER 6, 2006. | 500 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
407 | 2006-11-13 | AK | other | UNKNOWN (nan COUNTY) | ENSTAR NATURAL GAS COMPANY | ON NOVEMBER 13, 2006, AT 2314 AST, ENSTAR NATURAL GAS COMPANY WAS NOTIFIED OF A HOUSE FIRE AT LOT 11, LAKE ESTATES, ROSS DRIVE, IN SOLDOTNA ALASKA. THE ORIGIN OF THE FIRE IS UNKNOWN, BUT NATURAL GAS IS NOT BELIEVED TO HAVE CAUSED OR CONTRIBUTED TO THE FIRE. THE FIRE BURNED THE GAS METER AND HDPE RISER, RELEASING NATURAL GAS. THE SERVICE LINE WAS DUG UP AND PINCHED OFF TO SHUT OFF THE GAS. THE INCIDENT WAS UNDER CONTROL AT 0100 AST ON NOVEMBER 14, 2006. NATURAL GAS DID NOT CAUSE OR CONTRIBUTE TO THE FIRE. | 51050 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
408 | 2006-10-22 | IL | other | UNKNOWN (nan COUNTY) | NICOR GAS | STRUCTURE FIRE TRAVELED THROUGH THE HOUSE AND REACHED THE ATTACHED OUTSIDE METER SET CAUSING DAMAGE WHICH RESULTED IN A RELEASE OF GAS. | 100600 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
409 | 2006-10-14 | SD | natural disasters | UNKNOWN (MINNEHAHA COUNTY COUNTY) | MIDAMERICAN ENERGY COMPANY | MIDAMERICAN ENERGY COMPANY CONSIDERS THIS INCIDENT TO BE A SIGNIFICANT EVENT. A GAS LEAK WAS IGNITED BY A MOTOR VEHICLE STOPPED AT A TRAFFIC SIGNAL RED LIGHT. THE INVESTIGATION DISCOVERED THAT THE 4" CAST IRON MAIN INSTALLED IN 1950 CRACKED CIRCUMFERENTIALLY. THE CAUSE OF THE CRACK IS CONSIDERED TO BE BENDING STRESS FROM AN UNIDENTIFIED SOURCE. THE LOCATION OF THE CRACK IS IN THE PROXIMITY OF A SUBSTANTIAL NUMBER OF BURIED UTILITIES AND STRUCTURES THAT WERE INSTALLED SUBSEQUENT TO THE INSTALLATION OF THE CAST IRON MAIN IN 1950. | 25100 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
410 | 2006-10-27 | MO | maintenance | UNKNOWN (ATCHISON COUNTY) | EMPIRE DISTRICT GAS CO | COMPANY EMPLOYEE WAS SHUTTING OFF GAS METER FOR CUSTOMER EQUIPMENT MAINTENANCE. THE SHUT OFF VALVE CORE BROKE CAUSING GAS TO ESCAPE. ESCAPING GAS IGNITED CAUSING THE BUILDING TO CATCH ON FIRE AND BURN. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
411 | 2006-10-23 | OR | sabotage | UNKNOWN (WASHINGTON COUNTY) | NW NATURAL GAS COMPANY | A PAINTING CONTRACTOR HIRED BY THE HOMEOWNER AT 16229 S.W. STAHL DRIVE, TIGARD OREGON, BELIEVED THE HOUSE WAS NOT ELECTRICALLY GROUNDED. THE PAINTING CONTRACTOR CONTACTED AN ELECTRICIAN TO INSTALL A GROUNDING ROD. THE ELECTRICIAN DROVE A 3/4 INCH DIAMETER, 8-FOOT LONG ELECTRIC GROUNDING ROD INTO THE GROUND, PUNCTURING NW NATURAL'S 1/2 INCH DIAMETER CTS, PE 2406 POLYETHYLENE SERVICE LINE. GAS FROM THE DAMAGE WAS RELEASED UNDERGROUND. THE HOMEOWNER AND PAINTING CONTRACTOR NOTIFIED NW NATURAL OF THE DAMAGE AND A COMPANY CREW WAS IMMEDIATELY DISPATCHED TO THE SITE. WHILE A NW NATURAL CREW WAS ATTEMPTING TO MAKE SAFE, THERE WAS AN EXPLOSION AND THE HOUSE IGNITED. TWO NW NATURAL EMPLOYEES WERE TAKEN TO THE HOSPITAL AND TREATED FOR SECOND DEGREE BURNS TO ARMS AND FACE. ONE EMPLOYEE WAS HOSPITALIZED OVERNIGHT. | 450500 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
412 | 2006-10-20 | MD | other | UNKNOWN (PRINCE GEORGES COUNTY) | WASHINGTON GAS | WASHINGTON GAS WAS RESPONDED TO A HOUSE FIRE IN PROGRESS AT 6401 GREENVALE PARKWAY IN RIVERDALE, MARYLAND. UPON ARRIVAL, THE E WAS ENGULFED IN FLAMES. ACCESS TO THE METER, WHICH WAS LOCATED IN THE BASEMENT, COULD NOT BE GAINED WHICH MADE THE RETRIEVAL OR EXAMINATION OF THE METER BUILD-UP AND REGULATOR IMPOSSIBLE AT THIS TIME. THE GAS SUPPLY WAS SHUT OFF AT THE CURB COCK LOCATED AT THE SIDEWALK. DUE TO THE SEVERE DAMAGE AND SEVERAL FEET OF WATER IN THE BASEMENT OF THE DWELLING, THE FIRE INVESTIGATOR WOULD NOT ALLOW ENTRY INTO THE STRUCTURE DUE TO EXTREMELY UNSAFE CONDITIONS. CAUSE OF THE INCIDENT AT THIS TIME IN UNKNOWN/ UNDETERMINABLE. THE FIRE DEPARTMENT WILL NOT BE CONDUCTING ANY FURTHER INVESTIGATION OF THIS INCIDENT. UPDATED BY PHMSA ON 2/9/2016 PER THE OPERATOR'S MARK UP (PART A - GENERAL INFORMATION, QUESTION 3 LOCATION OF INCIDENT; AND PART F - APPARENT CAUSE, F7 - OTHER, QUESTION 25). | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
413 | 2006-10-26 | NY | other | UNKNOWN (MONROE COUNTY) | ROCHESTER GAS AND ELECTRIC | A RG&E EMPLOYEE WAS INJURED WHILE REMOVING A CAP FROM A 1 1/2" SAV-A-VALVE NIPPLE ON A 2" STEEL MAIN OPERATING AT 60PSI. THE INSERT TO THE SAV-A-VALVE HAD NOT BEEN REPLACED AT A TIME PRIOR TO THIS INCIDENT. FITTINGS IN THE CONDITION ARE TYPICALLY STRAPPED TO IDENTIFY THEN AS UNUSABLE. THIS FITTING WAS NOT STRAPPED AND THERE WAS NO OTHER MARKING TO INDICATE ITS CONDITION AT THE TIME OF THIS PROCEDURE. THE EMPLOYEE WAS TREATED AND RELEASED FROM THE HOSPITAL ON 10/26. THE EMPLOYEE RETURNED TO THE HOSPITAL ON 10/30 TO CLEAN THE SKIN AND REMOVE THE REMAINING DEBRIS FROM HIS ARM. ON 10/31, THE EMPLOYEE WAS AGAIN ADMITTED TO THE HOSPITAL. RG&E REPORTED THE INCIDENT TO THE DOT ON 10/31 (NRC - REPORT #816599) | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
414 | 2006-11-28 | NM | maintenance | UNKNOWN (LOS ALAMOS COUNTY) | KSL | ISOLATION VALVE FROM LOCAL TRANSPORTATION COMPANY (PNM) LEAKED BY DURING TIC INS FOR A NEW SERVICES. NO SIGNIFICANT SAFETY ISSUES OCCURED. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
415 | 2006-10-10 | CA | sabotage | UNKNOWN (NAPA COUNTY) | PACIFIC GAS & ELECTRIC COMPANY | A CONTRACTOR WORKING FOR CALTRANS STRUCK A 2" STUB OFF A 6" DFM TRANSMISSION LINE CAUSING THE STUB TO COME AWAY FROM THE WELD CREATING A LEAK. A PG&E STAND-BY PERSON WAS PRESENT. MEDIA WAS PRESENT ON SITE @ 0720 AND CPUC WAS NOTIFIED. COST OF INCIDENT WAS ESTIMATED TO REACH THE $50K CRITERIA @ 1020 AND DOT NOTIFIED. CREWS INJECTED CNG TO SUPPLY GAS TO APPROXIMATELY 3000 CUSTOMERS. LNG WAS ON STAND-BY. 39 SERVICES AND 70 CUSTOMERS WERE LOST. SHUT IN LINE AND INSTALLED 3' SECTION OF NEW 6" PIPE. RELIGHTS COMPLETED BY 1700 ON 10/12/06. | 75000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
416 | 2006-10-26 | TX | other | UNKNOWN (HARRIS COUNTY) | CENTERPOINT ENERGY | OUTSIDE FORCE DAMAGE TO 3/4'" POLY PIPE BY UNKNOWN PARTY ON UNKNOWN DATE AT 3714 QUITMAN WHERE A FIRE AND EXPLOSION OCCURRED. | 155122 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
417 | 2006-11-11 | NY | sabotage | UNKNOWN (nan COUNTY) | KEYSPAN ENERGY DELIVERY LONG ISLAND (KEYSPAN GAS EAST CORP, DBA) | ON SATURDAY, NOVEMBER 11, 2006, THE HOUSE AT 21 CARLEY AVE. IN HUNTINGTON SUSTAINED EXTENSIVE DAMAGE FROM A FIRE/EXPLOSION. THE INCIDENT WAS CAUSED BY A CONTRACTOR WHO WAS EXCAVATING WITH A BACKHOE ON THE PROPERTY DURING HOME RENOVATION WORK. THE BACKHOE HIT AND PULLED THE HIGH PRESSURE SERVICE TO THE HOUSE, RESULTING IN A SEPARATION OF THE HOUSELINE FROM THE METER VALVE INSIDE THE BASEMENT. THE CONTRACTOR EVACUATED 1 PERSON FROM THE HOUSE BEFORE IGNITION. NO INJURIES WERE REPORTED AS A RESULT OF THE INCIDENT. THE SUBSEQUENT INVESTIGATION CONFIRMED THAT THE PIPELINE MARKOUT WAS ACCURATE. | 400000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
418 | 2006-10-16 | TX | sabotage | UNKNOWN (COLLIN COUNTY) | ATMOS ENERGY CORP, MID-TEX DIVISION | THE INVESTIGATION BY GEO-TECHNICAL, MATERIALS, AND MECHANICAL ENGINEERS HAS DETERMINED THAT THE SERVICE LINE NEARLY COMPLETELY PULLED OUT OF THE COMPRESSION COUPLING DUE TO FORCES FROM THE OPERATION OF HEAVY VIBRATORY COMPACTING EQUIPMENT BY A THIRD PARTY CONTRACTOR DURING THE INSTALLATION OF A WATER LINE THAT UNDERCUT THE NATURAL GAS SERVICE LINE WITHOUT PROVIDING ADEQUATE SUPPORT FOR THE PIPE DURING BACKFILL PROCEDURES. MINIMAL SOIL MOVEMENT CAUSED BY HEAVY RAINS LED TO THE FINAL SEPARATION. THIS SOIL MOVEMENT WOULD NOT HAVE CAUSED A PULLOUT OF THE POLYETHYLENE NATURAL GAS SERVICE LINE BUT FOR THE PRIOR MOVEMENT OF THE PIPE CAUSED BY THE THIRD PARTY'S BACKFILLING AND COMPACTING. THE RESTRAINING FORCES OF THE COMPRESSION COUPLING WERE SUFFICIENT FOR ANTICIPATED EXTERNAL AND INTERNAL LOADS. THE FORCES FROM NATURAL SOIL MOVEMENT ON THE 13 FT. LENGTH OF ¾ IN. POLYETHYLENE SERVICE LINE DID NOT EXCEED THE RESTRAINT FORCE OF THE COMPRESSION COUPLING INSTALLED IN 1979. FORCES FROM THERMAL CONTRACTION, IF ANY OVER THE SERVICE LIFE OF THE PIPE, WERE NEGLIGIBLE. THE PIPE OPERATED WELL BELOW MAOP. A SECOND SEPARATION WAS DISCOVERED ON THE SAME DAY AS THE INCIDENT ON THE SAME SIDE OF THE DIRT ALLEY FOUR HOUSES TO THE SOUTH. THIS SERVICE LINE WAS ALSO UNDERCUT BY THE SAME THIRD PARTY CONTRACTOR DURING THE INSTALLATION OF THE NEW WATER LINE. THIS LEAK WAS REPAIRED WITHOUT INCIDENT. | 270000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
419 | 2006-11-03 | IL | other | UNKNOWN (nan COUNTY) | THE PEOPLES GAS LIGHT AND COKE COMPANY | ON NOVEMBER 3, 2006 AT 5:39 P.M., THE CHICAGO FIRE DEPARTMENT REPORTED AN EXPLOSION AT 5404 S. AVERS ("PREMISES") TO PEOPLES GAS. IT APPEARS TO HAVE BEEN A NATURAL GAS EXPLOSION. THE INVESTIGATION IN TO THE CAUSE IS COMPLETE. NO GAS LEAKS WERE FOUND OUTSIDE OVER THE MAIN OR THE SERVICE LINE TO THE PREMISES. IN POST-INCIDENT PRESSURE TESTING OF THE SERVICE LINE, EVIDENCE OF A DE MINIMIS LEAK (MEASURED AT APPROXIMATELY 1/10 OF A CUBIC FOOT PER HOUR) WAS FOUND WHEN A KUHLMAN GAUGE WAS PLACED ON THE GAS SERVICE LINE INSIDE THE PREMISES WHERE THER SERVICE ENTERED THE FRONT BASEMENT WALL. THE LEAK WAS TO MINUTE TO HAVE ACCOUNTED FOR THE EXPLOSION .. THE LOCATION OF THE INFINITESIMAL LEAK HAS NOT BEEN PINPOINTED, BUT SOAP TESTING OF THE SERVICE HEAD ADAPTER AND HEEL OF THE SERVICE INSIDE THE PREMISES DID NOT INDICATE ANY LEAKS. PEOPLES GAS DOES NOT PLAN ANY FURTHER INVESTIGATION AT THIS TIME. HOWEVER, SHOULD LITIGATION ENSUE THERE WILL BE A FURTHER INVESTIGATION. | 350000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
420 | 2006-11-20 | IN | sabotage | UNKNOWN (HUNTINGTON COUNTY) | INDIANA GAS COMPANY, INC. | THIRD PARTY DAMEGED VECTREN 1-INCH PE SERVICE TO 1117 N. JEFFERSON ST., HUNTINGTON, IN BY PIERCING THE SERVICE WITH WHAT APPEARS TO BE A 5/8" ROD THAT WAS TO BE USED FOR GROUNDING PURPOSES. WITHIN APPROXIMATELY 2 MINUTES OF ARRIVAL OF THE VECTREN FIRST RESPONDER, THE STRUCTURE AT 1117 N. JEFFERSON EXPLODED AND FIRE ENSUED. THE EXPLOSION AND FIRE RESULTED IN TWO FATALITIES AND TWO SERIOUS INJURIES REQUIRING HOSPITALIZATION. INHABITANTS OF TWO ADJACENT STRUCTURES WERE EVACUATED DUE TO FIRE SPREADING TO THOSE STRUCTURES. | 900000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
421 | 2006-12-08 | AL | leaks and spills | UNKNOWN (LAMAR COUNTY) | NORTHWEST ALABAMA GAS DISTRICT |  | 50160 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
422 | 2006-11-27 | VA | sabotage | UNKNOWN (nan COUNTY) | VIRGINIA NATURAL GAS | A VIRGINIA NATURAL GAS FIELD SERVICE REPRESENTATIVE (FSR) WAS OVERCOME BY NATURAL GAS WHEN REPAIRING A LEAK CAUSES BY A THIRD PARTY EXCAVATOR DAMAGE. THE FSR REQUIRED OVERNIGHT HOSPITALIZATION. A DESCRIPTION OF THE INCIDENT IS ATTACHED. | 3841 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
423 | 2006-11-14 | MI | other | UNKNOWN (ISABELLA COUNTY) | MICHIGAN CONSOLIDATED GAS COMPANY/DTE ENERGY | ON NOVEMBER 14, 2006 AT APPROXIMATELY 2:00 PM A DRIVER LEAVING 204 NORTH ADAMS PREPARED TO BACK A PASSENGER CAR FROM THE DRIVEWAY AT THAT ADDRESS. THE DRIVER REPORTED THAT AFTER SELECTING REVERSE GEAR THE VEHICLE SUDDENLY SPED UNCONTROLLED BACKWARDS ACROSS NORTH ADAMS STREET; THE REAR OF THE VEHICLE STRUCK BOTH THE CORNER OF THEHOME AND NCHCON'S METER ASSEMBLY AT 203 NORTH ADAMS. THE VEHICLE CAME TO REST AGAINST THE BUILDING ADN THE METER ASSEMBLY. IGNITED BY AN UNKNOWN SOURCE, NATURAL GAS LEAKING FROM THE METER ASSEMBLY AND/OR CUSTOMER FUEL LINE ENGULFED THE VEHICLE IN FLAMES ALMOST IMMEDIATELY. THE DRIVER, THE SOLE OCCUPANT OF THE PASSENGER CAR , WAS ABLE TO ESCAPE THE VEHICLE WITHOUT INJURY. THE RESIDENCE AT 203 NORTH ADAMS WAS SOON INVOLVED IN THE FIRE. INITIAL RESPONSE WAS MADE BY THE MOUNT PLEASANT FIRE DEPARTMENT. FIRE DEPARTMENT OFFICIALS NOTIFIED MICHCON AT 2:12 PM, AND A MICHCON EMPLOYEE ARRIVED AT THE ADDRESS AT 2:28 PM TO FIND THE FIRE CREW ATTEMPTING TO LOCATE AND SQUEEZE-OFF THE SERVICE LINE TO THE BUILDING IN ORDER TO CONTROL THE FLAMES SINCE THE SERVICE VALVE AND METER WERE NOT ACCESSIBLE BEHIND THE BURNING VEHICLE. MICHCON EMPLOYEES QUICKLY LOCATED THE SERVICE LINE NEAR THE SIDEWALK AND PINCHED IT OFF, CONTROLLING THE GAS LEAK. THE PASSENGER VEHICLE AND THE BUILDING AT 203 NORTH ADAMS WERE TOTALLY DESTROYED BY FIRE. | 142150 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
424 | 2006-11-13 | TX | sabotage | UNKNOWN (FT. BEND COUNTY) | CENTERPOINT ENERGY | THIRD PARTY DAMAGE TO 4" PLUG VALVE WHILE BACKFILLING WITH TRACKHOE. | 21264 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
425 | 2006-12-09 | PA | technical failure | UNKNOWN (LEIGH COUNTY COUNTY) | UGI UTILITIES, INC. | A SUBCONTRACTOR FAILED TO FOLLOW PROCEDURE AND MISTAKENLY REMOVED A PLUG AT THE HEAD OF A MEDIUM PRESSURE SERVICE RELEASING GAS INTO THE RESIDENCE AT 789 MOHAWK STREET ALLENTOWN, PA. THE GAS IGNITED CAUSING AN EXPLOSION, WHICH COLLAPSED THE BUILDING AND TWO ADJACENT ROW HOMES AT 791 & 787 MOHAWK STREET. THE RESIDENCE AT 785 MOHAWK STREET ALSO SUSTAINED DAMAGE FROM THE EXPLOSION AND RESULTING FIRE. THE SUBCONTRACTOR SUBMITTED TO DRUG AND ALCOHOL TESTING AFTER THE INCIDENT AND THE RESULTS OF THE BLOOD ALCOHOL TEST ARE STILL BEING ANALYZED. | 1000224 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
426 | 2006-12-09 | DC | other | UNKNOWN (nan COUNTY) | WASHINGTON GAS LIGHT COMPANY | UPON ARRIVAL IT WAS DETERMINED THAT AN ILLEGAL CONNECTION HAD BEEN INSTALLED FROM THE OUTLET OF THE RISER TO A METER THAT HAD BEEN STOLEN FROM ANOTHER LOCATION. THE SET WAS THEN PLACED IN TO SERVICE WITHOUT A SERVICE REGULATOR BY AN UNAUTHORIZED INDIVIDUAL. | 203500 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
427 | 2006-12-03 | CO | sabotage | UNKNOWN (LARIMER COUNTY COUNTY) | PUBLIC SERVICE COMPANY OF COLORADO | THE LANDOWNER OF THIS COMMERCIAL PROPERTY SET A MODULAR TRAILER OVER THE GAS SERVICE THAT SERVED A RESIDENTIAL HOUSE TOWARDS THE BACK OF HIS PROPERTY. THE ELECTRIC CONTRACTOR HIRED BY THE PROPERTY OWNER DAMAGED THE GAS LINE WHILE TRENCHING IN A NEW ELECTRIC LINE TO THE MODULAR. A CIRCUMFERENTIAL CRACK FORMED WHERE THE PIPE WAS DAMAGED. THE LENGTH OF TIME WHEN THE CRACK FIRST APPEARED COULD NOT BE DETERMINED. THE MODULAR TRAILER DID NOT HAVE GAS SERVICE TO IT. | 51000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
428 | 2006-12-06 | MD | other | UNKNOWN (MONTGOMERY COUNTY) | WASHINGTON GAS LIGHT COMPANY | A FIRE IN THE STRUCTURE CAUSED THE COPPER HOUSE LINE TO MELT. THE METER THAT IS LOCATED AT THE RESIDENCE WAS DAMAGED FROM THE FIRE. | 1504500 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
429 | 2007-01-02 | CO | other | UNKNOWN (JEFFERSON COUNTY COUNTY) | COLORADO NATURAL GAS, INC. | SNOW/ICE SLID OFF OF RESIDENTIAL BUILDING ROOF CAUSING DAMAGE TO METER ASSEMBLY RESULTING IN A NATURAL GAS LEAK. GAS TRAVELED APPROX. 15 FEET TO DIRECT VENT ASSEMBLY FOR FIREPLACE, CAUSING IGNITION AND FLASHBACK TO ORIGIN OF LEAK. INSUING FLAME MELTED METER (AMERICAN AC-250) AND REGULATOR (AMERICAN 1813-C), RESULTING IN IGNITED GAS LEAKS AT BOTH OPENINGS ON METER BAR. LOCAL FIRE DEPARTMENT RESPONDED, USED CNG PROVIDE PLUG TOOL TO STOP LEAK. AFTER FIRE WAS EXTINGUISHED CNG CREW CUT AND CAPPED THE 3/4" PE SERVICE LINE APPROX. FIVE FEET FROM THE BUILDING FOUNDATIONAL WALL. | 75140 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
430 | 2006-12-21 | IL | other | UNKNOWN (COOK COUNTY) | NICOR GAS | CONTRACTOR, HIRED BY THE HOMEOWNER TO BUILD AN ADDITION ON THE HOUSE, HIT THE SERVICE LINE RISER AND BROKE OFF THE REGULATOR ADJUSTMENT SCREW WHILE BACKING UP A PICK UP TRUCK. GAS MIGRATED INTO THE HOME AND IGNITED. | 76100 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
431 | 2006-12-06 | GA | maintenance | UNKNOWN (DEKALB COUNTY) | ATLANTA GAS LIGHT COMPANY | A LEAK WAS DETECTED ON PIPE INSTALLED ON THE ON THE ROADWAY BRIDGE ABOVE INTERSTATE 285. A TEMPORARY BYPASS WAS CONSTRUCTED AND THE LEAKING SECTION WAS REMOVED FROM SERVICE. COMPLETION OF A NEW TIE-IN NEARBY WILL ALLOW THE TEMPORARY PIPING TO BE REMOVED AND THE LEAKING SECTION WILL BE PERMANENTLY RETIRED. | 170000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
432 | 2006-11-16 | TX | sabotage | UNKNOWN (BOSQUE COUNTY) | ATMOS ENERGY CORP, MID-TEX DIVISION | AN EXCAVATOR STRUCK A GAS MAIN. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
433 | 2006-12-12 | MI | other | UNKNOWN (OAKLAND COUNTY) | MICHIGAN CONSOLIDATED GAS COMPANY/DTE ENERGY | AT 7:52 AM ON 12-12-06 THERE WAS AN EXPLOSION AND AN ENSUING FIRE THAT COMPLETELY DESTROYED A SINGLE FAMILY DWELLING AT 622 ELIZABETH. AT 16:19, THE CAST IRON MAIN IN FRONT OF 622 ELIZABETH WAS FOUND BROKEN AND WAS REPAIRED WITH A 4”X 12” REPAIR CLAMP. THE CAUSE OF THE BREAK WAS UNDETERMINED. THE INVESTIGATION HAS BEEN COMPLETED. THE CAUSE OF THE EXPLOSION WAS NEVER DETERMINED. | 255900 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
434 | 2006-12-26 | IL | technical failure | UNKNOWN (nan COUNTY) | THE PEOPLES GAS LIGHT AND COKE COMPANY | ON DECEMBER 26, 2006, WHILE PEOPLES GAS WAS REPAIRING A SERVICE LINE INSIDE THE PREMISES OF 3240 N. SACRAMENTO, NATURAL GAS FROM THE SERVICE LINE IGNITED. INVESTIGATION INTO THE SOURCE OF THE IGNITION REVEALED SERVICE PERSONNEL FAILED TO MAKE THE SERVICE LINE INACTIVE. THEREFORE, AT THE POINT OF PENETRATION NATURAL GAS WAS RELEASED INTO THE ATMOSPHERE. IT IS BELIEVED THERE WAS AN ELECTRICAL ARC ON THE SERVICE LINE WHICH CAUSED THE IGNITION. | 75000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
435 | 2007-01-24 | AK | other | UNKNOWN (ANCHORAGE COUNTY) | ENSTAR NATURAL GAS COMPANY |  | 51100 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
436 | 2006-04-20 | MN | other | UNKNOWN (MILLS COUNTY) | NEW YORK MILLS MUNICIPAL GAS | GOPHER CHEW ON 1/2" CTS PE SERVICE LINE | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
437 | 2006-12-13 | TX | sabotage | UNKNOWN (DALLAS COUNTY) | ATMOS ENERGY CORP, MID-TEX DIVISION | AN EXCAVATOR STRUCK A GAS MAIN. THE LOCATE REQUEST INDICATED TO MARK BOTH SIDES OF THE STREET AND THAT THE AREA TO BE MARKED WAS WHITE LINED. THE WHITE LINE WAS ONLY ON THE OTHER SIDE OF THE STREET AND THAT WAS THE AREA MARKED. THE DAMAGE OCCURERD ON THE OTHER SIDE OF THE STREET. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
438 | 2007-01-02 | OK | other | UNKNOWN (MARSHALL COUNTY) | OKLAHOMA NATURAL GAS COMPANY | CITY OF MADILL PUBLIC WORKS EMPLOYEES WERE USING A ROOT CUTTING DEVICE TO CLEAR AN OBSTRUCTION IN THE SEWER LINE NEAR THE INTERSECTION OF S.2ND AVE. AND MCARTHUR ST. THE OBSTRUCTION WAS ONG'S 2" POLY GAS MAIN. THE ROOT CUTTING DEVICE PUNCTURED THE MAIN, RESULTING IN A 1 1/3" X 2" HOLE IN THE MAIN. THE HOUSE AT 505 S. 2ND AVE. EXPLODED | 26747 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
439 | 2007-01-16 | CA | leaks and spills | UNKNOWN (LOS ANGELES COUNTY) | SOUTHERN CALIFORNIA GAS COMPANY | ON JANUARY 16, 2007, AN EXPLOSION OCCURRED 3552 OPAL, IN THE CITY OF LOS ANGELES AT APPROXIMATELY 0300. THE EXPLOSION DESTROYED THE HOME AT THIS ADDRESS AND CAUSED MINOR DAMAGE TO TWO ADJACENT HOMES. THE DESTROYED HOME WAS UNOCCUPIED, AND NO INJURIES RESULTED. ALL CUSTOMERS THAT WERE OUT OF GAS WERE RESTORED THE SAME DAY, AND NECESSARY REPAIRS COMPLETED. INVESTIGATION DETERMINED THAT SHORT SECTION OF TENITE PLASTIC IN STEEL CASING HAD FAILED, ALLOWING GAS TO MIGRATE INTO THE VACANT RESIDENCE. THIS PIPING WAS INSTALLED IN THE 1950'S, AND COMPRISED APPROXIMATELY 20 FEET OF THE 120 FOOT SERVICE. SOUTHERN CALIFORNIA GAS COMPANY WAS UNAWARE THAT THIS SECTION OF TENITE EXISTED IN THEIR SYSTEM, AS IT DID NOT APPEAR ON ANY AVAILABLE RECORDS. A PROGRAM OF REMOVING ALL KNOWN TENITE PLASTIC FROM THE SYSTEM WAS COMPLETED IN THE 1980'S. | 302600 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
440 | 2007-01-11 | CA | sabotage | UNKNOWN (SONOMA COUNTY) | PACIFIC GAS & ELECTRIC CO. | WHILE INSTALLING A SEWER LINE AT THE INTERSECTION OF SNYDER LANE AND EAST COTATI AVE IN ROHNERT PARK, THE CONTRATCOR DUG INTO PG&E'8-INCH STEEL DISTRIBUTION LINE. THE TRAFFIC WAS RE-ROUTED AND AREA WAS CORDONED OFF BY THE POLICE. THE AREA WAS MADE SAFE WHILE THE REPAIR WAS BEING MADE. BECAUSE OF THE CONFIGURATION OF THE DISTRIBUTION SYSTEM, THE GAS CREW HAD TO INSALL THREE PRESSURE CONTROLLER FITTINGS TO ISOLATE THE BREAK. THE GAS RELEASE WAS STOPPED AT 0350 HOUR. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
441 | 2007-02-02 | CO | leaks and spills | UNKNOWN (GILPIN COUNTY) | COLORADO NATURAL GAS INC. | EXCESSIVE SNOWS FROM 2 LOCAL BLIZZARDS IN DECEMBER 2006 AND 1 IN JANUARY 2007. ALSO CONTRIBUTING TO THE INCIDENT WAS RECENT HIGH WINDS AND BLOWING SNOW RESULTED IN ACCUMULATING 6 + FEET OF HEAVY SNOW ON THE NATURAL GAS METER ADJACENT TO THE REAR OF HOME. COMBINED ROOF SLOPES FROM THE HOME AND THE RECENT GARAGE ADDITION ALSO CONTRIBUTED AS WELL AS THE MOUNTAIN SLOPE. THE FORCE OF THE SNOW PUSHING AGAINST THE METER AND REGULATOR FORCED THE BOTTOM OF THE METER TOWARDS THE HOME. THIS RESULTED IN BREAKING THE THREADED SIDE OF THE 3/4 INCH SCHEDULE 40 PIPE NIPPLE FEEDING NATURAL GAS TOWARDS THE INLET (HIGH PRESSURE 45 PSIG) SIDE OF REGULATOR. IGNITION OF THE EXCAPING GAS CAUSED EXTENSIVE DAMAGE TO THE RESIDENCE AT 1606 HUGHESVILLE ROAD. THE HOMEOWNER WAS HOME AT THE TIME AND HEARD A POPING NOISE, SMELLED GAS AND WENT TO THE NEIGHBORS HOME TO CALL 911. GAS COMPANY WAS NOT NOTIFIED UNTIL 5:00PM SATURDAY EVENING, 2-3-07. MULTIPLE PHOTOS AVAILABLE. | 350267 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
442 | 2007-01-01 | TX | sabotage | UNKNOWN (TARRANT COUNTY) | ATMOS ENERGY CORP, MID-TEX DIVISION | 2 INCH STEEL MAIN WAS DAMAGED BY A THIRD-PARTY CONTRACTOR. THIRD-PARTY CONTRACTOR FAILED TO NOTIFY THE OPERATOR OF THE DAMAGE, RESULTING IN THE INCIDENT. | 75000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
443 | 2007-01-20 | CO | leaks and spills | UNKNOWN (DENVER COUNTY) | PUBLIC SERVICE COMPANY OF COLORADO | FOUND 3/4" CAB SERVICE PULLED OUT OF 3/4 X 3/4" COMPRESSION COUPLING. CREW EXCAVATED AND CUT OFF CAB SERVICE BEHIND CURB IN EFFORTS TO SHUT OFF GAS FOR LOCAL FIRE DEPARTMENT. THE SEPARATION OF THE CAB FROM THE COMPRESSION COUPLING MAY HAVE OCCURRED POST INCIDENT DURING THE EXCAVATION. | 200550 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
444 | 2007-01-04 | MO | other | UNKNOWN (SAINT LOUIS COUNTY) | LACLEDE GAS COMPANY | AN AUTO ACCIDENT CAUSED ENERGIZED POWER LINES TO CONTACT A METALLIC STREET SIGHN WHICH WAS INSTALLED IN POXIMITY TO AN UNDERGROUND FOUR-INCH NATURAL GAS MAIN. AS A RESULT OF THE POWER LINE CONTACT, ELECTRICAL ARCING BETWEEN THE SIGN POST AND THE GAS MAIN CREATED A BURN HOLE IN THE MAIN APPROXIMATELY 0.5 INCHES IN DIAMETER. | 51500 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
445 | 2007-01-09 | TX | sabotage | UNKNOWN (BASTROP COUNTY) | CENTERPOINT ENERGY | CITY OF SMITHVILLE WATER & SEWER DEPARTMENT DAMAGED A 1" STEEL SERVICE WITH A BACKHOE. THE ESCAPING GAS IGNITED AND THE HOUSE CAUGHT FIRE. | 50834 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
446 | 2007-01-23 | OK | maintenance | UNKNOWN (TULSA COUNTY) | OKLAHOMA NATURAL GAS COMPANY | 1" STEEL THREADS ON SERVICE RISER LEAKING IN COLLAR BELOW GROUND. SERVICE RISER WAS PUSHED OVER AND BURIED FOR UNKNOWN YEARS. OPERATIONS PERSONNEL DID NOT KNOW THE SERVICE WAS IN PLACE BECAUSE THE SERVICES OF THAT VINTAGE WERE NOT MAPPED. POSSIBLE PRE-CODE CONSTRUCTION. GROUND CONDITONS WERE ICE AND SNOW COVERED WITH SHALLOW FREEZING OF SOIL. GAS APPEARED TO MIGRATE TO WATER METRE BOX WHERE IT WAS IGNITED BY PERSON PERFORMING MAINTENANCE WORK FOR APARTMENT COMPLEX. | 3344 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
447 | 2007-02-01 | IL | other | UNKNOWN (nan COUNTY) | NICOR GAS | PERSON WORKING IN THE BASEMENT OF THE STRUCTURE ACCIDENTALLY STARTED THE FIRE. INTENSITY OF THE FIRE CAUSED THE STRUCTURE TO EVENTUALLY COLLAPSE. THE STRUCTURE FIRE REACHED THE METER SET AND CAUSED IT TO MELT, THUS CAUSING A RELEASE OF NATURAL GAS. | 80550 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
448 | 2007-02-10 | MI | maintenance | UNKNOWN (GENESEE COUNTY) | CONSUMERS ENERGY | THE FINAL INVESTIGATION DETERMINED THAT THE CAUSE OF THE INCIDENT WAS A CUSOTMER OWNED FUEL LINE FAILURE ON NONJURISDICTIONAL PIPING. THIS REPORT CAN BE ELIMINEATED FROM THE DOT DATABASE. . | 50200 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
449 | 2007-02-05 | IL | other | UNKNOWN (COOK COUNTY) | NICOR GAS | GREASE FIRE IN KITCHEN MIGRATED THROUGH THE STRUCTURE AND REACHED THE METER SET, CAUSING DAMAGE WHICH LED TO THE RELEASE OF GAS. | 217600 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
450 | 2007-02-04 | CA | sabotage | UNKNOWN (SANTA CLARA COUNTY) | PACIFIC GAS AND ELECTRIC COMPANY | HOMEOWNER DUG INTO A GAS SERVICE WITH A DIGGING BAR AND PUNCTURED THE GAS SERVICE. GAS IGNITED AND A HOUSE FIRE TO THE HOMEOWNERS HOME AND THE ADJACENT HOME RESULTED. GAS FLOW WAS STOPPED AT THE MAIN. GAS SERVICE TO BOTH HOUSES IS DISCONTINUED UNTIL REPAIRS TO THE STRUCTURES ARE COMPLETE. | 105950 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
451 | 2007-02-28 | NY | leaks and spills | UNKNOWN (STEUBEN COUNTY) | CORNING NATURAL GAS CORPORATION | TWO INCH STEEL MAIN WAS ASSEMBLED IN 1948 WITH THREADED COUPLINGS. FROST HEAVE CAUSED THE MAIN TO CRACK AT THE POINT WHERE THE MAIN SCREWED INTO THE COUPLING. | 30000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
452 | 2007-01-25 | MI | sabotage | UNKNOWN (WAYNE COUNTY) | MICHIGAN CONSOLIDATED GAS COMPANY/DTE ENERGY | AN EXCAVATOR INSTALLING WATER MAIN FAILED TO CONFIRM THE LOCATION OF A 12" CAST IRON MAIN PRIOR TO DIGGING. THE 12" MAIN WAS BROKEN BY THE EXCAVATOR'S BACKHOE. | 70770 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
453 | 2007-01-25 | TX | sabotage | UNKNOWN (FT. BEND COUNTY) | CENTERPOINT ENERGY | RAIN CAUSED A DIFFEREENTIAL SETTLEMENT OF CONSTRUCTION MATERIALS, CAUSING DRESSER STYLE COUPLING TO PARTIALLY SEPARATE. NATURAL GAS MIGRATED FROM THE SEPARATION TO THE HOUSE AND FOUND IGNITION SOURCE RESULTING IN EXPLOSION AND FIRE. | 56000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
454 | 2007-01-13 | IL | other | UNKNOWN (MADISON COUNTY) | AMERENCIPS | AMERENCIPS WAS MOTIFIED OF A HOUSE FIRE ON JANUARY 13, 2007 AT 0926 ARRIVED AT THE SCENE AT 0936. THE FIRE DEPARTMENT SUSPECTED THAT GAS IGNITIONWAS THE CAUSE OF THE FIRE THAT FAILED CONTROL VALVE ON THE WATER HEATER. GAS SERVICE TO THE STRUCTURE WAS DISCONNECTED AND A LEAK INVESTIGATION PERFORMED WITH NO LEAKAGE FOUND. OUTLET PRESSURE AT THE SERVICE REGULATOR WAS CHECKED AND RECORDED AT 22" W.C. DUE TO ICE BUILD UP ON THE REGULATOR VENT. THE CONTROL VALVE IS BEING ANALYZED TO DETERMINE THE CAUSE OF FAILURE. ADDITIONAL NARRATIVE: THE CONTROL VALVE MANUFACTURER IS IN POSSESSION OF THE WATER HEATER CONTROL VALVE AND AFTER 10 MONTHS HAS NOT ANALYZED THE VALVE TO DETERMINE THE CAUSE OF THE FAILURE. AMERENCIPS BELIEVES THAT THE TESTING OF THE CONTROL VALVE WILL NOT TAKE PLACE AND WISHES TO SUBMIT THIS FINAL INCIDENT REPORT. | 120000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
455 | 2007-01-09 | TX | sabotage | UNKNOWN (DALLAS COUNTY) | ATMOST ENERGY CORP, MID-TEX DIVISION | DURING A THIRD-PARTY DAMAGE EVENT, OUR 1 ¼ INCH STEEL SERVICE LINE WAS PULLED FROM A COMPRESSION COUPLING IN THE ALLEY BEHIND 715 E. CELESTE, GARLAND, TEXAS. THE OCCUPANTS OF 715 E. CELESTE WERE EVACUATED, AND A STRUCTURE FIRE RESULTED DUE TO THE THIRD-PARTY DAMAGE. | 92000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
456 | 2007-01-11 | TX | natural disasters | UNKNOWN (TRAVIS COUNTY) | TEXAS GAS SERVICE COMPANY | INVESTIGATION DETERMINED THE LEAKAGE WAS CAUSED BY A 30" LONG BY .125" WIDE FAILURE OF A WELD. INSTALLED A WELD SLEEVE OVER THE ENTIRE WELD TO MAKE A PERMANET REPAIR. | 183594 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
457 | 2007-02-17 | WI | other | UNKNOWN (PIERCE COUNTY) | ST. CROIX VALLEY NATURAL GAS CO. | A NORTH-BOUND 1991 GMC SIERRA PICKUP TRUCK TRAVELING AT AN UNKNOW RATE OF SPEED LEFT THE ROAD AND TRAVELED ACROSS A HOMEOWNER'S YARD TO IMPACT THE SIDE OF THE HOUSE. THE POSTED SPEED IS 25 MILES PER HOUR. THE HOUSE SITS APPROXIMATELY 45 FEET OFF THE ROAD (37 FEET OFF THE GAS MAIN). THE TRUCK WAS EMBEDDED 6 FEET INTO THE HOUSE AND THE DOORS WERE PINNED SHUT BY THE HOUSE WALLS, TRAPPING THE DRIVER. THE GAS METER SAT DIRECTLY IN THE PATH OF THE TRUCK AND WAS SEVERED FROM THE RISER BY THE TRUCK BUMPER JUST BELOW THE SHUTOFF VALVE. THE RISER WAS BENT 90 DEGREES OVER THE FOUNDATION TO POINT DIRECTLY INTO THE HOUSE. GAS FLOWED UNCONTROLLED INTO THE HOUSE. IT IS SUSPECTED THAT THE GS WAS IGNITED WHEN THE DRIVER RESTARTED HER VEHICLE TO BACK IT OUT OF THE HOUSE. THE INCIDENT REMAINS UNDER INVESTIGATION BY THE PRESCOTT POLICE DEPARTMENT. | 300225 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
458 | 2007-01-22 | OH | sabotage | UNKNOWN (MEDINA COUNTY) | COLUMBIA GAS OF OHIO, INC. | THIRD PARTY CONTRACTOR, INSTALLING UTILITY POLES FOR A TRAFFIC SIGNALIZATION PROJECT, AUGURED INTO OPERATOR'S 6" PLASTIC GAS MAIN CAUSING A RELEASE AND IGNITION OF NATURAL GAS. THE THIRD PARTY CONTRACTOR FAILED TO PLACE A CALL TO THE OHIO UTILITIES PROTECTION SERVICE (OUPS) FOR THE LOCATION OF THE EXCAVATION AND THUS OPERATOR HAD NO NOTICE OF THE EXCAVATION AND THE MAIN WAS NOT MARKED. | 404573 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
459 | 2007-02-01 | AL | other | UNKNOWN (JEFFERSON COUNTY) | ALABAMA GAS CORPORATION | THE LOCAL FIRE DEPARTMENT HAS REPORTED THAT THE INCIDENT RESULTED FROM PIPE RUPTURE AT A LOCATION ALONG THE SERVICE LINE WHERE AN IMPROPER REPAIR WITH NON-STANDARD FITTINGS HAS BEEN MADE BY A THIRD PARTY NOT AUTHORIZED BY ALABAMA GAS CORPORATION. | 250000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
460 | 2007-02-06 | UT | sabotage | UNKNOWN (UTAH COUNTY) | QUESTAR GAS COMPANY | AT SOME POINT PRIOR TO 13:00 HOURS ON FEBRUARY 6, 2007 (AND FOR THE SECOND TIME IN TWO DAYS) S&E CABLE FAILED TO EXCAVATE WITH HAND TOOLS A PROPERLY MARKED NATURAL GAS LINE IN VIOLATION OF UTAH CODE ANNOTATED §54-8A-2 ET. SEQ. AS A RESULT, S&E CABLE STRUCK A 2" POLYETHYLENE PLASTIC NATURAL GAS MAIN WITH A BORING MISSILE. QUESTAR GAS COMPANY WAS CONTACTED, RESPONDED TO THE THIRD PARTY DAMAGE, EVACUATED TWO HOMES, (TWO PEOPLE TOTAL), SECURED AND REPAIRED THE LINE. WHILE IN THE PROCESS OF CLEARING THE HOME, AN EXPLOSION OCCURRED RESULTING IN TWO FATALITIES AS WELL AS A TOTAL LOSS OF THE HOME LOCATED AT 682 NORTH BADGER LANE, SARATOGA SPRINGS, UTAH. TEMPORARY MARKINGS INCLUDED FLAGS AND PAINT. THERE WERE PERMANENT MARKINGS. THE PARTY THAT CAUSED THE DAMAGE TO QUESTAR GAS'S PIPE WAS S&E CABLE. S&E CABLE WAS A SUBCONTRACTOR FOR ANGILAU COMMUNICATIONS LLC, WHO WAS A SUBCONTRACTOR FOR NIELS FUGAL SONS COMPANY LLC, WHO WAS A SUBCONTRACTOR FOR QWEST COMMUNICATIONS CORP. S&E CABLE'S STATUS AS A CORPORATION HAD EXPIRED AT THE TIME OF THE INCIDENT. S&E CABLE WAS NOT PROPERLY LICENSED BY THE STATE OF UTAH AT THE TIME OF THE INCIDENT. | 206036 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
461 | 2007-02-06 | MD | other | UNKNOWN (MONTGOMERY COUNTY) | WASHINGTON GAS | A TWO-INCH ROCKWELL 461-57S DISTRIBUTION REGULATOR WAS UNABLE TO SUPPLY THE GAS DEMANDED ON AN EXTREMELY COLD DAY, DUE TO A 40-FOOT TEMPORARY DISCONNECT OF 4" PLASTIC PIPE. THE 40-FOOT SECTION OF PIPE PROVIDED AN ADDITIONAL FEED, WAS TEMPORARILY DISCONNECTED IN JULY 2006 BUT WAS NOT REESTABLISHED PRIOR TO THE HEATING SEASON. ADDITIONALLY, A LOW PRESSURE ALARM ORIGINATING FROM THE REGULATOR MENTIONED ABOVE WAS NOT CORRECTLY ADDRESSED ON JANUARY 26, 2007. APPROXIMATELY 660 CUSTOMERS LOST GAS SERVICE AS A RESULT. THE REGULATOR WAS REPLACED WITH A TWO-INCH FISHER EZR, AND THE 40-FOOT TEMPORARY DISCONNECT HAS BEEN REESTABLISHED, THEREBY SUPPLYING THE ADDITIONAL NECESSARY FEED INTO THAT AREA. ADDITIONALLY, PROCESS AND TECHNOLOGY IMPROVEMENTS ARE BEING IMPLEMENTED RELATED TO PRESSURE COMMUNICATIONS AND ALARMS. | 75000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
462 | 2007-02-06 | OH | other | UNKNOWN (LORAIN COUNTY COUNTY) | COUMBIA GAS OF OHIO | ORIGIN OF FIRE STILL UNDER INVESTIGATION. WILL PROVIDE AN UPDATE ON SUPPLEMENTAL REPORT. | 181112 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
463 | 2007-02-19 | PA | other | UNKNOWN (ALLEGHENY COUNTY) | COLUMBIA GAS OF PENNSYLVANIA INC. | IN PITTSBURGH, ALLEGHENY COUNTY, PENNSYLVANIA, WHILE CONTRACTOR EMPLOYEE WAS ATTEMPTING TO COMPLETE AN ABANDONMENT OF A 1 1/4 INCH SERVICE LINE AT 342 CLIMAX STREET, WA OVER COME BY NATURAL GAS. EMPLOYEE SPENT ONE NIGHT IN THE HOSPITAL FOR OBSERVATION. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
464 | 2007-03-23 | AK | other | UNKNOWN (KENAI PENINSULA BOROUGH COUNTY) | ENSTAR NATURAL GAS COMPANY | ENSTAR WAS NOTIFIED OF A STRUCTURE FIRE AT LOT 9, RAYMOND BURTON SUBDIVISION, KASILOF, ALASKA, AT 0017 ON 3/23/07. A SERVICE TECH WAS DISPATCHED. ENSTAR'S METER AND RISER WERE ON FIRE. A DISTRIBUTION CREW WAS DISPATCHED TO DIG UP AND PINCH OFF THE LINE. THE LINE WAS PINCHED OFF AT 0326. THE FIRE STARTED WHEN THE HOMEOWNER TURNED ON AN ELECTRICAL SWITCH AND A SPARK FROM THE SWITCH IGNITED FUMES FROM A NEARBY GASOLINE CAN. TWO OCCUPANTS WERE BURNED AND SENT TO THE HOSPITAL. NATURAL GAS DID NOT CAUSE OR CONTRIBUTE TO THE FIRE. | 31100 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
465 | 2007-03-15 | AZ | sabotage | UNKNOWN (MOHAVE COUNTY) | UNISOURCE ENERGY SERVICES INC. | ON MARCH 15, 2007 A GRADER OWNED BY D&R EXCAVATION WAS CREATING DEEP BAR BAR DITCHS ON A DIRT ROAD LEADING TO THEIR GRAVEL PIT EAST OF KINGMAN ARIZONA. THE GRADER WAS BEING OPERATED BY D&R EXCAVATION EMPLOYEE GENE WEISS WITHOUT CALLING IN THE STATE'S ONE CALL NOTIFICATION, ARIZONA BLUE STAKE. AT APPROXIMATELY 1011 THE GRADER HIT A 6" DISTRIBUTION NATURAL GAS PIPELINE CROSSING THE DIRT ROAD IN A VERY WELL MARKED EASEMENT CAUSING A TEAR APPROXIMATELY 6" IN LENGTH. THE OPERATOR MOVED AWAY FROM THE GRADER SAFELY AND THERE WAS NO IGNITION OF THE GAS. AT 1030 UNISOURCE GAS WAS NOTIFIED. 911 WAS NOTIFIED AND AREA SECURE. GAS OFF AT 1640. | 70997 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
466 | 2007-02-17 | PA | natural disasters | UNKNOWN (LEHIGH COUNTY COUNTY) | UGI UTILITIES, INC. | A LEAKING COPPER WATER SERVICE TO 1536 HOTTLE AVENUE, BETHLEHM, PA, UNDERMINED THE GAS IN FRONT OF 1534 HOTTLE AVE. THE SOIL BENEATH THE MAIN SUBSIDED, RESULTING IN A CIRCUMFERENTIAL SEPARATION/FRACTURE IN THE 4" CAST IRON MAIN. GAS MIGRATED INTO 1534 HOTTLE AVENUE AND IGNITED. | 400000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
467 | 2007-02-28 | PA | leaks and spills | UNKNOWN (YORK COUNTY) | COLUMBIA GAS OF PENNSYLVANIA INC. | IN SPRY, YORK COUNTY, PENNSYLVANIA, AN EXPLOSION OCCURRED AT 2433 S. QUEEN STREET. LEAKAGE WAS DETECTED IN THE AREA OF MEMORY LANE AND S. QUEEN STREET, YORK PA. CRITICAL VALVE CY-1918 WAS SHUT OFF AT 12:56 PM. THE 2 INCH BARE STEEL MAIN WAS EXPOSED AT THE INTERSECTION OF MEMORY LANE AND PRIVATE DRIVE FINDING A DENT AND 3 INCH CRACK ON THE BOTTOM OF THE MAIN. 398 FEET OF 2" BARE STEEL MAIN WAS REPLACED WITH 2 INCH PLASTIC PIPE ON MEMORY LANE. | 205000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
468 | 2007-03-14 | AZ | sabotage | UNKNOWN (PINAL COUNTY) | CITY OF MESA COM | ON MARCH 14, 2007, SUNDT CONSTRUCTION HIT AND DAMAGED MESA¿S 4¿ STEEL HIGH PRESSURE GAS LINE AT NORTH IRONWOOD DRIVE AND EAST WESTBROOK ROAD. ON MARCH 13, 2007, CITY OF MESA PERSONNEL MET WITH, SUNDT CONSTRUCTION STAFF, TO DISCUSS PENDING EXCAVATION. SUNDT WAS INSTALLING A STORM DRAIN AND MESA'S LINE HAD BEEN DROPPED PREVIOUSLY TO ACCOMMODATE THIS CROSSING. SUNDT PERSONNEL EXPOSED MESA'S STEEL GAS MAIN TO VERIFY LOCATION AND DEPTH. THE LINE WAS THEN BACKFILLED AND 4" PVC MARKERS WERE PLACED ON EACH SIDE OF THE CROSSING AT THE LOCATION OF THE DROP. SUNDT'S ON-SITE SUPERINTENDENT, MR. BRIAN KRUER INFORMED THE EQUIPMENT OPERATOR TO STAY AWAY FROM THE PVC PIPE MARKERS WHICH INDICATED THE LOCATION AND THE ALIGNMENT OF THE PIPE. THIS DIRECTION WAS WITNESSED BY CITY OF MESA LEAD UTILITY LOCATOR, MR. JOE CEJA. ON MARCH 14, 2007, SUNDT CONTINUED TO WORK THE EXCAVATION AND MR. CEJA MONITORED THE SITE FOR MESA. WHEN MR. CEJA LEFT THE SITE TO CHECK ANOTHER EXCAVATION, SUNDT'S EQUIPMENT OPERATOR PUNCTURED THE GAS LINE WITH THE TEETH OF THE FRONT-END LOADER. THE ESCAPING GAS IGNITED AND BURNED THE FRONT-END LOADER. FIRE PERSONNEL RESPONED AND EVACUATED APPROXIMATELY A DOZEN HOMES UNTIL THE FIRE WAS EXTINGUISHED. THE FOLLOWING TIME LINE PROVIDES A BRIEF OVERVIEW OF EVENTS. (THE * DENOTES APPROXIMATE TIME.) MARCH 13, 2007 9:20 AM ¿ CITY OF MESA STAFF MET SUNDT ON-SITE TO DISCUSS EXCAVATION. THE GAS LINE WAS EXPOSED TO IDENTIFY ACTUAL LOCATION AND THEN BACKFILLED. TWO 4¿ PVC STANDPIPES WERE INSTALLED ON BOTH SIDES OF THE PROPOSED EXCAVATION TO MARK THE LOCATION AND ALIGNMENT OF THE GAS LINE. MARCH 14, 2007 9:30 AM ¿ CITY OF MESA LEAD UTILITY LOCATOR ARRIVED TO MONITOR EXCAVATION ACTIVITIES. *1:45 PM ¿ LEAD UTILITY LOCATOR LEFT TO MONITOR PROGRESS OF ANOTHER EXCAVATION IN AREA. 2:07 PM ¿ GAS LINE HIT. 2:20 PM ¿ CITY OF MESA CONTROL ROOM RECEIVED BLOWING GAS CALL FROM RURAL METRO FIRE DEPARTMENT. RESPONDING PERSONNEL DISCOVER GAS HAS IGNITED AND A FRONT-END LOADER IS ON FIRE. NO INJURIES. 2:20 PM ¿ GAS SYSTEM SUPERVISOR RECEIVES CALL AND COORDINATES RESPONSE PERSONNEL. 2:40 PM ¿ CONTROL ROOM NOTIFIED THAT BLOWING GAS IS CONTROLLED. *3:30 PM ¿ RURAL METRO EXTINGUISHES FIRE ON FRONT-END LOADER. *4:00 PM ¿ RURAL METRO ALLOWS PERSONNEL INTO AREA. *5:30 PM ¿ ARIZONA CORPORATION COMMISSION AND CITY OF MESA COMPLETE PRELIMINARY INVESTIGATION AND ALLOW REPAIR WORK TO BEGIN. *6:30 PM ¿ SUNDT CONTRACTING REMOVES DAMAGED FRONT-END LOADER FROM SITE. *8:00 PM ¿ CITY OF MESA COMPLETES EXCAVATION. *9:00 PM ¿ GAS LINE TO SOUTH IS PURGED OF WATER. MARCH 15, 2007 *12:30 AM ¿ GAS LINE TO NORTH IS CLEANED. *2:30 AM ¿ REPAIRS TO GAS LINE COMPLETE. 3:43 AM ¿ GAS SYSTEM AND CUSTOMERS BACK IN SERVICE. *7:00 AM ¿ CREW ARRIVES TO CLEAN-UP AND BACKFILL SITE. | 264543 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
469 | 2007-03-14 | MD | other | UNKNOWN (BALTIMORE COUNTY) | BALTIMORE GAS & ELECTRIC COMPANY | ACCORDING TO FIRE INVESTIGATION BUREAU #2 CHIEF MARTIN FOR THE BALTIMORE CITY FIRE DEPARTMENT THAT THE POINT OF FIRE ORIGINATION IS UNKNOWN DUE TO THE EXTENT OF THE DAMAGE TO THE HOUSE. THE F.I.B. REPORTS THAT THE FIRE IMPINGED ON THE METER INSTALLATION CAUSING DAMAGE TO THE SAME, THEN IGNITION OF NATURAL GAS OCCURED. FIB 2 OF THE BALTIMORE CITY FIRE DEPARTMENT DETERMINED THE ESTIMATE OF PROPERTY DAMAGE. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
470 | 2007-03-16 | MD | maintenance | UNKNOWN (PRINCE GEORGES COUNTY) | BALTIMORE GAS & ELECTRIC COMPANY | FOUND 9155 HITCHING-POST LA UNIT C DAMAGED BY EXPLOSION AND FIRE. DURING THE INVESTIGATION, ICE WAS FOUND ON THE REGULATOR BODY SUPPLING 9155 HITCHING-POST LA UNIT C AND IT WAS FOUND THAT THE REGULATOR VENT WAS PAINTED OVER. ELEVATED PRESSURE WAS SUPPLED TO 9155 HITCHING POST LA UNIT C. IT WAS DETERMINED THAT EXCESS PRESSURE CAUSED CONTROL VALVE ON AUTOMATIC WATER HEATER (AWH) TO RELEASE GAS AND ALLOWED GAS TO BUILD UP IN BUILDING. THE SOURCE OF IGNITION WAS FOUND TO BE AUTOMATIC WATER HEATER (AWH) WHICH CAUSE DAMAGE TO BUILDING. | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
471 | 2007-03-06 | NM | sabotage | UNKNOWN (BERNALILLO COUNTY) | PUBLIC SERVICE COMPANY OF NEW MEXICO | CONTRACTOR HIT GAS LINE WHILE CLEANING ARROYO BEHIND CONTRACTOR'S BUILDING. | 120137 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
472 | 2007-03-08 | SD | sabotage | UNKNOWN (DAVISION COUNTY) | NORTHWESTERN ENERGY | AT 11:31 AM ON MARCH 8, 2007 A HOME AT 1612 BRIDLE DRIVE IN MITCHELL, SD EXPLODED. IN ADDITION TO 1612 BRIDLE DRIVE RESIDENCE THE EXPLOSION ALSO DAMAGED THE RESIDENCES AT 1608 AND 1616 BRIDLE DRIVE. A NORTHWESTERN EMPLOYEE READING METERS IN THE AREA HEARD THE EXPLOSION AND CONTACTED TWO ADDITIONAL NORTHWESTERN EMPLOYEES AS HE RESPONDED. ONCE ON SITE NORTHWESTERN EMPLOYEES BEGAN TO MONITOR THE GAS LEVELS IN THE AREA. NATURAL GAS WAS DETECTED IN THE 1612 BRIDLE DRIVE LOT. COMMUNICATION WAS ESTABLISHED WITH EMERGENCY RESPONDERS. THE SERVICE TO THE HOME WAS FUELING A FIRE IGNITED BY THE EXPLOSION. NORTHWESTERN WORKED WITH FIRE AND EMERGENCY CREWS IN ALLOWING THE FIRE TO BURN WHILE MEASURES WERE TAKEN TO SQUEEZE OFF NATURAL GAS TO THE AREA. EMERGENCY LOCATES WERE CALLED IN, CREWS ASSEMBLED TO DIG, AREA OF SAFE DIGGING WAS ESTABLISHED. AT 2:40 THE PIPE WAS SAFELY SQUEEZED OFF. THE EXPLOSION AREA WAS CONTINUOUSLY MONITORED THROUGHOUT THE EVENT TO ENSURE SAFETY OF CREWS. A LEAK IN THE MAIN LOCATED IN FROM OF 1612 BRIDLE DRIVE WAS LOCATED. A CREW BEGAN TO REPAIR LEAK, ANOTHER CREW BEGAN THE NO GAS PROCESS TO APPROXIMATELY 21 HOMES. REPAIRS TO THE MAIN AND SQUEEZED OFF MAIN WERE COMPLETED AT 8:15. AN AIR TEST WAS ADMINISTERED AND PRESSURE HELD. FINAL TIE WELDS WERE COMPLETED, SYSTEM WAS PURGED AND GAS WAS INTRODUCED. A FINAL LEAK SURVEY WAS COMPLETED WITH THE FI UNIT AND NO LEAKS WERE DETECTED. CUSTOMERS WERE RELIT AS ACCESS WAS GAINED TO THEIR HOME. NO TREATABLE INJURIES RESULTED FROM THE INCIDENT. IN NORTHWESTERN INVESTIGATION WITH DAVISON COUNTY EMERGENCY MANAGEMENT, FIRE AND POLICE DEPARTMENT ONLY HOUSES NOT PEOPLE WERE TRACKED IN THE EVACUATION. SINCE IT WAS DURING A WORK DAY MANY INDIVIDUALS WERE NOT HOME AND THE FOCUS BY EMERGENCY OFFICIALS WAS ON HOMES EVEN IF NO ONE WAS HOME INSTEAD OF PEOPLE. THE NUMBER 27 IS THE NUMBER OF RESIDENTIAL HOMES EVACUATED NOT THE NUMBER OF PEOPLE. NORTHWESTERN IS A GAS AND ELECTRIC UTILITY. WE DO NOT ESTIMATE PERSONAL PROPERTY DAMAGE OR HOUSE REPLACEMENT COSTS FOR A BUSISNESS. NOR HAS NORTHWESTERN HAD THE PRIVILEGE TO SURVEY THE PERSONAL PROPERTY OF THE THREE HOMES. DID THEY HAVE COLLECTOR FURNITURE, BASEBALL CARDS, ETC? TO CORRECTLY ESTIMATE THIS NUMBER THOSE ITEMS WOULD BE NEEDED. THE NUMBER LISTED IN PRIVATE/PERSONAL PROPERTY DAMAGE IS A GUESS FOR THREE HOMES AND THE PERSONAL PROPERTY IN THE HOMES. SINCE THE FORM REQUIRES A NUMBER AND WILL NOT ACCEPT A LIST OF WHAT WAS DAMAGED RATHER THAN THE COST ASSOCIATED WITH IT. JUNE 11, 2008 - ADDITIONAL NARRATIVE THE PIPE INVOLVED IN THE INCIDENT WAS TESTED UNDER THE DIRECTION OF THE SOUTH DAKOTA PUC'S INDEPENDENT EXPERT, JOHN F. KIEFNER, PH. D., PE FROM KIEFER & ASSOCIATES, INC. ON FEBRUARY 22, 2008, THE SD PUC STAFF RELEASED LAB RESULTS FROM STORK TWIN CITIES TESTING AND ON MAY 28, 2008 STAFF RELEASED JOHN KIEFNER'S FINAL REPORT. MR. KEIFNER'S REPORT ALSO ASSIGNED NO FAULT TO NORTHWEWSTERN ENERGY FOR THE INCIDENT. SPECIFICALLY, MR. KIEFNER'S REPORT STATED THAT" - A MECHANICALLY CREATED GOUGE CAUSED THE PIPE TO FAIL. - THE MODE OF FAILURE WAS A CIRCUMFERENTIALLY ORIENTED BRITTLE CRACK THAT SEVERED THE BOTTOM THREE QUARTERS OF THE PIPE. - NO EVIDENCE OF TIME-DEPENDENT ENLARGEMENT OF THE GOUGE WAS FOUND. - THE DAMAGE THAT CAUSED THE FAILURE IS NOT NEW, BUT IT WAS NOT POSSIBLE TO ESTABLISH WHEN IT OCCURRED. BASED ON THE INFORMATION CONTAINED IN MR. KEIFNER'S REPORT AND THE FORTHCOMING OF AN EXCAVATOR, NORTHWESTERN ENERGY HAS IDENTIFIED THE CAUSE OF THE INCIDENT AS F3.9, EXCAVATION. NORTHWESTERN HAS ALSO UPDATED PART D.2 AND D.4 BASED ON ADDITIONAL INFORMATION PROVIDED BY INFORMATION OBTAINED WHEN THE PIPE WAS TESTED AND THE REFERENCED REPORTS WERE RELEASED. F3.9.D DUE TO THE LENGTH OF TIME BETWEEN THE LOCATE AND THE INCIDENT IT IS NOT POSSIBLE TO DETERMINE THE METHOD (FLAGS, PAINT, STAKES) USED TO MARK THE LOCATE. | 471362 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
473 | 2007-04-11 | AK | other | UNKNOWN (MATANUSKA SUSITNA BOROUGH COUNTY) | ENSTAR NATURAL GAS COMPANY | ENSTAR WAS NOTIFIED OF A STRUCTURE FIRE AT 9120 N. SUN VALLEY DR, PALMER, ALASKA AT 0220 ON 4/11/2007. THE FIRE SEVERELY DAMAGED THE STRUCTURE AND BURNED ENSTAR'S REGULATOR AND METER CAUSING A RELEASE OF NATURAL GAS. FIRE DEPARTMENT PERSONNEL SHUT OFF THE SERVICE VALVE TO STOP THE RELEASE OF NATURAL GAS AT 0400. NATURAL GAS DID NOT CAUSE OR CONTRIBUTE TO THE FIRE. | 51100 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
474 | 2007-03-17 | TX | natural disasters | UNKNOWN (nan COUNTY) | CPS ENERGY | GAS IGNITION OCCURED WHEN THE CUSTOMER AT 5618 LAKEBEND WEST FLIPPED A SWITCH IN THE BATHROOM. AFTER INVESTIGATION, IT IS BELIEVED THAT THE SOURCE OF GAS ORIGINATED FROM A FAILURE AT THE THREADED END OF THE 1" STEEL SERVICE OF 5618 LAKEBEND WEST, WHERE IT ENTERED A 1" SCREWED COUPLING. IT IS BELIEVED THAT THE THREADS ON THE 1" STEEL PIPE CRACKED OPEN DUE TO THE FORCE CREATED FROM THE WEIGHT OF AN ELECTRIC TRANSFORMER THAT HAD SETTLED IN THE GROUND LOCATED DIRECTLY ABOVE THE FAILURE POINT. | 13627 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
475 | 2007-03-06 | TX | sabotage | UNKNOWN (EL PASO COUNTY) | TEXAS GAS SERVICE COMPANY | 2" POLYETHYLENE SERVICE LINE DAMAGED BY A TRENCHER. NO LINE LOCATES WERE REQUESTED. MEDIA WAS ON SITE. 350 PEOPLE WERE EVACUATED. | 2781 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
476 | 2007-02-21 | TX | sabotage | UNKNOWN (DALLAS COUNTY) | ATMOS ENERGY CORP. MID-TEX DIVISION | AN EXCAVATOR STRUCK A SERVICE LINE CAUSING A LEAK. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
477 | 2007-02-26 | TX | sabotage | UNKNOWN (DALLAS COUNTY) | ATMOS ENERGY CORP. MID-TEX DIVISION | AN EXCAVATOR STRUCK A MAIN, CAUSING A LEAK. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
478 | 2007-04-09 | MS | sabotage | UNKNOWN (MADISON COUNTY) | ATMOS ENERGY CORPORATION - MISSISSIPPI DIVISION | A FOUNDATION REPAIR CONTRACTOR FOR THE HOMEOWNER DUG A HOLE WITH A TILE SPADE ADJACENT TO THE CONCRETE SLAB AND NEAR THE METER SET. THE SPADE DAMAGED THE SERVICE LINE CAUSING NATURAL GAS TO LEAK. IT IS REPORTED THAT DUE TO THE NOISE OF THE BLOWING GAS, THE CONTRACT WORKER COVERED THE LEAK WITH BACKFILL. THIS CAUSED THE LEAKING GAS TO MIGRATE TO THE HOME, WHICH WAS SUBSEQUENTLY IGNITED BY AN UNDERTERMINED SOURCE OF IGNITION. THE ONE-CALL SYSTEM HAD NOT BEEN UTILIZED. | 200000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
479 | 2007-04-08 | MT | natural disasters | UNKNOWN (SILVER BOW COUNTY) | NORTHWESTERN ENERGY | CHANGES IN EXTERNAL ENVIRONMENT AND APPLICATION OF UNKNOWN ADDITIONAL LOADING. 01/27/2014 - THIS IS NORTHWESTERN ENERGY'S FINAL REPORT FOR THIS INCIDENT. SINCE THE LAST UPDATE METALLURGY TESTING HAS BEEN COMPLETED. THE REPORT HAS BEEN SUBMITTED TO THE MONTANA PUBLIC SERVICE COMMISSION. THE REPORT STATES, IN SUMMARY, THAT THERE WERE SEVERAL PRINCIPAL FACTORS INVOLVED IN THE PIPE SEPARATION. FACTORS INCLUDED EXTENDED LOADING OF THE PIPE, ENVIRONMENT AROUND THE PIPE, AND EXTERNAL FORCE. THE FRACTURE APPEARS TO HAVE INITIATED AT A PRE-EXISTING ENVIRONMENTALLY ASSISTED CRACK ON THE SURFACE OF THE PIPE. THIS ENVIRONMENTALLY ASSISTED CRACK IS BELIEVED TO HAVE OCCURRED PRIOR TO APPLICATION OF CATHODIC PROTECTION. THIS CRACK WAS NOT SUBSTANTIAL ENOUGH TO CAUSE FAILURE OF THE PIPE AND THAT SEPARATION WOULD HAVE REQUIRED SOME ADDITIONAL EXTERNAL LOADING THAT THE INVESTIGATION WAS UNABLE TO DETERMINE. THE CAUSE HAS BEEN UPDATED FROM F7 - OTHER TO F2 - NATURAL FORCES ON THIS SUBMITTAL. THE MONTANA PUBLIC SERVICE HAS CONCLUDED ITS INVESTIGATION. NWE BELIEVES THAT THIS INCIDENT IS CLOSED AND THERE WILL BE NO FURTHER UPDATES FOR THIS INCIDENT. 5/4/09 - THIS IS A SUPPLEMENTAL REPORT FOR THIS INCIDENT. THE SERVICE HAS BEEN EXPOSED AND REMOVED AND IS IN NORTHWESTERN ENERGY'S POSSESSION. THIS WAS COMPLETED IN APRIL OF 2007. THE INJURED INDIVIDUAL WAS HOSPITALIZED FOR AN EXTENDED PERIOD; HOWEVER, THE INDIVIDUAL HAS SENCE PASSED AWAY. CURRENTLY, IT IS UNKNOWN IF THE INJURIES SUSTAINED IN THE INCIDENT CAUSED OR CONTRIBUTED TO THE INDIVIDUALS DEATH. AT THE DIRECTION OF INSURANCE AND LEGAL DEPARTMENT, NO FURTHER INVESTIGATION HAS BEEN COMPLETED ON THE CAUSE OF THE INCIDENT. AT THIS TIME THE INVESTIGATION IS STILL ON GOING. ORIGINAL NARRATIVE AT DIRECTION OF INSURENCE ADJUSTOR, THE SITE IS NOT READY FOR EXCAVATION OR INVESTIGATION. SPECIFIC INCIDENT DETAILS ARE STILL UNKNOWN AT THIS TIME AND THE INCIDENT IS STILL UNDER INVESTIGATION | 120000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
480 | 2007-04-01 | TX | leaks and spills | UNKNOWN (nan COUNTY) | CENTERPOINT ENERGY | 1 1/4" X 1/2" PLASTIC SERVICE TEE PARTIALLY SEPARATED FROM 1 1/4" POLY MAIN LINE IN REAR EASEMENT OF 10735 LAKEWOOD OAKS DR, ESCAPING GAS MIGRATED TO 10727 LAKEWOOD OAKS DR. WHERE A FIRE/EXPLOSION OCCURED. | 55100 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
481 | 2007-04-06 | ME | maintenance | UNKNOWN (YORK COUNTY) | NORTHERN UTILITIES | AT APPROXIMATELY 2:47 A.M. ON 4/6/07 BLOWING GAS WAS REPORTED BY THE RACO FIRE DEPARTMENT AT AN APARTMENT COMPLEX IN THE VICINITY OF THE MOODY ROAD POINT OF DELIVERY OFF OF THE GRANITE STATE TRANSMISSION PIPELINE. EVACUATIONS OCCURED AT 34 OCEAN PARK AND PENELOPE TERRACE AND THE SWEETSER HOME COMPLEX ADJACENT TO THE MOODY ROAD REGULATOR STATION. APPROXIMATELY 300 PSIG WAS INJECTED INTO A 55 PSIG MAOP SYSTEM, THE RESULTS OF WHICH WERE TWO FIRE. PRELIMINARY INVESTIGATIONS WOULD INDICATE THAT MOISTURE WAS PRESENT IN THE MOODY ROAD REGULATORS OFF THE GRANITE TRANSMISSION LINE. | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
482 | 2007-04-12 | OR | sabotage | UNKNOWN (MARION COUNTY) | NW NATURAL GAS COMPANY | A CONTRACTOR WAS OPERATING AN INDUSTRIAL TILLER TO LOOSEN SOIL IN ORDER TO LOWER THE GRADE. THE CONTRACTOR STRUCK NW NATURAL'S 6-INCH DIAMETER PE 2406/SD11.5 POLYETHYLENE MAIN RESULTING IN THE RELEASE AND IGNITION OF NATURAL GAS. THE TILLER WAS INVOLVED IN THE FIRE RESULTING IN A TOTAL LOSS. TWO OF THE CONTRACTOR'S EMPLOYEES WERE TRANSPORTED TO THE HOSPITAL AND TREATED AND RELEASED THE SAME DAY. NO LOCATES WERE REQUESTED OR PRESENT, AND THE MAIN HAD 30 INCHES OF COVER AT THE TIME OF THE DAMAGE, EXCEEDING THE REQUIREMENTS OF 49 CFR 192.327(B). PIPELINE MARKERS WERE PRESENT. | 528460 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
483 | 2004-08-22 | NE | other | UNKNOWN (DOUGLAS COUNTY) | METROPOLITAN UTILITIES DISTRICT | THROUGH OUR INVESTIGATION IT WAS DISCOVERED THAT THE ORIGIN OF THE FIRE CAME FROM A TRASH CAS LOCATED AT 7515 NORTH 155TH TERRACE WHICH WAS IS THE DWELLING NORTH OF 7509 NORTH 155TH TERRACE. THE FIRE IN THE TRASH CAN THEN SPREAD TO THE NEIGHBORING HOME AND THE INTENSITY FROM THE HEAT OF THE FIRE CAUSED THE SERVICE LINE TO MELT AND LEAK. | 700000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
484 | 2007-04-19 | OR | sabotage | UNKNOWN (CLACKAMAS COUNTY) | NW NATURAL GAS COMPANY | INVESTIGATION COMPLETE A CONTRACTOR WAS DIRECTIONAL DRILLING TO INSTALL FIBER OPTIC TELEPHONE CABLE AND STRUCK NW NATURAL'S 2-INCH DIAMETER PE 2406 POLYETHYLENE MAIN. LOCATES WERE PRESENT AND ACCURATE. AN UNDERGROUND RELEASE OF NATURAL GAS OCCURRED. THE CONTRACTOR NOTIFIED NW NATURAL OF THE DAMAGE, AND A COMPANY CREW WAS IMMEDIATELY DISPATCHED TO THE SITE. NW NATURAL PERSONNEL EVACUATED TWO OCCUPANTS DUE TO HIGH NATURAL GAS CONCENTRATIONS AND CALLED 9-1-1. FIRE DEPARTMENT PERSONNEL ARRIVED AND BEGAN TO CLEAR THE HOUSE OF AGAS WHEN THE EXPLOSIION OCCURRED. THREE FIREFIGHTERS WERE TRANSPORTED TO THE HOSPITAL, ONE TREATED FOR BURNS. | 285180 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
485 | 2007-04-26 | PA | other | UNKNOWN (ALLEGHENY COUNTY) | DOMINIONPEOPLES | A 2" BRANCH PIPE NIPPLE SNAPPED OFF AN 8" STEEL MAINLINE CAUSING A LEAK. AN ELECTRICAL SHORT IN OVERHEAD LINES IGNITED THE ESCAPING GAS, RESULTING IN A FIRE. DOMINION-PEOPLES GAS COMPANY WAS CONDUCTING A ROUTINE LEAK REPAIR ON AN 8" MAINLINE. THE ELECTRIC COMPANY WAS CALLED TO THE SITE DUE TO THE PROXIMITY OF A TELEPHONE POLE IN THE EXCAVATION AREA. THE ELECTRIC COMPANY WAS ASSISTING DOMINION IN THE REPAIR OF A LEAK. THEIR ASSISTANCE WAS NEEDED TO SUPPORT A TELEPHONE POLE IN THE EXCAVATION AREA. THE GUY WIRE FOR THE POLE WAS CONCRETED IN A LARGE BLOCK. THIS BLOCK ALSO HAD THE CAP AND PIPE NIPPLE EMBEDDED INTO THE CONCRETE. THE ELECTRIC COMPANY PLACED TENSION ON THE POLE FOR SUPPORT DURING EXCAVATION. THE TENSION WAS RELEASED CAUSING THE PIPE NIPPLE TO SNAP OFF THE 8" MAINLINE AND SHORTING THE LIVE ELECTRIC WIRE TO THE GROUND WIRE. THIS SHORT IGNITED THE BLOWING GAS AND CAUGHT THE BACKHOE ON FIRE. THE GAS MAINLINE WAS SHUT DOWN AND THE FIRE WAS PUT OUT WITH EXTINGUISHERS. | 70000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
486 | 2004-06-29 | NE | other | UNKNOWN (DOUGLAS COUNTY) | METROPOLITAN UTILITIES DISTRICT |  | 3500 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
487 | 2007-04-23 | VA | other | UNKNOWN (FAIRFAX COUNTY) | WASHINGTON GAS LIGHT COMPANY | ACCORDING TO FAIRFAX FIRE MARSHAL'S REPORT 20071132600, THIS WAS AN ACCIDENTAL FIRE RESULTING FROM AN UNDETERMINED EVENT THAT CAUSED A PROPANE GRILL LOCATED ON THE REAR DECK OF 6400 DAKINE CIRCLE TO IGNITE THE COMBUSTIBLE VINYL SIDING AND SPREAD TO ADJACENT STRUCTURES. IF WASHINGTON GAS FACILITIES CONTRIBUTED TO THE FIRE, THEIR INVOLVEMENT WAS ONLY SECONDARY. NONE OF THE WASHINGTON GAS FACILITIES COULD BE RETRIEVED AS THE BUILDING COLLAPSED AND ENCOMPASSED THE FACILITIES. | 1529100 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
488 | 2007-04-24 | VA | other | UNKNOWN (LOUDOUN COUNTY) | WASHINGTON GAS LIGHT COMPANY | UPDATED BY PHMSA ON 1/13/2016 PER OPERATOR'S MARK UP (PART F - APPARENT CAUSE; AND PART I NARRATIVE). WASHINGTON GAS PERSONNEL RESPONDED TO A REPORT OF GAS INVOLVED FIRE ON 4/24/2007 AT 43655 PIERPOINT TERRACE, LEESBURG, VA. THE THREE STORY WOOD FRAME BRICK VENEERED TOWNHOUSE AT THAT LOCATION WAS VACANT AT THE TIME OF THE FIRE WITH A “FOR SALE” SIGN IN THE FRONT YARD. THE FIRE APPEARS TO HAVE ORIGINATED AT THE REAR OF THE TOWNHOUSE, BENEATH THE DECK AND TO THE RIGHT OF THE REAR BASEMENT ENTRY DOOR, IN THE IMMEDIATE AREA OF THE NATURAL GAS RISER, REGULATOR AND METER BUILDUP. IT WAS NOTED THAT A THREADED STEEL GAS PIPE NIPPLE ON THE INLET SIDE OF THE 43655 PIERPOINT TERRACE GAS METER WAS MISSING AT THE TIME OF THE FIRE AND WAS NOT FOUND IN THE DEBRIS. THE CORRESPONDING OUTLET NIPPLE WAS STILL PRESENT. THE MISSING NIPPLE ALLOWED NATURAL GAS TO ESCAPE AND IT WAS NOTED THAT THE NIPPLE CANNOT UNSCREW ITSELF. THE GAS LINE WAS INTACT AND HELD PRESSURE DURING A PRESSURE TEST (50 PSI FOR 10 MINUTES). THE BURIAL DEPTH OF THE GAS SERVICE WAS AT 36 INCHES. THE GAS WAS PROPERLY ODORIZED AND HAD BEEN CONFIRMED BY AN ODORANT TEST. A SOIL SAMPLE WAS OBTAINED AND SENT TO A LABORATORY FOR ANALYSIS THAT COULD NOT CONFIRM THE PRESENCE OF AN ACCELERANT FOR IDENTIFICATION OF IGNITABLE LIQUID RESIDUES. THE ANALYSIS DID CONFIRM THE PRESENCE OF FOUR CHEMICALS THAT ARE STRONG INDICATORS OF AN IGNITABLE LIQUID RESIDUE, AN ACCELERANT SUCH AS GASOLINE, PRESENT AT THE REAR OF THE HOUSE. IT WAS ALSO NOTED THAT THE NATURAL GAS LEAK, SUCH AS FROM THE MISSING NIPPLE, WOULD NOT RESULT IN A FIRE UNLESS AN IGNITION SOURCE IS PROVIDED. THE FIRE APPEARED TO GO UP THE SIDE OF THE TOWNHOUSE AT 43655 PIERPOINT TERRACE IN A V-SHAPE FROM THE GAS METER. THE FIRE THEN CAUGHT ON THE ROOF AND MOVED ACROSS THE ROOFTOPS, INVOLVING TWO OTHER TOWNHOUSE UNITS. THE FORENSIC ENGINEERING CONSULTANT CONTRACTED BY WASHINGTON GAS, PROPOSES THE LIKELIHOOD THAT THE NIPPLE TO THE METER HAD BEEN REMOVED AND AN ACCELERANT WAS UTILIZED TO START A FIRE AT THE GAS METER OF 43655 PIERPOINT TERRACE. NO FURTHER INFORMATION HAS BEEN PROVIDED BY THE LOUDOUN COUNTY FIRE MARSHALL OR LOUDOUN COUNTY SHERIFF’S OFFICE. THE WASHINGTON GAS INVESTIGATION OF THIS INCIDENT INDICATES ARSON AS THE CAUSE OF THE FIRE AND CONSIDERS THE INVESTIGATION CLOSED ON BEHALF OF THE UTILITY OPERATOR. | 1205100 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
489 | 2007-05-03 | TX | sabotage | UNKNOWN (TRAVIS COUNTY) | TEXAS COMMUNITY PROPANE, LTD. | PLUMBING COMPANY USING ROCKSAW INSTALL WATER LINES HIT SERVICE LINE AND CAUSED DAMAGE. | 174 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
490 | 2007-05-18 | MN | other | UNKNOWN (OLMSTED COUNTY) | MINNESOTA ENERGY RESOURCE CORPORATION | AT APPROXIMATELY 0430 ON THE 18TH OF MAY, 2007 A DRIVER LOST CONTROL OF HER CAR. THE VEHICLE TOPPLED A UTILITY POLE, HIT A 3¿ X 4¿ ELECTRICAL TRANSFORMER AND THEN THE GAS SERVICE AND METER. THE VEHICLE CLIPPED THE SERVICE LINE AT THE BUILDING, IGNITING THE BUILDING AND CAR. OUR GAS METER WAS LOCATED 17¿ IN FROM THE CURB; THE VEHICLE CLIPPED A LIGHT POLE OFF, TRAVELED ANOTHER 25 FEET DIAGONALLY WHERE THE VEHICLE STRUCK THE TRANSFORMER AND GAS SERVICE LINE. THE FIRE SPREAD TO THE OUTER WALL OF THE JEWELRY STORE AND THE ATTIC. | 81395 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
491 | 2007-05-01 | TX | sabotage | UNKNOWN (EL PASO COUNTY) | TEXAS GAS SERVICE COMPANY | EXCAVATOR INSTALLING A IRRIGATION SYSTEM HIT 1" POLY SERVICE LINE. REPAIRS WERE MADE BY REPLACING A TWO FOOT SECTION OF POLY PIPE. 600 PEOPLE WERE EVACUATED AND MEDIA WAS ON SITE. | 698 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
492 | 2007-04-04 | MD | other | UNKNOWN (WORCESTER COUNTY) | EASTERN SHORE GAS COMPANY |  | 250150 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
493 | 2007-05-14 | IL | other | UNKNOWN (COOK COUNTY) | NORTHERN ILLINOIS GAS D/B/A NICOR GAS | A CIGARETTE IGNITED LANDSCAPING WOOD CHIPS NEAR THE LOCATION OF THE METER SET. THE FIRE DAMAGED THE METER SET, THUS CAUSING A RELEASE OF NATURAL GAS INTO THE ATMOSPHERE. | 190600 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
494 | 2007-05-15 | VA | other | UNKNOWN (PRINCE WILLIAM COUNTY) | WASHINGTON GAS LIGHT COMPANY | WASHINGTON GAS (WGL) RESPONDED TO A WORKING HOUSE FIRE AT THE REQUEST OF THE PRINCE WILLIAM COUNTY FIRE DEPARTMENT TO TURN THE GAS OFF. WGL INTERVIEWED THE HOMEOWNER, LARRY STROUD, AND FOUND THAT THE FIRE WAS FIRST NOTICED ON THE FRONT PORCH AND LATER CONSUMED THE WGL FACILITIES. THE SERVICE LINE WAS CAPPED OFF AND PRESSURE TESTS WERE PERFORMED TO VERIFY THE INTEGRITY OF THE SYSTEM. | 805100 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
495 | 2007-05-03 | TX | sabotage | UNKNOWN (DALLAS COUNTY) | ATMOS ENERGY CORP., MID-TEX DIVISION | AN EXCAVATOR STRUCK A SERVICE LINE, CAUSING A LEAK. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
496 | 2007-05-02 | TX | sabotage | UNKNOWN (TARRANT COUNTY) | ATMOS ENERGY CORP., MID-TEX DIVISION | AN EXCAVATOR STRUCK A MAIN, CAUSING A LEAK. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
497 | 2007-05-16 | CA | other | UNKNOWN (KERN COUNTY) | SOUTHERN CALIFORNIA GAS COMPANY | ON MAY 16, 2007 A PIPELINE CONTRACTOR WORKING FOR SOUTHERN CALIFORNIA GAS COMPANY INSTALLED A 1¿ PE BYPASS SYSTEM ON A 3¿ PE MAIN, USING MECHANICAL TAPPING TEE FITTINGS. AFTER COMPLETION OF STAND-UP TEST, AND TAPPING OF TEES, 1¿ PIPE PULLED OUT OF TEE THROAT¿S COMPRESSION FITTING, ALLOWING FULL-OPEN BLOW. ESCAPING GAS IGNITED, BURNING 3 PIPELINE CONTRACTOR EMPLOYEES, 2 OF WHICH WERE HOSPITALIZED. ALL PIPING AND COMPONENTS WITHIN EXCAVATION WERE COMPLETELY DESTROYED. INTERVIEW WITH SOUTHERN CALIFONIA GAS COMPANY SUPERVISOR AND PIPELINE CONTRACTOR SUPERVISORS INDICATED THAT ALL PROCEDURES FOR INSTALLATION OF COMPONENTS WERE FOLLOWED PROPERLY. AS OF REPORT DATE, INJURED PIPELINE CONTRACTOR EMPLOYEES HAVE NOT BEEN INTERVIEWED BY SOUTHERN CALIFORNIA GAS COMPANY. AS A REMEDIAL ACTION, ALL 1¿ PE MECHANICAL TAPPING TEES WITH SCREW-TYPE COMPRESSION FITTINGS HAVE BEEN REMOVED FROM STOCK, AND ARE NO LONGER BEING INSTALLED. OTHER STYLE MECHANICAL TAPPING TEES AND FUSION PROCEDURES ARE BEING USED IN LEIU OF THIS PARTICULAR MODEL OF MECHANICAL TAPPING TEE. | 11000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
498 | 2007-05-17 | TN | other | UNKNOWN (DAVIDSON COUNTY) | PIEDMONT NATURAL GAS | 02/10/2010: AFTER THE FIRE ON MAY 17, 2007, PIEDMONT HIRED OUTSIDE EXPERTS TO INVESTIGATE THE CAUSE OF THE FIRE. PRIOR TO CONCLUSION OF THE EXPERT'S INVESTIGATION, PIEDMONT SETTLED SEVERAL PERSONAL INJURY AND PROPERTY DAMAGE CLAIMS WITHOUT ADMISSION OF LIABILITY ON THE PART OF PIEDMONT. HOWEVER, AT LEAST ONE EXPERT CONCLUDED THAT THE CRACK IN THE CAST IRON VALVE (AS PREVIOUSLY REPORTED) WAS LIKELY CAUSED BY IMPROPER INSTALLATION OF THIS PORTION OF THE LINE (UNDERNEATH THE DRIVEWAY AT THE ADDRESS OF THE FIRE) BY A THIRD PARTY CONTRACTOR OVER 20 YEARS PRIOR TO THE INCIDENT. NO CONCLUSIONS WERE REACHED REGARDING THE SOURCE OF IGNITION OR THE INVOLVEMENT, IF ANY, OF WORK DONE INSIDE THE HOUSE ON PIPING AND/OR APPLIANCES PRIOR TO THE INCIDENT. THERE HAVE BEEN NO SIMILAR PROBLEMS REPORTED ANYWHERE ELSE ON THE SAME LINE OR WITHIN THE SAME PROJECT LEADING PIEDMONT TO REASONABLY BELIEVE THAT THE OCCURRENCE WAS THE RESULT OF AN ISOLATED HUMAN ERROR ON THE PART OF THE THIRD PARTY INSTALLER APPROXIMATELY 20 YEARS AGO. ORIGINAL REPORT: AT 2:15 AM, ON MAY 17, 2007, PIEDMONT NATURAL GAS RECEIVED A CALL FROM THE LOCAL EMERGENCY MANAGEMENT OFFICE IN NASHVILLE, TENNESSEE NOTIFYING US THAT AN EXPLOSION WAS REPORTED AT 4601 BILLINGSGATE DRIVE. IN KEEPING WITH PIEDMONT'S STANDARD OPERATING PROCEDURE, FIRST RESPONDER PERSONNEL WERE SUBSEQUENTLY DISPATCHED TO THE SCENE. SHORTLY THEREAFTER, PIEDMONT NATURAL GAS PERSONNEL ARRIVED ON THE SCENE AND CONFIRMED THAT A FIRE AND POSSIBLY AN EXPLOSION HAD TAKEN PLACE. THE APPARENT CAUSE OF THIS INCIDENT IS STILL UNKNOWN AT THIS TIME, AND WE ARE WORKING CLOSELY WITH ACCIDENT RECONSTRUCTION AS PART OF THE OVERALL INVESTIGATION. AS SUCH, WE HOPE TO FURTHER UNDERSTAND THE EVENTS AND ACTIVITIES IN THE HOUSE LEADING UP TO THE TIME OF THE INCIDENT; HOWEVER, THEY ARE UNKNOWN AT THIS TIME. TO DATE, WE HAVE NOT BEEN ABLE TO TEST THE GAS APPLIANCES OR THE HOUSE PIPING, BUT HOPE TO ACCOMPLISH THIS SOON. REGARDING OUR NATURAL GAS INFRASTRUCTURE, WE HAVE DISCOVERED A LEAKING, CRACKED CAST IRON VALVE ON THE MAIN NEAR THE HOUSE, BUT WE HAVE NOT DETERMINED CONCLUSIVELY AT THIS POINT IF IT CONTRIBUTED TO THE INCIDENT. | 200000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
499 | 2007-05-18 | VA | other | UNKNOWN (FAIRFAX COUNTY) | WASHINGTON GAS LIGHT COMPANY | ACCORDING TO FAIRFAX FIRE MARSHAL'S REPORT 20071380315, THIS WAS AN ACCIDENTAL FIRE WHICH STARTED ON THE REAR DECK OF THE HOUSE AND LATER ENTERED THE HOUSE THROUGH THE WINDOWS, SOFFIT AND ROOF LINE. WASHINGTON GAS FACILITIES WERE CONSUMED BY THE FIRE AND COULD NOT BE RETRIEVED DUE TO STRUCTURAL CONCERNS IN THE AREA. WASHINGTON GAS CAPPED THE SERVICE OFF AT THE CURB VALVE. | 405100 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
500 | 2007-05-17 | MA | other | UNKNOWN (NORFOLK COUNTY) | BAY STATE GAS COMPANY | DISTRIBUTION CREW WAS WORKING ON A MAIN TIE-IN. FIRE OCCURED IN THE OPEN DITCH. ONE EMPLOYEE RECEIVED BURNS WHICH REQUIRED INPATIENT HOSPITALIZATION. | 28064 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
501 | 2007-05-10 | TX | sabotage | UNKNOWN (DENTON COUNTY) | ATMOS ENERGY CORP., MID-TEX DIVISION | AN EXCAVATOR STRUCK A MAIN, CAUSING A LEAK. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
502 | 2007-05-24 | IL | other | UNKNOWN (COOK COUNTY) | NICOR GAS | ARSON FIRE ENGULFED STRUCTURE. FIRE THEN PROGRESSED TO THE METER SET THUS CAUSING THE DAMAGE TO THE METER SET AND THE SUBSEQUENT RELEASE OF GAS. NOTE: THIS INCIDENT WAS ORIGINALLY REPORTED UNDER 15549 LATROP, HARVEY. | 51500 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
503 | 2007-06-07 | MD | other | UNKNOWN (PRINCE GEORGE'S COUNTY) | WASHINGTON GAS LIGHT COMPANY | WASHINGTON GAS RESPONDED TO A HOUSE FIRE AT THE REQUEST OF THE PRINCE GEORGE'S FIRE BOARD. THE GAS WAS OFF UPON THE ARRIVAL OF THE WGL SERVICE MAN, HOWEVER, DEBRIS AND ASHES FROM THE FIRE ACCUMULATED AROUND THE SERVICE RISER CAUSING A RELEASE. THE SERVICE WAS CAPPED OFF AND PRESSURE TESTS WERE PERFORMED TO VERIFY THE INTEGRITY OF THE SYSTEM. | 355100 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
504 | 2007-05-29 | TX | other | UNKNOWN (JOHNSON COUNTY) | ATMOS ENERGY CORP., MID-TEX DIVISION | THE CAUSE OF THIS EVENT APPEARS TO BE THE RESULT OF A COMBINATION OF FACTORS THAT WAS NOT READILY FORESEEABLE. DURING ATMOS ENERGY CORPORATION INVESTIGATION SUBSEQUENT TO THE INCIDENT, THREE LEAKS WERE FOUND AND REPAIRED ON WOODARD AVENUE. HOWEVER, THERE IS INSUFFICIENT EVIDENCE TO SUPPORT THAT GAS ESCAPING FROM THESE LOCATIONS (632 WOODARD, 634 WOODARD, AND 700 WOODARD) WAS SIGNIFICANT ENOUGH TO RELEASE GAS RAPIDLY ENOUGH TO HAVE CAUSED THE INCIDENT. ADDITIONALLY, THE LEAK LOCATED POST-ACCIDENT AT 632 WOODARD WAS DETERMINED TO HAVE BEEN CAUSED BY A MANUFACTURING OR MACHINING DEFECT IN THE RELEVANT COUPLING THAT WAS VISIBLE TO THE ORIGINAL INSTALLER. ATMOS ENERGY CORPORATION INVESTIGATION HAS ALSO RESULTED IN THE DETERMINATION THAT THE OCCUPANTS OF 632 WOODARD WERE AWARE OF A POTENTIAL HAZARD WHEN THEY CONTACTED LOCAL FIRE AUTHORITIES, BUT DISREGARDED INSTRUCTIONS BY SUCH AUTHORITIES IN LIGHTING ADDITIONAL CIGARETTES. | 250000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
505 | 2007-06-01 | GA | sabotage | UNKNOWN (DOUGLAS COUNTY) | ATLANTA GAS LIGHT | AN EXTERMINATING COMPANY EMPLOYEE DRILLED INTO A PLASTIC SERVICE WITH A GASOLINE ENGINE DRIVEN AUGER WHILE MAKING HOLES IN THE GROUND FOR INSTALLATION OF TERMITE BAITS. THE ESCAPING GAS IGNITED AND THE EXTERMINATING EMPLOYEE'S FACE WAS BURNED. HE WAS SUBSEQUENTLY HOSPITALIZED OVER NIGHT FOR TREATMENT. NO NOTIFICATION WAS MADE TO THE STATE ONE-CALL CENTER PRIOR TO THIS WORK. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
506 | 2007-07-11 | TX | sabotage | UNKNOWN (DENTON COUNTY) | COSERV GAS LTD | EXCAVATOR DAMAGED A 2" POLY MAIN WHILE MAKING AN ELECTRICAL CONNECTION TO A NEW STRUCTURE. EXCAVATOR STATED THAT THEY KNEW WHERE THE LINES WERE AND DIDN'T CALL FOR LOCATES. | 1135 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
507 | 2007-06-23 | VA | other | UNKNOWN (FAIRFAX COUNTY) | WASHINGTON GAS LIGHT COMPANY | WASHINGTON GAS RESPONDED TO A FIRE AT THE REQUEST OF THE FAIRFAX COUNTY FIRE DEPARTMENT TO TURN THE GAS OFF. ACCORDING TO A PRESS RELEASE FROM THE FAIRFAX COUNTY FIRE AND RESCUE DEPARTMENT, ¿MOLOTOV COCKTAILS WERE THROWN AND EXPLODED IN THE REAR OF THE STORE, IGNITING THE GAS METER AND CAUSING THE FIRE.¿ PRESSURE TESTS AND LEAKAGE SURVEYS WERE CONDUCTED TO VERIFY THE INTEGRITY OF THE GAS SYSTEM. | 301100 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
508 | 2007-06-29 | CA | sabotage | UNKNOWN (SACRAMENTO COUNTY) | PACIFIC GAS & ELECTRIC | WHILE TILLING IN LIME INTO THE SOIL TO CREATE A STRUCTURAL ROAD BASE MATERIAL, A PRIVATE SOIL STABILIZATION COMPANY HIT PACIFIC GAS & ELECTRIC'S 4-INCH DIAMETER HIGH PRESSURE PLASTIC DISTRIBUTION MAIN. A SUBSEQUENT FIRE WHICH DESTROYED THE CONTRACTOR'S CMI RS 650 RECLAIMER STABILIZATION EQUIPMENT. CONTRACTOR DID NOT CALL FOR USA. | 105000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
509 | 2007-06-19 | IL | sabotage | UNKNOWN (PEORIA COUNTY) | AMERENCILCO | The homeowner and person who was injured had just purchased a gasoline powered auger. the were augering a hole within 2 to 3 feet of the gas meter and had not called JULIE (1-call) to request a locate. They augered through a 1/2" PE service installed in 1981. The gas ignited resulting in 1 person receiving 2nd and 3rd degree burns requiring in-patient hospitalization. Property damage from the resulting fire included siding on the house, air conditioner, and damage to the service line. | 5000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
510 | 2007-06-24 | CA | other | UNKNOWN (EL DORADE COUNTY COUNTY) | SOUTHWEST GAS CORPORATION | A FOREST FIRE, LATER NAMED THE ANGORA FIRE, BEGAN AROUND 14:00 ON JUNE 24TH IN THE AREA WEST OF THE TAHOE PARADISE SUBDIVISION NEAR SOUTH LAKE TAHOE. SOUTHWEST GAS WAS CONTACTED BY THE LAKE VALLEY FIRE DEPARTMENT AT APPROXIMATELY 16:00 TO ASSIST BY SHUTTING OFF THE GAS TO THE ENTIRE SUBDIVISION. AT 18:10, SOUTHWEST GAS IMPLEMENTED ITS ISOLATION PLAN FOR THE AREA BY SHUTTING OFF GAS SERVICE TO APPROXIMATELY 1475 CUSTOMERS. AT 18:45, SOUTHWEST GAS ISOLATED APPROXIMATELY 38 ADDITIONAL CUSTOMERS. TWO HUNDRED TWENTY TWO METERS SUFFERED DAMAGE FROM THE FIRE. THE ORIGIN AND CAUSE OF THE FIRE WAS NOT ATTRIBUTED TO THE OPERATION OR MAINTENANCE OF SOUTHWEST TGAS FACILITIES NOR DID THE INITIAL FIRE INVOLVE SOUTHWEST GAS FACILITIES. ON JUNE 25TH, SOUTHWEST GAS BEGAN RELIGHT EFFORTS IN CERTAIN NO FIRE DAMAGE AREAS. RESTORATION EFFORTS CONTINUED THROUGH TO JUNE 27TH AS ALLOWED BY THE FIRE DEPARTMENT. AS OF JULY 23RD, 985 RELIGHTS HAVE BEEN COMPLETED WITH 140 REMAINING. ON JUNE 25TH, SOUTHWEST GAS BEGAN RELIGHT EFFORTS IN CERTAIN NO FIRE DAMAGE AREAS. RESTORATION EFFORTS CONTINUED THROUGH TO JUNE 27TH AS ALLOWED BY THE FIRE DEPARTMENT. AS OF JULY 23RD, 985 RELIGHTS HAVE BEEN COMPLETED WITH 140 REMAINING. ***SUPPLEMENTAL*** NO CHANGES WERE MADE OTHER THAN MARKING THE "FINAL REPORT" CHECK BOX. | 71050 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
511 | 2007-06-23 | LA | sabotage | UNKNOWN (ORLEANS COUNTY) | ENTERGY NEW ORLEANS, INC - GAS DISTRIBUTION BUSINESS | ENTERGY GAS OPERATION WAS CONTACTED AT ABOUT 1300 HOURS BY OWNER OF 6024 ARGONNE BLVD INDICATING THERE HAD BEEN AN EXPLOSION AT HIS RESIDENCE AT 0630 HRS. HOMEOWNER CONTACTED PLUMBER PRIOR TO CONTACTING ENTERGY BECAUSE HE INITIALLY THOUGHT IT WAS A PROBLEM WITH SOMETHING INSIDE HIS RESIDENCE. PLUMBER ADVISED THAT HE CONTACT ENTERGY. NO EMERGENCY RESPONSE GROUPS (POLICE, FIRE DEPARTMENT) WERE CONTACTED BY HOMEOWNER. INVESTIGATION AT THE SCENE DISCOVERED BROKEN GAS LINE WITH LIVE GAS IN VACANT LOT AT 6030 ARGONNE ST. TAP ON MAIN FOR THIS SERVICE WAS EXCAVATED, REMOVED, AND TAP PLUGGED FURTHER INVESTIGATION DETERMINED RESIDENCE AT 6030 ARGONNE BLVD WAS DEMOLISHED NOV/DEC 2006 SERVICE WAS OPEN IN THE GROUND FOR OVER SIX MONTHS INDICATING HIGH PROBABILITY OF MIGRATION UNDER SLAB AT 6024 ARGONNE BLVD; HOWEVER THERE WAS NO INDICATION OF FIRE INSIDE 6024 ARGONNE (SEE PART A, 5 E, ON PAGE 1) FURTHER INVESTIGATION OF EVERY SERVICE TAP ON THE 6" MAIN BETWEEN POLK ST. AND GERMAIN ST. INDICATED NO OTHER GAS ESCAPING FROM OUR SYSTEM DEMOLITION CONTRACTOR HAD A PERMIT FOR DEMOLITION BUT DID NOT CALL FOR LOCATES NOR CALL IN THE BREAK. NOTE: CAUSE OF INCIDENT AT 6024 ARGONNE BLVD IS STILL UNDER INVESTIGATION TO DETERMINE IF THERE ACTUALLY WAS AN EXPLOSION AND TO DETERMINE IF NATURAL GAS WAS INVOLVED. | 50250 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
512 | 2007-07-05 | VA | other | UNKNOWN (FAIRFAX COUNTY) | WASHINGTON GAS LIGHT COMPANY | WASHINGTON GAS RESPONDED TO A FIRE AT THE REQUEST OF THE FAIRFAX FIRE DEPARTMENT TO TURN THE GAS OFF. WGL CONDUCTED A LEAK SURVEY, ODORANT TEST, AND SEVERAL LEAK SURVEYS TO VERIFY THE INTEGRITY OF THE SYSTEM AND NO ISSUES WERE FOUND. THE CAUSE OF THE FIRE REMAINS UNDER INVESTIGATION BY THE FAIRFAX CITY FIRE MARSHAL'S OFFICE AND THEIR INCIDENT NUMBER IS 20071860198. | 251700 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
513 | 2007-07-12 | CA | sabotage | UNKNOWN (SONOMA COUNTY) | PACIFIC GAS & ELECTRIC | WHILE EXCAVATING THE SOIL FOR A PROJECT TO INSTALL CURB AND GUTTERS A CONTRACTOR HIT A PACIFIC GAS & ELECTRIC 8-INCH DIAMETER STEEL HIGH-PRESSURE GAS DISTRIBUTION MAIN. THE SUBSEQUENT RELEASE OF GAS RESULTED IN THE EVACUATION OF LOCAL BUSINESS AND CAUSED TRAFFIC TO BE REROUTED. THE LINE WAS MARKED PER USA #139058. THE CONTRACTOR HAD KNOWLEDGE OF THE MAIN FROM WALKING THE SITE WITH A PG&E LOCATOR. ALSO, AS REQUESTED BY PG&E ON SEVERAL OCCASIONS, THE CONTRACTOR WAS REQUIRED BUT FAILED TO REQUEST A STAND BY INSPECTOR WHILE WORKING OVER THIS FACILITY. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
514 | 2007-07-14 | MD | other | UNKNOWN (FREDERICK COUNTY) | WASHINGTON GAS LIGHT COMPANY | A WASHINGTON GAS REGULATOR STATION LOCATED APPROXIMATELY 25 FEET BEHIND THE CURB WAS DAMAGED AS A RESULT OF VEHICULAR TRAFFIC. THE STATION HAD BARRICADE PROTECTION, HOWEVER, THE CAR DID STRIKE THE ABOVE GROUND PIPING AND BROKE A ONE-INCH NIPPLE AT THE THREADS. LEAKING GAS IGNITED AND THE DRIVER OF THE VEHICLE WAS BURNED. THE POSTED SPEED LIMIT WAS 35 MPH. THE POLICE ACCIDENT REPORT NUMBER 10634453 STATED THAT THE VEHICLE ATTEMPTED TO NEGOTIATE A SHARP DOWNHILL TURN AT APPROXIMATELY 70 MPH. | 20700 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
515 | 2007-07-21 | CA | other | UNKNOWN (RIVERSIDE COUNTY) | SOUTHERN CALIFORNIA GAS COMPANY | ON JULY 21, 2007 A METER SET ASSEMBLY WAS DAMAGED FROM BEING STRUCK BY A MOTORIZED PALLET JACK, CRACKING A 1¿ BYPASS FITTING. ESCAPING GAS FROM THE DAMAGED METER SET ASSEMBLY IGNITED, CAUSING APPROXIMATELY $100K DAMAGE TO THE STRUCTURE. NO INJURIES WERE ATTRIBUTED IN ANY WAY TO THE ESCAPING GAS OR RESULTING FIRE. GAS SERVICE HAS BEEN ABANDONED UNTIL REPAIRS OF BUILDING ARE COMPLETED. | 101100 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
516 | 2007-07-10 | KY | sabotage | UNKNOWN (JEFFERSON COUNTY) | LOUISVILLE GAS AND ELECTRIC COMPANY | ATTACHED LG&E REPORT TO THE KPSC REPORT SUBMITTED SIMULTANEOUSLY. | 74297 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
517 | 2007-07-23 | CA | other | UNKNOWN (KINGS COUNTY) | SOUTHERN CALIFORNIA GAS COMPANY | ON JULY 23, 2007 A GAS SERVICE RISER WAS DAMAGED FROM A VEHICLE WHOSE DRIVER LOST CONTROL, LEAVING THE TRAVELED ROADWAY. ESCAPING GAS FROM THE DAMAGED METER SET ASSEMBLY IGNITED, CAUSING APPROXIMATELY $150K DAMAGE TO THE STRUCTURE. ALTHOUGH THE DRIVER WAS TRANSPORTED TO THE HOSPITAL FOR INJURIES FROM IMPACTING THE BUILDING, NO INJURIES WERE ATTRIBUTED IN ANY WAY TO THE ESCAPING GAS OR RESULTING FIRE. GAS SERVICE HAS BEEN ABANDONED UNTIL REPAIRS OF BUILDING ARE COMPLETED. | 151500 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
518 | 2007-08-22 | TX | sabotage | UNKNOWN (COLLIN COUNTY) | COSERV GAS LTD | CITY OF FAIRVIEW WAS EXCAVATING TO INSTALL A TAP ON A WATER LINE AND DAMAGE A 6" POLY MAIN | 3200 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
519 | 2007-07-03 | NY | other | UNKNOWN (CHEMUNG COUNTY) | NEW YORK STATE ELECTRIC & GAS | THIS REPORT IS BEING SUBMITTED IN AN ABUNDANCE OF CAUTION EVEN THOUGH THE INVESTIGATION DONE TO DATE INDICATES THAT NO MISFEANCE OCCURED ON THE PART OF NEW YORK STATE GAS AND ELECTRIC. THIS REPORT IS BEING FILED SINCE THE COMPANY MADE A TELEPHONE REPORT. AFTER THE INCIDENT, WHEN ENTRY WAS MADE INTO THE HOUSE, THE INLET RINSER PIPE WAS FOUND TO BE CUT AND DISCONNECTED. ON AUGUST 14, 2007, THE SERVICE LINE WAS TESTED AND WAS FOUND NOT TO BE LEAKING. THE INVESTIGATION IS CONTINUING AS TO WHAT HAPPENED TO THE PIPING INSIDE THE HOUSE AND WHO, IF ANYONE, CAUSED THIS TO OCCUR. UPDATED BY PHMSA ON 12/1/2015 PER OPERATOR'S MARK UP: THE INVESTIGATION WAS COMPLETED AND NYSEG DETERMINED THE INCIDENT WAS CAUSED BY AN INTENTIONAL ACT. THE INLET RISER PIPE WAS INTENTIONALLY CUT AND DISCONNECTED INSIDE THE HOME AND DOWNSTREAM OF THE METER. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
520 | 2007-07-17 | NC | sabotage | UNKNOWN (MECKLENBURG COUNTY) | PUBLIC SERVICE OF NORTH CAROLINA, INC | A CONTRACTOR USING A SKID STEER FRONT-END LOADER WAS EXCAVATING NEAR THE METER AT 525 DELBURG STREET, DAVIDSON, NC, AND DAMAGED THE 3/4" PLASTIC SERVICE. LEAKING GAS IGNITED CAUSING THE HOUSE TO BE DAMAGED BY FIRE BEFORE GAS COULD BE SHUT OFF AND THE FIRE EXTINGUISHED.A ONE CALL REQUEST FOR LOCATE #A071581021 WAS MADE FOR THIS ADDRESS BY PELICAN POOLS ON JUNE 7,2007, INDICATING THE WORK WOULD START JUNE 11, 2007, WITH A WORK DURATION OF TWO DAYS. LINES WERE MARKED AS REQUESTED. NO TICKET UPDATES WERE MADE OR NEW LOCATE TICKETS ISSUED. | 350350 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
521 | 2007-07-03 | NM | other | UNKNOWN (BERNALILLO COUNTY) | PUBLIC SERVICE COMPANY OF NEW MEXICO | AT APPROXIMATELY 13:50 ON JULY 3RD, 2007, A TRUCK WAS INTENTIONALLY DRIVEN INTO A METER SET WHICH SERVED A SUX UNIT APARTMENT BUILDING AT 246 TEXAS SE, ALBUQUERQUE, NEW MEXICO 87108. THE TRUCK STRUCK THE METERS AND THEN PUNCTURED THE BUILDING WALL THE TRUCK IGNITED, WHICH IN TURN IGNITED THE BUILDING AND THE GAS. DUE TO THE IMPACT, THE METER SET WAS SHEERED OFF BELOW THE INLET VALVE AND THE RISER WAS BENT INTO THE OPENING OF THE BUILDING, ALLOWING GAS TO BLOW IN, AT MAIN PRESSURE, INTO THE BUILDING. POLICE ARRIVED TO EVACUATE THE BUILDING AND THE FIRE DEPARTMENT ARRIVED SHORTLY AFTER MAKING ONE LAST CHECK OF THE BUILDING. IT WAS AT THIS POINT WHEN THE GAS IGNITED AND EXPLODED AS A RESULT OF THE FIRE. THE BUILDING BURNED AND COLLAPSED. PUBLIC SERVICE COMPANY OF NEW MEXICO HAD A GAS SERVICE TECHNICIAN ON SITE WITHIN TWENTY MINUTES OF FIRST RECEIVING THE CALL AND A CONSTRUCTION CREW HAD CUT GAS TO THE BUILDING AT 15:30. | 502782 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
522 | 2007-07-25 | TX | sabotage | UNKNOWN (DENTON COUNTY) | ATMOS ENERGY CORP. MID-TEX DIVISION | AN EXCAVATOR STRUCK A MAIN, CAUSING A LEAK. | 55000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
523 | 2007-08-13 | CO | sabotage | UNKNOWN (LARIMER COUNTY COUNTY) | PUBLIC SERVICE CO. OF COLORADO | THE SUBCONTRACTOR FOR THE CITY OF FORT COLLINS WAS WORKING ON A ROAD IMPROVEMENT PROJECT. THE SUBCONTRACTOR HAD CALLED THE ONE CALL SYSTEM FOR LOCATES ON 8/10/07 (FRIDAY) AND THE GAS LINE WAS SCHEDULED TO BE LOCATED IN THE FIELD ON 8-14-07 (TUESDAY). THE SUBCONTRACTOR RUPTURED THE GAS LINE ON 8/13/07 (MONDAY) WITH A RECYCLER EXCAVATION MACHINE BEFORE THE GAS LINE WAS SCHEDULED TO BE LOCATED. THE OPERATOR ABANDONED THE EQUIPMENT WITH THE MOTOR STILL RUNNING WHICH APPEARS TO BE THE SOURCE OF THE EVENTUAL IGNITION. THE SITE WAS ARLREADY BARRICADED FOR CONSTRUCTION AND NO ADDITIONAL EVACUATION WAS REQUIRED. | 413000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
524 | 2007-07-26 | CT | sabotage | UNKNOWN (nan COUNTY) | YANKEE GAS SERVICES COMPANY | A CONTRACTOR WHILE USING A RECLAIMING MACHINE WORKING FOR THE TOWN OF BETHEL, HIT AND BROKE A DRIP STEM LOCATED APPROXIMATELY TWO INCHES UNDER THE ASPHALT ON A SIX INCH, 35 LB STEEL NATURAL GAS DISTRIBUTION SYSTEM. AN IMMEDIATE IGNITION OF THE GAS CAUSED THE RECLAIMING MACHINE TO BE ABANDON BY THE OPERATOR WHILE STILL OVER THE LEAKING GAS. IDENTIFICATION, LOCATION, AND OPERATION OF ISOLATION VALVES REQUIRED TIME THAT ALLOWED THE FIRE TO BURN FOR 4.5 HOURS. A REPAIR WAS MADE TO THE DAMAGED FACILITY BY REMOVING THE DRIP STEM FROM THE GAS MAIN. A TOTAL OF 218 CUSTOMERS WERE SHUT DOWN AND HAD TO BE RE-ENERGIZED BEFORE THE INCIDENT WS OVER, WHICH CONTINUED INTO THE NEXT DAY. | 278400 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
525 | 2007-08-23 | CA | other | UNKNOWN (SAN MATEO COUNTY) | PACIFIC GAS AND ELECTRIC COMPANY | A CONTRACT EMPLOYEE JUST COMPLETED A WELD ON A STEEL-TO-PLASTIC COMPRESSION CONNECTION TO REPLACE A COPPER SERVICE. IN THE SAME BELL HOLE WAS A SECOND COPPER SERVICE WHICH WAS STILL PRESSURIZED. WHILE POSITIONING HIMSELF, THE WORKER BUMPED THE PRESSURIZED SERVICE AND THE BRAZED COPPER-TO-BRASS CONNECTION BROKE LOOSE, GAS ESCAPED AND WAS IGNITED BY THE WELDING TORCH. THE WORKER SUSTAINED BURNS TO HIS FACE AND NECK. HE WAS TAKEN TO THE HOSPITAL AND ADMITTED FOR IN-PATIENT CARE. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
526 | 2007-08-07 | NM | other | UNKNOWN (nan COUNTY) | PNM GAS SERVICES | CAR TURNED ON TO BERRYHILL AT HIGH RATE OF SPEED LOST CONTROL SIDING DOWN THE ROAD OVER CORRECTED AND RAN IN METER LOCATED AT PROPERTY LINE IN FRONT OF HOUSE. DESTROYING THE METER AND BREAKING THE SERVICE LINE AT THE STOP. DRIVER DIED AT THE SCENE DUE TO INJURIES SUSTAINED IN CAR CRASH. THREE OTHER OCCUPANTS OF THE CAR WERE SENT TO THE HOSPITAL. TWO REFUSED CARE AND LEFT HOSPITAL, THE THIRD WAS TREATED AND RELEASED. EDIT: ORIGINAL REPORT SHOWED THAT THERE WAS AN EVACUATION. THIS INFORMATION IS INCORRECT. THERE WAS NO EVACUATION. SUPPLEMENTAL SUBMITTED TO CORRECT THE INITIAL ERROR. - ANGELA DOW. THIS VEHICLE CRASH OCCURRED ON BERYHILL STREET, WEST OF THE INTERSECTION WIT HOWE STREET, CIBOLA COUNTY, MILAN, NM. THE CRASH OCCURRED IN A RESIDENTIAL AREA. AT THE TIME OF THIS CRAAHE, THE WEATHER CONDITION WAS OVERCAST, WITH THE TEMPERATURE OF 59 DEGREES. WEATHER WAS NOT A FACTOR IN THIS CRASH. EXAMINATION OF THE SCENE REVEALED TIRE FURROWS LOCATED IN THE URBAN EMBANKMENT AREA ON THE SOUTH SIDE OF BERRYHILL, WEST OF THE INTERSECTION WITH HOWE STREET. THE TIRE FURROWS LOCATED IN THE URBAN EMBANKMENT AREA ON THE SOUTH SIDE OF BERRYHILL, WEST OF THE INTERSECTION WITH HOWE STREET. THE TIRE FURROWS CONTINUED WEST. TIRE SKID MARKS WERE LOCATED ON THE PAVEMENT AT THE END OF THE FURROWS. VEHICLE SCUFF MARKS CONTINUED TO THE FINAL RESTING LOCATION OF VEHICLE #1. THE FENCE AND GAS METER IN FRONT OF 1504 BERRYHILL WERE DAMAGED BY VEHICLE #1. THE TELEPHONE POLE LOCATED IN FRONT OF 1504 BERRYHILL WAS STRUCK BY VEHICLE #1. BASED ON THIS EVIDENCE, VEHICLE #1 WAS TRAVELING NORTH ON HOWE STREET, VEHICLE #1 TURNED LEFT (WEST) ONTO BERRYHILL AND STAYED ON THE LEAFT SIDE OF THE ROADWAY. VEHICLE #1 CONTINUED THE BREAKING ACTION ONTO THE PAVEMENT, AT WHICH TIME, VEHICLE #1 BEGAN TO TURN SIDEWAYS (FACING SOUTHWEST). VEHICLE #1 TURNED TO THE EAST TOWARDS THE NORTH SIDE OF BERRYHILL. BECAUSE OF THIS SIDEWAYS MOTION OF VEHICLE #1, THE LEFT SIDE TIRES DEFLATED ON VEHICLE #1. VEHICLE #1 THEN STRUCK THE FENCE AND GAS METER IN FRONT OF 1504 BERRYHILL STREET. AT THIS TIME, VEHICLE #1 FLIPPED ONTO ITS LEFT SIDE AND VAULTED TO ITS FINAL RESTING LOCATION, FACING WEST. | 1180 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
527 | 2007-09-14 | GA | natural disasters | UNKNOWN (MONROE COUNTY) | FORT VALLEY UTILITIES | LIGHTNING STRIKE TO EL PASO(SOUTHERN NATURAL GAS) GATE STATION TO FORT VALLEY UTILITIES. LIGHTNING CAUSED DAMAGE AND FIRE AT EL PASO FACILITY. DUE TO CLOSE PROXIMITY OF FORT VALLEY UTILITIES METER STATION HEAT DAMAGE OCCURED TO METER COMPONENTS AND ODERAZITION EQUIPMENT. FIRE WAS CONTROLLED BY ISOLATING VALVES. FORT VALLEY EXPERIENCED PRESSURE LOSS AND HAD TO CUT OFF INDUSTRIAL AND COMMERCIAL CUSTOMERS UNTILL TEMPORARY GAS FEED FROM EL PASO WAS ESTABLISHED. | 15000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
528 | 2007-09-18 | TX | other | UNKNOWN (COLLIN COUNTY) | COSERV GAS LTD | THIRD PARTY REPAIRING A PHONE LINE UTILIZING A BLOW TORCH ADCCIDENTALLY CAME IN CONTACT WITH A BLANKET WHICH WAS LAYING OVER GAS LINE. THE BLANKET CAUGHT ON FIRE AND MELTED A SMALL PIN HOLE IN GAS PIPE. A SMALL FLASH FIRE OCCURRED AND WAS EXTINGUISHED IMMEDIATLY. | 400 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
529 | 2007-08-19 | MN | natural disasters | UNKNOWN (DAKOTA COUNTY) | CENTERPOINT ENERGY RESOURCES GROUP DBA CENTERPOINT ENERGY MINNESOTA GAS | METER SET AND OR HOUSE WAS STRUCK BY LIGHTNING CAUSING A FIRE. | 151000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
530 | 2007-09-09 | NM | other | UNKNOWN (SANTA FE COUNTY) | PUBLIC SERVICE COMPANY OF NEW MEXICO - GAS SVCS | A FIRE STARTED IN THE SHED AT #22 LOIS, SANTA FE, NM AND MIGRATED ITS WAY ACROSS GRASS AND WEEDS TO A MOBILE HOME. THE SANTA FE FIRE DEPT ESCORTED OUR SERVICE TECH TO THE GAS METER SET WHERE HE FOUND THE STOPCOCK ALREADY TURNED OFF BY SFFD. THE TECH REMOVED THE METER AND REPAIRED THE INSULATED STOP THAT WAS SEEPING GAS DUE TO THE ELEVATED TEMPERATURE FROM THE MIGRATING FIRE. THE FIRE EVENTUALLY BURNED DOWN THE MOBILE HOME BUT THE FAMILY LIVING THERE HAD BEEN SAFELY EVACUATED. GAS FROM THE METER SET NEVER IGNITED. THE SERVICEMAN PROBED FOR ANY UNDERGROUND GAS AND FOUND NONE. THE FIRE DEPT EVENTUALLY CALLED US TO LET US KNOW THE SOURCE OF THE FIRE WAS FAULTY ELECTRICAL WIRING IN THE SHED. THE ESTIMATE OF DAMAGE IS AN APPROXIMATION SINCE WE DO NOT HAVE ACCESS TO ANY OTHER INFORMATION. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
531 | 2007-08-30 | SC | natural disasters | UNKNOWN (RICHLAND COUNTY) | SOUTH CAROLINA ELECTRIC AND GAS | A LIGHTNING STRIKE APPEARS TO HAVE HIT AN ELECTRIC METER PEDESTAL AT TRAILER NUMBER 134 AT 2928 ALPINE ROAD. THE SURGE OF ENERGY ARCHED FROM THE ELECTRIC METER PEDESTAL ONTO THE REGULATOR ON OUR GAS METER SET. THE REGULATOR (SINGER 1813B) BODY SEPARATED AND THE ESCAPING GAS IGNITED. THE ENERGY SURGE APPEARS TO HAVE CONTINUED TO TRAVEL ALONG OUR 3/4" STEEL SERVICE LINE TO THE 2" STEEL MAIN WHERE IT BURNED THROUGH TWO DRESSER STYLE 850 INUSLATING SLEEVES CAUSING LEAKS. THE LEAKS AT THE INSULATORS DID NOT IGNITE. | 48994 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
532 | 2007-08-22 | PA | sabotage | UNKNOWN (BEAVER COUNTY) | COLUMBIA GAS OF PENNSYLVANIA INC | CONSTRUCTION CREW INSTALLING GUIDE RAIL ON RT 989 (NEAR SOLAR COURT) IN BEAVER COUNTY, POUNDED GUIDE RAIL INTO 4 INCH STEEL MAIN. CONSTRUCTION CREW STARTED INSTALLATION OF GUIDE RAIL PRIOR TO GAS LINE BEING LOCATED. LOCATOR FOR OPERATOR WAS COMMUNICATING WITH CONSTRUCTION CREW ON LOCATE AND START TIME OF JOB DUE TO RAIN. | 215000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
533 | 2007-08-28 | PA | sabotage | UNKNOWN (LEBANON COUNTY) | UGI UTILITIES, INC. | EXCAVATOR INSTALLING A SEWER MAIN STRUCK A 3/4" MEDIUM PRESSURE GAS SERVICE THAT WAS NOT MARKED. GAS ESCAPED AND RESULTED IN A FIRE THAT DESTROYED A TRAILER HOME. NO INJURIES WERE INCURRED. | 91200 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
534 | 2007-08-24 | SD | other | UNKNOWN (BROWN COUNTY) | NORTHWESTERN ENERGY | A FIRE UNRELATED TO NATURAL GAS OCCURRED AT 119 RAILROAD AVE IN ABERDEEN, SD. FIRE OFFICIALS WERE NOTIFIED OF THE FIRE AT 4;45 AM WHO IN TURN NOTIFIED NORTH WESTERN AT 5:00 AM. THE FIRE WAS ALREADY TOO SEVERE ONCE THE FIREFIGHTERS ARRIVED ON SCENE (FIRE STATION IS TWO BLOCKS SOUTH OF INCIDENT) THAT THE BUILDING COULDN'T BE SAVED. THE FIRE BURNED THROUGH THE ROOF AND WEAKENED AN OUTSIDE BRICK WALL. THE TOP OF THE BRICK WALL FELL INTO THE METER SET AND BROKE THE RISER OFF BELOW THE REGULATOR AND ABOVE THE SERVICE LOCKWING VALVE AROUND 5:52 AM. DAMAGING THE 6" NIPPLE BETWEEN THE REGULATOR AND LOCKWING VALVE. THE RESULTING BLOWING GAS DID IGNITE AND THE FIRE DEPARTMENT ALLOWED THIS TO BURN (ALONG WITH THE BUILDING FIRE) UNTIL EMERGENCY LOCATES WERE VERIFIED AND THE AREA COULD BE SAFELY EXCAVATED IN THE STREET. GAS TO THER SERVICE WAS SHUT OFF IN THE STREET SHORTLY AFTER 8:15 AM. ADDITIONAL PRESSURE TESTING INDICATED NO OTHER RELEASE OF GAS BESIDES AT THE METER SET. MARTIN BETTMAN FROM THE SOUTH DAKOTA PUBLIC UTILITIES COMMISSION/PIPELINE SAFETY WS ON SITE AT INCIDENT ON FRIDAY MORNING, AUGUST 24, 2007. | 225268 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
535 | 2007-09-10 | CA | other | UNKNOWN (SAN BERNARDINO COUNTY) | SOUTHERN CALIFORNIA GAS COMPANY | ON SEPTEMBER 10, 2007 A METER SET ASSEMBLY WAS DAMAGED BY AN ADJACENT BURNING BUILDING. THE FIRE THAT STARTED AT THE BUILDING WAS NOT RELATED TO NATURAL GAS. NO OR INJURIES OR THIRD PARTY DAMAGE WERE ATTRIBUTED TO ESCAPING GAS. REPAIRS WERE COMPLETED THE SAME DAY. THIS INCIDENT BECAME REPORTABLE TO THE CPUC BASED UPON ARRIVAL OF MAJOR MEDIA. THIS INCIDENT WAS ALSO REPORTED TO PHMSA WHEN THE FIRE INVESTIGATOR DETERMINED TOTAL FIRE DAMAGE COST WOULD EXCEED $50,000. FOR ANY FURTHER QUESTIONS, CONTACT JEFF KOSKIE AT 213-244-3283. | 75500 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
536 | 2007-09-02 | TX | natural disasters | UNKNOWN (JEFFERSON COUNTY) | TEXAS GAS SERVICE COMPANY | A HOUSE FIRE OCCURRED THAT WAS FUELED BY NATURAL GAS FROM UNDER THE HOUSE SLAB. AN ADDITION HAD BEEN ADDED ONTO THE HOME AND THE CONSTRUCTION WAS OVER THE NATURAL GAS SERVICE LINE. A LEAK OCCURRED UNDER THIS SLAB. THE ACTUAL PIECE OF THE SERVICE LINE THAT FAILED HAS NOT BEEN EXPOSED BECAUSE THE HOMEOWNER DOES NOT WANT THE SLAB DAMAGED. | 55000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
537 | 2007-08-22 | OH | sabotage | UNKNOWN (CUYAHOGA COUNTY COUNTY) | COLUMBIA GAS OF OHIO | THIRD PARTY CONTRACTOR, INSTALLING CABLE, BORED INTO COLUMBIA GAS OF OHIO INC'S 2" PLASTIC GAS MAIN CAUSING A RELEASE OF NATURAL GAS AND ULTIMATE EXPLOSION AT 20788/20806 SPEINGFIELD CIRCLE, STONGSVILLE, OHIO. THE GAS MAIN HAD BEEN CORRECTLY MARKED PER OUPS TICKET 0814-500-597-00 WITHIN THE REQUIRED TIME. | 505143 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
538 | 2007-08-29 | TX | sabotage | UNKNOWN (TAYLOR COUNTY) | ATMOS ENERGY CORP., MID-TEX DIVISION | AN EXCAVATOR STRUCK A SERVICE LINE, CAUSING A LEAK. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
539 | 2007-09-14 | UT | sabotage | UNKNOWN (TOOELE COUNTY) | QUESTAR GAS COMPANY | KRYPTONITE CONSTRUCTION WAS WORKING ON A SEWER LINE NEAR AN EXPOSED 2" PLASTIC DISTRIBUTION MAIN. A BACK-HOE OWNED AND OPERATED BY KRYPTONITE CONSTRUCTION FELL INTO THE TRENCH AND STRUCK THE EXPOSED GAS LINE. THE GAS LINE RUPTURED AND IGNITED. THE BACK-HOE OPERATOR WAS TAKEN TO THE HOSPITAL, TREATED AND RELEASED WITH MINOR BURNS TO BOTH ARMS; NOT REQUIRING INPATIENT HOSPITALIZATION. THE BACK-HOE WAS DAMAGED BEYOND REPAIR. TEMPORARY MARKINGS INCLUDED BOTH FLAGS AND PAINT. THERE WERE NO PERMANENT MARKINGS. | 70794 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
540 | 2007-09-20 | WI | other | UNKNOWN (FOND DU LAC COUNTY) | ALLIANT ENERGY - WISCONSIN POWER AND LIGHT COMPANY | CONTRACTOR CREW FOR THE OPERATOR WAS IN THE PROCESS OF RETIRING AN 8-INCH STEEL MAIN. THE SECOND CUT ON THE 8-INCH STEEL PIPE WAS BEING MADE WITH A BEVELING TORCH. DURING THE CUTTING PROCESS NATURAL GAS IGNITED. THE BEVELING TORCH IS THE KNOWN SOURCE OF IGNITION BUT THE SOURCE OF NATURAL GAS COULD NOT BE DETERMINED DURING THE INVESTIGATION. WITHIN THE SAME DITCH, NEARBY 60 PSIG MAOP PLASTIC MAIN AND SERVICE MELTED. THE ESCAPING NATURAL GAS FROM THE PLASTIC SYSTEM (55 PSIG OPERATING PRESSURE) CONTINUED TO FUEL THE FIRE UNTIL THE SHUT DOWN VALVE WAS CLOSED WITHIN 15 MINUTES OF IGNITION. NO EXISTING PRACTICES OR PROCEDURES WERE VIOLATED. THE TWO POSSIBLE SOURCES OF NATURAL GAS ARE 1) RESIDUAL GAS IN THE 8-INCH STEEL OR 2) HEAT OR SPARK FROM THE BEVELING TORCH MELTING THE PLASTIC AND THEREFORE A RELEASE OF GAS. THE FIRST CUT AROUND THE 8-INCH STEEL PIPE WAS COMPLETED WITH NO INCIDENT. AS A RESULT OF THE INVESTIGATION OF THIS INCIDENT, THE OPERATOR WILL MORE PRECISELY DEFINE PURGING REQUIREMENTS DURING RETIREMENT OF PIPELINE FACILITIES. IN ADDITION, PROTECTION OF PLASTIC PIPE WITH FIRE RESISTANT COVERINGS WILL BE ADDED TO THE CURRENT PRACTICES. | 80980 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
541 | 2007-09-17 | WI | leaks and spills | UNKNOWN (nan COUNTY) | WISCONSIN GAS COMPANY, D/B/A WE-ENERGIES | A GAS COMPANY CONTRACTOR CREW WAS IN THE PROCESS OF REPLACING TWO 8" VALVES IN AN ASSEMBLY TAPPED OFF A NEARBY 20" - 100# LINE (ONE 8" VALVE WHICH WAS IN-OPERABLE AND NECESSITATED THE WORK) WHICH WERE REQUIRED TO BE ABLE TO SHUT DOWN A DOWNSTREAM OPERATOR-MONITOR PRESSURE REDUCTION DISTRIBUTION FEED IN AN EMERGENCY. SEE ATTACHED EXHIBIT #3. THE CREW, AFTER WORKING SEVERAL DAYS, HAD EXCAVATED THE SITE, INSTALLED TWO 8" LINE STOPPER FITTINGS (BUT HAD NOT TAPPED THEM) WHEN THEY WERE CALLED OFF THE PROJECT LATE IN THE MORNING OF MONDAY SEPTEMBER 17, 2007 TO COMPLETE A WELDING ASSIGNMENT ELSEWHERE. THE CREW SECURED THE SITE, PLANNING TO RETURN THE NEXT DAY TO COMPLETE THE TAPPING, CUT OUT THE EXISTING 8" VALVES, INCLUDING AN INSULATED DRESSER STYLE 323, 8" COUPLING LOCATED IN THE ASSEMBLY, AND INSTALL TWO NEW 8" VALVES AND A NEW WELDED INSULATOR COUPLING. APPROXIMATELY 10 HOURS LATER AFTER LEAVING THE SITE, THE EXISTING 8" INSULATED STAB COUPLING PULLED OUT RELEASING GAS INTO THE OPEN DITCH AND ATMOSPHERE. AS PART OF THE POST INCIDENT REVIEW, THE FAILED MECHANICAL COUPLING WAS EXAMINED AND PHOTOGRAPHED. IT IS APPARENT FROM THE PHYSICAL EVIDENCE THAT THE COUPLING WAS IMPROPERLY INSTALLED AT THE TIME OF ITS INSTALLATION IN 1963. ONE END OF THE COUPLING WAS OVERSTABBED TO THE EXTENT THAT IT LEFT A MAXIMUM STAB OF LESS THAN 1 & 1/2 INCHES FOR THE OTHER PIPE END. PHOTOGRAPHS ATTACHED TO THIS REPORT LABELED EXHIBITS 1 &2. SHOW THE CUT OUT COMPRESSION COUPLING WITH ONE END OF THE 8" PIPE STILL IN PLACE AND OVER STABBED (NOTE LOCATION OF PIPE END) AT THE OTHER END. A CORRECTLY INSTALLED COUPLING WITH A 7" MIDDLE RING SHOULD HAVE A STAB DEPTH BETWEEN 3 AND 3.5 INCHES AT EACH END. DISCOLORATION OF THE INTERIOR OF THE FAILED END OF THE COUPLING INDICATES THAT THE PULLED OUT PIPE MAY HAVE BEEN STABBED TO LITTLE MORE THAN 1 INCH OF THE DEPTH AVAILABLE TO IT. ALTHOUGH THERE IS NO ONE EVENT THAT CAN BE PROVEN OR SHOWN TO HAVE CAUSED THE FINAL FAILURE OF THE IMPROPERLY INSTALLED COUPLING, IT IS PROBABLE THAT REMOVAL OF RESTRAINING SOIL FROM THE ASSEMBLY AND THE WORK OF INSTALLING OF THE 8" LINE STOPPER FITTINGS IN THE AREA OF THE COUPLING, CONTRIBUTED TO FORCES AND/OR RELEASE OF RESTRAINTS THAT RESULTED IN THE ULTIMATE FAILURE (PULL-OUT). AT THIS TIME, THE COMPANY HAS NO REASON TO BELIEVE THAT SIMILAR IMPROPER COUPLINGS HAVE BEEN INSTALLED IN ITS DISTRIBUTION SYSTEM AND THAT THE SITUATION ENCOUNTERED WAS AN ISOLATED CONDITION. THE COMPANY ALREADY ATTEMPTS TO REMOVE COMPRESSION COUPLINGS WHEN ENCOUNTERED AS WAS TO BE THE CASE IN THIS MAINTENANCE WORK. HOWEVER, TO ENHANCE SAFETY, IT IS IN THE PROCESS OF REVIEWING ITS CONSTRUCTION PRACTICES AND WILL BE INCORPORATING A REQUIREMENT TO STRAP COMPRESSION COUPLINGS AS SOON AS THEY ARE EXPOSED, EVEN IF THE WORK PROCEDURE ULTIMATELY REQUIRES THEIR REMOVAL. | 53240 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
542 | 2007-09-10 | MA | sabotage | UNKNOWN (PLYMOUTH COUNTY) | BAY STATE GAS COMPANY | COMPANY WAS WORKING ON A MAIN REPLACEMENT. THE INCIDENT LOCATION WAS SCHEDULED FOR A SERVICE REPLACEMENT. THE OLD SERVICE WAS SCHEDULED FOR REPLACEMENT ON THE DAY OF THE INCIDENT. UPDATED BY PHMSA PER OPERATOR ON 11/20/2015: EXCAVATION DAMAGE TO CUSTOMER SERVICE PIPING. WHILE INSTALLING NEW SERVICE LINE TO RESIDENCE @ 39 LIND ST., EXISTING SERVICE WAS STRUCK BY LARGE STONE DURING EXCAVATION CAUSING DAMAGE TO FITTING IN BASEMENT. GAS RELEASE IN BASEMENT IGNITED CAUSING EXPLOSION. | 2000859 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
543 | 2007-09-17 | TX | sabotage | UNKNOWN (MONTGOMERY COUNTY) | CENTERPOINT ENERGY ENTEX | 3RD PARTY DAMAGED A 2" PLASTIC MAIN WITH A BACKHOE WHILE BUILDING A NEW ADDITION. | 1452 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
544 | 2007-09-25 | WV | sabotage | UNKNOWN (LEWIS COUNTY) | HOPE GAS INC DBA DOMINION HOPE | ON 9/25/2007, JON J. SHIMKO WAS OPERATING A DITCH WITCH TO INSTALL A WATER SERVICE LINE AT THE PROPERTY OF JOEL BRUFFEY IN WALKERSVILLE, WEST VIRGINIA. MR. SHIMKO HIT A TWO INCH PLASTIC GAS LINE WITH 34 LBS. OF PRESSURE. THE GAS LEAK IGNITED, BURNING THE MACHINE OPERATOR. DOMINION HOPE DID NOT RECEIVE A ONE-CALL NOTICE FROM MR. SHIMKO, THE OPERATOR OF THE EQUIPMENT. HOWEVER, IN JULY 2007, DOMINION HOPE DID RESPONSE TO TWO ONE-CALL NOTICES (06/28/2007, 07/10/2007) FROM THE PROPERTY OWNER. DURING THESE EARLIER ONE-CALL RESPONSES, A SECTION OF THE GAS LINE WHICH RUNS ACROSS THE FRONT OF THE BRUFFEY PROPERTY WAS NOT LOCATED BY DOMINION EMPLOYEES. | 62181 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
545 | 2007-09-28 | IL | technical failure | UNKNOWN (COOK COUNTY) | PEOPLES GAS LIGHT AND COKE COMPANY | AT 4:15 P.M. ON SEPTEMBER 28, 2007, THE PEOPLES GAS LIGHT AND COKE COMPANY (PEOPLES GAS) WAS NOTIFIED BY THE CHICAGO FIRE DEPARTMENT OF AN EXPLOSION AT 410 E. 107TH STREET CHICAGO, IL. A PEOPLES GAS EMPLOYEE WAS IMMEDIATELY DISPATCHED TO THE SCENE. WHILE THE INCIDENT IS STILL UNDER INVESTIGATION, IT APPEARS THAT THERE WAS A LOW LEVEL EXPLOSION AND THAT THERE WAS A GAS LEAK INSIDE THE CUSTOMER'S PREMISE, FROM CUSTOMER EQUIPMENT. *PLEASE NOTE THE UNITS FOR "6" IN PART A8A AND THE "12" IN PART A8B ARE INCHES OF WATER COLUMN (I.E., 0.21 PSIG, AND 0.43 PSIG RESPECTIVELY). [THIS NOTE ADDED IN SUPPLEMENTAL REPORT SUBMITTED 12/03/07] THE TECHNICIAN FAILED TO FOLLOW PROCEDURES AND DID NOT DETECT AN OPEN - ENDED APPLIANCE CONNECTION DURING GAS SERVICE TURN ON. (FINAL REPORT SUBMITTED 10/31/2011) | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
546 | 2007-09-17 | GA | sabotage | UNKNOWN (FORSYTH COUNTY) | ATLANTA GAS LIGHT | A 3RD-PARTY EXCAVATOR GRADING FOR ROAD WIDENING HIT A CORRECLT-LOCATED 2" LATERAL OFF OF A 12" MAIN CAUSING PARTIAL SEPARATION BETWEEN THE TWO. STATE HIGHWAY 9 WAS SHUT DOWN AND A NEARBY ELEMENTARY SCHOOL WAS EVACUATED BY EMERGENCY OFFICIALS AS A PRECAUTION. | 113739 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
547 | 2007-10-07 | NE | other | UNKNOWN (nan COUNTY) | SOURCEGAS LLC | VEHICLE DRIVEN BY ANTHONY MATTISON OF 518 N. CLAY AVE CLAY CENTER NE,68933 DRIVERS LICENSE # H 13076143 DATE OF BIRTH 12/30/88 WAS DRIVING 1983 GMC S1500 JIMMY LEFT ROADWAY CROSSED DITCH TAKING OUT FENCE AND RUNNING INTO AND DESTROYING METER GUARD AND 2 METERS THAT GUARD WAS PROTECTING. VEHICLE STOPPED RESTING ON TOP OF BARRICADE AND METER LOOP. GAS WAS ESCAPING FROM PIPE AT 90LBS OF PRESSURE. BRETT ARCHER WAS A PASSENGER IN THE VEHICLE. BOTH DRIVER AND PASSENGER WERE TAKEN TO HOSPITAL. DRIVER RECEIVED INPATIENT HOSPITALIZATION. | 4609 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
548 | 2007-09-30 | IL | other | UNKNOWN (LA SALLE COUNTY) | NICOR GAS | STRUCTURE FIRE DUE TO ARSON SPREAD THROUGH THE HOUSE AND MELTED THE METER SET, THUS CAUSING A RELEASE OF NATURAL GAS. | 50600 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
549 | 2007-09-15 | MS | sabotage | UNKNOWN (nan COUNTY) | CENTERPOINT ENERGY | ON SEPTEMBER 15, 2007 AT APPROX. 8:30 A.M., CNP RECEIVED A CALLFROM THE PHILADELPHIA, MS POLICE DEPT REPORTING A NATURAL GAS LEAK AT 566 HOLLAND AVE. A CENTERPOINT ENERGY EMPLOYEE ARRIVED ON SITE AND STARTED SOME ROUTINE CHECKS IN THE AREA. WHILE ATTEMPTING TO LOCATE THE MIGRATION OF THE LEAK A BUILDING EXPLODED (912 HOLLAND AVE.) THE EXPLOSION INJURED NINE PEOPLE, THEY ALL WERE TREATED AND RELEASED FROM THE HOSPITAL THE SAME DAY OF THE EXPLOSION. ACE UTILITIES BORING AND TRENCHING LLC WAS INSTALLING A COMMUNICATION LINE FOR DEVINEY CONSTRUCTION, WHEN THEY BORED INTO OUR (CENTERPOINT ENERGY) 2 INCH STEEL MAIN LOCATED NEAR THE GAS LINE. GAS MIGRATED FROM THE DAMAGED GAS LINE INTO THE DAMAGED SEWER LINE AND EVENTUALLY INTO THE BUILDING THAT WAS AFFECTED. CENTERPOINT RETAINED THE SERVICES OF SAMMY RUSSO OF APR CONSULTANTS TO INVESTIGATE THE INCIDENT. MR. RUSSO IS AN EXPERT IN NATURAL GAS OPERATION AND FACILITIES AND IN CONDUCTING FIRE AND EXPLOSION CAUSE AND ORIGIN INVESTIGATIONS. AS A RESULT OF HIS INVESTIGATION, MR. RUSSO CONCLUDED: (I) THE EXPLOSION AT THE RILEY MEDICAL COMPLEX OCCURRED AS A RESULT OF THE ESCAPE OF NATURAL GAS FROM CENTERPOINT’S PUNCTURED TWO-INCH PIPELINE INTO THE CITY OF PHILADELPHIA’S PUNCTURED SEWER LINE, WHICH IN TURN ACCUMULATED IN AN UNOCCUPIED DOCTOR’S OFFICE WHERE IT ULTIMATELY WAS IGNITED AND EXPLODED. (II) THE EXPLOSION WOULD NOT HAVE OCCURRED HAD ACE UTILITY BORING AND TRENCHING NOT PUNCTURED BOTH CENTERPOINT’S TWO-INCH NATURAL GAS PIPELINE AND THE CITY OF PHILADELPHIA’S UNMARKED SEWER LINE. A BLOCKED SEWER GAS VENT IN ONE OF THE DOCTOR’S OFFICES ALSO WAS A CONTRIBUTING FACTOR IN CAUSING THE EXPLOSION. (III) CENTERPOINT’S ACTIONS IN RESPONDING TO THE REPORT OF THE PIPELINE PUNCTURE WERE CONSISTENT WITH COMPANY POLICIES AND PROCEDURES, RULES AND REGULATIONS OF GOVERNING REGULATORY AUTHORITIES, AND INDUSTRY NORMS AND BEST PRACTICES. (IV) A SUFFICIENT VOLUME OF NATURAL GAS TO HAVE CAUSED THE EXPLOSION ACCUMULATED IN THE BUILDING IN A SHORT AMOUNT OF TIME AFTER THE PIPELINE WAS PUNCTURED AND CERTAINLY BEFORE CENTERPOINT COULD HAVE TAKEN ANY ACTIONS TO HAVE PREVENTED AN EXPLOSIVE VOLUME FROM ACCUMULATING. (V) NOTHING CENTERPOINT DID OR FAILED TO DO WOULD HAVE PREVENTED THE EXPLOSION FROM OCCURRING. (VI) CENTERPOINT’S PERSONNEL WERE NOT AWARE OF ANY FACTS THAT WOULD HAVE REQUIRED THEM TO EVACUATE THE OCCUPANTS OF THE NEW DIVA BEAUTY SALON. (VII) THE RESPONSE TIME BY CENTERPOINT’S CONSTRUCTION CREW WAS REASONABLE UNDER THE CIRCUMSTANCES, AND THE EXPLOSION COULD NOT HAVE BEEN AVOIDED EVEN IF THE CREW HAD ARRIVED EARLIER. | 2388 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
550 | 2007-10-08 | CO | sabotage | UNKNOWN (JEFFERSON COUNTY) | PUBLIC SERVICE CO. OF COLORADO | GREEN TREE LANDSCAPING WAS REMOVING TREE ROOTS WITH A BACKHOE, AND ENDED UP SEVERING THE SERVICE LINE FROM THE METER. THE CONTRACTOR PLACED HIS COAT OVER THE BLOWING SERVICE, AND A FEW MOMENTS LATER THE GAS IGNITED IN THE HOUSE. LOCATES WERE NOT CALLED IN BY THE CONTRACTOR BEFORE CONDUCTING THE WORK. PREVIOUS LOCATES WERE CALLED IN BY THE HOME OWNER ON MAY 3, 2007 | 196150 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
551 | 2007-10-03 | CA | natural disasters | UNKNOWN (SAN DIEGO COUNTY) | SAN DIEGO GAS AND ELECTRIC | ON OCTOBER 3, 2007, THE LOCATIONS OF MAIN, SERVICES, AND METER SET ASSEMBLIES WERE COMPROMISED WHEN A LANDSLIDE OCCURRED IN THE COMMUNITY OF LA JOLLA. A TOTAL OF 7 HOMES WERE DETERMINED TO BE UNINHABITABLE, AND A 390¿ SECTION OF 3¿ PE MAIN ABANDONED. SHORTLY AFTER THE LANDSLIDE, SDG&E CREWS ABANDONED THE INVOLVED MAIN AND SERVICES, PENDING STREET REPAIR AND RESTORATION OF HOMES. THE ONLY ESCAPING GAS DURING THIS INCIDENT CAME FROM A ½¿ PE SERVICE BELONGING TO ONE OF THE HOMES THAT SLIPPED DOWN THE HILL. NO FIRE OR INJURIES RESULTED FROM THE ESCAPING GAS. THIS INCIDENT BECAME REPORTABLE TO THE CALIFORNIA PUBLIC UTILITIES COMMISSION WHEN MAJOR MEDIA COVERAGE RESULTED FROM COVERAGE OF THE LANDSLIDE. ON OCTOBER 12, 2007, THE INCIDENT MET DOT CRITERIA WHEN IT WAS DETERMINED THAT TOTAL SERVICE AND MAIN RESTORATION COST, IF ALL CUSTOMERS REBUILD AND RETURN TO THE SYSTEM, COULD EXCEED $50,000. FOR ANY FURTHER QUESTIONS, CONTACT JEFF KOSKIE AT 213-244-3283. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
552 | 2007-10-09 | UT | sabotage | UNKNOWN (SALT LAKE COUNTY) | QUESTAR GAS COMPANY | QUESTAR GAS RESPONDED TO A CUSTOMER GAS LEAK CALL. A QUESTAR GAS EMPLOYEE BARRED THE LINE AS PART OF QUESTAR'S STANDARD LEAK LOCATING PROCEDURE. IN BARRING THE LINE, THE BAR WAS PUNCHED THROUGH THE PLASTIC LINE MAKING A 3/8" HOLE AND RESULTED IN A RELEASE OF GAS. A HOLE WAS DUG AWAY FROM THE INITIAL PUNCTURE EXPOSING THE PIPE SO THAT QUESTAR GAS COULD SQUEEZE THE LINE AND STOP THE FLOW OF GAS. PRIOR TO SQUEEZING THE LINE, THE ESCAPING GAS FROM THE PUNCTURE IGNITED, CAUSING A 12 UNIT APARTMENT BUILDING TO CATCH FIRE. THE HEAT OF THE FIRE CAUSED THE EXPOSED PIPE IN THE SQUEEZE HOLE TO MELT CONTRIBUTING TO A SECONDARY RELEASE OF GAS. PROPERTY DAMAGES ARE ONLY ESTIMATED. | 503550 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
553 | 2007-10-12 | CA | other | UNKNOWN (ORANGE COUNTY) | SOUTHERN CALIFORNIA GAS COMPANY | ON OCTOBER 12, 2007, EMPLOYEE WAS ATTEMPTING TO REPLACE A SERVICE STOPCOCK DUE TO BROKEN OPERATING TANG. WHILE ATTEMPTING TO PERFORM REPLACEMENT, CORE SEPARATED FROM STOPCOCK, RELEASING GAS TO ATMOSPHERE WHICH WAS LIKELY IGNITED BY A NEARBY WATER HEATER. RESULTING FIRE DAMAGED HOME AND INJURED EMPLOYEE. EMPLOYEE WAS TRANSPORTED TO HOSPITAL AND ADMITTED FOR TREATMENT. EMPLOYEE IS CURRENTLY OFF WORK. FURTHER INVESTIGATION WILL BE PERFORMED UPON HIS RETURN. GAS WAS PUT UNDER CONTROL, RESULTING IN ONE CUSTOMER BEING OUT OF GAS. SERVICE WILL NOT BE RESTORED UNTIL PROPERTY IS REPAIRED. INCIDENT BECAME REPORTABLE AT 16:00 WHEN DAMAGE ESTIMATE WAS DETERMINED TO EXCEED $50,000 AND EMPLOYEE¿S DOCTOR INDICATED HE WOULD BE ADMITTED INTO THE HOSPITAL. | 100500 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
554 | 2007-10-10 | NC | sabotage | UNKNOWN (WAKE COUNTY) | PUBLIC SERVICE CO OF NORTH CAROLINA | EXCAVATION STARTED AT THIS SITE PRIOR TO THE LOCATE REQUEST BECOMING VALID WHICH REQUIRE A MINIMUM 48 HOUR NOTIFICATION. HOWEVER, PRIOR LOCATE MARKS AT THIS SITE WERE STILL ACCURATE AND VISIBLE AT THE TIME THIS EXCAVATION AND DAMAGE WAS DONE. | 285955 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
555 | 2007-10-14 | MI | other | UNKNOWN (KENT COUNTY) | MICHIGAN CONSOLIDATED GAS CO (MICHCON) | ON SUNDAY, OCTOBER 14, 2007 AT APPROXIMATELY 1:49 AM A NORTHBOUND VEHICLE FAILED TO NEGOTIATE A CURVE ON PETTIS AVENUE, LEFT THE ROADWAY, AND STRUCK A HOUSE AT 600 PETTIS AVENUE. THE DRIVER FLED THE SCENE IN THE VEHICLE. AT APPROXIMATELY 1:58 AM MICHCON RECEIVED A REPORT OF A STRUCTURE FIRE AT 600 PETTIS AVENUE. THE LOCAL FIRE DEPARTMENT REQUESTED THE GAS TO BE SHUT OFF TO ENABLE FIREFIGHTING OPERATIONS. GAS SERVICE WAS TERMINATED AT APPROXIMATELY 4:10 AM BY A MICHCON CREW EXCAVATING THE 5/8" POLYTHYLENE SERVICE LINE NEAR THE PROPERTY LINE, PINCHING THE PLASTIC TUBING, AND CUTTING AND CAPPING THE SERVICE LONE. THE OUTSIDE METER ASSEMBLY AND THE SERVICE LINE RISER WAS DESTROYED IN THE FIRE, AND WERE NOT RECOVERED. SUBSEQUENT INVESTIGATION REVEALED THAT THE CAUSE OF THE STRUCTURE FIRE WAS LIKELY THE IMPACT OF THE VEHICLE ON THE ABOVE GRADE SERVICE LINE RISER AND/OR OUTSIDE METER ASSEMBLY, APPARENTLY BREAKING THE METTER AND OTHER COMPONENTS, POSSIBLY INCLUDING THE CUSTOMER'S FUEL LINE, AND CAUSING A GAS LEAK. NATURAL GAS LEAKING FROM THE METER ASSEMBLY AND/OR CUSTOMER FUEL LINE WAS IGNNITED BY AN UNKNOWN SOURCE AND WAS FOUND BURNING AT THE SOUTH WALL OF THE HOUSE. THE OCCUPANTS OF THE HOUSE ESCAPED WITHOUT INJURY. THE TWO-STORY HOME AT 600 PETTIS AVENUE N.E. SUSTAINED MAJOR FIRE DAMAGE TO THE STRUCTURE AND CONTENTS. | 101482 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
556 | 2007-10-05 | FL | sabotage | UNKNOWN (BROWARD COUNTY) | FLORIDA CITY GAS | DUE TO A BROKEN TRACER WIRE, THE LOCATING EQUIPMENT SIGNAL BLED FROM THE GAS MAIN ONTO ANOTHER FACILITY PARALLELING THE GAS MAIN. THE GAS MAIN WAS MARKED INCORRECTLY AND WAS SUBSEQUENTLY DAMAGED BY AN EXCAVATOR. GAS SERVICE TO APPROXIMATELY 1625 CUSTOMERS WAS LOST. | 87578 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
557 | 2007-10-01 | ME | sabotage | UNKNOWN (CUMBERLAND COUNTY) | NORTHERN UTILITIES INC (ME) | ON 10/01/2007, AT APPROXIMATELY 8:25AM, NORTHERN UTILITIES RECEIVED A CALL REGARDING A LEAK DUE TO A THIRD PARTY DAMAGE ON A SERVICE LINE T0 #47 D STREET, SOUTH PORTLAND, MAINE. AT APPROXIMATELY 8:25AM, NORTHERN UTILITIES' PERSONNEL WERE DISPATCHED TO THE SITE. UPON ARRIVING AT THE SITE, IT WAS OBSERVED THAT A SERVICE LINE TO #47 D STREET WAS SEVERED BY A CONTRACTOR DURING THE INSTALLATION OF A WATER LINE. THE CONTRACTOR ATTEMPTED TO PLUG THE SEVERED SERVICE LINE. NORTHERN UTILITIES' PERSONNEL BEGAN CONDUCTING LEAK SURVEYS OF THE AREA. AT APPROXIMATELY 9:40AM, NORTHERN UTILITIES' PERSONNEL WERE IN THE PROCESS OF CLOSING THE CURB VALVE TO #47 D STREET WHEN THE NEARBY STRUCTURE AT #43 D STREET EXPLODED. THE SITE OF THE EXPLOSION WAS AN UNOCCUPIED STRUCTURE THAT WAS BEING RENOVATED. THE CAUSE OF THE EXPLOSION IS STILL UNDER INVESTIGATION. | 200000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
558 | 2007-11-11 | AK | other | UNKNOWN (MATANUSKA SUSITNA BOROUGH COUNTY) | ENSTAR NATURAL GAS CO |  | 50550 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
559 | 2007-10-22 | CA | other | UNKNOWN (SAN DIEGO COUNTY) | SAN DIEGO GAS & ELECTRIC CO | ON OCTOBER 21, 2007 NUMEROUS FIRES BROKE OUT ACROSS SAN DIEGO GAS AND ELECTRIC¿S (SDG&E) SERVICE TERRITORY, DAMAGING SERVICES, RISERS AND METER SET ASSEMBLIES. DAMAGE TO SDG&E GAS FACILITIES WAS LIMITED TO THESE COMPONENTS AND ONE SMALL ONE-WAY FEED PE DISTRIBUTION MAIN THAT SERVED A SINGLE RESIDENTIAL CUSTOMER. WHILE GAS ESCAPING FROM THESE FACILITIES DID IGNITE ON OCCASION, IT WAS NOT RESPONSIBLE FOR CAUSING ANY ADDITIONAL DAMAGE OR INJURIES. ALL REPAIRS OF GAS FACILITIES HAVE BEEN COMPLETED. MANY OF THE INVOLVED FACILITIES WERE ATTACHED TO BUILDINGS THAT HAVE BEEN DESTROYED, SO NO RESTORATION IS NECESSARY AT THIS TIME. THE ESTIMATE OF COSTS ASSOCIATED WITH THESE DAMAGES ($300,000) IS FOR RESTORATION OF ALL DAMAGED GAS FACILITIES. IT DOES NOT INCLUDE COSTS ASSOCIATED WITH EMERGENCY RESPONSE, STANDBY, AND GOVERNMENTAL AGENCY SUPPORT. THIS INCIDENT WAS REPORTABLE TO PHMSA DUE TO FACILITY DAMAGE EXCEEDING $50,000, AS WELL AS SIGNIFICANT NATIONAL MEDIA COVERAGE. FOR ANY FURTHER QUESTIONS, CONTACT JEFF KOSKIE AT 213-244-3283. | 300000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
560 | 2007-10-21 | CA | other | UNKNOWN (LOS ANGELES COUNTY) | SOUTHERN CALIFORNIA GAS CO | ON OCTOBER 21, 2007 NUMEROUS FIRES BROKE OUT ACROSS SOUTHERN CALIFORNIA GAS COMPANY (SOCALGAS) SERVICE TERRITORY, DAMAGING SERVICES, RISERS AND METER SET ASSEMBLIES. DAMAGE TO SOCALGAS GAS FACILITIES WAS LIMITED TO THESE COMPONENTS. NO DAMAGE TO DISTRIBUTION MAINS OR TRANSMISSION LINES OCCURRED. WHILE GAS ESCAPING FROM THESE FACILITIES DID IGNITE ON OCCASION, IT WAS NOT RESPONSIBLE FOR CAUSING ANY ADDITIONAL DAMAGE OR INJURIES. ALL REPAIRS OF GAS FACILITIES HAVE BEEN COMPLETED. MANY OF THE INVOLVED FACILITIES WERE ATTACHED TO BUILDINGS THAT HAVE BEEN DESTROYED, SO NO RESTORATION IS NECESSARY AT THIS TIME. THE ESTIMATE OF COSTS ASSOCIATED WITH THESE DAMAGES ($250,000) IS FOR RESTORATION OF ALL DAMAGED GAS FACILITIES. IT DOES NOT INCLUDE COSTS ASSOCIATED WITH EMERGENCY RESPONSE, STANDBY, AND GOVERNMENTAL AGENCY SUPPORT. THIS INCIDENT WAS REPORTABLE TO PHMSA DUE TO FACILITY DAMAGE EXCEEDING $50,000, AS WELL AS SIGNIFICANT NATIONAL MEDIA COVERAGE. FOR ANY FURTHER QUESTIONS, CONTACT JEFF KOSKIE AT 213-244-3283. | 250000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
561 | 2007-10-27 | IL | other | UNKNOWN (KENDALL COUNTY) | NORTHERN ILLINOIS GAS CO | STRUCTURE FIRE OF UNKNOWN CAUSE DAMAGED THE METER SET THUS CAUSING A RELEASE OF NATURAL GAS INTO THE ATMOSPHERE. | 150600 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
562 | 2007-11-03 | LA | other | UNKNOWN (IBERVILLE COUNTY) | IBERVILLE PARISH NATURAL GAS SYSTEM | RESIDENT WAS CUTTING THE REMAINS OF A TRAILER FLOOR WITH A WELDING TORCH AND WAS NOT AWARE THAT A GAS SERVICE LINE WAS BENEATH THE PILE OF MATERIALS. THE GAS SERVICE LINE WAS A 0.75 POLYETHYLENE PIPE WITH AND ANODELESS RISER, VALVE AND PLUG. WHILE THE RESIDENT WAS ATTEMPTING TO CUT THE REMAINS OF THE TRAILER, THE VALVE WAS BROKEN OFF OF THE RISER AND THE GAS LINE IGNITED, APPARENTLY MELTING THE POLYETHYLENE INSIDE OF THE ANODELESS RISER. UPON ARRIVAL OF FIRE AND UTILITY DEPARTMENT PERSONNEL, THE FIRE WAS DISTINGUISHED AND A TEMPORARY PLUG WAS INSTALLED TO STOP THE FLOW OF GAS. THE HEAT ALSO CAUSED DAMAGE TO THE CONNECTION OF THE ANODELESS RISER AT THE POLYETHYLENE PIPE, CAUSING A MINOR UNDERGROUND LEAK. PERSONNEL SQUEEZED OFF THE SERVICE LINE NEAR THE ROAD, REMOVED ALL DAMAGED MATERIALS AND PERMANENTLY ABONDONED THE LINE TO PREVENT FUTURE INCIDENTS | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
563 | 2007-11-14 | TX | sabotage | UNKNOWN (HARRIS COUNTY) | ENTEX, A NORAM ENERGY COMPANY (FORM. DIV OF ARKLA | 3RD PARTY DAMAGED A 4" POLY MAIN WHILE DIRECTIONAL BORING INSTALLING WATER LINES FOR CITY OF HUMBLE. | 5493 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
564 | 2007-11-08 | DC | sabotage | UNKNOWN (DC COUNTY) | WASHINGTON GAS LIGHT CO | FLIPPO CONSTRUCTION COMPANY, INC. DAMAGED A FOUR-INCH PLASTIC GAS SERVICE WITH MINI-EXCAVATOR WHILE EXCAVATING TO INSTALL A 12-WAY ELECTRIC DUCT BANK. | 5500 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
565 | 2007-11-20 | CA | sabotage | UNKNOWN (FRESNO COUNTY) | PACIFIC GAS & ELECTRIC CO | PG&E ELECTRIC DEPARTMENT WAS HAND-DIGGING TO FIND AN ELECTRIC FAULT ON A RESIDENTIAL SERVICE IN A JOINT TRENCH AND HIT A 1/2-INCH PLASTIC GAS SERVICE. A GAS CREW WAS DISPATCHED AND ATTEMPTED TO USE A BATTERY-OPERATED RECIPROCATING SAW TO CLEAR TREE ROOTS IN A NEW ADJACENT EXCAVATION DUG TO SQUEEZE OFF THE GAS SERVICE. GAS MIGRATED TO THIS NEW EXCAVATION AND WAS IGNITED BY THE SAW, CAUSING BURNS TO THE EMPLOYEE'S FACE. THE BURNS WERE DETERMINED TO BE VERY MINOR BUT THE EMPLOYEE'S HEART BEAT REMAINED ACCELERATED, SO HE WAS ADMITTED INTO THE HOSPITAL AT 2030. ALTHOUGH THE EMPLOYEE'S HEART CONDITION WAS CONSIDERED TO BE UNRELATED TO THE INCIDENT , A DECISION WAS MADE TO CONSIDER THIS A REPORTABLE INCIDENT ON THE FOLLOWING MORNING. | 1000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
566 | 2007-11-29 | IL | other | UNKNOWN (LAKE COUNTY) | NORTHERN ILLINOIS GAS CO | HOMEOWNER BACKED A TRAILER AND STRUCK THE METER SET, CAUSING A RELEASE OF GAS AND IGNITION. NOTE: THIS INCIDENT WAS OGINALLY REPORTED AS "FIRE FIRST". FURTHER INVESTIGATION REVEALED ACTUAL CAUSE OF THE FIRE WAS OTHER OUTSIDE FORCE DAMAGE. | 50600 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
567 | 2007-11-25 | VA | other | UNKNOWN (FAIRFAX COUNTY) | WASHINGTON GAS LIGHT CO | WASHINGTON GAS RESPONDED TO A HOUSE FIRE AT 5103 & 5105 MYRTLE LEAF DRIVE IN FAIRFAX COUNTY VIRGINIA AT THE REQUEST OF THE FAIRFAX COUNTY FIRE DEPARTMENT. UPON ARRIVAL OF THE EMERGENCY RESPONDER, GAS WAS FOUND OFF TO BOTH ADDRESSES AND THE FIRE WAS EXTINGUISHED. THE METER AND REGULATOR FEEDING 5103 WERE COMPROMISED FROM THE HEAT OF THE FIRE AT 5105. THE PRELIMINARY FIRE INVESTIGATION INDICATED THAT A VEHICLE IN THE GARAGE OF 5105 STARTED THE FIRE AND THEN SPREAD TO 5103. A PRESSURE TEST WAS CONDUCTED ON THE SERVICE FEEDING 5103 AND IT HELD. THE SERVICE WAS LEFT CAPPED OFF IN THE YARD. | 501100 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
568 | 2007-11-09 | TX | natural disasters | UNKNOWN (MCLENNAN COUNTY) | ATMOS ENERGY CORP., MID-TEX DIVISION | WHILE PERFORMING A LEAK SURVEY, A LEAK WAS DETECTED. WHILE PERFORMING THE LEAK INVESTIGATION, THE DETERMINATION WAS MADE TO EVACUATE A BUILDING. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
569 | 2007-12-02 | TX | other | UNKNOWN (EL PASO COUNTY) | TEXAS GAS SERVICE COMPANY | 1" STEEL RISER TO METER SETTING WAS DAMAGED AFTER A TWO CAR COLLISION SENT ONE OF THE VEHICLES INTO THE METER SETTING. REPAIRS WERE MADE BY REPLACING THE GAS METER. THERE WERE TWO FATALITIES AND ONE INJURY DUE TO THE NATURE OF THE COLLISION. | 157 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
570 | 2007-11-21 | NY | leaks and spills | UNKNOWN (QUEENS COUNTY) | CONSOLIDATED EDISON CO OF NEW YORK | ON NOVEMBER 21, 2007, AT 3:33 P.M., THE FIRE DEPARTMENT OF NEW YORK (FDNY) CONTACTED CON EDISON'S GAS EMERGENCY RESPONSE CENTER (GERC) TO REPORT AN ODOR OF GAS IN FRONT OF 48-15 41ST STREET IN SUNNYSIDE, QUEENS. AT 4:04 P.M., A CON EDISON CREW, CONSISTING OF TWO GAS MECHANICS ARRIVED AT THAT LOCATION AND INITIATED EFFORTS TO DETERMINE THE SOURCE OF THE ODOR. UPON THEIR ARRIVAL, THE CON EDISON CREW WAS MET BY REPRESENTATIVES OF THE FDNY WHO REPORTED THAT THEY HAD CHECKED HOUSES ON THE BLOCK FOR GAS AND OBTAINED NO GAS READINGS IN THE ATMOSPHERE OF THE HOUSES EXCEPT FOR INSIDE THE BUILDING AT 48-15 WHICH THE FDNY VENTED. CON EDISON'S "LEAD MECHANIC" ENTERED THE BUILDING AT 48-15 WITH A MEMBER OF THE FDNY AND, UPON INVESTIGATION, CONFIRMED THAT THERE NO LONGER WERE GAS READINGS IN THE ATMOSPHERE INSIDE THE BUILDING. CON EDISON'S LEAD MECHANIC THEN BEGAN A LEAK INVESTIGATION OUTSIDE ON 41ST STREET. OF THE SEVEN SUBSURFACE STRUCTURES TESTED OUTSIDE, FIVE WERE FOUND TO HAVE GAS-IN-AIR READINGS OF 20% TO 90%. CON EDISON'S CREW BEGAN REMOVING THE MANHOLE COVERS IN ORDER TO VENT THE SUBSURFACE STRUCTURES; HOWEVER, THEY WERE UNABLE TO REMOVE THE COVER ON THE MANHOLE IN FRONT OF THE BUILDING AT 48-19 BECAUSE A CAR WAS PARKED ON TOP OF IT. AT 4:10 P.M., THE CON EDISON CREW CONTACTED THE GERC TO REQUEST ASSISTANCE IN MOVING THAT CAR. CON EDISON'S GERC CONTACTED THE 911 OPERATOR WHO DISPATCHED BOTH THE FDNY AND NYPD TO THE 41ST STREET LOCATION TO ASSIST WITH THE CAR REMOVAL. CON EDISON'S CREW CONTINUED WITH ITS LEAK INVESTIGATION AND REMOVAL OF MANHOLE COVERS UNTIL A RESIDENT OF THE BUILDING LOCATED AT 48-20 CAME OUT AND TOLD THEM THAT SHE SMELLED GAS IN HER APARTMENT. CON EDISON'S CREW PERFORMED AN INVESTIGATION INSIDE THE BUILDING AT HER ADDRESS AND FOUND 0.5% GAS IN THE ATMOSPHERE OF THE HALLWAY. SHORTLY AFTER THEY COMPLETED VENTING HER BUILDING AT 48-20, THE CON EDISON CREW CALLED THE GERC TO REPORT AN EXPLOSION WITH FIRE AT 48-19 41ST STREET. THE TIME OF THE EXPLOSION WAS 4:35P.M. AT THE SAME TIME, 4:35 P.M., THE FDNY ARRIVED AT THE 41ST STREET LOCATION AND EVACUATED THE OCCUPANTS OF 14 BUILDINGS. A TEMPORARY SHELTER FOR THE EVACUEES WAS SET UP IN PUBLIC SCHOOL 199 LOCATED AT 39-20 48TH AVENUE. A WOMAN, WHO RESIDED AT 49-19 41ST STREET, WAS SERIOUSLY INJURED IN THE EXPLOSION AND WAS TAKEN TO THE CORNELL BURN CENTER. THE FDNY EXTINGUISHED THE FIRE AT 48-19 41ST STREET AT 5:15 P.M. ADDITIONAL CON EDISON CREWS ARRIVED AT THE 41ST STREET INCIDENT LOCATION; THEY SHUT-OFF GAS SERVICE TO 17 BUILDINGS AND PREPARED FIRE BANKS TO ISOLATE THE GAS IN THE AREA OF THE INCIDENT. AT THE SAME TIME THE CON EDISON CREWS EXCAVATED OVER THE SIX-INCH CAST IRON MAIN IN FRONT OF 48-19 41ST STREET AND DETERMINED THAT THE GAS MAIN WAS CRACKED AND LEAKING. THE CREWS INSTALLED A REPAIR CLAMP AT 9:29 P.M. AND SECURED THE GAS LEAK. THE CON EDISON CREWS THEN CHECKED THE BUILDINGS WITH THE FDNY AND, UPON FINDING NO FURTHER INDICATIONS OF GAS, ENDED THE EVACUATION AT 11:15 P.M. THE CON EDISON CREWS REMAINED AT 41ST STREET TO RESTORE GAS TO THE 17 SHUT-OFF BUILDINGS AND MONITOR THE AREA UNTIL THE FOLLOWING DAY. THE SIX-INCH CAST IRON GAS MAIN AT 41ST STREET WAS INSTALLED IN 1927. IN JANUARY 2007, CON EDISON COMPLETED ITS ANNUAL LEAK SURVEY OF THAT GAS MAIN, AND NO LEAKS WERE DETECTED AT THAT TIME. CON EDISON REVIEWED ITS RECORDS OVER THE PAST THREE YEARS AND FOUND THAT THERE WERE NO LEAKS REPORTED OR DETECTED ON THE GAS MAIN OR ANY OF THE GAS SERVICES TO THE 14 BUILDINGS THAT WERE EVACUATED AT THE ABOVE-DESCRIBED 41ST STREET LOCATION. CON EDISON ALSO REVIEWED ITS RECORDS OF CUSTOMER CALLS TO THE COMPANY FOR THE SEVEN-DAY PERIOD PRIOR TO THIS INCIDENT AND FOUND THAT THERE WERE NO CUSTOMER COMPLAINTS OF GAS ODORS OR GAS- RELATED PROBLEMS IN THIS AREA. THE CRACKED SECTION OF GAS MAIN IN FRONT OF 48-19 41ST STREET WAS REMOVED ON NOVEMBER 30, 2007 AND SENT TO A METALLURGICAL LAB FOR ANALYSIS. | 300100 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
571 | 2007-09-18 | CA | other | UNKNOWN (ORANGE COUNTY) | SOUTHERN CALIFORNIA GAS CO | ON SEPTEMBER 18, 2007, A LEAK WAS DISCOVERED ON A 10¿ HIGH PRESSURE DISTRIBUTION MAIN. LEAK WAS DISCOVERED BY CITY WATER CREW PERFORMING EMERGENCY WATER LEAK REPAIR. AFTER EXCAVATING, IT WAS DETERMINED THAT LEAK ON GAS MAIN WAS LIKELY THE RESULT OF HIGH PRESSURE WATER, DIRT AND MUD SCOURING THE MAIN WALL TO THE POINT OF PENETRATION. NO FIRE RESULTED FROM THE ESCAPING GAS. THE MAIN WAS REPAIRED WITH NO LOSS OF SERVICE TO CUSTOMERS. THIS INCIDENT BECAME REPORTABLE TO THE CPUC WHEN MAJOR MEDIA ARRIVED. IT WAS INITIALLY REPORTED TO DOT/PHMSA AS WELL DUE TO POTENTIAL THAT REPAIRS COULD EXCEED $50,000. WHEN ACTUAL REPAIR COSTS CAME IN UNDER THIS AMOUNT, A REQUEST TO RESCIND WAS FILED WITH DOT/PHMSA. ON DECEMBER 12, 2007, IT WAS DISCOVERED THAT WATER WHICH ENTERED THE MAIN HAD COLLECTED IN AN AREA IMPACTING A MAJOR CUSTOMER AND REQUIRING INSTALLATION OF A FILTERING SYSTEM, BOOSTING THE PRICE OF POTENTIAL REPAIRS OVER $50,000. IT WAS THEN AGAIN FILED WITH DOT/PHMSA. IN ADDITION, SUBSEQUENT TO THIS FILING, IT HAS BEEN DETERMINED THAT THE LINE MAY NEED TO BE PIGGED, WHICH WOULD FURTHER INCREASE COSTS. | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
572 | 2007-10-21 | CT | other | UNKNOWN (HARTFORD COUNTY) | CONNECTICUT NATURAL GAS CORP | THE BUILDING AT 75 1/2 BIRCH ST. MANCHESTER CAUGHT FIRE AND BURNED TO THE POINT WHICH THE BUILDING COLLAPSED ONTO THE GAS METER SET LOCATED OUTSIDE AND ADJACENT TO THT BUILDING. THIS CAUSED THE METER TO BECOME DAMAGED AND RELEASED GAS THUS FURTHER FUELING THE FIRE. THE SERVICE WHICH WAS AT 11/4" PE PIPE WAS CUT OFF AT THE PROPERTY LINE TO ELIMINATE THE NATURAL GAS SOURCE. ONCE THE FIRE WAS COMPLETELY EXTINGUISHED THE SERVICE PIPING WAS PRESSURE TESTED AND FOUND TO BE WITHIN STANDARDS. NO LEAK WAS DETECTED. SUBSEQUENTLY THE STATE FIRE MARSHALL'S OFFICE BROUGHT IN A DOG TO SNIFF FOR ANY ACCELERANTS IN THE AREA. THIS TEST PROVED TO BE POSITIVE FOR THE PRESENCE OF ACCELERANTS. IT WAS ALSO DETERMINED LATER THAT DAY THAT A YOUNG MALE WHO LIVED AT THE RESIDENCE HAD CHECKED HIMSELF INTO THE LOCAL HOSPITAL WITH SEVERE BURNS ON HIS BODY. THE HOSPITAL REPORTED THIS TO THE TOWN FIRE MARSHALL. THE TOWN AND STATE'S INVESTIGATION RULED OUT NATURAL GAS AS THE CAUSE OF FIRE AND WERE PURSUING CRIMINAL CHARGES. | 250180 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
573 | 2007-12-11 | MA | other | UNKNOWN (nan COUNTY) | BOSTON GAS CO |  | 425000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
574 | 2007-12-17 | MD | other | UNKNOWN (BALTIMORE COUNTY) | BALTIMORE GAS & ELECTRIC CO | ACCORDING TO BALTIMORE COUNTY FIRE DEPARTMENT, THE POINT OF ORIGINATION IS UNKNOWN DUE TO THE EXTENT OF DAMAGE. BALTIMORE COUNTY FIRE DEPARTMENT'S REPORT STATED THAT THE DWELLING WAS HEAVILY ENGULFED UPON ARRIVAL. FIRE INVESTIGATION DEPARTMENT WAS REQUESTED TO INVESTIGATE. DUE TO THE INTENSITY OF THE FIRE, THE 1ST FLOOR TO COLLAPSED ONTO THE HOUSELINE AND GAS METER. THIS IS WHEN GAS BECAME INVOLVED. THE BALTIMORE COUNTY FIRE DEPARTMENT DETERMINED THE COST OF DAMAGES. | 114000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
575 | 2007-12-01 | OH | other | UNKNOWN (LUCAS COUNTY) | COLUMBIA GAS OF OHIO INC | A STRUCTURE FIRE AT A COMMERCIAL BUILDING CAUSED A ROOF COLLAPSE, WHICH FRACTURED A FITTING ON THE SERVICE LINE SERVING THE BUILDING. THERE IS NO INDICATION THAT THE FIRE WAS CAUSED BY A RELEASE OF GAS FROM A JURISDICTIONAL PIPELINE FACILITY, BUT AS A RESULT OF THE DAMAGE TO THE SERVICE LINE, THE FIRE WAS FED BY NATURAL GAS UNTIL COLUMBIA GAS CREWS ARRIVED AND TURNED OFF A CURB VALVE IN ORDER TO STOP THE FLOW OF GAS TO THE STRUCTURE. COLUMBIA CREWS ARRIVED AT THE SCENE IN APPROXIMATELY 17 MINUTES, HOWEVER THE FIRE DEPARTMENT HAS ESTABLISHED A PERMIMETER TO KEEP COLUMBIA'S CREW AWAY FROM THE DANGER OF THE UNSTABLE STRUCTURE. ONCE THE FIRE DEPARTMENT STABILIZED THE SITUATION THE CREW WAS ABLE TO SAFELY STOP THE FLOW OF GAS. | 60100 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
576 | 2007-12-28 | NM | leaks and spills | UNKNOWN (BERNALILLO COUNTY) | PUBLIC SERVICE COMPANY OF NEW MEXICO - GAS SVCS | PIPE SEGMENT SENT TO LAB FOR FAILURE ANALYSIS. THERE WAS NO EVIDENCE OF PROGRESSIVE OR FATIGUE CRACKING AT THE ORIGIN NOR AT ANY POINT ON THE FRACTURE SURFACE. THE CRACK HAS THE APPEARANCE OF A TOUGH, DUCTILE MATERIAL. | 215000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
577 | 2007-12-24 | MN | natural disasters | UNKNOWN (CLAY COUNTY) | NORTHERN STATES POWER CO. OF MINNESOTA | WATER DRIPPING FROM A LARGE ICE DAM ON THE ROOF FROZE OVER THE SERVICE REGULATOR VENT, CAUSING AN OVER PRESSURE CONDITION ON THE CUSTOMERS HOUSE PIPING. CUSTOMER EQUIPMENT FAILED, CAUSING A FIRE THAT DAMAGED THE LOWER LEVEL OF THE HOUSE. | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
578 | 2007-12-27 | NV | sabotage | UNKNOWN (CLARK COUNTY) | SOUTHWEST GAS CORP | WHILE EXCAVATING AROUND NATURAL GAS PIPELINE FACILITIES LOCATED AT NORTH 5TH STREET AND COLDWELL STATION AVENUE, AN OPERATOR FOR TEJAS UNDERGROUND, PERFORMING WORK FOR SOUTHWEST GAS CORPORATION, DAMAGED A 1-INCH PE PURGE ASSEMBLY ON A ONE WAY FED 4-INCH PE DISTRIBUTION MAIN. IGNITION AND ONE FATALITY OCCURRED PRIOR TO SWG CREWS ARRIVING ON THE SCENE. THE FIRE WAS EXTINGUISHED WHEN THE 4-INCH PE MAIN WAS SQUEEZED TO STOP THE FLOW OF GAS. THE EXCAVATOR HAD A CURRENT ONE CALL CENTER TICKET.THE INCIDENT IS CURRENTLY UNDER INVESTIGATION AND A SUPPLEMENTAL REPORT WILL BE PROVIDED WHEN INVESTIGATION IS COMPLETED. THE ESTIMATE GAS LOSS IS 283 THERMS. THERE WERE NO OUTAGES THAT RESULTED FROM THE INCIDENT. SUPPLEMENTAL 04/25/2008: THE DAMAGE WAS NOT TO A 1-INCH PE "PURGE ASSEMBLY" AS ORIGINALLY REPORTED. THE DAMAGE WAS TO A 1-INCH STUB TO WHICH A TEMPORARY PURGE ASSEMBLY HAD BEEN ATTACHED AND SUBSEQUENTLY REMOVED. THE EXCAVATOR FAILED TO HAND-DIG NEXT TO THE GAS PIPELINE AND BROKE THE 1-INCH STUB WITH A BACKHOE. A CONTRACTOR'S EMPLOYEE'S FAILURE TO FOLLOW THE EMERGENCY RESPONSE PROCEDURES AND ASSOCIATED TRAINING ULTIMATELY LED TO THE FATALITY. THE INVESTIGATION IS COMPLETE. | 2494 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
579 | 2008-01-04 | NY | maintenance | UNKNOWN (SUFFOLK COUNTY) | KEYSPAN ENERGY DELIVERY - LONG ISLAND | AT 0444, NATIONAL GRID LI RECEIVED A CALL REPORTING A DISTURBANCE AT 96 CARLETON AVENUE, CENTRAL ISLIP. UPON ARRIVAL, NATIONAL GRID PERSONNEL FOUND THAT THE LOCATION HAD SUSTAINED DAMAGE TO WINDOWS, DOORS, AND THE BUILDING INTERIOR DUE TO AN APPARENT DISTURBANCE. THE BUILDING WAS NOT OCCUPIED AT THE TIME, THEREFORE, THERE WERE NO INJURIES. AN INSPECTION OF THE GAS REGULATOR REVEALED CORROSION AND ICE BLOCKAGE OF THE REGULATOR VENT PIPING. ALL OTHER GAS FACILITIES IN THE SURROUNDING AREA WERE INSPECTED AND FOUND TO BE IN GOOD CONDITION. THE COUNTY FIRE MARSHALL AND NEW YORK STATE PUBLIC SERVICE COMMISSION RESPONDED TO THE SCENE AND THE INVESTIGATION IS STILL IN PROGRESS. AS OF THIS TIME, IT IS SUSPECTED THAT THE ICE BLOCKAGE IN THE VENT CAUSED AN OVER PRESSURIZATION OF THE PIPING DOWNSTREAM OF THE REGULATOR, RESULTING IN A RELEASE OF GAS SOMEWHERE DOWNSTREAM OF THE REGULATOR. | 350000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
580 | 2008-01-05 | PA | other | UNKNOWN (YORK COUNTY) | COLUMBIA GAS OF PENNSYLVANIA | ON JANUARY 5, 2008 AT APPROXIMATELY 02:37 COLUMBIA GAS RECEIVED A CALL FROM 911. A VEHICLE CRASHED INTO A METER SET ADJACENT TO A RESIDENTIAL HOME LOCATED AT 3445 EAST PROSPECT RD. IN YORK, PA. ACCORDING TO THE RESPONDING FIRE AND POLICE, THE OCCUPANTS OF THE HOUSE WERE EVACUATED ALONG WITH THE OCCUPANTS (2) OF THE VEHICLE. FOUR MINUTES AFTER THE EVACUATION, THE HOUSE EXPLODED. THE CRASH SEVERED THE RISER OF THE METER. FIRE COMPLETELY DESTROYED THE RESIDENCE. | 203250 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
581 | 2008-01-12 | CA | other | UNKNOWN (ELDORADO COUNTY) | SOUTHWEST GAS CORP | ON JANUARY 9, 2008, A ROOFING CONTRACTOR SHOVELED WET SNOW OFF OF THE ROOF AND PILED IT ON TOP OF THE GAS METER. THE WET SNOW AND ICE THAT WAS PILED BETWEEN THE STRUCTURE AND THE GAS FACILITIES EXPANDED DUE TO ITS PARTIAL MELTING AND SUBSEQUENT FREEZING (A FREEZE/THAW CYCLE). THE FREEZE/THAW CYCLE(S) IMPOSED A HORIZONTAL LOADING ONTO THE GAS FACILITIES AND CAUSED THE METER PIPING TO BREAK DOWNSTREAM OF THE SHUT-OFF VALVE AND UPSTREAM OF THE SERVICE REGULATOR SOMETIME BETWEEN JANUARY 9 AND JANUARY 12, 2008. ESCAPING GAS ENTERED THE STRUCTURE THROUGH EAVE VENTS AND CONTINUED TO BUILD UP UNTIL IT REACHED AN IGNITION SOURCE. UPON IGNITION, STRUCTURAL DAMAGE WAS SUSTAINED TO THE REAR PORTION OF THE RESTAURANT AND SEVERAL GLASS WINDOWS BROKE INSIDE AND OUTSIDE OF THE STRUCTURE. FLYING GLASS DEBRIS CAUSED MINOR INJURIES TO TWO CONFIRMED CUSTOMERS AND ONE UNCONFIRMED. THEY WERE TREATED AND RELEASED AT THE SCENE. THE EXPLOSION WAS GENERATED FROM A FLASH FIRE ONLY WITH NO SUSTAINED COMBUSTION, AND THEREFORE NO FIRE DAMAGE TO THE STRUCTURE. ***SUPPLEMENTAL*** THE PREVIOUS FINAL REPORT SUBMITTED ON FEBRUARY 17, 2009 WAS PREPARED BEFORE AN ANALYSIS WAS UNDERTAKEN BY AN INDEPENDENT METALLURGICAL ENGINEER RETAINED BY SOUTHWEST GAS CORPORATION. THAT ANALYSIS DETERMINED THAT THE FAILURE WAS NOT CAUSED BY THE WEIGHT OF THE WET SNOW THAT WAS SHOVELED ONTO ON THE GAS FACILITIES. INSTEAD, THE FAILURE WAS CAUSED BY THE FREEZE/THAW CYCLE(S) ACTING UPON THE LARGE AMOUNT OF WET SNOW (AND ICE) THAT HAD BEEN SHOVELED ONTO THE GAS FACILTIES WHICH INDUCED HORIZONTAL FORCES ON THE GAS FACILITIES AND CAUSED THEM TO FAIL. | 504909 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
582 | 2008-01-09 | IN | natural disasters | UNKNOWN (WHITE COUNTY) | NORTHERN INDIANA PUBLIC SERVICE CO | HEAVY RAINS AND MELTING SNOW CAUSED EXTREMELY HEAVY WATER FLOW IN THE TIPPECANOE RIVER AND THROUGH THE NORWAY DAM IN MONTICELLO, IN. THE 6" STEEL GAS PIPE, REFERENCED IN THIS REPORT, WAS INSTALLED UNDER THE RIVER...JUST DOWNSTREAM FROM THE DAM. ON JANUARY 9, 2008, NIPSCO RECEIVED COMPLAINTS OF LOW GAS PRESSURE. AFTER INVESTIGATION, AND THE PRESENCE OF ODOR, IT WAS DETERMINED THE PIPE UNDER THE TURBULENT WATER WAS LEAKING. THE DAMAGED PIPE UNDER THE RIVER WAS ISOLATED AND PRESSURES RESTORED. A TEMPORARY 6" PLASTIC PIPE WAS INSTALLED ON A NEARBY BRIDGE, PENDING A FUTURE PERMANENT INSTALLATION. SEVERAL HUNDRED CUSTOMERS WERE INTERRUPTED FOR 11 TO 19 HOURS, PENDING ISOLATION OF THE DAMAGED PIPE AND RE-LIGHTING. SUPPLEMENT: 8/01/2008 LATER FIELD INVESTIGATION HAS REVEALED THE PIPE SEVERED. SECTIONS OF PIPE, ON BOTH SIDES OF THE POINT OF SEPARATION, HAVE BEEN RECOVERED. THE EVIDENCE WOULD INDICATE THAT THE EXTRAORDINARY WATER FLOW (HIGHEST VOLUME ON RECORD) WAS RESPONSIBLE FOR EXPOSING AND/OR RUPTURING THE PIPE. A 6" PLASTIC PIPE (HIGH DENSITY SDR-11) HAS BEEN DIRECTIONALLY BORED UNDER THE RIVER BED AND TIED TO THE SURROUNDING SYSTEM. THE TEMPORARY 6" PLASTIC PIPE HAS BEEN REMOVED FROM THE BRIDGE. | 215000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
583 | 2008-01-28 | AZ | natural disasters | UNKNOWN (GILA COUNTY) | ENERGY WEST AZ | 1 1/4" ALDYL PIPE APPEARED TO HAVE BEEN PREVIOUSLY SQUEEZED OFF, CAUSING DAMAGE TO PIPE. ALSO A FACTOR WAS THAT THE GROUND HAD SUBSIDENCE IN THIS AREA. DURING EXCAVATION WE ALSO FOUND BROKEN SEWER PIPE IN THE GAS LINE TRENCH. APPRAISED VALUE FOR PROPERTY @ 209 E. MCKAMEY WAS $160,000. THE FIRST VALUATION OF $100,000 WAS FROM A THIRD PARTY. | 161200 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
584 | 2008-01-14 | VA | other | UNKNOWN (FAIRFAX COUNTY) | WASHINGTON GAS LIGHT CO | WASHINGTON GAS RESPONDED TO A HOUSE FIRE AT 3162 MARY ETTA LANE, HERNDON, VA AT THE REQUEST OF THE FAIRFAX COUNTY FIRE DEPARTMENT. THE REAR WALL OF THE STRUCTURE HAD COLLAPSED ON THE METER BUILD-UP. WASHINGTON GAS CUT AND CAPPED THE SERVICE IN THE YARD. A BAR-HOLE SURVEY AND ODORANT SAMPLE WERE TAKEN. THE FIRE IS STILL UNDER INVESTIGATION BY THE FAIRFAX COUNTY FIRE MARSHAL'S OFFICE. | 1005500 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
585 | 2008-01-17 | CA | other | UNKNOWN (LOS ANGELES COUNTY) | SOUTHERN CALIFORNIA GAS CO | ON JANUARY 17, 2008 A METER SET ASSEMBLY WAS DAMAGED BY A DUMP TRUCK THAT LOST CONTROL, LEAVING THE ROADWAY AND STRIKING INTO THE METER SET ASSEMBLY. THE ESCAPING GAS IGNITED, CAUSING A FIRE THAT DAMAGED A BUILDING. DUE TO BUILDING DAMAGE, THIS FACILITY WILL NOT BE RESTORED AT THIS TIME. THE METER LOCATION WAS NOT SUBJECT TO TRAFFIC. THIS INCIDENT BECAME REPORTABLE TO DOT WHEN ESTIMATED DOLLAR AMOUNT OF FIRE DAMAGE EXCEEDING $50,000. FOR ANY FURTHER QUESTIONS, CONTACT JEFF KOSKIE AT 213-244-3283. | 101000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
586 | 2008-01-17 | CA | other | UNKNOWN (SAN DIEGO COUNTY) | SAN DIEGO GAS & ELECTRIC CO | ON JANUARY 17, 2008 A RISER AND METER SET ASSEMBLY WAS DAMAGED BY AN ELDERLY DRIVER WHO EXPERIENCED A SEIZURE, LOST CONTROL OF HIS VEHICLE AND CRASHED THROUGH A GARAGE, STRIKING INTO THE METER SET ASSEMBLY. THE ESCAPING GAS IGNITED, CAUSING A FIRE THAT DAMAGED A BUILDING. DUE TO BUILDING DAMAGE, THIS FACILITY WILL NOT BE RESTORED AT THIS TIME. THE METER LOCATION WAS NOT SUBJECT TO TRAFFIC. THIS INCIDENT BECAME REPORTABLE TO DOT BASED UPON THE ESTIMATE DOLLAR AMOUNT OF FIRE DAMAGE EXCEEDING $50,000. FOR ANY FURTHER QUESTIONS, CONTACT JEFF KOSKIE AT 213-244-3283. | 101000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
587 | 2005-07-07 | CA | maintenance | UNKNOWN (SANTA CLARA COUNTY) | PACIFIC GAS & ELECTRIC CO | AT 0810, JULY 7, 2005, AN EXPLOSION OCCURRED AT THIS LOCATION. THE SINGLE FAMILY HOME WAS SEVERELY DAMAGED. TWO CHILDREN, 4 AND 6 YEARS OLD, WERE TRANSPORTED TO THE HOSPITAL AND LATER RELEASED WITH MINOR INJURIES. THE FATHER WAS TRAPPED UNDER DEBRIS FOR ~2-1/2 HOURS AND WAS SUBMITTED AND TREATED FOR A BROKEN COLLAR BONE AND ANKLE. HE WAS RELEASED THE NEXT DAY. THE FIRE DEPARTMENT INFORMED THE MEDIA THAT IT WAS NATURAL GAS EXPLOSION. THE GAS SUPPLY WAS SQUEEZED OFF INITIALLY AT 0840 HOURS AND AGAIN AT 0940 HOURS. A SUBSEQUENT LEAK SURVEY REVEALED A GRADE 1 LEAK IN FRONT OF THE PREMISES NEAR THE STREET. THE LEAK WAS REPAIRED AT 1113 HOURS. [NOTE: THIS INFORMATION DOCUMENTED ON FORM F7100.0 AND WAS FAXED TO THE OPS/PHMSA ON AUGUST 4, 2005.] | 405100 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
588 | 2006-06-13 | CA | other | UNKNOWN (SANTA CLARA COUNTY) | PACIFIC GAS & ELECTRIC CO | ON JUNE 13, 2006, A PASSENGER VEHICLE CRASHED INTO A RESIDENTIAL GARAGE AND DAMAGED A GAS METER AT 935 MCCREERY AVENUE, SAN JOSE, CALIFORNIA. FIREFIGHTERS EXTINGUISHED TEH RESULTING STRUCTURAL FIRE AND VALVED OFF THE GAS RISER FOR SAFETY. THERE WERE NO INJURIES OR DEATHS. THE HOUSE WAS VACANT, AND FOR SALE. THE GAS METER WAS LOCATED ON THE SIDE OF THE GARAGE, AROUND THE CORNER FOR THE DRIVEWAY. THE METER DOES NOT QUALIFY FOR METER PROTECTION, AS RECOMMENDED BY THE CALFORNIA PUBLIC UTILITIES COMMISSION, DUE TO ITS DISTANT PROXIMITY FROM VEHICULAR TRAFFIC. [THIS INFORMATION WAS DOCUMENTED ON FORM F7100.1 AND WAS FAXED TO OPS/PHMSA ON JUNE 28, 2006.] | 90000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
589 | 2006-12-03 | CA | other | UNKNOWN (SANTA CLARA COUNTY) | PACIFIC GAS & ELECTRIC CO | OUR INVESTIGATION DETERMINED THAT, AT APPROXIMATELY 0120 HOURS ON DECEMBER 3, 2006, THERE WAS A STRUCTURE FIRE CAUSING DAMAGE TO THE ENTIRE RESIDENTIAL HOME. THIS STRUCTURE FIRE STARTED IN THE BACK OF THE HOME AND ADVANCED TOWARDS THE GAS METER SET LOCATED NEAR THE FRONT OF THE STRUCTURE. THE EXTREME HEAT RESULTING FROM THE FIRE CAUSED THE ½¿ POLYETHYLENE TUBING INSERTED IN A STEEL RISER CASING TO FAIL AT THE RISER LOCATION; RELEASING HIGH PRESSURE GAS AT THE LOWER PORTION OF THE STEEL CASING. THIS GAS THEN MIGRATED UNDERGROUND, ACCUMULATED UNDER THE STRUCTURE, CREATED AN EXPLOSIVE ENVIRONMENT AND IGNITED. THIS INCIDENT WAS REPORTED TO THE DOT DUE TO COSTS IN EXCESS OF $50,000. [NOTE: THIS REPORT WAS PREVIOUSLY ENTERED INTO DOT WEBSITE AS WELL AS A COPY SENT TO THE CALIFORNIA PUBLIC UTILITIES COMMISSION ON DECEMBER 27, 2006.] | 53000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
590 | 2006-12-05 | CA | other | UNKNOWN (SAN FRANCISCO COUNTY) | PACIFIC GAS & ELECTRIC CO | ON 12/05/06 AN EXPLOSION AND RESULTING FIRE OCCURRED AT 1650 HOURS AT 456 14THSTREET, SAN FRANCISCO, CALIFORNIA. A RESIDENT WAS ATTEMPTING TO RELIGHT A NATURAL GAS STOVE WHEN THE STOVE UNIT EXPLODED RESULTING IN THE FIRE. TWO ADJACENT APARTMENTS INCLUDING THE ONE WHERE THE EXPLOSION TOOK PLACE WERE EXTENSIVELY DAMAGED FORM THE FIRE. THE NATURAL GAS SERVICE TO THE COMPLEX WAS SHUT BY THE SAN FRANCISCO FIRE DEPARTMENT. AN OCCUPANT OF THE BUILDING RECEIVED MINOR INJURIES AND WAS TREATED AND RELEASED AT THE SCENE. THE NINE UNIT COMPLEX WAS EVACUATED, AND 14TH STREET WAS CLOSED BY THE SAN FRANCISCO FIRE DEPARTMENT. PACIFIC GAS AND ELECTRIC FACILITIES WERE NOT INVOLVED IN THE INCIDENT. THIS INCIDENT WAS REPORTED TO THE DOT DUE TO COSTS IN EXCESS OF $50,000. [NOTE: THIS REPORT WAS ENTERED INTO DOT WEBSITE AND COPIES OF THIS REPORT WAS SENT TO THE CALIFORNIA PUBLIC UTILITIES COMMISSION ON DECEMBER 27, 2007.] | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
591 | 2008-01-19 | IL | other | UNKNOWN (MC HENRY COUNTY) | NORTHERN ILLINOIS GAS CO | STRUCTURE FIRE AT THIS LOCATION. FIRE PROGRESSED THROUGH THE STRUCTURE AND REACHED THE OUTSIDE METER SET, CAUSING DAMAGE WHICH RESULTED IN A RELEASE OF NATURAL GAS INTO THE ATMOSPHERE. | 126000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
592 | 2008-01-03 | MA | other | UNKNOWN (MIDDLESEX COUNTY) | NSTAR GAS COMPANY | NSTAR GAS WAS NOTIFIED OF A HOUSE FIRE BY THE MAYNARD FIRE DEPARTMENT AT 6:50 PM AND REQUESTED TO SHUT THE GAS TO THE BUILDING AT THE STREET. IT WAS BELIEVED THAT GAS MAY BE FUELING THE FIRE IN THE CRAWL SPACE AREA OF THE BASEMENT. THE HOMEOWNER HAD BEEN USING KEROSENE-FIRED TORPEDO HEATERS TO THAW FROZEN WATER PIPES IN THE CRAWL SPACE, IN THE VICINITY OF THE GAS SERVICE PIPING PASSING THROUGHTHE CRAWL SPACE. THE FIRE INVOLVED TIMBER FRAMING AND FLOORING ADJACENT TO AND ABOVE THE HEATER LOCATION. THE GAS SERVICE PIPING WAS BARE STEEL INSTALLED IN 1911 AND INSERTED WITH PLASTIC IN 1982. AFTER THE AREA WAS MADE SAFE NSTAR PERSONNEL OBSERVED BUBBLING FROM A POOL OF WATER ON THE DIRT CRAWL SPACE FLOOR, AT A THREADED UNION IN THE STEEL CASING PIPE. AN INDEPENDENT TESTING LABORATORY DETERMINED THAT THE PLASTIC PIPE FAILED DUE TO THE APPLICATION OF LOCALIZED HIGH TEMPERATURE MOST LIKELY FROM THE TWO BULLET TYPE SPACE HEATERS. THE LOCATION OF THE RELEASE OF GAS INTO THE ATMOSPHERE WAS POSSIBLE AT THE THREADED UNION. THE TWO SPACE HEATERS ARE POSSIBLE SOURCES FOR THE IGNITION OF THE RELEASED GAS. UPDATED BY PHMSA ON 1/15/2016 PER OPERATOR'S MARK UP. (PART A, QUESTION 4 - TYPE OF LEAK OR RUPTURE; PART C, QUESTIONS 2 FAILURE OCCURRED ON & 3 MATERIAL INVOLVED; AND PART F - APPARENT CAUSE, F7 - OTHER, QUESTION 24 MISCELLANEOUS; AND PART I - NARRATIVE). | 152449 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
593 | 2008-01-22 | DC | other | UNKNOWN (nan COUNTY) | WASHINGTON GAS LIGHT CO | INCIDENT IS STILL UNDER INVESTIGATION BY THE DC FIRE DEPARTMENT AND THE ATF. WASHINGTON GAS RESPONDED TO A FIRE AT 2412 WISCONSIN AVE, NW, WASHINGTON DC AT THE REQUEST OF THE DC FIRE DEPARTMENT. WASHINGTON GAS DID DIG THE SERVICE UP AND CAP IT OFF, HOWEVER, AT THE TIME OF THIS FILING, WASHINGTON GAS HAS BEEN UNABLE TO SECURE THE METER OR PERFORM ANY TESTING. **NOTE - THE PRESSURES INDICATED ON PAGE 1 FOR 8A, ESTIMATED OPERATING PRESSURE, AND 8B, MAXIMUM ALLOWABLE OPERATING PRESSURE, ARE IN INCHES WATER COLUMN, NOT PSIG. UPDATED BY PHMSA ON 2/9/2016 PER OPERATOR'S MARK UP (PART F - APPARENT CAUSE, F7 - OTHER, QUESTION 25). PRELIMINARY REPORT FROM DISTRICT OF COLUMBIA FIRE DEPARTMENT INDICATED THAT FLAMES WERE OBSERVED IN A ROOM INSIDE THE STRUCTURE PRIOR TO THE FIRE BREACHING THE ROOF. NO FURTHER INFORMATION IS AVAILABLE AND WASHINGTON GAS CONSIDERS THE INVESTIGATION CLOSED. | 202000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
594 | 2005-08-18 | CA | leaks and spills | UNKNOWN (STANISLAUS COUNTY) | PACIFIC GAS & ELECTRIC CO | MIGRATING GAS ACCUMULATED IN AN UNVENTED WATER HEATER ENCLOSURE, EXPLODED AND CAUSED DAMAGE TO RESIDENT. THE CITED COPPER SERVICE LEAK MAY HAVE CAUSED OR CONTRIBUTED TO THE INCIDENT. THE GAS LEAK AND GAS METER WERE ON THE OPPOSITE SIDE OF THE BUILDING WHERE THE SEPTIC TANK IS LOCATED AND THE EXPLOSION OCCURRED. LATER, GAS CHROMATOGRAPH TESTS REVEALED THE PRESENSE OF NATURAL GAS IN THE SOIL AT VARIOUS TEST LOCATIONS AROUND THE RESIDENCE. THERE WAS A DISPROPORTIONATELY HIGH METHANE CONCENTRATION NEAR THE SEPTIC AREA AND SOURCE OF IGNITION COMPARED TO THE OTHER LOCATIONS TESTED. THE SERVICE WAS REPLACED AND GAS SERVICE WAS RESTORED AT 0700 HOURS THE SAME DAY. ANALYSIS OF SERVICE: CORROSION OCCURRED AT THE SOLDERED COPPER-STEEL TRANSITION FITTING. [ON SEPTEMBER 16, 2005, PG&E SENT THE INFORMATION RESOURCE MANAGER, THE COMPLETED 7100.1 FORM FOR THE AUGUST 18, 2005 GAS INCIDENT THAT OCCURRED IN CERES, CALIFORNIA (RSPA NO.769574)] | 51100 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
595 | 2008-02-09 | NE | other | UNKNOWN (ANTELOPE COUNTY) | SOURCEGAS LLC | SEMI-TRUCK ROLLED OVER WHILE MAKING CURVE ON HWY, SLID INTO HOUSE AND METER LOOP AT STRUCTURE. DAMAGED REGULATOR & METER. SHUT OFF BUSINESS DISTRICT VALVE AND INSTALLED SHORT STOP ON EAST SIDE OF L STREET. REMOVED DAMGAE SECTION OF ABOVE GRADE PIPING. PLUGGED AND CAPPED LINE. | 63661 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
596 | 2008-01-31 | IA | maintenance | UNKNOWN (JASPER COUNTY) | CONSUMERS ENERGY | RE: INCIDENT REPORT #861109, CONSUMER ENERGY ATTACHMENT TO RSPA FORM F7100.1 AND F7100.2 INCIDENT REPORTS. THIS NARRATIVE PROVIDE AS PER INSTRUCTION FOR PART G OF THE ABOVE REFERENCED FORMS. OVER PRESSURES OF MINGO/HARVESTER GAS TRANSMISSION AND DISTRIBUTION SYSTEMS. ON JANUARY 31, 2008 AT 12:15 A.M. AN OVER PRESSURE ALARM, FROM THE ELECTRONIC METERING, WAS RECEIVED BY NORTHERN NATURAL GAS AND CALLED TO CONSUMER ENERGY FROM OUR MINGO TBS, LOCATED AT 12359 NORTH 59TH AVENUE WEST MINGO, IOWA 50168. CONSUMERS ENERGY PERSONNEL RESPONDED AND FOUND THAT TWO EZR REGULATORS IN A WORKER MONITOR CONFIGURATION HAD FAILED IN THE OPEN POSITION AND THE PRESSURE TO BE 475 PSI. AT 1:15 A.M. THIS TBS FEEDS 6 INCH PE PIPE 3408 SDR 11 PIPE WITH AN MAOP OF 100 PSI. CONSUMER'S PERSONNEL SHUT DOWN THE REGULATOR STATION AND BEGAN TO VENT THE GAS. AFTER VENTING WAS STARTED A SECOND CREW WAS CALLED TO CHECK OUR REGULATOR STATION AT THE HARVESTER DEVELOPMENT, LOCATED NEAR THE CRONER OF W100TH STREET NORTHAND HIGHWAY 330. THE PRESSURE AT THIS STATION HAD PEGGED THE PRESSURE GAGE AT 160 PSI. CREW 2 BEGAN VENTING GAS FROM THE DISTRIBUTION SYSTEM AT 2 A.M. THIS SYSTEM CONSISTS OF 4 INCH, 2 INCH AND 1 INCH PE PIPE 3408 SDR 11 WITH AN MAOP OF 60 PSI. DURING VENTING HOUSE REGULATORS WERE CHECKED TO SEE IF ANY WERE VENTING AND ALL REGULATORS APPEARED NORMAL. CREW 3 WAS DISPATCHED AT 6:30 A.M. AND BEGAN VENTING GAS AT A FARM TAP CENTRALLY LOCATED ALONG THE TRANSMISSION LINE. CREW 4 ARRIVED AT 8 A.M. AND BEGAN VENTING GAS AT THE DISTRIBUTION TBS AT HARVESTER. GAGES THAT HAD BEEN PEGGED WERE CHANGED. WITH THE PRESSURE IN THE TRANSMISSION SYSTEM AT 300 PSI CONSUMERS CHECKED ALL FARM TAP METERS DOWN STREAM SIDES AND FOUND PRESSURES TO THE HOUSE TO BE NORMAL. SPOT CHECKS WERE TAKEN ON THE DOWN STREAM SIDE OF METERS ON OUR DISTRIBUTION SYSTEM AND ALL CHECKS WERE NORMAL FOR PRESSURE GOING INTO HOUSES. WHEN PRESSURE REACHED 75 PSI AT THE TBS AT HARVESTER THE STATION WAS LOCKED IN AND LINE PACK WAS USED TO FEED THE CONSUMERS. 3 P.M. PRESSURE WAS DOWN TO 100 PSI AT THIS TIME A SHUT IN TEST WAS PERFORMED ON THE TRANSMISSION SYSTEM FOR ONE HOUR WITH NO LOSS OF PRESSURE DURING THAT HOUR. GAS WAS TURNED BACK ON AND SHUT IN TEST WERE PERFORMED ON THE HOUSES. 4 P.M. PRESSURE WAS RESTORED TO HARVESTER TBS AND REGULATORS CHECKED. GASKETS WERE DAMAGED ON ONE SIDE OF THE DUAL FEED WORKER MONITOR SYSTEMS FISHER 299H REGULATORS. THIS SIDE WAS LOCKED OUT AND THE SYSTEM WAS OPERATED OFF OF THE ALTERNATE SIDE. 5 P.M. MINGO TBS CREWS RESTORED HIGH PRESSURE FEED TO MINGO STATION LEAVING MALFUNCTIONING REGULATORS LOCKED OUT. CREWS CHECKED FUNCTION OF FISHER EZR REGULATORS ON OPPOSITE SIDE OF DUAL RUN AND IT WAS DECIDED THAT REGULATORS ON THE OPPOSITE SIDE WOULD ALSO BE LOCKED OUT AND THAT A FISHER 627 THAT FEEDS THE VORTEX HEATER WOULD FEED SYSTEM FOR THE NIGHT. FEBRUARY 1, 2008 AN INFRARED LEAK SURVEY WAS PERFORMED BY IOWA ASSOCIATION OF MUNICIPAL UTILITIES. THESE SURVEYS ARE PLANNED TO BE CONDUCTED MONTHLY FOR MINIMUM OF THE NEXT 90 TO 120 DAYS. REGULATORS AT HARVESTER TBS WERE REPAIRED. EZR REGULATORS AT MINGO WERE ALSO TAKEN APART FOR REPAIR. THERE WAS A LARGE AMOUNT OF FOREIGN MATTER IN THE REGULATORS. DIAPHRAGMS APPEARED INTACT BUT WERE REPLACED. CONTACT WAS MADE WITH EAGLE PIPE, MANUFACTURES OF 3408 SDR 11 PIPE. MINIMUM BURST FOR THIS PIPE IS 504 PSI. EAGLE INFORMED CONSUMERS THAT THE PIPE REGAINS IT STRENGTH WHEN EXCESSIVE PRESSURE IS RELIEVED FROM THE PIPE AND PIPE IS OPERATED AT NORMAL PRESSURES. EAGLE DECLINED TO PUT THIS IN WRITING. FEBRUARY 2, 2008 CONSUMERS PERFORMED A SHUT IN TEST ON OUR DISTRIBUTION SYSTEM FOR ONE HOUR. STARTING AND ENDING PRESSURES WAS 19.2 PSI. AT THIS TIME CONSUMER PLANS TO ADD RELIEF TO OUR MINGO STATION AND CHANGE REGULATORS AND CONTINUE INFRARED LEAK SURVEYS. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
597 | 2008-01-27 | ND | leaks and spills | UNKNOWN (MORTON COUNTY) | MONTANA - DAKOTA UTILITIES CO | THIS FAILURE WAS IN A SECTION OF THE PIPELINE THAT WAS MOVED DUE TO ROAD CONSTRUCTION. THE PIPELINE WAS MOVED TO THE EAST BY TWO FEET AND LOWERED BY 18 INCHES DUE TO THE CONSTRUCTION OF A NEW RETAINING WALL. THE FAILURE/RELEASE WAS AN ACETYLENE GIRTH WELD THAT SPLIT OPEN ON THE WESTSIDE OF THE PIPELINE. THE WELD WAS NEXT TO A PERPENDICULAR TRENCH THAT WAS DUG TO INSTALL A WATER LINE, WHICH PASSED UNDER THIS PIPELINE. THERE WAS A RETAINING WALL THAT WAS BUILT APPROXIMATELY SIX FEET TALL PARALLEL TO THIS PIPELINE. ALL THIS CONSTRUCTION TOOK PLACE IN THE SUMMER OF 2007. THE DAY OF FAILURE WAS WARM 45 DEGREES. THE WEATHER PRIOR TO THIS WAS COLD WITH SOME DAYS BELOW ZERO. THERE ARE A NUMBER OF FORCES THAT ARE BEING INVESTIGATED TO DETERMINE THE REASON FOR FAILURE. THE WELD WAS REPAIRED BY SHUTTING IN THE EFFECTED LINE SECTION AND A NEW SECTION OF PIPE WAS INSTALLED. THE RESULT OF SHUTTING IN THIS LINE SECTION CAUSED APPROXIMATELY 5200 CUSTOMERS TO HAVE THEIR GAS SERVICE INTERRUPTED. THE WELD IS BEING SENT TO STRUCTURAL INTEGRITY FOR FAILURE TESTING. ACCORDINGLY, THE INCIDENT WAS NOT REPORTED TO THE NATIONAL RESPONSE CENTER. NORTH DAKOTA OFFICE OF PIPELINE SAFETY OFFICER AL MOCH WAS KEPT INFORMED THROUGHOUT THE EVENT. AFTER THE EVENT WAS UNDER CONTROL AN ESTIMATE WAS MADE FOR THE REPAIRS AND RECOVERY OF CUSTOMERS. THE REPAIRS WOULD COST APPROXIMATELY $15,000 AND THE RECOVERY COSTS ARE ESTIMATED AT $335,000. THE HIGH COST IS DUE TO THE NEED FOR ADDITIONAL PERSONNEL TO BE BROUGHT IN TO RELIGHT ALL THE CUSTOMERS IN A TIMELY FASHION. BASED ON THIS INFORMATION, MDU IS FILING THIS REPORT. A TELEPHONIC REPORT WAS CALLED IN ON FEB. 4TH, 2008 @ 1:20 PM REPORT #861454. 4/6/08 INVESTIGATION REVEALED THAT THE 1950'S VINTAGE OXYACETYLENE WELD HAD INSUFFICIENT PENETRATION AND FAILED DUE TO AN EXTERNAL FORCE, WHICH COULD NOT BE DETERMINED. THERE WERE A NUMBER OF EXTERNAL FORCES PRESENT FROZEN GROUND, RECENTLY DUG WATERLINE TRENCH, AND RECENT ROAD CONSTRUCTION. | 355500 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
598 | 2008-02-02 | CA | other | UNKNOWN (MONTEREY COUNTY) | PACIFIC GAS & ELECTRIC CO | A DRUNK DRIVER CRASHED THROUGH A GARAGE AND SHEARED THE NATURAL GAS RISER BELOW THE SERVICE VALVE. THE ESCAPING GAS IGNITED AND THE ENSUING FIRE WAS CONFINED TO THE GARAGE. THE DRIVER ESCAPED WITHOUT INJURY AND WAS ARRESTED AT THE SCENE. THE METER SET AND RISER WAS SET BACK 36 FEET FROM THE ROAD ON THE SIDE OF THE GARAGE, AND IN A LOCATION WHERE METER PROTECTION IS NOT NECESSARY. THE RESIDENCE WAS UNOCCUPIED AT THE TIME OF INCIDENT. GAS FLOW WAS STOPPED BY SQUEEZING THE ¾¿ STEEL SERVICE AT PROPERTY LINE. GAS AND ELECTRIC SERVICE HAS BEEN DISCONNECTED PENDING REBUILDING OF THE DAMAGED PORTION OF THE RESIDENCE. | 154400 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
599 | 2008-02-17 | PA | maintenance | UNKNOWN (JEFFERSON COUNTY) | T W PHILLIPS GAS & OIL CO | A LEAK WAS FOUND IN THE MAINLINE IN FRONT OF THE HOUSE. THE PIPE WAS INSTALLED IN 1964. IT IS BARE STEEL. THE PIPE WAS LAID IN SOIL PRIMARILY COMPOSED OF SHALE AND CLAY. THE WEATHER CONDITIONS WERE SUCH THAT TEMPERATURES WERE FLUCTATING FOR SEVERAL DAYS WITH LOWS IN THE SINGLE DIGITS TO HIGHS IN THE UPPER 30'S. THE GROUND WAS SATURATED DUE TO RAIN EARLIER IN THE WEEK. BOTH RESIDENTS WERE UNHURT. THE LADY WAS SENT TO THE HOSPITAL FOR OBSERVATION DUE TO A PREVIOUS HEART CONDITION. | 119060 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
600 | 2008-02-01 | TX | sabotage | UNKNOWN (HARRIS COUNTY) | ENTEX, A NORAM ENERGY COMPANY (FORM. DIV OF ARKLA | 3RD PARTY DAMAGE TO A 12" HP STEEL MAIN WITH A TRACK-HOE. | 6795 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
601 | 2008-01-27 | NM | sabotage | UNKNOWN (SAN JUAN COUNTY) | PUBLIC SERVICE COMPANY OF NEW MEXICO - GAS SVCS | RESULTS OF PNM S INVESTIGATION INDICATE THAT THIRD PARTY DAMAGE WAS THE CAUSE OF THE INCIDENT. IT APPEARS THE PIPELINE WAS DAMAGED (BENT) DURING THE INSTALLATION OF A WATER MAIN IN 1998 THAT INTERSECTS THE GAS PIPELINE AT A 90 DEGREE ANGLE. IT APPEARS, FROM A VISUAL INSPECTION OF THE DAMAGED PIPE, THAT THE ORIGIN OF THE LEAK WAS THE DAMAGED AREA (BENT) OF THE PIPE. PNM WAS NOT NOTIFIED OF THE DAMAGE TO ITS PIPELINE. A GAS LEAK RESULTED FROM THE THIRD-PARTY DAMAGE THAT EVENTUALLY LED TO THE EXPLOSION. PNM LEAK SURVEYED THE SUBJECT AREA IN OCTOBER 2006 AND DID NOT FIND ANY LEAKS IN THE AREA OF THE INCIDENT. | 250000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
602 | 2008-01-16 | TX | sabotage | UNKNOWN (LAMAR COUNTY) | ATMOS ENERGY CORPORATION, MID-TEX DIVISION | AN EXCAVATOR STRUCK A MAIN, CAUSING A LEAK. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
603 | 2008-01-24 | WI | maintenance | UNKNOWN (SAWYER COUNTY) | WISCONSIN GAS CO | ON THE MORNING OF JANUARY 24, 2008, WITH TEMPERATURES AROUND -24 DEGREES , WE ENERGIES EXPERIENCED CONSECUTIVE FAILURES OF A REGULATOR AND RELIEF VALVE AT ITS HAYWARD, WISCONSIN DISTRICT REGULATOR STATION LOCATED ON U.S. HWY. 63, SOUTH OF GEHRTS ROAD IN THE TOWN OF HAYWARD, WISCONSIN. THE FAILURES ULTIMATELY RESULTED IN A LITTLE MORE THAN 1,700 RESIDENTIAL, COMMERCIAL AND INDUSTRIAL CUSTOMERS WITHOUT NATURAL GAS SERVICE. THE MAKE-UP OF THE STATION CONSISTED OF TWO, FULL CAPACITY, PARALLEL RUNS, OF 2", TYPE FG-76-75 MOONEY REGULATORS. OVER PRESSURE PROTECTION FOR THE REGULATORS WAS PROVIDED BY A FISHER, TYPE 63EG, 6" RELIEF VALVE. THE STATION IS FED BY A 475 MAOP SYSTEM AD SUPPLIES THE COMMUNITY OF HAYWARD WITH A 60 PSIG DISTRIBUTION SYSTEM.AFTER REVIEW OF RECORDED DATA, INTERVIEWS WITH PERSONNEL INVOLVED AND EXAMINATION OF EQUIPMENT, THE FOLLOWING SEQUENCE OF EVENTS WAS DETERMINED TO HAVE OCCURRED. AT AROUND 5 AM ON THE MORNING OF THE FAILURE, THE PRIMARY REGULATOR RUN AT THE HAYWARD DISTRIBUTION REGULATION FACILITY BEGAN TO FAIL. THE DISTRIBUTION SYSTEM PRESSURE BEGAN TO INCREASE UNTIL THE PRESSURE RELIEF VALVE BEGAN TO RELIEVE AT APPROXIMATELY 5:30 AM. THE RELIEF VALVE CONTINUED TO RELIEVE BUT DID NOT RE-SEAT ITSELF WHEN THE PRESSURE GOT BACK DOWN TO 60 PSIG. WITH THE RELIEF VALVE CONTINUING TO RELIEVE, THE PRESSURE ON THE SYSTEM CONTINUED TO FALL AT WHICH POINT AT APPROXIMATELY 6:39 AM, CUSTOMERS BEGAN TO CONTACT WE ENERGIES THAT THEY WERE WITHOUT GAS. WE-ENERGIES GAS CONTROL CENTER HAD ALREADY RESPONDED TO A LOW PRESSURE ALARM RECEIVED AT 5:50 AM WITH THE DISPATCHING OF A FIRST RESPONDER. UPON ARRIVAL, THE FIRST RESPONDER STATED THAT THE RELIEF VALVE WAS BLOWING. KNOWING THAT CUSTOMERS WERE REPORTING NO GAS AND GAS CONTROL CONFIRMING ZERO PRESSURE, THE RESPONDER WAS INSTRUCTED TO SHUT THE STATION DOWN. THE PROCESS OF CHECKING THE STATION EQUIPMENT FOR THE CAUSE OF THE FAILURE BEGAN. THE STATION REGULATORS WERE DISMANTLED AND NEW RUBBER GOODS INSTALLED BY APPROXIMATELY 11 AM. A NEW RELIEF VALVE WAS SHIPPED TO THE SITE AND WAS INSTALLED BY APPROXIMATELY 3:30 PM. THE PRIMARY CAUSE OF REGULATION FAILURE WAS DETERMINED TO BE THE PASSAGE OF DUST/DEBRIS THROUGH THE STATION PLUGGING BOTH THE PRIMARY FILTER AND ERODING THE RUBBER PRODUCTS IN THE REGULATOR.ON JANUARY 30TH, 2008, TWO REPRESENTATIVES FROM THE FISHER COMPANY, MR. THOMAS STEMRICH, PIPELINE PROGRAM SAFETY MANAGER FROM THE PUBLIC SERVICE COMMISSION OF WISCONSIN AND REPRESENTATIVES OF WE ENERGIES INSPECTED THE FAILED RELIEF VALVE. THE INSPECTION REVEALED THAT A SIGNIFICANT AMOUNT OF PIPELINE DUST/DEBRIS WAS FOUND IN THE PILOTS. A SUMMARY OF THE INVESTIGATION WITH REPRESENTATIVES FROM THE FISHER RESULTED IN THE BELIEF BY FISHER AND WE ENERGIES PERSONNEL, THAT THE DEBRIS THAT GOT INTO THE PILOTS DID NOT ALLOW LOADING PRESSURE TO CLOSE THE MAIN BODY OF THE RELIEF.WE-ENERGIES AS OF THE DATE OF THIS REPORT HAS TAKEN THE FOLLOWING STEPS TO REDUCE THE POSSIBILITY OF A RE-OCCURRING FAILURE. A STATION FILTER WITH A 10 MICRON FILTERING CAPABILITY WAS INSTALLED AT THE INLET AT THE INLET OF THE STATION AND ANOTHER FILTER IN THE SUPPLY TO THE PILOT OF THE RELIEF VALVE. IN ADDITION, THE STATION REGULATION WAS REPLACED WITH AN OPERATOR-MONITOR CONFIGURATION SUPPORTED WITH A FULL CAPACITY RELIEF DEVICE. AN INCIDENT REVIEW WAS CONDUCTED TO REVIEW NOT ONLY THE FAILURE BUT OUR EMERGENCY RESPONSE PROCEDURES TO SAFELY AND EFFICIENTLY GET CUSTOMERS BACK ON SERVICE AS SOON AS POSSIBLE. A MUTUAL AID PROCESS WAS IMPLEMENTED DURING THIS OUTAGE WITH THE MAJORITY OF THE CUSTOMERS BACK ON SERVICE BEFORE MIDNIGHT THAT SAME DAY WITH ALL THE REMAINING TURNED BACK ON BY 10AM THE FOLLOWING DAY EXCEPT FOR A COUPLE "COULD NOT GET INS" REMAINING. ARRANGMENTS WERE MADE WITH THE LOCAL POLICE DEPARTMENT TO GAIN ACCESS TO THOSE REMAINING CUSTOMERS.THE MANUFACTURER OF THE RELIEF VAVLE CONTINUES TO REVIEW THE RELIEF FAILURE MODE. IF ANY CHANGES IN THEIR VIEW OF THE FAILURE ANALYSIS OCCURS, WE ENERGIES WILL FI LE AN AMENDED REPORT. OTHERWISE, THIS REPORT IS CONSIDERED A FINAL REPORT. | 525833 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
604 | 2008-02-01 | TX | sabotage | UNKNOWN (VICTORIA COUNTY) | ENTEX, A NORAM ENERGY COMPANY (FORM. DIV OF ARKLA | CITY OF VICTORIA SEWER CREW PULLED AN 1-1/4" STEEL SERVICE LINE SERVING 1402 E. WARREN OUT OF A 1-1/4" X 6" TWO BOLT MECHANICAL PIPE COUPLING WITH A GRADALL EXCAVATOR. ESCAPING GAS MIGRATED TO THE STRUCTURE AT 1401 E WARREN RESULTING IN AN EXPLOSION AND FIRE. | 57718 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
605 | 2007-12-17 | TX | sabotage | UNKNOWN (LUBBOCK COUNTY) | ATMOS ENERGY - WEST TEXAS DIVISION | A 2 INCH NATURAL GAS LINE WAS SEVERED BY A BACKHOE OPERATOR. DUE TO THE HIGH WINDS THE ESCAPING GAS WAS BLOWN IN THE GENERAL DIRECTION OF RAMIREZ CHARTER SCHOOL. COMPANY EMPLOYEES GAS IN THE SCHOOL. THE 400 STUDENTS AND STAFF WERE EVACUATED AS A PRECAUTION. THE SCHOOL DISTRICT MOVED THE STUDENTS TO ANOTHER SCHOOL FOR LUNCH AND RETURNED AFTER TWO HOURS. | 550 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
606 | 2008-02-07 | PA | natural disasters | UNKNOWN (PHILADELPHIA COUNTY) | PHILADELPHIA GAS WORKS | INCIDENT EXECUTIVE SUMMARY 709 SOUTH SIXTH ST. FEBRUARY 7, 2008 THE FOLLOWING IS AN ACCOUNT OF THE INCIDENT WHICH OCCURRED IN THE QUEEN VILLAGE SECTION OF PHILADELPHIA, 709 SOUTH SIXTH STREET ON THURSDAY AFTERNOON, AT 1602 HOURS. THURSDAY FEBRUARY 7, 2008 TIME 1602 - INITIAL CALL THE INITIAL CALL TO PGW WAS MADE BY THE PHILADELPHIA FIRE DEPARTMENT AND WAS REPORTED TO PGW TO RESPOND TO A BUILDING COLLAPSE, ONE ALARM FIRE, ENGINE ON THE WAY, INJURIES UNKNOWN AT THIS TIME. 1602 - 1609 ¿ PGW INITIAL PERSONNEL DISPATCHING TIME PGW FIELD OPERATIONS INITIALLY DISPATCHED THE FOLLOWING: 1604 - DISTRIBUTION CREW 1602 - DISTRIBUTION SUPERVISOR 1604 - GREASE EQUIPMENT. 1604 - FSD SUPERVISOR, 1609 - FSD TECHNICIAN, 1615 ¿ FIRST PGW EMPLOYEE ON LOCATION WITHIN 13 MINUTES OF THE INITIAL CALL THE FIRST PGW EMPLOYEE ARRIVED ON LOCATION AND PROVIDED A PRELIMINARY REPORT OF A HOUSE COLLAPSE AND AN ENSUING FIRE. VISUAL OBSERVATION OF A GAS FIRE WAS NOT INDICATED. NO INDICATION OF A GAS LEAK (ODOR OR READINGS) AT THIS TIME. NO INJURIES REPORTED AT THIS TIME. 1620 ¿ FIRST EMERGENCY ACTION 707 S. 6TH STREET WAS SHUT OFF. THE FIRST OF FIVE BUILDINGS WERE SHUT OFF AS AN EMERGENCY ACTION. 1625 ¿ SECOND EMERGENCY ACTION 711 S. 6TH STREET GAS WAS SHUT OFF. THIS ENSURED THAT THE FIRST TWO BUILDINGS ALONG SIDE OF THE INCIDENT ADDRESS, 709 S. 6TH STREET, WERE SHUT OFF AS SAFETY MEASURES. OTHER PREMISES WERE SHUT OFF SHORTLY THEREAFTER, 705 S. 6TH STREET TO 715 S. 6TH STREET. CONTINUED ACTIONS ¿ PGW CONTINUED TO INVESTIGATE AND CONTINUALLY MONITOR FOR ANY SIGNS OF A GAS LEAK OR POTENTIAL MIGRATION TO OTHER STRUCTURES ON THE BLOCK. REPORTS CONTINUED THAT THERE WERE NO INJURIES. GENERAL SUPERVISOR DISTRIBUTION WAS DESIGNATED AS THE INCIDENT COMMANDER FOR PGW ACTION AND REPORTED TO DEPUTY CHIEF OF THE PHILADELPHIA FIRE DEPARTMENT. THERE WERE REPORTS OF A GAS ODOR FROM FIRE FIGHTERS ABOVE GROUND LEVEL AND OCCASIONALLY ON THE GROUND BY PGW WORKERS. THE PUC WAS NOTIFIED OF A POTENTIAL GAS INCIDENT AT 1744. THE NATIONAL RESPONSE CENTER IN WASHINGTON WAS NOTIFIED OF A POTENTIAL GAS LEAK INCIDENT AS PER §191.5 AT 1832 THAT EVENING. 1725 ¿ ORDER TO SHUT DOWN GAS. CHIEF GROGAN ORDERED THE GAS IN FRONT OF 709 S. 6TH STREET BE SHUT OFF. DUE TO FIRE FIGHTING EQUIPMENT ON SCENE, THE EMERGENCY ON LOCATION WAS BROUGHT IN TO A SUITABLE STAGING AREA; AIR COMPRESSORS AS WELL. PREPARATIONS TO GREASE WERE MADE AT THE HEAD OF SERVICE TO 705 S. 6TH STREET AND 715 S. 6TH STREET. 1744 ¿ GAS OFF THE GAS MAIN WAS SHUT DOWN BY GREASE INJECTION. ZERO GAS FLOW CHECKS CONFIRMED POSITIVE SHUT DOWN INSIDE THE PROPERTIES OF 707 S. 6TH STREET AND 713 S. 6TH STREET. 2300 ¿ CUT AND CAP AS PER PGW PROCEDURES, THE MAIN WAS PHYSICALLY DISCONNECTED BY CUTTING AND CAPPING. FINAL LEAK SURVEY OF THE ENTIRE BLOCK WAS CONDUCTED AND NO READINGS WERE FOUND. AT THIS TIME THE FIRE MARSHALL CONCLUDED THE DAY¿S INVESTIGATION AND CALLED FOR CONTINUATION THE NEXT MORNING. FRIDAY, FEBRUARY 8, 2008 INVESTIGATION PGW ON SCENE DURING THE FIRE MARSHALL (FM) INVESTIGATION OF THE EXPLOSION/FIRE AT 709 S. 6TH STREET. FIRE MARSHALL CLAY WAS THE LEAD INVESTIGATOR IN CHARGE. PUC SAFETY DIVISION WAS REPRESENTED BY PAUL METRO, PETE STANLEY AND MICHAEL NYGUEN. AFTER DEBRIS AND UNSAFE OVERHANGING STRUCTURES WERE REMOVED IN FRONT OF THE PROPERTY, PGW CONTINUED TO ASSIST THE FM BY PREPARING AND TESTING THE MAIN AND SERVICES ABANDONED THE PREVIOUS NIGHT. A 6¿ WATER COLUMN PRESSURE TEST (OPERATING PRESSURE AT THE TIME) WAS PLACED ON THE MAIN AND SERVICES. THIS TEST FAILED. WHEN DEBRIS WAS REMOVED IN FRONT OF 709 S. 6TH STREET, PGW PROVIDED BARHOLES FOR LEAK INVESTIGATION. HIGHEST READING FOUND WAS A 3% GAS READING IN A BARHOLE. THIS WAS ASSUMED TO BE RESIDUAL GAS FROM THE DISCONTINUED MAIN. SINCE THE MAIN AND SERVICES FAILED TEST, THE NEXT STEP OF THE INVESTIGATION WAS TO DISCONNECT THE SERVICES AND TEST THEM INDIVIDUALLY. THEY ALL PASSED AN AIR TEST. THE MAIN WAS THEN TESTED AND THIS TEST FAILED. THE FIRE MARSHALL CONCLUDED THE INVESTIGATION AND SCHEDULED CONTINUATION THE FOLLOWING DAY. SATURDAY, FEBRUARY 9, 2008 INVESTIGATION STEVEN GROEBER, DIRECTOR, FIELD OPERATIONS REPRESENTING PGW, FIELD MARSHALL CLAY, PETE STANLEY AND MICHAEL NYGUEN WERE ON LOCATION SATURDAY, FEBRUARY 9, 2008 AT 0700. THE INVESTIGATION CONTINUED BY SETTING UP A FLOW LOSS TEST ON THE MAIN. FLOW LOSS WAS MEASURED AT 150 ¿ 200 CFH. VACUUM EXCAVATION WAS PERFORMED IN FRONT OF 709 S. 6TH STREET. AT 0915 A 6¿ CAST IRON, BROKEN MAIN WAS UNCOVERED ALMOST CENTER TO THE PROPERTY OF 709 S. 6TH STREET. THE MAIN WAS CLEANED, SCALED AND RECORDED (PHOTOS) IN PLACE. SOAPY WATER TEST OF THE MAIN INDICATED THAT THE MAIN WAS BROKEN ON THE TOP FROM 9AM TO 3PM. THE BOTTOM OF THE MAIN WAS NOT LEAKING. A SLEEVE WAS PLACED AROUND THE BREAK AND THE PRESSURE TEST THEN HELD; CONFIRMATION THAT THAT WAS THE ONLY BREAK ON THE LINE. PUC REPRESENTATIVES DIRECTED PGW TO CUT THE PIPE 12¿ EITHER SIDE OF THE BREAK. THE SECTION WAS CUT OUT AND REMOVED. THIS ALONG WITH OTHER EXCAVATED PIPING FROM THE SERVICES WERE TAGGED AND PLACED IN THE PGW EVIDENCE LOCKER. ALL EXCAVATIONS MADE BY PGW WERE BACKFILLED AND STEEL PLATE WAS LEFT IN THE FOOTWAY IN FRONT OF 709 S. 6TH STREET SO HEAVY EQUIPMENT COULD ACCESS THE BUILDING FOR THE FINAL INVESTIGATION. THE FIRE MARSHALL INDICATED THAT HE WOULD CHECK ALL GAS APPLIANCES BEFORE MAKING ANY CONCLUSIONS. ON SUNDAY, FEBRUARY 10, THE FIRE MARSHALL CONTINUED THE INVESTIGATION TO EXAMINE APPLIANCES AND CONDITIONS WITHIN THE STRUCTURE (709). THE FIRE MARSHALL REPORTED NO RECOGNIZABLE PROBLEMS WITH THE APPLIANCES. ON MONDAY MORNING, FEBRUARY 11 THE FIRE MARSHALL¿S OFFICE ANNOUNCED THAT THE CAUSE OF THE EXPLOSION WAS A BREAK IN PGW¿S LINE. | 925000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
607 | 2008-03-05 | PA | sabotage | UNKNOWN (ALLEGHENY COUNTY) | DOMINION PEOPLES | A RELEASE OF GAS IS SUSPECTED TO BE THE CAUSE OF AN EXPLOSION AT 171 MARDI GRAS DRIVE, PLUM BOROUGH, PENNSYLVANIA. SEVERAL ADJACENT HOUSES WERE DAMAGED BY THE EXPLOSION. ONE FATALITY AND ONE HOSPITALIZED INJURY OCCURRED. THE NATIONAL TRANSPORTATION SAFETY BOARD (NTSB) CONDUCTED AN INVESTIGATION, AND THEIR FINAL REPORT WAS ADOPTED NOVEMBER 21, 2008. PAGE 6 (SIX) OF THE BRIEF (PROBABLE CAUSE) STATES: PROBABLE CAUSE THE NATIONAL TRANSPORTATION SAFETY BOARD DETERMINES THAT THE PROBABLE CAUSE OF THE LEAK, EXPLOSION, AND FIRE IN PLUM BOROUGH, PENNSYLVANIA, ON MARCH 5, 2008, WAS EXCAVATION DAMAGE TO THE 2-INCH NATURAL GAS DISTRIBUTION PIPELINE THAT STRIPPED THE PIPE'S PROTECTIVE COATING AND MADE THE PIPE SUSCEPTIBLE TO CORROSION AND FAILURE. A COPY OF THE COMPLETE REPORT IS AVAILABLE ON THE NTSB WEBSITE, AND IS IDENTIFIED AS PIPELINE ACCIDENT BRIEF, DOCKET DCA-08-FP-006. | 702000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
608 | 2008-02-24 | ID | other | UNKNOWN (nan COUNTY) | AVISTA CORP | AFTER A LENGTHY INVESTIGATION, MARK AAMODT, IDAHO DEPUTY STATE FIRE MARSHAL (208-769-1447), HAS DETERMINED THE CAUSE AS UNKNOWN. | 302160 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
609 | 2008-03-10 | AK | other | UNKNOWN (MATANUSKA SUSITNA BOROUGH COUNTY) | ENSTAR NATURAL GAS CO | ENSTAR RESPONDED TO A RESIDENTIAL STRUCTURE FIRE AT 621 CREEKSIDE DR, WASILLA, AK AT 2:57 AM ON 3/11/08. THE STRUCTURE FIRE MELTED THE 1/2" CTS HDPE SERVICE LINE INSIDE THE STEEL RISER CAUSING NATURAL GAS TO VENT TO THE ATMOSPHERE. THE GAS DID NOT IGNITE. ENSTAR CREWS PINCHED OFF THE RISER AT 5:15AM. THE METER WAS LOCKED OFF AND NON CONSUMING AT THE TIME OF THE FIRE. NO ONE WAS RESIDING AT THE HOME AT THE TIME OF THE INCIDENT. THE FIRE IS UNDER INVESTIGATION BUT IT IS BELEIVED THAT NATUAL GAS DID NOT CAUSE OR CONTRIBUTE TO THE CAUSE OF FIRE. | 151050 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
610 | 2006-02-25 | NY | sabotage | UNKNOWN (nan COUNTY) | KEYSPAN ENERGY DELIVERY - NY CITY | ON FEBRUARY 25, 2006 AT APPROXIMATELY 0730 KEYSPAN ENERGY DELIVERY WAS NOTIFIED OF A GAS EXPLOSION AT BLDG 93 IN THE RED HOOK HOUSING PROJECTS CENTRE MALL BROOKLYN NY. AFTER AN INVESTIGATION IT WAS DETERMINED THERE WAS A GAS LEAK IN A 6" EAST IRON MAIN 93 FT AWAY FROM THE BUILDING INVOLVED. PRIOR TO THE EXPLOSION AN UNDERMINE CONDITION WAS DISCOVERED ASSOCIATED WITH SEWER REPLACEMENT WORK. THE SEWER WORK CROSSED THE 6" CAST IRON MAIN AND LEFT THE MAIN UNSUPPORTED. NATURAL GAS WAS DETERMINED TO HAVE MIGRATED TO THE BASEMENT OF THE BUILDING THROUGH CON EDISON ELECTRICAL DUCTS AND IGNITED WHEN A SUMP PUMP IN THE UTILITIES ROOM OF THE BASEMENT TURNED ON. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
611 | 2008-02-17 | MD | other | UNKNOWN (PRINCE GEORGES COUNTY) | BALTIMORE GAS & ELECTRIC CO | THE GENERAL DESCRIPTION OF THE PROPERTY IS THREE(3) MULTI-FAMILY APARTMENT DWELLINGS. THE INVOLVED STRUCTURES ARE DESCRIBED AS AN ENCLOSED BUILDINGS, WHICH WERE UNDER MAJOR RENOVATION. THE FIRE OCCURRED ON THE FIRST FLOOR REAR APARTMENT THEN SPREAD BEYOND THE BUILDING OF ORIGIN. THE HEAT FROM THE FIRE DAMAGED THE DIAPHRAM OF THE REGULATOR CAUSING GAS TO VENT OUT OF THE RELIEF VENT WHICH IS WHEN GAS WAS IGNITED BY THE FIRE ON THE EXTERIOR OF BUILDING. | 3200000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
612 | 2008-02-16 | MI | other | UNKNOWN (WAYNE COUNTY) | MICHIGAN CONSOLIDATED GAS CO (MICHCON) | THIS IS TO NOTIFY THAT THE INVESTIGATION IS FINAL. THERE WERE NO CHANGES TO PREVIOUS INCIDENT REPORT DATED MARCH 14, 2008. | 150000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
613 | 2008-02-10 | GA | technical failure | UNKNOWN (FULTON COUNTY) | ATLANTA GAS LIGHT CO | A COMPANY EMPLOYEE WAS ATTEMPTING TO LIGHT A HOT WATER HEATER WHEN ESCAPING GAS IGNITED CAUSING THE HOUSE TO BURN. AN INVESTIGATION DETERMINED THAT THE DELIVERY PRESSURE ON THE HOUSE PIPING WAS EXCESSIVE. THIS WAS DUE TO A REGULATOR NOT BEING INSTALLED ON THE METER SET BY A COMPANY CONTRACTOR PURSUANT TO DIRECTION FROM THE COMPANY. THIS REGULATOR INSTALLATION WAS SUPPOSED TO HAVE BEEN DONE IN CONJUNCTION WITH A RECENTLY COMPLETED MAIN RENEWAL PROJECT FOR THAT AREA. THE MAIN SYSTEM WAS A LOW PRESSURE (LP) SYSTEM PRIOR TO THE RENEWAL AND A MEDIUM HIGH PRESSURE (MHP) SYSTEM AFTERWARDS. | 220000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
614 | 2007-05-25 | MO | maintenance | UNKNOWN (JACKSON COUNTY) | MISSOURI GAS ENERGY | CREW DIGGING TO EXPOSE GAS LEAK OVER 24 INCH CAST IRON MAIN. TOP OF PIPE WAS EXPOSED WHEN THE PIPE BEGAN TO COME APART CAUSING DEBRIS TO HIT 4 EMPLOYEES. TWO EMPLOYEES WERE HOSPITALIZED OVERNIGHT AND THE OTHER TWO TREATED AND RELEASED. NO IGNITION. NO PROCEDURE VIOLATIONS. | 103300 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
615 | 2007-12-07 | MS | other | UNKNOWN (COAHOMA COUNTY) | ATMOS ENERGY CORPORATION - MISSISSIPPI DIVISION | WE HAVE ENGAGED SERVICES OF SEVERAL EXPERTS IN THE INVESTIGATION OF THIS INCIDENT, INCLUDING A METALLURGIST FOR ANALYSIS OF A BROKEN GAS MAIN FOUND IN A NEARBY ALLEY MORE THAN THREE DAYS AFTER THE INCIDENT OCCURRED. THE DEBRIS AND BURN PATTERNS AT THE SCENE DO NOT APPEAR TO BE CONSISTENT WITH A NATURAL GAS FIRE OR EXPLOSION. THE METALLURGIST'S REPORT ON THE BROKEN GAS PIPE FOUND SUBSEQUENT TO THE INCIDENT CONCLUDES THAT THE BREAK WAS A RESULT OF VIBRATIONS CAUSED BY THE EXPLOSION. UPON CONSIDERATION OF THE RESULTS OF EXPERTS' INVESTIGATIONS, IT DOES NOT APPEAR THAT NATURAL GAS WAS THE CAUSE OF THIS INCIDENT. | 350 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
616 | 2008-02-23 | CA | other | UNKNOWN (RIVERSIDE COUNTY) | SOUTHERN CALIFORNIA GAS CO | ON FEBRUARY 23, 2008, A STRUCTURE FIRE OCCURRED AT THE ABOVE ADDRESS. THE BUILDING WAS SEVERELY DAMAGED FROM FIRE DAMAGE. THE GAS METER SET ASSEMBLY WAS FOUND TO BE MELTED FROM THE INTENSE HEAT. THIS INCIDENT BECAME REPORTABLE WHEN IT WAS DETERMINED THAT TOTAL VALUE OF STRUCTURE LOSS EXCEEDED $50,000 THE GAS SERVICE WAS SHUT OFF AND REPAIRS PERFORMED. DAMAGE TO METER SET ASSEMBLY APPEARS TO BE THE RESULT OF INTENSE HEAT FROM THE STRUCTURE FIRE. INVESTIGATION OF CUSTOMER FACILITIES IS ONGOING. | 101000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
617 | 2008-02-23 | MI | sabotage | UNKNOWN (OAKLAND COUNTY) | CONSUMERS ENERGY CO | GAS EXPLOSION AT VACANT HOME. A GAS SERVICE WORKER WAS THE FIRST RESPONDER TO THE SCENE. UPON ARRIVAL, THE FERNDALE FIRE DEPARTMENT KEPT THE FIRE CONTROL. A DISTRIBUTION CREW WAS CALLED IN TO RETIRE THE SERVICE. THE CREW CLAMPED 2" STEEL MEDIUM PRESSURE MAIN LEAK. TWO NEXT DOOR NEIGHBORS WERE SEEN BY THE EMERGENCY MEDICAL PERSONNEL. NO INJURIES OR FATALATIES. THE INCIDENT IS STILL BEING INVESTIGATED BY A COMPANY INVESTIGATOR. INVESTIGATION AFTER THE INCIDENT CONSISTED OF EXCAVATING AND EXAMINING THE 2 INCH STEEL MEDIUM PRESSURE GAS MAIN. THE EXCAVATION AND EXAMINATION WAS PERFORMED ON 03/18/2008, AND WAS ATTENDED BY A CONSUMERS ENERGY LEGAL INVESTIGATOR, A MICHIGAN PUBLIC SERVICE COMMISSION GAS SAFETY ENGINEER, AN INSURANCE INVESTIGATOR AND A CONSUMERS ENERGY CREW. THE EXAMINATION REVEALED THAT THE 2 INCH STEEL MEDIUM PRESSURE MAIN HAD EXPERIENCED SIGNIFICANT THIRD PARTY DAMAGE. THE DAMAGE LIKELY OCCURRED DURING INSTALLATION OF A STORM SEWER WHICH CROSSES BENEATH THE GAS MAIN. THE GAS MAIN HAD MARKS AND WAS BOWED BY THE THIRD PARTY DAMAGE. THE ROYAL OAK TOWNSHIP AND OAKLAND COUNTY WERE NOT ABLE TO FIND ANY RECORDS OF THE STORTM SEWER INSTALLATION. DRAWINGS INDICATE IT WAS LIKELY INSTALLED IN THE 1960S OR 1970S. | 55000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
618 | 2008-02-26 | AL | other | UNKNOWN (JEFFERSON COUNTY) | ALABAMA GAS CORPORATION | AT THE REQUEST OF THE LOCAL FIRE DEPARTMENT, OPERATOR RESPONDED TO A HOUSE FIRE WHICH HAD BEEN REPORTED AT THE GAS METER. THE FIRE WAS REPORTED SHORTLY AFTER RESTORATION OF ELECTRIC SERVICE IN THE GENERAL AREA FOLLOWING A POWER OUTAGE. THE FIRE MAY HAVE RESULTED FROM A POWER FAULT NEAR THE METER BUT IT IS STILL BEING INVESTIGATED. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
619 | 2007-04-20 | MD | sabotage | UNKNOWN (BALTIMORE COUNTY) | BALTIMORE GAS & ELECTRIC CO |  | 512044 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
620 | 2008-02-28 | VA | other | UNKNOWN (LOUDOUN COUNTY) | WASHINGTON GAS LIGHT CO | WASHINGTON GAS RESPONDED TO A HOUSE FIRE AT THE REQUEST OF THE LOUDOUN COUNTY FIRE DEPARTMENT. THE METER AND REGULATOR HAD BEEN COMPROMISED BY HEAT EXPOSURE CAUSING A RELEASE OF GAS. THE GAS MAIN WAS VALVED OFF AND SERVICE WAS INTERRUPTED TO SEVEN RESIDENCES. A SUBSURFACE LEAK INVESTIGATION WAS CONDUCTED AND NO LEAKS WERE FOUND. SERVICES TO 46026 AND 46024 BAYSWATER TERRACE WERE CAPPED OFF AT THE MAIN. THE MAIN WAS PRESSURE TESTED PRIOR TO BEING PLACED BACK INTO SERVICE. THE FIRE IS BELIEVED TO HAVE STARTED IN THE DETACHED GARAGE AND HAS BEEN RULED UNDETERMINED BY THE LOUDOUN COUNTY FIRE MARSHALL. | 455100 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
621 | 2008-02-26 | MI | other | UNKNOWN (KENT COUNTY) | MICHIGAN CONSOLIDATED GAS CO (MICHCON) | AT 14:56 ON FEBRUARY 26, 2008, MICHCON RECEIVED A REPORT OF A GAS LEAK INSIDE A TWO-STORY COMMERCIAL BUILDING AT 1500-1502 WEALTHY STREET SE, ON THE SOUTHEAST CORNER OF WEALTHY AND ETHEL AVENUE. THE CALLER REPORTED A STRONG ODOR OF GAS, PARTICULARLY IN THE BASEMENT OF THE BUILDING. A MICHCON TECHNICIAN WAS DISPATCHED TO THE ADDRESS AT 14:59, AND ARRIVED AT 15:21. A SECOND GAS LEAK REPORT WAS RECEIVED AT 15:04 FOR THE SAME BUILDING; THIS CALLER ALSO REPORTED A STRONG GAS ODOR IN THE BASEMENT BUT ALSO AN ODOR OF GAS IN HIS BUSINESS ON THE SECOND FLOOR. UPON ARRIVAL, THE MICHCON TECHNICIAN ENTERED THE FIRST FLOOR OF THE BUILDING AND BEGAN CHECKING FOR THE PRESENCE OF COMBUSTIBLE GAS. FINDING NO COMBUSTIBLE GAS READINGS ON THE FIRST FLOOR, THE TECHNICIAN CHECKED AROUND THE DOORWAY LEADING TO THE BASEMENT OF THE BUILDING TO CONTINUE HIS INVESTIGATION IN THE BASEMENT WHERE THE ODOR INTENSITY HAD BEEN REPORTED AS BEING STRONGEST. THE BASEMENT DOOR AT THE TOP OF THE FIRST FLOOR STAIRWELL WAS CLOSED, AND THE TECHNICIAN CHECKED FOR THE PRESENCE OF COMBUSTIBLE GAS AROUND THE FRAME AND AT THE BASE OF THE CLOSED DOOR. FINDING NO INDICATIONS OF COMBUSTIBLE GAS, THE TECHNICIAN OPENED THE DOOR AND IMMEDIATELY HIS GAS DETECTOR REGISTERED A READING OF 4% GAS CONCENTRATION AND RISING. WHILE TURNING TO EXIT THE BUILDING, THE TECHNICIAN WAS STRUCK BY A RUSH OF HEATED GASES AND DEBRIS. AN EXPLOSION LEVELED THE TWO-STORY STRUCTURE, DAMAGING NEARBY BUILDINGS AND STREWING DEBRIS ACROSS THE INTERSECTION OF WEALTHY AND ETHEL. A REPORT WAS RECEIVED FROM THE GRAND RAPIDS FIRE DEPARTMENT AT 15:40 ADVISING MICHCON THAT AN EXPLOSION HAD OCCURRED ON WEALTHY STREET, BUT THAT THEY HAD NO ADDRESS. MICHCON CREWS BEGAN ARRIVING ON THE SCENE AT 15:48. COMBUSTIBLE GAS READINGS WERE FOUND IN SEVERAL ADJACENT BUILDINGS AND IN SOME OF THE SEWER LINES IN WEALTHY STREET EAST AND WEST OF ETHEL. HIGHEST CONCENTRATIONS OF COMBUSTIBLE GAS WERE FOUND NEAR THE PARKING AREA ALONG THE EAST SIDE OF THE BUILDING AND ALONG THE WALLS OF THE BUILDINGS ON THE NORTH SIDE OF WEALTHY STREET, ACROSS FROM 1500-1502 WEALTHY. MICHCON FOUND A CIRCUMFERENTIAL BREAK WITH APPROXIMATELY 1/4-INCH OF SEPARATION BETWEEN THE PIPE ENDS ON A 6” CAST IRON MAIN IN WEALTHY STREET, WHICH WAS SUCCESSFULLY REPAIRED AT 21:14 USING A BOLT-ON STAINLESS STEEL CLAMP. AT 23:30, MICHCON SHUT DOWN THE MAINS IN THE INTERSECTION AS A PRECAUTIONARY MEASURE. THE 1-INCH COPPER SERVICE LINE TO 1500-1502 WEALTHY WAS DISCONNECTED FROM THE MAIN AT 23:36, BUT DUE TO CONTINUING FIREFIGHTING ACTIVITIES AND THE SUBSTANTIAL DEBRIS MICHCON WAS UNABLE TO LEAK TEST OR RECOVER THE REMNANTS OF THE SERVICE LINE AT THAT TIME. MICHCON GAVE TELEPHONIC NOTICE TO THE MICHIGAN PUBLIC SERVICE COMMISSION IN LANSING AT 16:31 AND TO THE NATIONAL RESPONSE CENTER AT 16:44. FIVE PEOPLE, INCLUDING FOUR BUILDING OCCUPANTS AND MICHCON’S TECHNICIAN, WERE TRANSPORTED TO LOCAL HOSPITALS. MICHCON’S SERVICE TECHNICIAN WAS ADMITTED AND THE REST WERE RELEASED LATER THAT DAY. MICHCON PERFORMED A SUCCESSFUL LEAK TEST OF THE SERVICE LINE AT NORMAL 2 PSIG OPERATING PRESSURE ON MARCH 20, 2008, INCLUDING APPROXIMATELY 20 FEET OF 1-INCH COPPER PIPE BETWEEN THE MAIN AND THE BUILDING, 2 FEET OF 1-INCH COATED STEEL PIPE WHICH SERVED AS THE BUILDING ENTRANCE, AND A 1-INCH COUPLING OUTSIDE THE BUILDING WALL CONNECTING THE TWO PIPING MATERIALS. NO LEAKAGE WAS FOUND ON THE SERVICE LINE. THE CAUSE OF THE EXPLOSION AND THE SOURCE OF THE GAS HAVE NEVER BEEN DETERMINED. ON MARCH 20, 2008, A SEGMENT OF THE BROKEN 6-INCH CAST IRON MAIN FOUND ON FEBRUARY 26, 2008, INCLUDING THE CIRCUMFERENTIAL FRACTURE SEALED BY THE STAINLESS STEEL CLAMP, WAS CUT AND REMOVED FROM WEALTHY STREET. LABORATORY EXAMINATION OF THE 6-INCH PIPE REMOVED FROM THE MAIN IN FRONT OF 1500-1502 WEALTHY STREET SE REVEALED IT TO BE GREY CAST IRON WITH A COMPLETE CIRCUMFERENTIAL CRACK, THE RESULT OF A SINGLE OVERLOAD EVENT. THE FRACTURE FACES EXHIBITED GRAPHITIC CORROSION AT SEVERAL LOCATIONS UP TO DEPTHS OF 70 TO 80 PERCENT OF THE PIPE WALL THICKNESS. THE REMAINING WALL THICKNESS WAS SUFFICIENT TO MAINTAIN THE INTEGRITY OF THE PIPE UNDER NORMAL OPERATING CONDITIONS. THE CONDITION OF THE FRACTURE FACES RULED OUT THE POSSIBILITY THAT THE BREAK OCCURRED WEEKS OR MONTHS PRIOR TO THE EXPLOSION AT 1500-1502 WEALTHY, BUT METALLURGICAL TESTING WAS UNABLE TO ESTABLISH WHETHER THE BREAK RESULTED FROM THE FORCE OF THE EXPLOSION OR IF IT OCCURRED JUST PRIOR TO THE EXPLOSION. BOTH POSSIBILITIES WERE DETERMINED TO BE EQUALLY LIKELY. MICHCON AND SEVERAL OTHER INVESTIGATORY ENTITIES, INCLUDING FIRE OFFICIALS, INSURANCE ADJUSTERS, AND FAILURE ANALYSTS, WERE UNABLE TO EVALUATE THE POSSIBILITY THAT NATURAL GAS HAD LEAKED FROM FUEL PIPING INSIDE THE BUILDING AT 1500-1502 WEALTHY. DEBRIS FROM THE EXPLOSION WAS PUSHED FROM THE SURROUNDING STREETS AND ALLEYS BACK INTO THE BASEMENT WITHIN HOURS OF THE EXPLOSION, DAMAGING OR DESTROYING THE BUILDING FUEL PIPING IN THE PROCESS. NONE OF THIS PIPING COULD BE EXAMINED TO DETERMINE IF IT COULD HAVE BEEN A POSSIBLE SOURCE OF A GAS LEAK INTO THE BASEMENT OF THE BUILDING, NOR COULD AN IGNITION SOURCE BE DETERMINED. HOWEVER, ANALYSIS DID CONFIRM THAT A RELATIVELY MINOR LEAK FROM THE CUSTOMER FUEL PIPING INSIDE THE BUILDING COULD HAVE PRODUCED AN EXPLOSIVE ENVIRONMENT IN THE BASEMENT WITHIN HOURS. MICHCON WAS NOT ABLE TO DETERMINE WHETHER THE FRACTURE OF THE 6-INCH CAST IRON PIPE OCCURRED PRIOR TO OR AS A RESULT OF THE EXPLOSION AT 1500-1502 WEALTHY STREET SE ON FEBRUARY 26, 2008. THEREFORE, MICHCON CANNOT DETERMINE WHETHER THE EXPLOSION WAS CAUSED BY NATURAL GAS LEAKING FROM THE CAST IRON MAIN OR, AS HAS BEEN SUGGESTED BY SOME FIRE AND EXPLOSION INVESTIGATORS, THE EXPLOSION RESULTED FROM THE IGNITION OF NATURAL GAS LEAKING FROM A CUSTOMER’S FUEL LINE INSIDE THE BUILDING. BOTH POTENTIAL CAUSES WERE DEEMED POSSIBLE; NEITHER COULD BE ELIMINATED. THE CAUSE OF THIS INCIDENT HAS BEEN CLASSIFIED AS “UNKNOWN.” | 1035900 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
622 | 2006-07-27 | IA | other | UNKNOWN (HENRY COUNTY) | WINFIELD MUNICIPAL GAS | CAR OUT OF CONTROL HIT GAS METER + BROKE IT OFF AFTER SHUT OFF VALVE. A FIRE STARTED AT FOUR MINUTES AFTER ACCIDENT + TOTALLY DESTROYED THE CAR + HEAVY DAMAGES TO THE HOUSE. | 151044 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
623 | 2006-07-27 | MS | other | UNKNOWN (HINDS COUNTY) | ATMOS ENERGY CORPORATION - MISSISSIPPI DIVISION | CAR RAN OFF ROAD AND STRUCK REGULATOR STATION. STATION WAS LEVELED AND THEN GA INGNITED. DRIVER ESCAPED UNINJURED. A SIX THOUSAND FEET SECTION OF 12" AND 8" H.P. STEEL MAIN HAD TO BE ISOLATED AND SEVERAL REGULATOR STATIONS AND INPUT STATIONS REQUIRED SHUT IN. EMS AND FIRE DEPT. EVACUATED APPROXIMATELY 100 PEOPLE IN THE AREA FOR PRECAUTIONARY REASONS. ONCE GAS SUPPLY WAS STOPPED, THE LINE WAS EXCAVATED AND A 2" WELDED BALL VALVE WAS INSTALLED AND CAPPED ON THE UPSTREAM SIDE OF THE DESTROYED REGULATOR STATION. PIPE WAS EXAMINED FOR OTHER DAMAGE; NONE FOUND. 12" PIPELINE WAS PURGED AND REINSTATED. A TOTAL OF EIGHT CUSTOMERS WERE INTERRUPTED AND THERE WERE NO INJURIES. FOLLOW UP LEAK INVESTIGATION ON 8/16/06; NO LEAKS FOUND. | 22302 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
624 | 2008-03-12 | CA | sabotage | UNKNOWN (LOS ANGELES COUNTY) | SOUTHERN CALIFORNIA GAS CO | ON MARCH 12, 2008, AN EIGHTH INCH PE MAIN WAS DAMAGED BY A CONTRACTOR INSTALLING AN ELECTRICAL VAULT WITH A BACKHOE. THERE WAS NO USA REQUEST FOR THIS WORK. NO FIRE OR INJURIES RESULTED FROM THE ESCAPING GAS. THE LINE WAS REPAIRED, AND NO CUSTOMERS WERE OUT OF SERVICE. TO ELIMINATE OUTAGES TO LARGE CUSTOMERS, THE LINE WAS ALLOWED TO BLOW IN A CONTROLLED MANNER WHILE PRESSURE CONTROL FITTINGS AND BYPASS WERE INSTALLED. THIS INCIDENT BECAME REPORTABLE TO THE CPUC AND DOT WHEN IT WAS DETERMINED THAT TOTAL COSTS ASSOCIATED WITH THIS INCIDENT COULD EXCEED $50,000. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
625 | 2008-03-12 | MN | leaks and spills | UNKNOWN (OLMSTED COUNTY) | MINNESOTA ENERGY RESOURCES CORPORATION | LEAK FROM CRACK IN ALDYL A 4" TEE. INCIDENT OCCURRED FROM MIGRATION OF GAS 3 HOUSES AWAY FROM LEAK. FITTING HAS BEEN SENT IN FOR TESTING. SUPPLEMENTAL REPORT TO FOLLOW WHEN TEST RESULTS ARE BACK. 2/13/2012: SEE APPARENT CAUSE ANALYSIS BY THIRD PARTY LAB IN PART F7. 6/12/2012: CIRCUMFERENTIAL CRACK APPEARED IN A 4-INCH SOCKET FUSED ALDYL A TEE. ANALYSIS OF THE TEE SHOWED THAT THE CRACK INITIATED AT THE INSIDE DIAMETER OF THE TEE IN A BRITTLE FASHION. ALTHOUGH LAB ANALYSIS CONCLUDED THAT THE PLASTIC DID NOT EXHIBIT ANY DEGRADATION OR OXIDATION THE CRACK DID APPEAR TO BE TYPICAL OF EARLY PLASTIC BRITTLE FAILURE. THE TEE DID NOT INCLUDE A DATE STAMP THEREFORE IT COULD NOT BE DETERMINED IF THE TEE WAS MANUFACTURED PRE 1973 POSSIBLY SUSCEPTIBLE TO LOW DUCTILE INNER WALL PROPERTIES. IT WAS ALSO NOTED THAT THERE WAS MISALIGNMENT OF THE FUSION THAT MAY HAVE CONTRIBUTED TO THE FAILURE. | 325000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
626 | 2008-03-16 | UT | other | UNKNOWN (SALT LAKE COUNTY) | QUESTAR GAS COMPANY | A 1999 CHEVROLET TAHOE WAS TRAVELLING EAST ON 2700 SOUTH IN SALT LAKE COUNTY, UTAH, WENT THROUGH AN INTERSECTION AT 8000 WEST, WHERE 2700 SOUTH ENDS, STRIKING A POWER POLE THAT WAS LOCATED ON THE EAST SIDE OF 8000 WEST AND THEN HITTING A QUESTAR GAS COMPANY REGULATOR STATION LOCATED JUST SOUTH OF 2700 SOUTH ON THE EAST SIDE OF 8000 WEST, DAMAGING THE NORTH SIDE OF THE METAL BUILDING AND BRAKING A 1" RELIEF VALVE INSIDE THE BUILDING. THE DRIVER WAS TAKEN TO A HOSPITAL DUE TO INJURIES SUSTAINED IN THE VEHICLE CRASH. THE DAMAGES TO THE REGULATOR STATION WAS LIMITED TO THE BUILDING AND THE 1" RELIEF VALVE (FISHER 289HH). | 10000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
627 | 2007-05-09 | KY | sabotage | UNKNOWN (HENDERSON COUNTY) | HENDERSON MUNICIPAL GAS | A RELATIVE OF HOMEOWNER (RESIDENTIAL NEIGHBORHOOD) RENTED A WALK BEHIND TRENCHER TO PERFORM SMALL DIAMETER WATER LINE INSTALLATION. DURING THE COURSE OF TRENCHING, INDIVIDUAL CUT THROUGH ONE INCH POLYETHENE SERVICE LINE IN VERY NEAR PROXIMITY TO METER. OPERATOR OF TRENCHER SUSPECTED CUTTING GAS LINE AND TURNED TRENCHER OFF. AT THAT TIME, IGNITION OCCURRED, FLASH BURNING INDIVIDUAL ON ARMS AND ENGULFING TRENCHER AND EVENTUALLY CAUSING THE RESIDENCE TO CATCH FIRE. WEATHER CONDITIONS WERE SUNNY AND WARM. NO LOCATES WERE REQUESTED. | 73474 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
628 | 2008-03-31 | ID | other | UNKNOWN (BONNERS COUNTY) | AVISTA CORP | FIRE MARSHALL'S REPORT IS NOT PREPARED AT THIS TIME. HEAVY SNOW WAS PRESENT IN SANDPOINT AT THIS TIME. SHOW COULD HAVE FALLEN FROM ROOF ONTO METER CAUSING METER TO LEAK GAS, FIND IGNITION SOURCE AND CAUSE FIRE, OR FIRE CAUSED BY OTHER MEANS COULD HAVE CAUSED SNOW TO MELT FROM ROOF AND FALL ON METER CAUSING LEAK. INCONCLUSIVE AT THIS TIME. 5/04/2009 -- FIRE MARSHALL SUBMITTED "REPORT OF INVESTIGATION" ON JUNE 5, 2008. IT WAS DETERMINED THAT GAS LEAK WAS CAUSED BY SNOW FALLING ONTO METER AS SUGGESTED ABOVE. GAS MIGRATED INTO STRUCTURE AND WAS IGNITED BY GAS WATER HEATER. SUBMITTING AS "FINAL REPORT" | 201850 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
629 | 2008-03-19 | NE | technical failure | UNKNOWN (GAGE COUNTY) | AQUILA NETWORKS | ON MARCH 19, AQUILA PERSONNEL WERE PERFORMING ANNUAL MAINTENANCE TASK ON AN 8" "KEY VALVE¿ AT 8TH & BELL. VALVE MAINTENANCE WAS NEEDED BECAUSE OF A BROKEN GREASE STEM, WAS TURNED TO OFF POSITION TO PERFORM WORK, WHEN WORK WAS COMPLETED, THE VALVE WAS NOT RETURNED TO "ON" POSITION. AT APPROXIMATELY 06:00 HOURS MARCH 20, 2008, AQUILA PERSONNEL WERE ALERTED TO NUMEROUS CALLS OF NO HEAT. AT APPROXIMATELY 07:20 HOURS RICK SCHWARTZ WAS NOTIFIED THAT PRESSURES IN THE SYSTEM HAD "DROPPED" TO A POINT WHERE SAFETY WAS COMPROMISED. CONTACTS WITH ENGINEERING INDICATED WHERE PROBLEM MAY BE VALVE #4 OR VALVE # 19. VALVE #19 WAS VERIFIED AS BEING IN THE "OFF" POSITION. AFTER CONSULTATION, THE DECISION WAS MADE TO START SHUTTING THE SYSTEM DOWN. (APPROXIMATELY 09:00 ). APPROXIMATELY 09:30 DEPUTY ARNIE BATES FROM THE NEBRASKA STATE FIRE MARSHAL'S OFFICE WAS NOTIFIED OF THE INCIDENT. AT APPROXIMATELY 10:15 ON 3/19/08, THE NRC WAS NOTIFIED OF INCIDENT. APPROXIMATELY 4500 SERVICES OF 4800 SERVICES WERE INTERRUPTED. 31 DAY CHARTS (DRS 1 & 9) INDICATE THAT AT APPROXIMATELY 1500 HOURS 3/19/08 PRESSURE WAS BETWEEN 65 AND 70 PSIG, SHORTLY AFTER 1500 HOURS PRESSURES THE HP LINE BEGAN TO DECLINE UNTIL APPROXIMATELY 2400 HOURS WHEN PRESSURES LEVELED OUT AT APPROXIMATELY 50 PSIG, THIS PRESSURE WAS ERRATIC BUT WITHIN 5 PSIG DEFERENTIAL UNTIL 0600 HOURS 3/20/08 WHEN A NOTICEABLE DROP IN PRESSURE TO NEAR ZERO BY 0900 CUSTOMER METER SERVICE VALVE SHUT OFF STARTED APPROXIMATELY 1000 HOURS 3/20/08 ALL METERS ACCOUNTED FOR BY 0045 HOURS 03/21/08. PRESSURIZING SYSTEM WAS COMPLETED AT APPROXIMATELY 0132 HOURS 03/21/08, AND RE-LITES STARTED SHORTLY THEREAFTER. BY EVENING ON MARCH 22, 2008 APPROXIMATELY 99% OF CUSTOMERS HAD SERVICE RESTORED. | 156851 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
630 | 2008-03-22 | NM | other | UNKNOWN (BERNALLILO COUNTY) | PUBLIC SERVICE COMPANY OF NEW MEXICO - GAS SVCS | A FIRE STARTED IN A SHED LOCATED DIRECTLY BEHIND A COMMERCIAL BUILDING. THE FIRE SPREAD TO OTHER FLAMMABLE MATERIALS WHICH EVENTUALLY STARTED THE COMMERCIAL BUILDING ON FIRE. THE GAS METER WAS LOCATED ON THE BACK SIDE OF THE COMMERCIAL BUILDING. THE COMMERCIAL BUILDING FIRE MELTED THE METER WHICH CAUSED GAS TO BE RELEASED INTO THE ATMOSPHERE. PNM RESPONDED BY SHUTTING THE GAS OFF AT THE METER VALVE AND PINCHING AND CAPPING THE SERVICE LINE. ON MARCH 27, 2008, PNM PERFORMED A PRESSURE TEST OF THE SERVICE LINE, WHICH WAS OBSERVED BY THE NEW MEXICO PIPELINE SAFETY BUREAU, AND NO LEAKS WERE DETECTED. | 80000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
631 | 2008-03-21 | CA | natural disasters | UNKNOWN (EL DORADO COUNTY) | SOUTHWEST GAS CORP | PRELIMINARY INVESTIGATION INDICATES THAT A SLAB OF SNOW FELL ON TOP OF THE METER SET ASSEMBLY FROM A STRUCTURE'S ROOF, BREAKING THE RISER BELOW THE STOP COCK. THE ESCAPING GAS IGNITED. SOUTHWEST GAS IS STILL INVESTIGATING THE ROOT CAUSE OF THE INCIDENT TO DETERMINE IF THE RISER BREAK WAS THE PRIMARY OR SECONDARY CAUSE OF THE STRUCTURE FIRE AND WILL BE FILING A SUPPLEMENTAL REPORT ONCE THE INVESTIGATION IS COMPLETE. ***SUPPLEMENTAL*** SOUTHWEST GAS HAS DETERMINED THAT THE RISER BREAK WAS THE PRIMARY CAUSE OF THE STRUCTURE FIRE. | 130660 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
632 | 2008-03-29 | CA | other | UNKNOWN (SANTA CLARA COUNTY) | PACIFIC GAS & ELECTRIC CO | A CONTRACTOR HAD BEEN UPGRADING AN ELECTRIC PANEL FOR A RESIDENTIAL CUSTOMER. NO ONE WAS DIGGING AT THE TIME OF THE INCIDENT, HOWEVER THE UNDERGROUND UTILITIES WERE EXPOSED. THE PROBABLE CAUSE WAS THAT THE CONTRACTOR HAD NICKED THE ELECTRIC SERVICE LINE AT A PREVIOUS DATE. THE DAMAGE TO THE ELECTRIC SERVICE, COMBINED WITH MOISTURE MAY HAVE CAUSED THE ELECTRIC LINE TO ARC. THE ARC APPEARS TO HAVE MELTED THE NEARBY 1/2-INCH PLASTIC GAS SERVICE CAUSING ESCAPING GAS AND A FIRE. AS A RESULT, THE FIRE DAMAGED THE CUSTOMER'S GARAGE, A 20-FOOT SECTION OF 1/2-INCH PLASTIC SERVICE, GAS REGULATOR, AND METER. SERVICE WILL BE RESTORED AT A LATER DATE FOLLOWING REPAIRS TO THE GARAGE AND GAS FACILITIES. [NOTE: THIS REPORT ALONG WITH A COPY OF THE 7100.1 FORM WAS SUBMITTED TO THE CALIFORNIA CPUC ON 4/28/08] | 103000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
633 | 2007-05-04 | KS | natural disasters | UNKNOWN (nan COUNTY) | KANSAS GAS SERVICE | ON MAY 4, 2007 AT APPROXIMATELY 2230 HRS A MILE WIDE TORNADO HIT AND DESTROYED 90% TO 95% OF THE TOWN OF GREENSBURG, KS. MULTIPLE GAS FACILITIES WERE DAMAGED OR DESTROYED. THE GAS WAS SHUT OFF TO THE TOWN AT APPROXIMATELY 0000 HRS ON 5/5/07. DUE TO THE NATURE OF THE EMERGENCY DISCOVERY THAT SYSTEM DAMAGES WERE GREATER THAN $50,000 DID NOT OCCUR UNTIL MAY 8, 2007. THERE WERE NO EXPLOSIONS OR FIRES NOR WERE THERE ANY INJURIES OR FATALITIES ASSOCIATED WITH THE RELEASE OF GAS CAUSED BY THE TORNADO. | 1606000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
634 | 2008-04-02 | VA | other | UNKNOWN (FREDERICK COUNTY) | SHENANDOAH GAS CO | SHENANDOAH GAS RESPONDED TO A HOUSE FIRE AT 101 COOPWORTH COURT, STEPHENS CITY, VA ON 4/2/08. THE GAS WAS CONFIRMED TO BE OFF AT 15:12. SHENANDOAH GAS REMOVED THE METER BUILD-UP AND SECURED IT AS EVIDENCE. THE SERVICE WAS CAPPED OFF AT THE MAIN. A PRESSURE TEST OF THE SERVICE WAS CONDUCTED AND THE SERVICE HELD THE TEST. A LEAK SURVEY WAS CONDUCTED AND NO INDICATIONS WERE FOUND. ODORANT SAMPLES WERE TAKEN AND DETERMINED TO BE APPROPRIATE. PER WITNESS STATEMENTS, THE FIRE STARTED AT REAR OF THE HOUSE AS A RESULT OF DISCARDED SMOKING MATERIALS. THE HOUSE CAUGHT FIRE AND LATER ENGULFED THE METER BUILD-UP. | 151100 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
635 | 2008-04-07 | CO | other | UNKNOWN (nan COUNTY) | ATMOS ENERGY CORPORATION, COLORADO - KANSAS DIVISION | A THREADED FITTING SEPERATED ON THE UPSTREAM SIDE OF THE SERVICE VALVE ABOVE GROUND. THIS RELEASE OF GAS IGNITED, AND BURNED THE PREMISE. | 61000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
636 | 2008-04-12 | CA | other | UNKNOWN (ALAMEDA COUNTY) | PACIFIC GAS & ELECTRIC CO | TWO CARS SUSPECTED TO BE IN AN ILLEGAL "SIDE SHOW" (RECKLESS EXHIBITION DRIVING) CRASHED INTO HOME. ONE CAR STRUCK THE GAS METER SET AND RISER, RELEASING GAS. THE DRIVERS ABANDONED THEIR CARS AND FLED THE SCENE. THE GAS IGNITED AND CAUGHT THE HOME ON FIRE, COMPLETELY DESTROYING IT. KGO-TV CHANNEL 7 ARRIVED ON SCENE AT 0547 HOURS. GAS AND ELECRIC SERVICE TO THE RESIDENCE WAS DISCONNECTED AND WILL BE RESTORED WHEN THE STRUCTURE IS RE-BUILT. | 155000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
637 | 2008-04-07 | VA | other | UNKNOWN (CHESAPEAKE CITY COUNTY) | VIRGINIA NATURAL GAS | AT APPROXIMATELY 2:12 AM ON 04/07/08, AN AUTOMOBILE TRAVELING SOUTH ON WILLIAMSON STREET IN CHESAPEAKE, VIRGINIA LOST CONTROL AND CRASHED THROUGH A ROAD BARRICADE NEAR THE INTERSECTION OF WILLIAMSON STREET AND LINSTER STREET. THE PURPOSE OF THE BARRICADE WAS TO BLOCK VEHICULAR TRAFFIC FROM USING A BACK ENTRANCE TO THE HUNTER'S POINT APARTMENT COMPLEX (4200 REID STREET, CHESAPEAKE). THE WOOD BARRICADE CONSISTED OF SIX WOODEN 8" X 8" POSTS THAT WERE BURIED IN CONCRETE. THE VEHICLE WAS TRAVELING AT A HIGH RATE OF SPEED AND CRASHED THROUGH THE BARRICADE SHEARING ONE OF THE WOOD POSTS, AND CONTINUED ANOTHER 50' AND CRASHED THROUGH THE METER SET PROTECTIVE BOLLARDS AND DESTROYED THE METER SET AT THE APARTMENT COMPLEX. THE METER SET WAS PROTECTED BY THREE 10" DIAMETER STEEL PIPES WHICH WERE FILLED AND BURIED IN CONCRETE AND PLACED APPROXIMATELY 5-FEET APART. THE VEHICLE PLOWED OVER ONE OF THE PROTECTIVE BOLLARDS AND HIT THE AL-10,000 METER AND THE ASSOCIATED 2" STEEL INLET AND OUTLET PIPING. THE VEHICLE COLLISIOIN WITH THE METER SET CAUSED A RELEASE OF GAS AND IGNITED A FIRE. THE VEHICLE AND THE APARTMENT BUILDING ENGULFED IN FLAMES, DAMAGING 8-APARTMENTS. VNG CREWS CLOSED AN UPSTREAM 2" VALVE WHICH ISOLATED THE 2" STEEL SERVICE TO THE APARTMENT COMPLEX. THERE WERE NO INJURIES CAUSING HOSPITALIZATION NOR FATALATIES CAUSED BY THE INCIDENT. | 524100 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
638 | 2008-04-02 | SC | sabotage | UNKNOWN (ANDERSVILLE COUNTY) | FORT HILL NATURAL GAS AUTH | WATER CONTRACTOR MISCALCULATED HIS MEASUREMENTS FOR THE BORE. WHEN PIPE WAS DAMAGED THE GAS MIGRATED BACK THROUGH THE BORE HOLE AND WAS IGNITED BY THE BORING MACHINE. | 26293 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
639 | 2008-03-30 | ND | other | UNKNOWN (BURLEIGHT COUNTY) | MONTANA - DAKOTA UTILITIES CO | A HOME WAS DESTROYED BY FIRE. NO ONE WAS HOME AND DUE TO THE HIGH WINDS (IN EXCESS OF 40 MPH), THE FIRE RAPIDLY PROGRESSED AND MELTED THE ALUMINUM METER AND REGULATOR. THE SERVICE LINE WAS DUG UP AND SQUEEZED OFF TO CONTROL THE RELEASE OF GAS. LATER, THE PORTION OF THE SERVICE THAT HAD BEEN CUT OFF WAS PRESSURE TESTED TO 100 PSIG WITH NO INDICATION OF LEAKAGE. THE FIRE CHIEF RULED THE CAUSE OF THE FIRE AS UNDETERMINED. WE BELIEVE THAT JURISDICTIONAL PIPING WAS NOT INVOLVED AND THE RELEASE OF THE NATURAL GAS AND IGNITION WAS THE DIRECT RESULT OF THE BUILDING FIRE. FIRE OFFICIALS WERE UNABLE TO DETERMINE THE AREA OF ORIGIN, HEAT SOURCE, ITEM FIRST IGNITED, TYPE OF MATERIAL, OR CAUSE OF IGNITION. | 250250 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
640 | 2008-04-14 | CA | other | UNKNOWN (SAN JOAQUIN COUNTY) | PACIFIC GAS & ELECTRIC CO | A YOUNG MAN LOST CONTROL OF HIS VEHICLE WHILE FLEEING A SCENE OF A STREET FIGHT IN WHICH HE WAS INVOLVED. THE VEHICLE CRASHED INTO A VACANT HOME AT 1731 CRESTWOOD CIRCLE, STOCKTON. THE VEHICLE ALSO STRUCK THE GAS METERSET AND RISER. THE RISER PIPE WAS SEVERED AND THE ESCAPING GAS IGNITED. THE FIRE BURNED THE GARAGE AND THE PORTION OF THE HOUSE. THE GAS COMPANY CREW EXCAVATED THE BRANCH SERVICE IN THE YARD AND PROCEEDED TO CUT OFF SERVICE TO THE VACANT HOUSE. | 55000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
641 | 2008-03-22 | TX | other | UNKNOWN (NACOGDOCHES COUNTY) | BLUEBONNET NATURAL GAS LLC | ON SATURDAY, MARCH, 22, 2008 I RECEIVED A CALL FROM THE NACOGDOCHES SHERRIFF DEPT. I WAS INFORMED WE HAD A LEAK ON STATE HWY 21, AND TRAFIC WAS STOPED. TIME 1627. I ARRIVED ON LOCATION AT 1710, AND STOPED LEAK AT 1720. IT APPEARS LAND OWNER WAS BURNING BRUSH AND AN EMBER BURNED A 1/4 INCH HOLE IN THE PVC PIPE. PIPE WAS EXPOSED IN A WASHOUT. IT ALSO APPEARS THAT THE FIRE DEPT. PUT OUT ALL FIRES AND CLOSED HWY. | 120 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
642 | 2008-04-02 | WI | sabotage | UNKNOWN (WAUKESHA COUNTY) | WISCONSIN ELECTRIC - GAS OPERATIONS, D/B/A WE ENERGIES | ON WEDNESDAY, APRIL 2, 2008 AT 12:22 P.M., A CONTRACTOR INSTALLING CATCH BASINS AND ASSOCIATED LATERALS IN THE INTERSECTION OF WISCONSIN AVENUE AND WORTHINGTON STREET IN THE CITY OF OCONOMOWOC, WISCONSIN, CALLED WE ENERGIES GAS EMERGENCY RESPONSE NUMBER. THE CONTRACTOR STATED HE HAD PUSHED DOWN ON AN OLD PIPE BECAUSE IT WAS GETTING IN THE WAY OF THEIR CONSTRUCTION WHEN HE HEARD A HIZZING NOISE AND SMELLED GAS. GAS DISPATCH CATEGORIZED THE LEAK AS A GRADE 1 (GRADE 1 IS DEFINED AS A POTENTIALLY HAZARDOUS LEAK) AND SENT THE FIRST RESPONDER TO THE SITE. THE FIRST RESPONDER ARRIVED AT THE SITE AT 12:39 P.M. AND INSPECTED THE EXCAVATED AREA INDICATED BY THE CONTRACTOR. HE OBSERVED AN EXPOSED 2" GAS LINE IN THE DITCH AND ANOTHER UNKNOWN BENT BLACK PIPE NEAR A NEWLY INSTALLED CATCH BASIN. HE FOUND NO INDICATIONS OF THE SOURCE OF THE GAS LEAK IN THE EXCAVATION, ALTHOUGH HE WAS READING THE PRESENCE OF GAS ON HIS INSTRUMENT. HE PROCEEDED TO CHECK THE SURROUNDING AREA INCLUDING THE AREA ALONG THE WALL OF THE NEARBY CHURCH. HIS READINGS INDICATING THE PRESENCE OF GAS REMAINED THE HIGHEST IN THE EXCAVATED AREA. AT 12:44 P.M. HE RETURNED TO HIS VEHICLE TO CALL FOR ADDITIONAL ASSISTANCE ON HIS VEHICLE RADIO. WITHIN MINUTES, ADDITIONAL UNITS ARRIVED TO ASSIST WITH THE LEAK LOCATING EFFORT. THE AREA AROUND THE CHURCH WAS CHECKED AGAIN, BUT INDICATIONS POINTED TO THE EXCAVATED AREA AS A POTENTIAL LEAK SOURCE. HAND EXCAVATION AND EXAMINATION BEGAN AROUND THE TWO PIPES IN THE OPEN EXCAVATION TO CHECK FOR LEAKS. NONE WERE FOUND. WITH CONTINUED PROBING INDICATING THE PRESENCE OF GAS AND POSITIVE INSTRUMENT READINGS, THE ONSITE PERSONNEL PROCEEDED TO DO THE FOLLOWING: CHECK ADJACENT BUILDINGS INCLUDING THE CHURCH AGAIN FOR THE PRESENCE OF GAS AND OCCUPANTS, PREPARE FOR AN AREA SHUT DOWN OF GAS SUPPLY ACCORDING TO THE EMERGENCY PLAN DEVELOPED FOR THE ROAD RECONSTRUCTION PROJECT AND, CONTINUE SEARCHING FOR THE SOURCE OF THE GAS LEAK. AROUND 1 P.M., THE TECHNICIAN INVOLVED WITH THE PROJECT WAS CONTACTED REGARDING THE LEAK INVESTIGATION. RESEARCH REVEALED THAT THE EXPOSED SECTION OF 2" BLACK PIPE WAS POSSIBLY ASSOCIATED WITH THE RETIREMENT AND REPLACEMENT OF A FORMER 2" LINE IN 1968. FURTHER REVIEW INDICATED THAT A SHORT SEGMENT (STUB) OF PIPE CONTAINING A COMPRESSION COUPLING, THOUGHT TO HAVE BEEN RETIRED, MAY STILL BE ACTIVE UNDER THE PAVEMENT TO THE NORTH OF THE EXCAVATION. GIVEN THAT INFORMATION AND LOCATION, THE SEARCH EFFORT WAS DIRECTED TO VERIFYING THE STATUS OF THE LINE AND LOCATING THE COUPLING. PROBING INTHE CONCRETE PAVEMENT BEGAN AT THE LOCATION GIVEN AND THE SECOND PROBE TAKEN RESULTED IN A BLOW OUT OF SAND AND GRAVEL MATERIAL INDICATING THE THEY WERE NEAR THE SOURCE OF THE LEAK. GIVEN THE KNOWLEDGE THAT THE SOURCE OF THE LEAK WAS UNDER UNEXCAVATED SOIL AND PAVEMENT AND NOT KNOWING THE EXTENT OF THE LEAK AREA, THE FOLLOWING ACTIONS WERE TAKEM: THE GAS DISPATCH CENTER WAS ASKED AT 1:16 P.M. TO REQUEST ASSISTANCE FROM THE FIRE & POLICE DEPARTMENTS TO CLOSE OFF THE STREETS TO THE AREA AND GAIN ACCESS TO THE UNOCCUPIED CHURCH. THE PROCESS OF VALVING OFF THE AREA BEGAN AND THE IMMEDIATE AREA WAS CLEARED OF UNNECESSARY PERSONNEL. BY THIS TIME, WE ENERGIES HAD A TOTAL OF 6 PEOPLE IN THE AREA. AT APPROXIMATELY 1:20 P.M., NATURAL GAS THAT HAD ACCUMULATED IN THE LOCKED NEARBY CHURCH, WAS IGNITED BY AN UNKNOWN SOURCE, EXPLODED AND DESTROYED THE CHURCH. ANOTHER BUILDING BEHIND THE CHURCH WAS ALSO DESTROYED BY THE SUBSEQUENT FIRE. SEVERAL OTHER BUILDINGS IN THE AREA ALSO SUFFERED DAMAGE DUE TO THE EXPLOSION AND SUBSEQUENT FIRE. THE FORCE OF THE EXPLOSION PUSHED ONE OF THE GAS EMPLOYEES AGAINST A NEARBY MOBILE COMPRESSOR INJURING HIM AND REQUIRING SEVERAL DAYS OF HOSPITALIZATION. TWO OTHER EMPLOYEES WERE EXAMINED THE FOLLOWING DAY BY THE WE ENERGIES NURSE AND A CLINIC AND WERE GIVEN LIGHT DUTY ASSIGNMENTS DUE TO STRAINS AND OTHER MINOR INJURIES. A TOTAL OF THREE COMPANY EMPLOYEES WERE INJURED IN THE EXPLOSION AND AN INDIVIDUAL WHO WAS IN O NE OF THE NEARBY HOMES WAS BELIEVED TO HAVE BEEN MEDICALLY EXAMINED. NEWS REPORTS INDICATED THAT SOME EMERGENCY PERSONNEL MAY HAVE BEEN TREATED FOR SMOKE INHALATION. POST INCIDENT REVIEWS, INTERVIEWS AND FURTHER EXCAVATION AND EXAMINATION OF THE BURIED PIPE INDICATE THE CONTRACTOR UNCOVERED A 2" PIPE STUB THAT WAS CONNECTED TO THE GAS DISTRIBUTION SYSTEM. THEY ASSUMED IT TO BE ABANDONED AND PUSHED DOWN ON IT WITH THE BUCKET OF THE BACKHOE TO MAKE ROOM FOR A NEW STORM SEWER. THE SIGNIFICANT DISTORTION TO THE PIPE CAUSED IT TO SEPARATE FROM A BURIED UPSTREAM INSULATED COMPRESSION STYLE COUPLING. THE PATHWAY OF THE RELEASED GAS TO AND INTO THE CHURCH IS NOT KNOWN BECAUSE THE SEPARATION OCCURRED UNDER PAVEMENT AND IN SOILS STILL FROZEN FROM WINTER CONDITIONS. ALL SIX OF THE WE ENERGIES EMPLOYEES ON SITE AT THE TIME OF THE INCIDENT UNDERWENT DRUG AND ALCOHOL TESTING AND THE RESULTS WERE NEGATIVE FOR ALL SIX. | 2088 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
643 | 2008-04-09 | NV | other | UNKNOWN (CLARK COUNTY) | SOUTHWEST GAS CORP | WHILE A SOUTHWEST GAS CREW WAS WORKING TO REPAIR AN ABOVE GROUND LEAK ON THE STOPCOCK AT 1104 STONE RIVER DRIVE, THE STOPCOCK FAILED AND GAS IGNITED. TWO SOUTHWEST GAS EMPLOYEES SUFFERED INJURIES REQUIRING OVERNIGHT HOSPITALIZATION. SOUTHWEST GAS CREWS STOPPED THE FLOW OF GAS AND THE FIRE WAS EXTINGUISHED AT 1031. THERE WERE 11 EVACUATIONS FROM TWO RESIDENCES AND 32 OUTAGES THAT RESULTED FROM THE INCIDENT. THE INCIDENT IS CURRENTLY UNDER INVESTIGATION AND A SUPPLEMENTAL REPORT WILL BE PROVIDED WHEN THE INVESTIGATION IS COMPLETE. UPDATE MARCH 26, 2009 - FINAL REPORT THE PLUG DISPLODGED FROM THE BODY OF THE STOPCOCK VALVE, CAUSING NATURAL GAS TO ESCAPE INTO THE ATMOSPHERE AND TO BE IGNITED BY AN UNKNOWN SOURCE. A THIRD PARTY LABORATORY ANALYSIS DETERMINED THAT IT WAS UNLIKELY THAT THE RETAINING NUT WAS ENGAGED WITH THE RETAINING THREADS ON THE PLUG SHAFT WHEN THE STOPCOCK PLUG DISLODGED FROM THE BODY OF THE STOPCOCK VALVE. THE RESULTS OF THE INVESTIGATION CONCERNING THE CAUSE OF THIS FAILURE WERE INCONCLUSIVE. | 191436 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
644 | 2008-04-13 | UT | other | UNKNOWN (WASHINGTON COUNTY) | QUESTAR GAS COMPANY | THE FIRE DEPARTMENT DETERMINED THAT THE FIRE ORIGINATED IN THE PROXIMITY OF THE METER. THE EXACT IGNITION SOURCE WAS UNDETERMINED. FURNITURE AS WELL AS OTHER ITEMS WERE VERY CLOSE TO THE METER. THE RESIDENTS WERE IN THE PROCESS OF MOVING AND VEHICLES WERE BACKING IN TO BE LOADED WITH THESE ITEMS. IT WAS THOUGHT THAT DAMAGE TO THE METER OCCURRED AS A RESULT OF THE RESIDENCE MOVING SINCE NO GAS LEAKS HAS BEEN REPORTED. | 151044 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
645 | 2008-04-05 | NM | other | UNKNOWN (LEA COUNTY) | PUBLIC SERVICE COMPANY OF NEW MEXICO - GAS SVCS | A MECHANIC SHOP CAUGHT FIRE AND A WALL COLLAPSED ON THE METER. THE METER MELTED, CAUSING THE RELEASE OF GAS. THE METER WAS REMOVED AND THE LINE WAS PLUGGED AT THE STOP. THE SERVICE LINE WAS REPAIRED, BAR TESTED AND PRESSURE TESTED ON 4/5/2008. NO LEAKS WERE DETECTED. A FOLLOW-UP BAR TEST WAS CONDUCTED ON 4/6/08 AND NO LEAKS WERE DETECTED. SUPPLEMENTAL: NATURAL GAS WAS NOT THE CAUSE OF THE FIRE THAT RESULTED IN THE DAMAGE. DAMAGE TO STRUCTURE ARE ESTIMATED AND NO ADDITIONAL INFORMATION IS AVAILABLE. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
646 | 2008-05-10 | CA | other | UNKNOWN (SANTA CRUZ COUNTY) | PACIFIC GAS & ELECTRIC CO | A CAR STRUCK AND SHEARED OFF A ½¿ RISER AT THE METER SET. THE GAS IGNITED AND THE CAR CAUGHT FIRE. THE DRIVER OF THE VEHICLE SUSTAINED SIGNIFICANT BURNS AND WAS TAKEN TO THE HOSPITAL. NO STRUCTURES WERE INVOLVED BECAUSE THE METER SET IS LOCATED APPROXIMATELY 30 FEET AWAY. THE FLOW OF GAS WAS STOPPED BY SQUEEZING OFF THE SERVICE LINE AT 0454 HOURS AND THE SERVICE WAS CUT OFF AT THE TEE. REPAIRS TO THE METER SET AND HOUSELINE WERE MADE AND SERVICE WAS RESTORED ON 5/17/08. | 32000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
647 | 2008-01-18 | OH | sabotage | UNKNOWN (ALLEN COUNTY) | DOMINION EAST OHIO | ON JANUARY 18, 2008, AT APPROXIMATELY 1:08 P.M. DOMINION EAST OHIO GAS CALL CENTER RECEIVED A REPORT FROM TOP QUALITY CABLE CONSTRUCTION OF A LINE HIT AT 880 SHAWNEE ROAD, LIMA, ALLEN COUNTY, OH. TOP QUALITY CABLE CONSTRUCTION, A CONTRACTOR DIRECTIONAL BORING THE SERVICE ROAD FOR TIME WARNER CABLE AT 880 SHAWNEE, LIMA ALLEN COUNTY, OH, HAD HIT A 2¿, MEDIUM PRESSURE, HIGH DENSITY PLASTIC MAINLINE. AT APPROXIMATELY 1:34 P.M. DOMINION EAST OHIO GAS PERSONNEL ARRIVED AT THE SCENE. AT 1:36 P.M. THE STRUCTURE LOCATED AT 880 SHAWNEE, LIMA, ALLEN COUNTY, OH WAS INVOLVED IN AN EXPLOSION AND FIRE. AT APPROXIMATELY 2:47 P.M., THE PIPELINE WAS SHUTDOWN AT THE MAINLINE VALVE AND STOPPING THE FLOW OF GAS TO 11 COMMERCIAL ACCOUNTS. A PRELIMINARY DAMAGE ASSESSMENT WAS THEN CONDUCTED, WHEN IT WAS DETERMINED THAT THE ESTIMATED PROPERTY DAMAGE WAS OVER $50,000 AND 5 PERSONS WERE TAKEN TO THE HOSPITAL, VERBAL NOTIFICATION WAS MADE TO THE NATIONAL RESPONSE CENTER AND TO THE PUBLIC UTILITIES COMMISSION OF OHIO BY TELEPHONE. NRC #860032 WAS ASSIGNED TO THIS EVENT AT THAT TIME. THE PUBLIC UTILITIES COMMISSION OF OHIO RESPONDED AND CONDUCTED AN ON-SITE INVESTIGATION OF THIS INCIDENT ON JANUARY 19, 2008. PRELIMINARY INVESTIGATIONS REVEALED THAT THE PIPELINE WAS PROPERLY MARKED. TOP QUALITY CABLE FAILED TO DIG TEST HOLES AT THE MAIN AS REQUIRED IN ORDER TO ACCURATELY DETERMINE THE DEPTH AND LOCATION OF THE PIPELINE. | 1817605 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
648 | 2008-04-08 | GA | sabotage | UNKNOWN (COBB COUNTY) | ATLANTA GAS LIGHT CO | A CONTRACTOR WORKING FOR THE COBB COUNTY AND GEORGIA DEPARTMENT OF TRANSPORTATIONS BORED INTO A 6" HP GAS MAIN AT SANDY PLAINS ROAD AND WEST OAK PARKWAY WHILE INSTALLING SIGNAL CABLES. THE IMPACTED GAS MAIN WAS MIS-LOCATED BY THE COMPANY'S LOCATE CONTRACTOR. IN ADDITION, THERE WERE PERMANENT MARKERS NEARBY IDENTIFYING THE COMPANY'S 24" STEEL GAS MAIN. | 109969 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
649 | 2006-07-20 | GA | other | UNKNOWN (nan COUNTY) | AUSTELL NATURAL GAS SYSTEM, CITY OF | JULY 20, 2006 AT APPROXIMATELY 0259 HRS, THIS INVESTIGATOR RESPONDED TO THE RESIDENTIAL PROPERTY LOCATED AT 4702 JAY BIRD LANE, POWDER SPRINGS, GEORGIA 30127 AFTER RECEIVING NOTIFICATION THERE WAS A POSSIBLE NATURAL GAS EXPLOSION. IT WAS REVEALED DURING THE INVESTIGATION THAT IN AN ATTEMPT TO COMMIT SUICIDE BY ASPHYXIATION, THE OCCUPANT OF THIS RESIDENCE LOOSENED THE NATURL GAS FITTING BEHIND THE NATURAL GAS CLOTHES DRYER IN THE BASEMENT AND WENT UPSTAIRS TO LIE DOWN IN BED. A FIRE/EXPLOSION RESULTED AND WAS CAUSED BY THE IGNITION OF ESCAPING NATURAL GAS VAPORS REACHING THE LOT LIGHT ON THE WATER HEATER LOCATED APPROXIMATELY 15 FEET AWAY IN THE SAME ROOM OF THE BASEMENT. DAMAGE TO THE STRUCTURE WAS APPROXIMATELY $50,000 -$100,000. THE OCCUPANT ESCAPED WITHOUT INJURY. | 85000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
650 | 2008-04-26 | NJ | other | UNKNOWN (HUNTERDON COUNTY) | ELIZABETHTOWN GAS CO | BUILDING FIRE, UNRELATED TO GAS, DAMAGED METERS AND CAUSED THEM TO LEAK. EXCESS FLOW VALVE STOPPED GAS FLOW. GAS WAS NOT A CONTRIBUTING FACTOR DAMAGE. | 400284 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
651 | 2008-04-14 | MN | other | UNKNOWN (SAINT LOUIS COUNTY) | CITY OF DULUTH PUBLIC WORKS & UTILITIES | THE EXPLOSION OCCURED ON 4/14/08. THE UTILITY PERFORMED THE FOLLOWING ACTIVITIES: A. LEAK SURVEYED THE DISTRIBUTION SYSTEM IN THE AREA ON 4/14. B. LEAK SURVEYED INSIDE THE HOUSES IN THE AREA ON 4/14. C. BARHOLED OVER THE GAS MAIN ON W. 8TH ST ON 4/14. D. ISOLATED AND PRESSURE TESTED THE GAS SERVICE TO 1011 W 8TH ST TO 22 PSI (SYSTEM PRESSURE) ON 4/14. E. LEAK SURVEYED THE MAIN AND SERVICE IN THE AREA 1011 W 8TH ST ON 4/30 AT THE REQUEST OF THE INSURANCE COMPANY INVESTIGATORS. F. BARHOLED THE MAIN AND SERVICE IN THE AREA AROUND 1011 W 8TH ST ON 4/30 AT THE REQUEST OF THE INSURANCE COMPANY INVESTIGATORS. G. TESTED THE METER SET REGULATOR FOR LOCK-UP ON 4/29 AT THE REQUEST OF THE INSURANCE COMPANY INVESTIGATORS. AT THIS TIME, WE'VE DETERMINED THE GAS UTILITY FACILITIES/ACTIONS DID NOT CAUSE THIS EXPLOSION. ALL INFORMATION GATHERED TO THIS POINT INDICATES THE CAUSE OF THE EXPLOSION WAS ON CUSTOMER-OWNED FACILITIES AND THEREFORE NOT A REPORTABLE INCIDENT. | 400000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
652 | 2008-05-13 | AK | other | UNKNOWN (ANCHORAGE COUNTY) | ENSTAR NATURAL GAS CO | AT 0415, TUESDAY MAY 13, 2008, ENSTAR NATURAL GAS COMPANY WAS NOTIFIED OF A STRUCTURE FIRE BY THE ANCHORAGE FIRE DEPARTMENT AT 6258 41ST COURT, ANCHORAGE, AK. A SERVICE TECHNICIAN RESPONDED TO FIND AN 8 UNIT CONDO COMPLEX ON FIRE. THE FIRE HAD MELTED 2 OF 8 NATURTAL GAS METERS AND GAS WAS BLOWING. AN ENSTAR CREW WAS CALLED IN TO DIG UP THE GAS MAIN TO SHUT OFF THE FLOW OF GAS. THE HEAT OF THE FIRE MELTED HOLES IN FIVE OF THE 8 HDPE SERVICE LINE RISERS, CAUSING ADDITIONAL NATURAL GAS TO BE RELEASED. AT LEAST 3 EXPLOSIONS REPORTEDLY OCCURED WHILE THE FIRE WAS BEING EXTINGUISHED. THE GAS MAIN WAS SHUT DOWN AT 0618. THE FIRE IS BELIEVED TO HAVE STARTED IN A SAUNA IN UNIT 3. NATURAL GAS IS NOT BELEIVED TO HAVE CAUSED OR CONTRIBUTED TO THE FIRE. | 1002700 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
653 | 2008-05-08 | NM | other | UNKNOWN (LUNA COUNTY) | PUBLIC SERVICE COMPANY OF NEW MEXICO - GAS SVCS | UPON ARRIVAL...VALVE WAS TUNRED OFF BY SUNSHINE VOLUNTEER FIRE DEPARTMENT PERSONNEL. NIPPLE WAS BROKEN ABOVE STOP, PROBED ENTIRE AREA, 0% LEL - NO GAS. SOAP TESTED VALVE/FITTINGS AND BENT RISER...REFERRED TO C&M TO REPLACE 1" PE RISER AND TEST BACK TO MAIN AND INSTALL A METER GUARD. | 5300 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
654 | 2008-04-29 | MI | sabotage | UNKNOWN (KENT COUNTY) | MICHIGAN CONSOLIDATED GAS CO (MICHCON) | AT APPROXIMATELY 7:20 AM ON TUESDAY, APRIL 29, 2008, AN EXCAVATOR INSTALLING A SECTION OF CONCRETE SEWER STRUCK A 6-INCH PLASTIC NATURAL GAS DISTRIBUTION MAIN AT THE SOUTHEAST CORNER OF THE INTERSECTION OF SHELDON AVENUE AND WEALTHY STREET. THE 6-INCH MAIN WAS COMPLETELY SEVERED AND SEPARATED FROM THE 12-INCH STEEL MAIN TO WHICH IT HAD BEEN CONNECTED. MICHCON RECEIVED A TELEPHONIC LEAK REPORT OF THIS EVENT AT 7:30 AM, AND A MICHCON EMPLOYEE WAS DISPATCHED TO THE SCENE AT 7:32 AM. MICHCON REPAIR PERSONNEL ARRIVED AT 7:35 AM TO ASSESS THE DAMAGE; IT WAS DETERMINED THAT THREE CONTROL TO THE NORTHER, WEST, AND EAST OF THE BREAK WOULD BE REQUIRED TO SAFELY SHUT DOWN THE MAINS IN THE INTERSECTION. APPROXIMATELY 71 CONSTRUCTION WORKERS IN A BUILDING ON THE NORTHWEST CORNER OF SHELDON AND WEALTHY WERE EVACUATED AS A PRECAUTIONARY MEASURE DUE TO THE BUILDING'S PROXIMITY TO THE MAIN BREAK. THE MICHIGAN PUBLIC SERVICE COMMISSIONI WAS TELEPHONICALLY NOTIFIED OF THE EVENT AT 9:31 AM. PRESSURE CONTROL FITTINGS WERE WELDED TO THE MAINS AT ALL THREE LOCATIONS AND PREPARATIONS WERE MADE FOR SHUT-DOWN. THE 6-INCH MAIN TO THE NORTH WAS SHUT DOWN AT 10:55 AM; THE 12-INCH MAIN WEST OF THE BREAK WAS SHUT DOWN AT 12:38 PM. AT 13:05 PM THE 12-INCH MAIN EAST OF THE BREAK WAS SHUT DOWN AND THE AREA WAS MADE SAFE. MICHCON TELEPHONICALLY NOTIFIED THE NATIONAL RESPONSE CENTER IN WASHINGTON DC OF THE EVENT AT 13:08 PM WHEN IT WAS DETERMINED THAT TOTAL PROPERTY DAMAGES AND LOST GAS MAY EXCEED $50,000. REPAIRS WERE MADE BY INSTALLING A NEW SECTION OF 6-INCH PLASTIC PIPE, AND NORMAL OPERATION WAS RESTORED AT 17:10 PM. THERE WERE NO CUSTOMER OUTAGES, INJURIES, OR FATALATIES EXPERIENCED AS A RESULT OF THIS EVENT. | 60400 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
655 | 2008-04-28 | VA | natural disasters | UNKNOWN (SUFFOLK CITY COUNTY) | VIRGINIA NATURAL GAS | AT APPROXIMATELY 4:30 PM ON APRIL 28, 2008 AN EF-3 TORNADO HIT THE CITY OF SUFFOLK. APPROXIMATELY 1,200-HOMES WERE DAMAGED AND 145-HOMES WERE CONDEMNED AS A RESULT OF THE VIOLENT STORM. TWO SUBDIVISIONS, BURNETT'S MILL AND HILL POINT FARMS (OFF OF GODWIN BLVD) WERE SEVERALLY DAMAGED. THE TORNDADO CAUSED THE COLLAPSE OF MULTIPLE RESIDENTIAL STRUCTURES WHICH DESTROYED THE ADJACENT METER SETS. THE DESTRUCTION OF THE METER SETS CAUSED A RELEASE OF GAS THROUGH THE SEVERED METER SET PIPING. VIRGINIA NATURAL GAS CREWS MADE THE AREAS SAFE BY SQUEEZING OFF THE 2" PLASTIC GAS MAIN FEEDING BURNETT'S MILL, AND CLOSING A 6" VALVE THAT FED HILL POINT FARMS. THIS CAUSED THE INTERRUPTION OF APPROXIMATELY 500-HOMES. SERVICE WAS RESTORED TO BURNETT'S MILL BY MAY 1, 2008 AND TO HILL POINT FARMS BY MAY 10, 2008. THERE WERE NO FATALATIES AND 3-PEOPLE WERE INJURED (NON-GAS RELATED) REQUIRING HOSPITALIZATION SUE TO THE STORM. A SUPPLEMENTAL REPORT WAS SUBMITTED AS REQUESTED BY MICHAEL YAZEMBOSKI (PHMSA EASTERN REGION PITTSBURGH)TO REMOVE THE INJURIES AND COST THAT WERE NOT RELATED TO THE RELEASE OF GAS. | 71000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
656 | 2008-04-29 | MD | maintenance | UNKNOWN (BALTIMORE CITY COUNTY) | BALTIMORE GAS & ELECTRIC CO | MR. ADAMS WHILE ATTEMPTING TO SHUT OFF WATER TO THE HOUSE AT THE WATER METER VAULT AT 2252 ANNAPOLIS RD. MR. ADAMS WAS INJURED WHEN GAS ACCUMULATED IN THE WATER METER VAULT WAS IGNITED BY MS. JACKSON USING HER "BIC" LIGHTER AS A FLASH LIGHT. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
657 | 2008-04-17 | IN | sabotage | UNKNOWN (DECATUR COUNTY) | FOUNTAINTOWN GAS CO INC | FARM EMPLOYEE REPAIRING FIELD DRAINAGE TILE CUT GAS MAIN IN COUNTY HIGHWAY RIGHT-OF-WAY UNDER WATER AT CULVERT UNDER COUNTY ROAD 650 S. NO LOCATE REQUEST WAS MADE. GAS LINE MARKER IS IN PROXIMITY TO DIG SITE. | 35000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
658 | 2008-05-06 | CO | other | UNKNOWN (SUMMIT COUNTY) | PUBLIC SERVICE CO OF COLORADO | BROKEN THREADS WERE FOUND ON A PIPE NIPPLE BETWEEN THE SERVICE VALVE AND THE METER SET REGULATOR. THERE WAS UNANTICIPATED STRESS ON THE CUSTOMER FUEL LINE THAT TRANSFERRED STRESS TO THE METER SET. THE LEAKING GAS FROM THE RUPTURED PIPE NIPPLE ENTERED THE STRUCTURE THROUGH THE GAS FIREPLACE VENT WHICH WAS THE SOURCE OF IGNITION. THE VENT WAS LOCATED BEYOND OUR STANDARD SETBACK FROM THE METER SET. | 200250 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
659 | 2008-05-12 | MD | other | UNKNOWN (PRINCE GEORGE'S COUNTY) | WASHINGTON GAS LIGHT CO | WASHINGTON GAS WAS CALLED BY THE PRINCE GEORGE'S FIRE BOARD TO ASSIST WITH A HOUSE FIRE AT 13005 MINETTA LANE IN BOWIE. THE FIRE IS BELIEVED TO HAVE STARTED IN THE HOUSE AND LATER INVOLVED THE WASHINGTON GAS FACILITIES. THE SERVICE WAS CUT OFF AT THE METER VALVE UPON ARRIVAL. THE SERVICE WAS ALSO CAPPED OFF AT THE MAIN. THE SERVICE WAS PRESSURE TESTED AND NO LEAKS WERE FOUND. WASHINGTON GAS ALSO LEAK SURVEYED THE ADJACENT SERVICES AND MAIN AND NO INDICATIONS OF LEAKS WERE FOUND. | 351100 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
660 | 2008-04-03 | NY | sabotage | UNKNOWN (WESTCHESTER COUNTY) | CONSOLIDATED EDISON CO OF NEW YORK | ON THURSDAY, APRIL 3, 2008 AT 14:22, CON EDISON¿S GAS EMERGENCY RESPONSE CENTER (GERC) RECEIVED A CALL FROM WESTCHESTER FIRE CONTROL REPORTING A GAS EXPLOSION AT 60 FAYETTE ROAD, SCARSDALE, NEW YORK. GAS DISTRIBUTION SERVICES (GDS) RESPONDED AND REPORTED THAT FD WAS ON LOCATION, A PRIVATE HOME HAD EXPLODED AND THAT THE FD WAS FIGHTING AN ACTIVE GAS FED FIRE. GDS TURNED OFF THE CURB VALVE TO SECURE THE LEAK AND THE GAS SERVICE WAS CUT & CAPPED FOR SAFETY. CON ED ELECTRIC OPERATIONS RESPONDED AND CUT THE SERVICE AT THE POLE. THE FIRE WAS EXTINGUISHED BY THE SCARSDALE FIRE DEPARTMENT AT 15:30, THERE WERE NO REPORTED INJURIES. AN INVESTIGATION REVEALED THE BUILDING WAS UNDER RENOVATION BY THE OWNER DANCER REALTY AND THEY WERE ACTING AS THE GENERAL CONTRACTOR. THE EXCAVATING CONTRACTOR DAMAGED THE 1¿ HP ST SERVICE WITH A BACKHOE WHILE INSTALLING DRAINAGE PIPE TO A DRYWELL. THE SERVICE MARK OUT WAS VISIBLE AND CORRECT. STRUCTURAL DEBRIS WAS REMOVED NEAR THE EXCAVATION AND IT WAS PROVEN THAT THE RUN OF THE SERVICE WAS STRAIGHT FROM THE CURB VALVE INTO THE BUILDING. CON EDISON¿S CENTRAL INFORMATION GROUP (CIG) NOTIFIED THE NEW YORK STATE PUBLIC SERVICE COMMISSION (PSC) AND U.S. DEPARTMENT OF TRANSPORTATION (DOT/NRC), THERE WAS MEDIA ON LOCATION. CON EDISON¿S LAW DEPARTMENT, PHOTOGRAPHER, ENVIRONMENTAL HEALTH & SAFETY, GAS CONSTRUCTION, CONSTRUCTION MANAGEMENT, GAS & ELECTRIC EMERGENCY RESPONSE GROUP¿S WERE ALL ON LOCATION. PSC REPRESENTATIVE SURESH THOMAS ALSO RESPONDED TO THE LOCATION. GDS MANAGER DELUCA WAS THE WHITE HAT AND GDS FIELD PLANNER LUCA WAS THE COMMUNICATOR. THIS WAS AN UPGRADE LEVEL INCIDENT. PLEASE CONTACT ME IF YOU REQUIRE ADDITIONAL INFORMATION AT (718) 319-2310 EDWARD OLSEN GENERAL MANGER GAS EMERGENCY RESPONSE CENTER | 1255200 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
661 | 2008-06-10 | CA | other | UNKNOWN (SANTA CLARA COUNTY) | PACIFIC GAS & ELECTRIC CO | A FIRE, THE CAUSE OF WHICH IS CURRENTLY UNKNOWN, SEVERLY DAMAGED THE METER SET AT 5890 MACADAM COURT LEADING TO ESCAPING GAS BEING IGNITED. THE FIRE DAMAGED ONE HOUSE AND CAUSED MINOR DAMAGE TO A SECOND. A PG&E GAS CREW EXCAVATED THE SERVICE TEE AT THE GAS MAIN AND SHUT OFF GAS TO BOTH 5890 AND 5892 MACADAM COURT. GAS SERVICE WAS RESTORED TO 5892 MACADAM COURT ON JUNE 12TH. SERVICE WILL BE RESTORED TO 5890 MACADAM COURT PENDING REPAIRS TO THE STRUCTURE. | 65000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
662 | 2008-05-03 | IL | sabotage | UNKNOWN (DOUGLAS COUNTY) | CENTRAL ILLINOIS LIGHT CO | HOME OWNER RENTED A DITCHWITCH WALK BEHIND TRENCHER AND WAS IN THE PROCESS OF TRENCHING IN SEWER LATERALS WHEN THE 2" P.E. GAS MAIN WAS DAMAGE. THE DAMAGE TO THE GAS MAIN RESULTED IN A RELEASE OF GAS WHICH IGNITED. THE HOME OWNER AND HIS FATHER WERE EXPOSED TO THE IGNITION AND RECEIVED OUTPATIENT MEDICAL CARE FOR THEIR BURNS. THIS INCIDENT WAS REPORTED DUE TO LIMITED KNOWLEDGE ON THE EXTENT OF THE BURNS AND THE POSSIBILITY OF THE REQUIREMENTS FOR INPATIENT MEDICAL CARE. INPATIENT MEDICAL CARE WAS NOT ADMINISTERED. | 16500 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
663 | 2008-05-29 | NE | natural disasters | UNKNOWN (BUFFALO COUNTY) | NORTHWESTERN ENERGY LLC | ON MAY 29, 2008 SEVERAL EF2 TORNADO HIT THE CITY OF KEARNEY, NE. AS A RESULT OF THE SEVERE WEATHER HIGH WINDS CAUSED DAMAGE TO THE STRUCTURE/BUILDING AT 4855 AIRPORT ROAD, AN AIRPLANE HANGER. THE COLLAPSE OF THE BUILDING AND DEBRIS CAUSED DAMAGE TO NORTHWESTERN¿S METER FIT. THE WEIGHT OF THE BUILDING DEBRIS ON THE METERFIT CAUSED THE ABOVE GROUND METERFIT TO BREAK BETWEEN THE ANODELESS RISER AND THE SERVICE VALVE. THE BUILDING, A METAL HANGAR, WAS USED TO STORE A PRIVATE PLANE FOR CORPORATION, BUCKLE INC. NORTHWESTERN ESTIMATES THE BUILDING DAMAGE TO BE $100,000. ACCORDING TO NEWS REPORTS THE PLANE HOUSED INSIDE OF THE BUILDING WAS ALSO DAMAGED. HOWEVER, SINCE THE PLANE IS PRIVATELY OWNED NORTHWESTERN IS UNSURE OF HOW EXTENSIVE THE DAMAGES WERE TO THE PLANE AND THOSE COSTS ARE NOT REFLECTED IN THE COST ESTIMATES. NO TREATABLE INJURIES RESULTED FROM THE INCIDENT. | 100385 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
664 | 2008-05-19 | MI | sabotage | UNKNOWN (BERRIEN COUNTY) | MICHIGAN GAS UTILITIES CO | CONTRACTOR HAD EXPOSED MAIN AND WAS USING A TRACK HOE TO SCRAPE THE COVER FROM THE TOP IN ORDER TO EXPOSE IT. HE SNAGGED A RETIRED SERVICE TEE WITH THE BUCKET AND TORE IT OFF THE MAIN. THE CONTRACTOR THEN CURLED THE TRACK HOE BUCKET AND SET IT ON THE DAMAGED AREA BEFORE TURNING OFF AND ABANDONING THE MACHINE. THE CONTRACTOR DID NOT HAND EXPOSE WITH IN 12" OF THE MAIN. | 187158 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
665 | 2008-05-16 | TX | sabotage | UNKNOWN (COLLIN COUNTY) | ATMOS ENERGY CORPORATION, MID-TEX DIVISION | A COMPANY CONTRACTOR OPERATING A DIRECTIONAL DRILLING MACHINE PUNCTURED A MARKED 3 INCH GAS MAIN. | 225000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
666 | 2008-05-21 | PA | sabotage | UNKNOWN (DAUPHIN COUNTY COUNTY) | U G I CORP | ON WEDNESDAY MAY 21, 2008, A BACKHOE OPERATOR WITH HANDWERK MATERIALS STRUCK A 1975 3/4" MEDIUM PRESSURE STEEL SERVICE LINE AT 298 E. MAIN STREET, HUMMELSTOWN, PA. THE DAMAGE RESULTED IN THE SERVICE LINE BEING PULLED FROM THE METER SET IN THE BASEMENT, RELEASING 57 PSI GAS INTO THE BUILDING. THE GAS IGNITED RESULTING IN AN EXPLOSION THAT DESTROYED THE BUILDING. THE SERVICE LINE WAS MARKED CORRECTLY. | 479400 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
667 | 2008-05-21 | IN | other | UNKNOWN (WHITLEY COUNTY) | NORTHERN INDIANA PUBLIC SERVICE CO | NIPSCO CENTRAL OPERATIONS WAS ADVISED THAT A VEHICLE HAD HIT A REGULATOR STATION AT THE ABOVE LOCATION, AND GAS WAS BLOWING. NIPSCO¿S FIRST RESPONDER WAS ON SITE AT 8:13 P.M. THE WEATHER WAS CLEAR, NO CLOUDS, AROUND 49 DEGREES, AND A VERY SLIGHT WIND +- 2 MPH OUT OF THE SOUTHWEST. ACCORDING TO THE POLICE REPORT, THE DRIVER WAS OPERATING THE VEHICLE AT AN UNSAFE SPEED, AND ¿ALCOHOLIC BEVERAGES¿ WAS LISTED AS THE PRIMARY CAUSE. THE VEHICLE CRACKED A FOUR X TWO INCH REDUCING FLANGE ON THE INLET TO THE STATION, AND GAS WAS BLOWING. THE LOCAL FIRE DEPARTMENT EVACUATED A PIZZERIA AND TWO (2) NEARBY RESIDENCES, AND BLOCKED OFF TRAFFIC FOR AN AREA AROUND THE STATION (APPROXIMATELY 300 FEET IN EACH DIRECTION FROM THE STATION). ADDITIONAL NIPSCO PERSONNEL ARRIVED AT 10:00 P.M., AND THE STATION WAS SHUT DOWN AT 10:20 P.M. SHUTDOWN INCLUDED THE INLET VALVE ON THE HIGH-PRESSURE SIDE, AND THE OUTLET VALVE¿ TO PREVENT BACK FLOW FROM THE MEDIUM-PRESSURE SYSTEM. NO CUSTOMERS WERE LOST UNTIL THAT STATION WAS SHUT DOWN. A PORTABLE, TRAILER-MOUNTED STATION WAS INSTALLED TO RESTORE SERVICE. THIS WAS COMPLETED AT 7:15 P.M. ON THURSDAY, MAY 22, 2008. DUE TO THE NON-HEATING SEASON LOAD, A TEMPORARY PEDESTAL STATION WAS INSTALLED ON FRIDAY, MAY 23, 2008 PENDING PERMANENT REPAIRS. AN ESTIMATED 759 CUSTOMERS WERE ¿OUT OF SERVICE,¿ AND RE-LIGHTS BEGAN THURSDAY EVENING. THE BULK OF THE CUSTOMERS WERE ¿BACK IN SERVICE¿ BY MID-DAY ON FRIDAY, MAY 23, 2008. SINCE THIS IS NOT THE HEATING SEASON, AND GIVEN THE SEASONAL NATURE OF THE CUSTOMER BASE AROUND THE LAKE AREA, SOME CUSTOMERS WERE LEFT OFF UNTIL THEY CALLED IN FOR RE-LIGHT. PERMANENT REPAIRS ARE ¿PENDING¿ AND WILL BE DONE THIS SUMMER. | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
668 | 2008-01-24 | OR | other | UNKNOWN (CLACKAMAS COUNTY) | LEGACY PROPANE VANCOUVER, LLC | THE ACCIDENT OCCURRED AT THE COLLINS LAKE RESORT, A RESORT COMMUNITY WHICH SITS AT THE BASE OF MT. HOOD SKIBOWL SKI AREA LOCATED IN GOVERNMENT CAMP, OREGON. IT IS AN ELEVATION OF NEARLY 4000 FEET. LEGACY PROPANE INSTALLED THE PROPANE SYSTEM FROM 2003-2005 WHILE THE CONDOMINIUMS WERE BEING BUILT BY THE DEVELOPER, KIRK HANNAH. LEGACY PROVIDES PROPANE TO 151 CONDOMINIUMS THROUGH VAPOR METERS. THE CONDOMINIUMS ARE THREE STORIES HIGH AND THERE ARE THREE-TEN UNITS IN EACH BUILDING. ON JANUARY 24TH, 2008 A PROPANE GAS EXPLOSION OCCURRED IN TWO OF THE GARAGE UNITS IN ONE OF THE BUILDINGS. SUBSEQUENTLY, A FIRE ENSUED AND CAUSED CONSIDERABLE DAMAGE TO TWO OF THE UNIT. THE AFFECTED BUILDING HAD FIVE INDIVIDUAL CONDOMINIUM UNITS, SIDE BY SIDE. THE HOODLAND FIRE DEPARTMENT RESPONDED WITHIN 15 MINUTES BUT TOOK A NUMBER OF HOURS TO CONTAIN THE FIRE. THE FIRE FIGHTERS BATTLED RIGOROUS CONDITIONS, 17-DEGREE TEMPERATURES, FROZEN HOSES AND EQUIPMENT AND HEAVY SNOW ON AND AROUND THE CONDOS. LEGACY PROPANE WAS ABLE TO SHUT THE GAS OFF AND CUT THE SUPPLY LINE TO THE AFFECTED BUILDING AND CAP IT. THERE IS AN ONGOING INVESTIGATION TO DETERMINE THE CAUSE OF THE ACCIDENT. ISSUE, WAS RELATED TO THE PIPING ON THE CUSTOMER SIDE OF THE METER. JBT 4/30/2009 | 701500 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
669 | 2007-03-08 | MA | other | UNKNOWN (ESSEX COUNTY) | BOSTON GAS CO | UPDATED BY PHMSA ON 2/9/2016 PER OPERATOR'S MARK UP (PART F - APPARENT CAUSE, F4 - OTHER OUTSIDE FORCE DAMAGE, ITEM 10; AND PART I - NARRATIVE). PART G - KEYSPAN RECEIVED A CALL FROM THE PEABODY FIRE DEPARTMENT TO SHUT OFF GAS TO 19 DEARBORN ROAD, PEABODY, MA DUE TO A WORKING FIRE. A PFR TECH WAS DISPATCHED AT 1354, ARRIVING AT APPROXIMATELY 1410. UNITS 325, 326, 335, AND 336 AT THE BUILDING WERE FED BY A ONE-INCH PLASTIC SERVICE TO FOUR OUTSIDE METERS THROUGH A TWO-INCH MANIFOLD. THE METERS AND REGULATOR WERE MELTED. EVIDENCE OF BURN DAMAGE WAS ALSO OBSERVED ON THE ABOVE-GROUND RISER VALVE AND INSULATING UNION AND ON THE BELOW-GROUND RISER SWEEP. UNDER THE DIRECTION OF THE DTE AND FIRE OFFICIALS, SUBSEQUENT PRESSURE TESTING FROM THE SERVICE VALVE TO THE RISER VALVE REVEALED LEAKAGE AT THE RISER VALVE POSSIBLY FROM THE FIRE. APPROXIMATELY 35 FEET OF UNDERGROUND SERVICE LINE WAS PRESSURE TESTED FROM THE SERVICE VALVE TO APPROXIMATELY FIVE FEET FROM THE RISER VALVE, AND IT HELD. THE REMAINING FIVE GROUND RISER, AND THE METER MANIFOLD WERE REMOVED FROM THE SITE BY THE FIRE MARSHAL. PER DTE REQUEST, THE REMOVED EQUIPMENT WAS EXAMINED AND FOUND THAT THE LIKELY CAUSE WAS MELTED RISER VALVE FOLLOWING IMPROPER EXTINGUISHING OF A LIT CIGARETTE OR OTHER BURNING ITEM. | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
670 | 2008-05-29 | CA | maintenance | UNKNOWN (SAN JOAQUIN COUNTY) | PACIFIC GAS & ELECTRIC CO | IN PREPARATION OF RECOATING A SHORT SECTION OF DISTRIBUTION FEEDER MAIN, A PG&E PAINT CREW WAS SANDBLASTING THE 8-INCH DIAMETER PIPE SURFACE. DURING THE SANDBLASTING, A PINHOLE LEAK WAS OBSERVED. A TEMPORARY BYPASS WAS INSTALLED AND A 5.5-FOOT SECTION OF PIPE WAS CUT OUT AND REPLACED. THE REPAIR WAS COMPLETED 0115 HOUR THE FOLLOWING MORNING.. THE SANDBLASTING WAS BEING PERFORMED TO FINALIZE THE REPAIR WORK OF AN INDEPENDENT CORROSION LEAK WHICH WAS REPAIRED APPROXIMATELY FOUR FEET AWAY ON MAY 8, 2008. THERE WAS NO EVIDENCE OF CORROSION PRIOR TO SANDBLASTING OPERATIONS. THE CUT OUT SECTION OF PIPE HAS BEEN SENT TO A LAB FOR ANALYSIS. RESULTS INDICATE THAT THIS LEAK WAS CAUSED BY EXTERNAL CORROSION. | 50100 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
671 | 2004-05-10 | PA | other | UNKNOWN (GREENE COUNTY) | COLUMBIA GAS OF PENNSYLVANIA | AIR WAS INTRODUCED INTO COLUMBIA GAS DISTRIBUTION LINE NEAR HUPP STATION. GATHERING 2" INLET LINE WAS CRACKED AND ALLOWING AIR TO BE SUCKED INTO GATHERING LINE, THEN PUMPED INTO COLUMBIA GAS LINE. NOTE: THIS IS A RE-SUBMITTAL OF THE ORIGINAL INCIDENT REPORT FROM 6/4/04. PER THE REQUESET OF ANGELA DOW TO GET THE REPORT ON FORM7100-1 (3-04) | 123000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
672 | 2008-06-02 | VA | other | UNKNOWN (PRINCE WILLIAM COUNTY) | WASHINGTON GAS LIGHT CO | WASHINGTON GAS RESPONDED TO A HOUSE FIRE AT 2563 SYLVAN MOOR LANE IN WOODBRIDGE AT THE REQUEST OF THE PRINCE WILLIAM COUNTY FIRE DEPARTMENT. UPON ARRIVAL, THE SERVICE LINE WAS DUG UP AT THE SERVICE TEE CONNECTION AT THE MAIN AND SQUEEZED-OFF TO STOP THE FLOW OF GAS TO THE METER THAT WAS INVOLVED. THE SERVICE WAS ALSO CAPPED OFF AT THIS LOCATION. THE SERVICE WAS PRESSURED TESTED AND NO LEAKS WERE FOUND. WASHINGTON GAS ALSO LEAK SURVEYED THE ADJACENT SERVICES AND MAIN AND NO INDICATIONS OF LEAKS WERE FOUND. ODORANT SAMPLES WERE ALSO COLLECTED AND THE RESULTS WERE FOUND TO BE ACCEPTABLE. THE FIRE IS BELIEVED TO HAVE STARTED IN THE BASEMENT AND LATER SPREAD TO THE WASHINGTON GAS FACILITIES. | 401100 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
673 | 2008-06-18 | NE | other | UNKNOWN (RED WILLOW COUNTY) | SOURCEGAS LLC | VEHICLE (PICKUP TRUCK) WENT OUT OF CONTROL AND LEFT ROADWAY STRIKING A POWER POLE FLIPPING VEHICLE INTO THE AIR. COMBINATION OF VEHICLE AND POWER POLE COLLIDED WITH PRESSURE REGULATION FACILITY/BARRICADE SHEARING OFF THREE NEEDLE VALVES. | 16322 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
674 | 2008-06-07 | MD | natural disasters | UNKNOWN (MONTGOMERY COUNTY) | WASHINGTON GAS LIGHT CO | WASHINGTON GAS RESPONDED TO A HOUSE FIRE AT 5826 CONWAY ROAD, BETHESDA AT THE REQUEST OF THE MONTGOMERY COUNTY FIRE BOARD ON SATURDAY, JUNE 7, 2008 AT 21:43. THE FIRE HAD REPORTEDLY BEEN STARTED BY A LIGHTNING STRIKE TO THE NATURAL GAS METER SET. WASHINGTON GAS CAPPED THE SERVICE OFF AT THE MAIN AND PERFORMED A SUB-SURFACE LEAK SURVEY OVER THE SERVICE AND MAIN TO VERIFY THE INTEGRITY OF THE SYSTEM. NO LEAK INDICATIONS WERE FOUND. | 51100 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
675 | 2008-06-10 | NY | natural disasters | UNKNOWN (DUTCHESS COUNTY) | CENTRAL HUDSON GAS & ELECTRIC CORP | ON JUNE 10, 2008, AT APPROXIMATELY 21:23, THERE WAS A LIGHTNING STRIKE WHICH CAUSED AN ELECTRIC PRIMARY PHASE WIRE ON SWENSON DRIVE IN THE TOWN OF POUGHKEEPSIE TO FALL TO THE GROUND IN THE VICINITY OF THE SWENSON DRIVE GAS REGULATOR STATION RELIEF VALVE. THE ELECTRIC PRIMARY WIRE CAME INTO CONTACT WITH THE RELIEF VALVE PIPING AND IT IS SUSPECTED THAT THE STEEL GAS DISTRIBUTION PIPING BECAME ENERGIZED. SHORTLY THEREAFTER, TWO NEARBY HOMES LOCATED AT 2 MEADOW DRIVE AND 11 SWENSON DRIVE WERE OBSERVED TO BE ON FIRE. THE NEW YORK STATE DEPARTMENT OF PUBLIC SERVICE AND CENTRAL HUDSON ARE STILL INVESTIGATING. | 530006 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
676 | 2008-05-25 | IA | natural disasters | UNKNOWN (BUTLER COUNTY) | MIDAMERICAN ENERGY COMPANY | THE CAUSE OF THE INCIDENT WAS AN EF-5 TORNADO THAT HIT THE TOWN OF PARKERSBURG, IOWA. THIS INCIDENT IS BEING REPORTED BECAUSE IT IS CONSIDERED TO BE A SIGNIFICANT EVENT. MIDAMERICAN ENERGY COMPANY'S FACILITIES THAT WERE DAMAGED BY THE TORNADO INCLUDE SEVERAL GAS SERVICES AND A REGULATOR STATION FED BY THE 50 PSIG SYSTEM THAT SERVED THE 25 PSIG SYSTEM. MIDAMERICAN ENERGY COMPANY TURNED OFF THE SUPPLY OF GAS TO THE TOWN AT THE TOWN BORDER STATION RESULTING IN AN OUTAGE OF 901 CUSTOMERS. | 200000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
677 | 2008-06-27 | UT | other | UNKNOWN (SUMMIT COUNTY) | QUESTAR GAS COMPANY | A HOUSE FIRE MELTED THE METER WHICH RESULTED IN THE RELEASE OF GAS. THE CAUSE OF THE FIRE HAS NOT BEEN RELEASED TO THE PUBLIC, THE LEAD FIRE INVESTIGATOR DID INDICATE THAT NATURAL GAS WAS NOT INVOLVED IN THE ORIGIN OF THE FIRE. | 1500600 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
678 | 2008-06-28 | UT | other | UNKNOWN (SALT LAKE COUNTY) | QUESTAR GAS COMPANY | A GRASS FIRE CAUGHT THE BUILDING ON FIRE AND MELTED THE METER SET. | 2002746 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
679 | 2008-07-02 | CA | other | UNKNOWN (TULARE COUNTY) | SOUTHERN CALIFORNIA GAS CO | ON JULY 2, 2008, A FIRE ERUPTED AT A RESIDENTIAL HOME AND A METER SET WAS MELTED AND IGNITED. DAMAGE FROM FIRE EXCEEDED $50,000, AND AS A RESULT, THE INCIDENT WAS REPORTED TO DOT AND CPUC. FURTHER INVESTIGATION DETERMINED THAT THE FIRE STARTED INSIDE THE HOME, AND THAT METER DAMAGE AND IGNITION OCCURRED SOMETIME LATER. FURTHER, IGNITED GAS DID NOT IMPACT FIREFIGHTING EFFORTS AND DID NOT CONTRIBUTE TO ANY RESIDENCE DAMAGE. IF YOU HAVE ANY QUESTIONS, FEEL FREE TO CONTACT JEFF KOSKIE AT 213 244-3283. | 201050 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
680 | 2008-07-17 | CA | technical failure | UNKNOWN (SAN DIEGO COUNTY) | SAN DIEGO GAS & ELECTRIC CO | ON JULY 17, 2008, A FIRE ERUPTED WHILE AN SDG&E CREW WAS WORKING TO REPAIR A LEAK ON A MEDIUM PRESSURE 3¿ PE MAIN. SINCE ONE EMPLOYEE RECEIVED FIRST AND SECOND DEGREE BURNS AND WAS TRANSPORTED TO THE HOSPITAL, THE INCIDENT WAS REPORRTED TO DOT AND CPUC. INVESTIGATION DETERMINED THAT THE FIRE STARTED AS A RESULT OF FAILURE TO KEEP SOURCES OF IGNITION OUT OF THE IMMEDIATE AREA. SPECIFICALLY, THE INJURED EMPLOYEE LIT A CIGARETTE WHILE TAKING A BREAK WITHIN THE LEAK REPAIR EXCAVATION. INJURED EMPLOYEE HAS BEEN RELEASED FROM THE HOSPITAL, AND ALL REPAIRS TO PIPELINE HAVE BEEN COMPLETED. IF YOU HAVE ANY QUESTIONS, FEEL FREE TO CONTACT JEFF KOSKIE AT 213 244-3283. | 2000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
681 | 2008-07-31 | TX | sabotage | UNKNOWN (DENTON COUNTY) | COSEAY GAS | 6" POLY MAIN DAMAGED BY CONTRACTOR DRILLING HOLES FOR NEW POWER POLES. AUGER WAS PLACED AND OPERATED WITHIN TOLERANCE ZONE OF LOCATE MARKINGS. | 12000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
682 | 2008-07-07 | LA | other | UNKNOWN (JEFFERSON COUNTY) | ATMOS ENERGY CORP (LOUISIANA DIVISION) | INTOXICATED DRIVER RAN OVER NATURAL GAS LOW PRESSURE REGULATOR STATION WITH A TRUCK. THE TRUCK BROKE A 2" GAS LINE CAUSING A FIRE. NOTE: THE TRUCK WAS LOST IN THE FIRE. THERE WAS ALSO DAMAGE TO A UTILITY POLE, AND THE RESIDENT AT THE INCIDENT LOCATION HAD DAMAGE TO THE FENCE, AND HOUSE. | 69116 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
683 | 2008-01-11 | MN | maintenance | UNKNOWN (CARVER COUNTY) | CENTERPOINT ENERGY RESOURCES CORP., DBA CENTERPOINT ENERGY MINNESOTA GAS | ABOUT A WEEK PRIOR TO THE INCIDENT, HOMEOWNER SMELLED GAS. HOMEOWNER CONTACTED A LOCAL APPLIANCE REPAIR COMPANY, SUSPECTING HIS OLD FURNACE WAS THE SOURCE OF THE LEAK. THE REPAIR TECHNICIAN SOLD THE HOMEOWNER A USED FURNACE AND INSTALLED THE FURNACE ON WEDNESDAY, JANUARY 9TH. ON FRIDAY, JANUARY 11TH, THE HOUSE CAUGHT FIRE. THE NEXT DAY, AS PART OF THE FIRE INVESTIGATION, THE SERVICE LINE WAS PRESSURE TESTED FOR LEAKS AND FAILED. A PINHOLE LEAK WAS FOUND ON THE UNDERGROUND COPPER PIPE. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
684 | 2008-08-22 | AK | other | UNKNOWN (ANCHORAGE COUNTY) | ENSTAR NATURAL GAS CO | A FIRE STARTED INSIDE A TRAVEL TRAILER THAT WAS PARKED UNDER A CARPORT AT THIS ADDRESS. THE FIRE PROGRESSED FROM THE TRAVEL TRAILER TO THE HOUSE AND SUBSEQUENTLY BURNED THE GAS METER AND REGULATOR. ENSTAR CREWS DUG UP THE SERVICE LINE AND SHUT IF OF AT THE GAS MAIN TO EXTINGUISH THE BURNING METER. | 201050 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
685 | 2008-07-25 | NY | technical failure | UNKNOWN (QUEENS COUNTY) | CONSOLIDATED EDISON CO OF NEW YORK | ON FRIDAY, 7/25/2008 AT 16:50, CON EDISON'S GAS EMERGENCY RESPONSE CENTER (GERC) RECEIVED A CALL FROM THE FIRE DEPARTMENT OF NEW YORK (FDNY) REPORTING A GAS EXPLOSION AT 147-25 SANFORD AVENUE, FLUSHING, NEW YORK. GAS DISTRIBUTION SERVICES (GDS) RESPONDED AND CONFIRMED THAT THERE HAD BEEN A GAS EXPLOSION AND THE GAS HAD BEEN TURNED OFF TO THE BUILDING BY THE FDNY AT THE OUTSIDER RISER VALVE PRIOR TO OUR ARRIVAL. GDS TURNED OFF AND LOCKED THE SERVICE HEAD VALVE IN THE BASEMENT. NINETY APARTMENTS (TOTAL PERSONS UNKNOWN) WERE EVACUATED FOR SAFETY; EIGHTEEN PEOPLE WERE REPORTED INJURED; THREE OF THE EIGHTEEN WERE HOSPITALIZED, TWO OF WHOM WERE REPORTED TO BE IN CRITICAL CONDITION WITH ONE SUBSEQUENT FATALITY . CON EDISON'S CENTRAL INFORMATION GROUP (CIG) NOTIFIED THE NEW YORK STATE PUBLIC SERVICE COMMISSION (PSC), THE U.S. DEPARTMENT OF TRANSPORTATION (DOT/NRC) AND THE DEPARTMENT OF ENVIRONMENTAL PROTECTION (DEP). CON EDISON'S LAW DEPARTMENT, ENERGY SERVICES, PUBLIC AFFAIRS, ELECTRIC OPERATIONS, PHOTOGRAPHIC SERVICES, ENVIRONMENTAL HEALTH & SAFTEY, GAS CONSTRUCTION AND THE GAS EMERGENY RESPONSE GROUP WERE ALL ON LOCATION. DEP HAZMAT AND PSC REPRESENTATIVE MOHAMMED MAHMOOD RESPONDED TO THE LOCATION. THE INCIDENT INVESTIGATION HAS BEEN CONCLUDED. | 1000000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
686 | 2008-07-21 | CA | sabotage | UNKNOWN (HUMBOLDT COUNTY) | PACIFIC GAS & ELECTRIC CO | A LARGE EXCAVATOR, DIGGING TO INSTALL A CULVERT, WAS MANEUVERING AROUND SOME GROUND SUBSIDENCE AND STRUCK A 4-INCH GAS TRANSMISSION LINE WITH ITS TRACK. THE GAS LINE WAS PROPERLY MARKED AND PG&E HAD STOOD BY DURING CONSTRUCTION ON PRIOR DAYS. NO STANDBY WAS CALLED FOR BY THE EXCAVATOR ON THE DAY OF THE INCIDENT. REPAIRS TO THE LINE WERE MADE AND THE LINE WAS PUT BACK IN SERVICE ON 7/22/08 AT 0340. PG&E INITIALLY ESTIMATED THE COST OF THE INCIDENT TO BE APPROXIMATELY $35,000. ON 8/6/08, ACTUAL COSTS IN PG&E ACCOUNTING SYSTEM WERE FOUND TO EXCEED $50,000. | 70500 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
687 | 2008-08-07 | UT | technical failure | UNKNOWN (SALT LAKE COUNTY) | QUESTAR GAS COMPANY | THE RELEASE OF GAS AND THE RESULTING EMPLOYEE INJURY WAS THE RESULT OF THE EMPLOYEE INADVERTENTLY OPERATING A SLIDE GATE VALVE RESULTING IN INJURIES TO THAT EMPLOYEE. THE EMPLOYEE WAS INJURED IN THE FACE AND WAS HOSPITALIZED FOR SEVERAL DAYS. THE EMPLOYEE HAS RECOVERED AND HAS RETURNED TO SERVICE. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
688 | 2008-08-07 | MD | sabotage | UNKNOWN (CECIL COUNTY) | ELKTON GAS SERVICE - DIV PENNS & SOUTHERN GAS CO | THOMPSON ELECTRIC, CONTRACT FOR MD STATE HIGHWAY ADMINISTRATION, HIT ELKTON GAS 4" STEEL WHILE PREPARING A TRENCH FOR INSTALLATION OF ELECTRIC FOR NEW TRAFFIC LIGHTS AT THE INTERSECTION OF NORTH STREET AND RAILROAD AVENUE, IN ELTON MD 21921. GAS LINE WAS MARKED. NO APPARENT TEST HOLES WERE DUG BY CONTRACTOR. CONTRACTOR OPERATED HEAVY EQUIPMENT OVER MARKED LINES. A FIRE ENSUED, ENGULFING CONTRACTOR EQUIPMENT FOR 90 MINUTES. | 46841 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
689 | 2008-08-05 | TX | other | UNKNOWN (HARRIS COUNTY) | ENTEX, A NORAM ENERGY COMPANY (FORM. DIV OF ARKLA | ESCAPING GAS FROM A 1" STL SERVICE LINE ENTERED STRUCTURE & REACHED AN UNKNOWN IGNITION SOURCE. | 260227 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
690 | 2008-08-24 | CA | other | UNKNOWN (TULARE COUNTY) | SOUTHERN CALIFORNIA GAS CO | ON AUGUST 24, 2008, A STRUCTURE FIRE OCCURRED AT THE ABOVE ADDRESS. THE BUILDING WAS SEVERELY DAMAGED FROM FIRE. THE GAS METER WAS MELTED FROM THE INTENSE HEAT, AND ESCAPING GAS IGNITED. IGNITED GAS DID NOT CREATE FURTHER DAMAGE, NOR DID IT IMPACT FIREFIGHTING PROGRESS. THIS INCIDENT BECAME REPORTABLE WHEN MEDIA ARRIVED, AND TOTAL DAMAGE FROM FIRE WAS DETERMINED TO EXCEED $50,000. THE GAS SERVICE WAS SHUT OFF AND REPAIRS PERFORMED. DAMAGE TO METER SET APPEARS TO BE THE RESULT OF INTENSE HEAT FROM THE STRUCTURE FIRE. CAUSE OF FIRE WAS DETERMINED TO BE ARSON-RELATED AND NOT INVOLVING UTILITY FACILITIES. | 100500 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
691 | 2008-08-07 | KS | other | UNKNOWN (SHAWNEE COUNTY) | KANSAS GAS SERVICE | A DELIVERY VAN USED BY DRY CLEANING BUSINESS WAS BEING STOLEN FROM THE PROPERTY WHEN THE DRIVER BACKED OVER THE CUSTOMERS METER SET AND RISER LOCATED AT THE PROPERTY LINE. THE COLLISION WITH THE METER SET AND RISER BROKE THE RISER JUST BELOW GROUND LEVEL AND RELEASED GAS TO THE ATMOSPHER. THE DRIVER OF THE VEHICLE ATTEMPTED TO DRIVE THE VEHICLE OFF THE METER SET AND RISER AND WAS UNSUCCESSFUL. THIS ACTION POTENTIALLY CREATED SPARKS FROM METAL TO METAL FRICTION CAUSING THE GAS TO IGNITE. WHEN THE IGNITION OCCURRED THE DRIVER AND A PASSENGER FLED THE SCENE. | 139600 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
692 | 2008-08-27 | WY | other | UNKNOWN (UINTA COUNTY) | QUESTAR GAS COMPANY | GAS FROM THE METER IGNITED AS A RESULT OF THE BUILDING BEING ON FIRE. | 600800 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
693 | 2008-09-02 | ND | leaks and spills | UNKNOWN (CASS COUNTY) | NORTHERN STATES POWER CO OF MINNESOTA |  | 152000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
694 | 2008-09-12 | CA | other | UNKNOWN (LOS ANGELES COUNTY) | SOUTHERN CALIFORNIA GAS CO | ON SEPTEMBER 13, 2008 A METER SET ASSEMBLY WAS DAMAGED BY A VEHICLE THAT LOST CONTROL, LEAVING THE ROADWAY, CRASHING THROUGH A BLOCK WALL AND STRIKING INTO THE METER SET ASSEMBLY. THE ESCAPING GAS IGNITED, CAUSING A FIRE THAT DAMAGED A BUILDING. DUE TO BUILDING DAMAGE, THIS FACILITY WILL NOT BE RESTORED AT THIS TIME. THE METER LOCATION WAS NOT SUBJECT TO TRAFFIC. THIS INCIDENT BECAME REPORTABLE TO DOT BASED UPON THE ESTIMATE DOLLAR AMOUNT OF FIRE DAMAGE EXCEEDING $50,000. | 50500 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
695 | 2008-09-16 | CA | other | UNKNOWN (RIVERSIDE COUNTY) | SOUTHERN CALIFORNIA GAS CO | ON JUNE 18TH, 2007, A STRUCTURE FIRE OCCURRED AT THIS LOCATION. THE BUILDING WAS SEVERELY DAMAGED FROM FIRE. THE INTENSE HEAT ALSO DAMAGED THE ½ PE SERVICE RISER, WITH ESCAPING GAS ULTIMATELY IGNITING. THIS INCIDENT BECAME REPORTABLE WHEN TOTAL FIRE DAMAGE ESTIMATES EXCEEDED $50,000. THE GAS SERVICE WAS SHUT OFF AND REPAIRS PERFORMED. IGNITED GAS DID NOT CONTRIBUTE TO ANY PROPERTY DAMAGE, AND DID NOT HINDER FIREFIGHTING EFFORTS. THE FIRE STARTED AWAY FROM ANY UTILITY GAS FACILITIES. | 61000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
696 | 2008-07-09 | WA | sabotage | UNKNOWN (KING COUNTY) | PUGET SOUND ENERGY | A CONTRACTING FIRM RETAINED BY A LOCAL MUNICIPAL HOUSING AUTHORITY TO INSTALL SITE UTILITIES AND PERFORM GENERAL CONSTRUCTION ACTIVITIES DAMAGED (SEVERED) THE 2¿ WELDED TEE SECTION WELDED ON A 6¿ DISTRIBUTION WELD. ALL APPLICABLE PSE (PUDGET SOUND ENERGY) GAS SYSTEM ASSETS WERE LOCATED ON TIME AND WERE ACCURATE. IN ADDITION, PSE REPRESENTATIVES REGULARLY ATTENDED THE SITE ENSURING THAT THE CONTRACTOR REMAINED AWARE OF THE LOCATION AND THE IMPORTANCE OR REMAINING CLEAR OF THE GAS DISTRIBUTION SYSTEM. THE EXCAVATION ARE HAD BEEN OPEN FOR SOME TIME AND AS VERIFIED THROUGH THE POST-INCIDENT REVIEW PROCESS THE EXCAVATION CONTRACTOR STATED THAT THEY WERE WELL AWARE OF THE LOCATION OF THE MAIN. IN THE PROCESS OF PERFORMING THERE ACTIVITIES, THEY WERE TRAVERSING ALONG THE UPPER PORTION ON THE EXCAVATION AREA WHEN THE EXCAVATOR (TRACK BACKHOE) SLIDE INTO THE DITCH AT WHICH POINT THE TRACK PORTION OF THE BACKHOE SEVERED THE 2¿ WELDED ON TOP OF THE 6¿ DISTRIBUTION MAIN. EVACUATION WAS LIMITED TO THE IMMEDIATE PROXIMITY (EXACT NUMBER OF CUSTOMERS UNKNOWN) HOWEVER IT WAS LESS THAN 50. THE LARGEST PORTION OF THE COSTS RELATED TO THIS INCIDENT WERE RELATED TO THE AMOUNT OF LOST GAS WHICH WAS IN EXCESS OF $30,000. RESULTS WERE THAT THERE WAS NO OTHER PERSONAL PROPERTY OR INJURY TO ANY WORKERS, EMPLOYEES OR CUSTOMERS BESIDES THE SPECIFIC DAMAGE TO THE GAS DISTRIBUTION SYSTEM. THE RESPONSE, LOST GAS AND REPAIR OF THE GAS DISTRIBUTION SYSTEM EXCEEDED $50,000. FOR INFORMATION PURPOSES THE INFORMATION BELOW CONTAINS THE INFORMATION SUBMITTED TO THE STATE: "PSE RESPONDED TO A REPORT FROM A CONTRACTOR OF A DAMAGED GAS MAIN. THE CONTRACTOR DAMAGED A 6¿ STW MAIN WHILE EXCAVATING WITH A TRACK HOE. PSE¿S FIRST RESPONDER CONTROLLED THE FLOW OF GAS BY INSTALLING A STOPPER AND HUTTING OFF VALVES. PSE¿S SERVICE PROVIDER MADE PERMANENT REPAIRS. THERE WERE NO INJURIES NOR WAS ANY PROPERTY DAMAGED EXCEPT FOR THE GAS MAIN. COSTS OF THE RESPONSE AND REPAIR ARE BEING ACCUMULATED AND THE COMMISSION WILL BE NOTIFIED WHEN THE TOTAL IS KNOWN. THE COMMISSION WAS NOTIFIED OF THIS INCIDENT AT 15:30 HOURS ON JULY 9, 2008. KUANG CHU RECEIVED THE CALL." | 70239 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
697 | 2008-09-11 | VA | other | UNKNOWN (FAIRFAX COUNTY) | WASHINGTON GAS LIGHT CO | WASHINGTON GAS RESPONDED TO THE REPORT OF A COMMERCIAL BUILDING FIRE AT 6065 RICHMOND HIGHWAY, ALEXANDRIA ON THE EVENING OF SEPTEMBER 11, 2008. THE CREW DUG DOWN ON THE TWO-INCH PLASTIC SERVICE, SQUEEZED IT OFF, AND THEN CAPPED IT OFF. A SUBSURFACE LEAK SURVEY AND SERVICE LINE PRESSURE TEST WERE CONDUCTED TO ENSURE THE INTEGRITY OF THE SYSTEM. DISCUSSIONS WITH THE FIRE MARSHALL INDICATED THAT GAS WAS SECONDARY. | 2005000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
698 | 2008-09-20 | MI | other | UNKNOWN (OAKLAND COUNTY) | CONSUMERS ENERGY CO | A CALL FROM 911 CAME INTO THE CUSTOMER SERVICE CENTER AND A SERVICE WORKER WAS DISPATCHED TO 850 S. PEMBERTON. UPON ARRIVAL THE SERVICE WORKER FOUND A HOME DESTROYED BY AN EXPLOSION AND SUBSEQUENT FIRE. ONE RESIDENCE AT THE HOME DIED IN THE EVENT. A CONSUMER ENERGY CREW PRESSURE TESTED THE OUTSIDE PIPING AND FOUND NO LEAKS ON THE SERVICE PIPING. THE CREW ALSO PREFORMED BAR TESTING PROCEDURES AT ALL FOUR CORNERS OF THE STRUCTURE, ALONG THE SERVICE LINE AND MAIN, AND FOUND NO INDICATION OF GAS IN THE GROUND. NO CAUSE HAS BEEN DETERMINED AT THIS TIME. THE INCIDENT IS STILL UNDER INVESTIGATION. THE METER/REGULATOR WAS REMOVED AND WAS ORIGINALLY SECURED AT THE BLOOMFIELD TOWNSHIP FIRE HALL BUT HAS SUBSEQUENTLY BEEN SECURED BY A THIRD PARTY FOR FUTURE EVALUATION. THIS REPORT IS BEING SUBMITTED TO SATISFY REQUIREMENTS IN 49CFR191.9 DISTRIBUTION SYSTEM: INCIDENT REPORT; REQUIRING A WRITTEN REPORT AS SOON A PRACTICABLE BUT NO LATER THAN 30 DAYS. A SUBSEQUENT REPORT WILL BE SUBMITTED WHEN ADDITIONAL INFORMATION BECOMES AVAILABLE. THIS INCIDENT LED TO LITIGATION. THE PLAINTIFF'S EXPERT BLAMED THE INCIDENT ON CORROSION OF THE GAS SERVICE RISER PIPE. CONSUMERS ENERGY'S EXPERTS CONCLUDED THE CAUSE WAS AN INSIDE GAS LEAK. AFTER FIVE (5) TRIAL DAYS THE PARTIES SETTLED THE CASE. THE CAUSE OF THIS INCIDENT REMAINS UNDETERMINED. | 400120 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
699 | 2008-09-25 | UT | other | UNKNOWN (SWEETWATER COUNTY) | QUESTAR GAS COMPANY | GAS FROM THE METER IGNITED AS A RESULT OF THE BUILDING BEING ON FIRE. | 501000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
700 | 2008-09-20 | IN | other | UNKNOWN (MARION COUNTY) | CITIZENS GAS & COKE UTILITY | UPON A COMPLETE INVESTIGATION IT WAS DETERMINED THIS RESIDENTIAL FIRE ORIGINATED INSIDE THE BUILDING AND THE HEAT, FROM THE FIRE, IMPINGED ON THE RISER CAUSING THE RELEASE OF GAS. | 225000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
701 | 2008-10-01 | CA | sabotage | UNKNOWN (ORANGE COUNTY) | SOUTHERN CALIFORNIA GAS CO | ON OCTOBER 1, 2008 A 3 INCH PE MAIN WAS DAMAGED BY A BACKHOE EXCAVATING FOR STREET LIGHTING. THE ESCAPING GAS IGNITED, CAUSING A FIRE THAT DAMAGED THE BACKHOE. NO INJURIES OR OUTAGES RESULTED FROM THIS INCIDENT. REPAIRS WERE COMPLETED THE SAME DAY. INVESTIGATION DETERMINED THAT CONTRACTOR DID HAVE A CURRENT USA REQUEST FOR THIS LOCATION AND WORK BEING PERFORMED. THE FACILITY WAS LOCATED AND MARKED CORRECTLY. DAMAGE WAS LIKELY DUE TO FAILURE TO HAND-EXPOSE FACILITIES PRIOR TO MACHINE EXCAVATION. THIS INCIDENT BECAME REPORTABLE TO DOT BASED UPON THE ESTIMATE DOLLAR AMOUNT OF FIRE DAMAGE EXCEEDING $50,000. | 77500 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
702 | 2008-10-02 | MD | other | UNKNOWN (MONTGOMERY COUNTY) | WASHINGTON GAS LIGHT CO | WASHINGTON GAS RESPONDED TO A HOUSE FIRE AT THE REQUEST OF THE MONTGOMERY COUNTY FIRE DEPARTMENT AT 219 FREDERICK AVENUE, ROCKVILLE, MD. THE FIRE IS BELIVED TO HAVE STARTED ON A MATTRESS AND THEN CONSUMED THE METER BUILD-UP. WASHINGTON GAS PERFORMED A LEAK SURVEY AROUND THE RESIDENCE AND NO INDICATIONS WERE FOUND. WASHINGTON GAS ALSO PERFORMED A PRESSURE TEST AT 20 PSI FOR 15 MINUTES THAT THAT TEST SHOWED NO INDICATIONS OF A LEAK. ODORANT SAMPLES WERE TAKEN AND ALSO FOUND TO BE ACCEPTABLE. | 251100 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
703 | 2008-10-16 | CO | sabotage | UNKNOWN (EL PASO COUNTY) | BLACK HILLS ENERGY | PRIVATE CONTRACTOR INSTALLING ELECTRIC SERVICE AT NEW RESTAURANT STRUCK A 2" GAS SERVICE PREVIOUSLY INSTALLED AT THE SAME LOCATION. LOCATES WERE NOT CALLED IN PRIOR TO EXCAVATION. RESULTING FIRE DESTROYED A TRENCHER BELONGING TO THE EXCAVATOR AND DID EXTENSIVE DAMAGE TO THE UNFINISHED RESTAURANT BELONGING TO MCDONALDS. | 51650 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
704 | 2008-10-15 | CA | other | UNKNOWN (CONTRA COSTA COUNTY COUNTY) | PACIFIC GAS & ELECTRIC CO | TRASH FIRE SPREAD FROM RESIDENCE GREEN CAN TO THE ADJACENT FENCE, THEN TO THE HOME AND THE GAS METER SET. THE GAS METER, REGULATOR, AND RISER MELTED, AND THE ESCAPING GAS CONTRIBUTED TO THE FIRE. IT IS BELIEVED THAT RAGS SOAKED WITH CHEMICALS CAUSED THE IGNITION IN THE RECYCLE CONTAINER. PG&E CONTROLLED THE FLOW OF GAS BY EXCAVATING AND SQUEEZING THE GAS SERVICE LINE. DAMAGE TO THE PROPERTY AND THE GAS FACLITIES COULD EXCEED $50,000. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
705 | 2008-10-22 | AZ | leaks and spills | UNKNOWN (YUMA COUNTY) | SOUTHWEST GAS CORP | ON 10/22/08 AT 2016 HOURS, SOUTHWEST GAS CORPORATION (SWG) WAS NOTIFIED OF A STRUCTURE FIRE AT THE ABOVE ADDRESS BY THE YUMA RURAL METRO FIRE DEPARTMENT. THE SWG TECHNICIAN ARRIVED ON SITE AT 2048 HOURS AND FOUND THE FIRE, WHICH HAD BEEN EXTINGUISHED, HAD DAMAGED THE GARAGE AND CONSUMED THE VEHICLE IN THE GARAGE. THE TECHNICIAN THEN TURNED OFF THE NATURAL GAS METER TO THE RESIDENCE AND BEGAN A LEAK INVESTIGATION. AT 2126 HOURS THE TECHNICIAN DETECTED UNDERGROUND READS AT THE FOUNDATION OF THE STRUCTURE, RESULTING IN THE EVACUATION OF THE TWO RESIDENTS. FURTHER DISCUSSION BETWEEN SWG PERSONNEL, THE RESIDENT AND THE FIRE DEPARTMENT INDICATED THAT THERE MAY HAVE BEEN AN IGNITION OF NATURAL GAS. ONCE THE EXTENT OF THE UNDERGROUND GAS MIGRATION HAD BEEN DETERMINED (RESULTING IN THE ADDITIONAL EVACUATIONS) AND THE AREA SECURED, THE 2" PE MAIN SUPPLYING GAS TO THE AREA WAS SHUT DOWN AT 0107 HOURS WITH THE UTILIZATION OF TWO DIG AND SQUEEZE POINTS. FURTHER INVESTIGATION INTO THE INCIDENT FOUND THE LEAK TO HAVE OCCURRED ON A 1" PE SERVICE STUB. THE CAUSE OF THE LEAK ON THE 1" PE LINE REMAINS UNDER INVESTIGATION. A SUPPLEMENTAL REPORT WILL BE SUBMITTED UPON COMPLETION OF THE INVESTIGATION BY SWG. THERE WERE NO INJURIES OR FATALITIES AS A RESULT OF THIS INCIDENT. SUPPLEMENTAL/FINAL REPORT 6/30/2010 - FURTHER INVESTIGATION BY SWG INDICATES THAT THE CAUSE OF THIS INCIDENT WAS A MATERIAL FAILURE. OUTSIDE LAB ANALYSIS SUBMITTED TO THE ARIZONA CORPORATION COMMISSION ON JUNE 25, 2010. | 152136 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
706 | 2008-10-18 | NC | other | UNKNOWN (GUILFORD COUNTY) | PIEDMONT NATURAL GAS CO INC | AT 11:49 AM ON OCTOBER 18, 2008, PIEDMONT NATURAL GAS (PNG) RECEIVED A CALL FROM THE LOCAL FIRE DEPARTMENT IN GREENSBORO, NC NOTIFYING US OF A FIRE AT 2215 TEXTILE DRIVE. THE FIRST RESPONDER WAS DISPATCHED TO THE SCENE SHORTLY THEREAFTER. PNG PERSONNEL ARRIVED APPROXIMATELY AT 12:00 P.M. TO SHUT THE SERVICE OFF AT THE HOUSE, ONLY TO FIND THAT THE FIRE DEPARTMENT HAD SHUT THE SERVICE OFF AT APPROXIMATELY 11:57 AM. THE HOUSE WAS VACANT AND RECENTLY REMODELED. THE EXPLOSION RESULTED IN THE COMPLETE LOSS OF THE HOUSE, THERE WERE NO INJURIES NOR FATALITIES. THE CAUSE OF THIS INCIDENT, AS DETERMINED BY THE FIRE DEPARTMENT INVESTIGATION TEAM AND BY PNG¿S EXTERNAL INVESTIGATIVE CONSULTANT, WAS A STOLEN 3-FOOT SECTION OF COPPER TUBING FROM THE CUSTOMER¿S FUEL LINE UNDER THE HOUSE, THUS MAKING THIS A NON-JURISDICTIONAL EVENT. OUR RECORDS DETERMINED THAT THE SERVICE TO THE HOME WAS ACTIVE (¿ON¿). | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
707 | 2008-10-18 | MD | other | UNKNOWN (PRINCE GEORGES COUNTY) | WASHINGTON GAS LIGHT CO | WASHINGTON GAS WAS CALLED BY THE PRINCE GEORGES FIRE DEPARTMENT TO ASSIST WITH A HOUSE FIRE LOCATED AT 6600 TROWBRIDGE PLACE, FORT WASHINGTON, MARYLAND. THE FIRE DAMAGED THE METER AND REGULATOR ASSEMBLY LOCATED IN THE BASEMENT. THE FIRE DEPARTMENT TURNED OFF THE VALVE AT THE INSIDE METER. THE WASHINGTON GAS SERVICE TECHNICIAN ARRIVED ON SITE AND SHUT OFF THE OUTSIDE CURB VALVE FOR THE SERVICE LINE. A SUBSURFACE LEAK SURVEY WAS CONDUCTED OVER THE SERVICE, MAIN, AND AROUND THE PERIMETER OF THE BUILDING. A PRESSURE TEST WAS CONDUCTED ON THE SERVICE LINE FROM THE OUTSIDE CURB VALVE TO THE BUILDING WALL AND THE PRESSURE TEST HELD. AN ODORANT SAMPLE WAS ALSO TAKEN AND SHOWED ACCEPTABLE LEVELS OF ODORANT. WASHINGTON GAS BELIEVES THE FIRE MAY HAVE STARTED FROM A POSSIBLY SHORTED ELECTRICAL CONDUCTOR LOCATED IN THE CEILING OF THE BASEMENT. | 251100 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
708 | 2008-10-22 | CA | other | UNKNOWN (SAN FRANCISCO COUNTY) | PACIFIC GAS & ELECTRIC CO | A FLASH FIRE IN A WORKING TRENCH WAS CAUSED BY A 3RD PARTY WHO WAS SOLDERING A WATER PIPE AND INADVERTENTLY LET THE FLAME DAMAGE A 1/2 INCH PG&E PLASTIC GAS PIPE NEARBY. THE USA TICKET WAS EXPIRED IN THIS AREA. ACCORDING TO THE 3RD PARTY, THE WORKER WAS CHECKED INTO A HOSPITAL AND KEPT FOR OBSERVATION OVERNIGHT. THE WORKER SUSTAINED A BACK INJURY WHILE ESCAPING FROM THE TRENCH. | 3050 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
709 | 2008-10-18 | WY | other | UNKNOWN (SWEETWATER COUNTY) | QUESTAR GAS COMPANY | AT APPROXIMATELY 4:30 A.M. ON SATURDAY, OCTOBER 18, 2008 A VEHICLE TRAVELING EAST ON FOOTHILL BOULEVARD APPROXIMATELY 1.5 MILES WEST OF ROCK SPRINGS WYOMING, LEFT THE ROADWAY AND IMPACTED AN ABOVE GROUND QUESTAR FACILITY CONSISTING OF A 2" TAP AND RISER, A 2" X 3/4" REDUCER, AND A 3/4" PIPE WHICH PROVIDED SERVICE TO A REGULATOR LOCATED ABOUT 50 FEET AWAY. THE VEHICLE STRUCK AND BROKE TWO 4" POST TYPE BARRIERS THEN STRUCK THE 2" RISER CAUSING THE 3/4" LINE TO FAIL AND LEAK AT THE POINT WHERE IT WAS WELDED TO A 2" X 3/4" REDUCER FITTING. DURING THE REPAIRS, US INTERSTATE 80 WAS CLOSED IN BOTH THE EAST AND WEST DIRECTIONS AND SERVICE WAS LOSS TO 382 CUSTOMERS INCLUDING SEVERAL BUSINESSES AND RESIDENTS AT A NEARBY MOBILE HOME PARK. THE DRIVER WAS TREATED AND RELEASED FROM THE HOSPITAL AND WAS CITED BY THE WYOMING HIGHWAY PATROL FOR CHARGES INCLUDING DRIVING UNDER THE INFLUENCE AND FAILURE TO MAINTAIN HIS VEHICLE WITHIN A SINGLE LANE. | 28640 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
710 | 2008-11-15 | CA | technical failure | UNKNOWN (COLUSA COUNTY) | PACIFIC GAS & ELECTRIC CO | A PG&E EMPLOYEE WAS INJURED WHILE INSTALLING AND PURGING A COMMERCIAL METER SET. WHILE GAS WAS VENTING, THE EMPLOYEE BEGAN TIGHTENING THE FLANGE BOLTS WITH AN 18-VOLT WRENCH WHEN THE FIRE IGNITED. THE EMPLOYEE WAS TRANSPORTED TO THE HOSPITAL WHERE HE SPENT THE NIGHT AND WAS RELEASED 11/16/08. THE INCIDENT WAS DETERMINED TO BE REPORTABLE DUE TO THE HOSPITALIZATION OF THE EMPLOYEE. THE INCIDENT WAS REPORTED LATE DUE TO FAILURE OF THE SUPERVISOR TO NOTIFY GAS CONTROL. THERE WERE NO FIRES, POLICE OR MEDIA PRESENT AT THE SCENE AND DAMAGE WAS LESS THAN $50,000. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
711 | 2008-10-22 | VA | other | UNKNOWN (PRINCE WILLIAM COUNTY) | WASHINGTON GAS LIGHT CO | WASHINGTON GAS RESPONDED TO A HOUSE FIRE LOCATED AT 3225 CONKLIN WAY, HAYMARKET, VA AT THE REQUEST OF THE PRINCE WILLIAM FIRE DEPARTMENT. UPON ARRIVAL WASHINGTON GAS FOUND THE METER VALVE HAD BEEN TURNED OFF BY THE FIRE DEPARTMENT. WASHINGTON GAS ALSO DUG THE SERVICE UP AT THE MAIN AND CAPPED IT OFF. WASHINGTON GAS CONDUCTED A 360-DEGREE BAR AND TEST SURVEY WITH NO LEAK INDICATIONS ON THE EVENING OF WEDNESDAY, OCTOBER 22, 2008. ADDITIONALLY, ON THURSDAY, OCTOBER 23, 2008, WASHINGTON GAS CONDUCTED A PRESSURE TEST OF THE BRANCHED SERVICE LINE SERVING 6225 & 6223 CONKLIN WAY AT 55 PSI FOR 10 MINUTES ON A GAUGE AND 5 MINUTES ON A BOTTLE AND THE TEST PASSED. AN ODORANT SAMPLE WAS TAKEN AND THE ODORANT WAS FOUND TO BE DETECTABLE AT 0.17% GIA. THE FIRE APPEARS TO HAVE STARTED ON THE DECK ABOVE THE WASHINGTON GAS FACILITIES POSSIBLY CAUSED BY IMPROPERLY DISCARDED SMOKING MATERIALS. | 751100 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
712 | 2008-11-03 | CA | other | UNKNOWN (LOS ANGELES COUNTY) | SOUTHERN CALIFORNIA GAS CO | ON NOVEMBER 3, 2008, A SERVICE RISER WAS DAMAGED WHEN A FORK LIFT STRUCK A CUSTOMER HOUSELINE, SHIFTING THE METER SET ASSEMBLY AND CRACKING THE RISER BELOW THE SHUTOFF VALVE. ESCAPING GAS IGNITED, DAMAGING THE FORKLIFT AND NEARBY TRUCK. FORKLIFT OPERATOR RECEIVED SECOND DEGREE BURNS AND WAS TREATED AND RELEASED AT A NEARBY HOSPITAL. METER SET ASSEMBLY WAS PROTECTED FROM TRUCK TRAFFIC BY STEEL GUARDPOSTS. SOUTHERN CALIFORNIA GAS COMPANY WAS UNAWARE THAT A FORKLIFT WOULD BE OPERATED IN THIS VICINITY. THE METER SET ASSEMBLY HAS BEEN REMOVED FROM THIS LOCATION, AND WILL NOT BE REINSTALLED UNTIL A PLAN FOR PROTECTION CAN BE DEVELOPED AND IMPLEMENTED. | 61000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
713 | 2008-11-04 | NJ | other | UNKNOWN (MONMOUTH COUNTY) | NEW JERSEY NATURAL GAS CO | IT IS NJNG UNDERSTANDING FROM INFORMATION GATHERED THAT THE HOMEOWNER WAS TRYING TO RELIGHT HIS HOUSE FURNACE AT WHICH TIME THE GAS IGNITED AND AN EXPLOSION OCCURED. THIS INCIDENT IS UNDER INVESTIGATION BY THE AUTHORITIES. UPDATE: THE FINAL CAUSE OF THIS INCIDENT WAS DETERMINED TO BE "BUILDUP OF GAS IN THE BASEMENT FROM AN UNDETERMINED SOURCE" AND THAT THE SOURCE OF IGNITION WAS POSSIBLY THE "FURNACE CONTROL SWITCH". NJNG RESPESCTFULLY REQUEST THAT THIS INCIDENT BE CONSIDERED CLOSED. | 500000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
714 | 2008-10-31 | OH | sabotage | UNKNOWN (FRANKLIN COUNTY) | COLUMBIA GAS OF OHIO INC | THIS INCIDENT WAS CAUSED BY 3RD PARTY DAMAGE RESULTING IN THE RELEASE OF GAS AND SUBSEQUENT EXPLOSION. NOTE. PART A SECTION 8-A WILL ALLOW ONLY WHOLE NUMBERS WITH NO DECIMALS TO BE ENTERED AND THAT 1.0 WAS ENTERED WHILE THE ACTUAL MAOP FOR THIS SYSTEM IS 0.50 PSIG. | 251480 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
715 | 2008-10-31 | KY | sabotage | UNKNOWN (FAYETTE COUNTY) | COLUMBIA GAS OF KENTUCKY INC | ATS CONTRACTING WAS GRADING ALONG THE SHOULDER OF NEW CIRCLE ROAD ON THE OUTER LOOP SHOULDER FOR ROAD CONSTRUCTION, THEY HAD CALLED FOR CURRENT LOCATES AND DPS LOCATING HAD PROPERLY LOCATED THE 12" HIGH PRESSURE MAIN. (LOCATE TICKET #810160081). ATS ASSUMED THAT THEY WERE EXCAVATING WITHIN ABOUT 6" OF THE MAIN HORIZONTALLY AND ALSO ASSUMED THAT THE MAIN WAS APPROXIMATELY 2.8' IN VERTICAL DEPTH. HOWEVER AT THE POINT THE MAIN WAS DAMAGED THERE WAS ONLY ABOUT 1' OF COVER. THE REVISED KENTUCKY DIG LAW CLEARLY STATES UNDER KRS 367.4911 PART (9). WHEN EXCAVATION OR DEMOLITION IS NECESSARY WITHIN THE APPROXIMATE LOCATION OF THE UNDERGROUND FACILITY, THE EXCAVATOR SHALL HAND DIG OR USE NONINTRUSIVE MEANS TO AVOID DAMAGE TO THE UNDERGROUND FACILITY. THIS IS FURTHER DEFINED ON PAGE 12 UNDER LOCATION TOLERANCE ZONES FOR SMALL PIPELINES. IT STATES THE TOLERANCE ZONE INCLUDES THE WIDTH OF THE FACILITY AND 18" MEASURED HORIZONTALLY FROM EACH SIDE OF THE FACILITY. ATS HAD NOT UNCOVERED THE MAIN TO VERIFY DEPTH THEREFORE CAUSING DAMAGE TO THE MAIN BY STRIKING IN WITH A BULLDOZER. | 408567 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
716 | 2008-10-25 | OH | other | UNKNOWN (RICHLAND COUNTY) | COLUMBIA GAS OF OHIO INC | COLUMBIA'S INVESTIGATION HAS DETERMINED THAT THIS EVENT DID NOT INVOLVE A RELEASE OF NATURAL GAS FROM A DOT JURISDICTIONAL FACILITY. THEREFORE, COLUMBIA HAS CONCLUDED THAT THIS WAS NOT A REPORTABLE INCIDENT. PLEASE CLOSE YOUR FILE IN THIS MATTER. | 65011 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
717 | 2008-11-07 | MD | sabotage | UNKNOWN (nan COUNTY) | BALTIMORE GAS & ELECTRIC CO | MILLER PIPELINE A CONTRACTOR WORKING FOR BALTIMORE GAS & ELECTRIC COMPANY INSTALLING A 12" STEEL MAIN FOR A REINFORCEMENT/REPLACEMENT PROJECT STRUCK 1-1/4" STEEL SERVICE TO 8860 GORMAN RD CAUSING GAS LEAK. | 95674 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
718 | 2008-11-13 | CA | other | UNKNOWN (nan COUNTY) | SOUTHERN CALIFORNIA GAS CO | ON NOVEMBER 13, 2008 A FIRE BROKE OUT IN THE CITY OF MONTECITO, DAMAGING SERVICES, RISERS AND METER SET ASSEMBLIES. DAMAGE TO SOCALGAS GAS FACILITIES WAS LIMITED TO THESE COMPONENTS. NO DAMAGE TO DISTRIBUTION MAINS OR TRANSMISSION LINES OCCURRED. WHILE GAS ESCAPING FROM THESE FACILITIES DID IGNITE ON OCCASION, IT WAS NOT RESPONSIBLE FOR CAUSING ANY ADDITIONAL DAMAGE OR INJURIES. ALL REPAIRS OF GAS FACILITIES HAVE BEEN COMPLETED. MANY OF THE INVOLVED FACILITIES WERE ATTACHED TO BUILDINGS THAT HAVE BEEN DESTROYED, SO NO RESTORATION IS NECESSARY AT THIS TIME. THE ESTIMATE OF COSTS ASSOCIATED WITH THESE DAMAGES ($50,000) IS FOR RESTORATION OF ALL DAMAGED GAS FACILITIES. IT DOES NOT INCLUDE COSTS ASSOCIATED WITH EMERGENCY RESPONSE, STANDBY, AND GOVERNMENTAL AGENCY SUPPORT. THIS INCIDENT WAS REPORTABLE TO PHMSA DUE TO FACILITY DAMAGE EXCEEDING $50,000, AS WELL AS SIGNIFICANT NATIONAL MEDIA COVERAGE. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
719 | 2008-11-15 | CA | other | UNKNOWN (LOS ANGELES AND ORANGE COUNTY) | SOUTHERN CALIFORNIA GAS CO | ON NOVEMBER 15, 2008 NUMEROUS FIRES BROKE OUT ACROSS SOUTHERN CALIFORNIA GAS COMPANY (SOCALGAS) SERVICE TERRITORY, DAMAGING SERVICES, RISERS AND METER SET ASSEMBLIES. DAMAGE TO SOCALGAS GAS FACILITIES WAS LIMITED TO THESE COMPONENTS. NO DAMAGE TO DISTRIBUTION MAINS OR TRANSMISSION LINES OCCURRED. WHILE GAS ESCAPING FROM THESE FACILITIES DID IGNITE ON OCCASION, IT WAS NOT RESPONSIBLE FOR CAUSING ANY ADDITIONAL DAMAGE OR INJURIES. ALL REPAIRS OF GAS FACILITIES HAVE BEEN COMPLETED. MANY OF THE INVOLVED FACILITIES WERE ATTACHED TO BUILDINGS THAT HAVE BEEN DESTROYED, SO NO RESTORATION IS NECESSARY AT THIS TIME. THE ESTIMATE OF COSTS ASSOCIATED WITH THESE DAMAGES ($300,000) IS FOR RESTORATION OF ALL DAMAGED GAS FACILITIES. IT DOES NOT INCLUDE COSTS ASSOCIATED WITH EMERGENCY RESPONSE, STANDBY, AND GOVERNMENTAL AGENCY SUPPORT. THIS INCIDENT WAS REPORTABLE TO PHMSA DUE TO FACILITY DAMAGE EXCEEDING $50,000, AS WELL AS SIGNIFICANT NATIONAL MEDIA COVERAGE. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
720 | 2008-11-13 | CO | sabotage | UNKNOWN (PUEBLO COUNTY) | PUBLIC SERVICE CO OF COLORADO | AFTER THE EXPLOSION, A LEAK WAS DISCOVERED ON THE NATURAL GAS SERVICE FOR 105 W. C STREET. THIS SERVICE SUPPLIED NATURAL GAS TO THE BUILDING ACROSS C STREET FROM 301 S. UNION. THE SERVICE TO 105 W. C STREET WAS A 3/4" PLASTIC CAB LINE (CELLULOSE ACETATE BUTALRATE) THAT REPLACED THE ORIGINAL SERVICE. THE CAB WAS INSERTED INTO THE OLD 1 1/4" MV SERVICE LINE. THE CAB SERVICE LINE WAS FOUND TO HAVE SEPARATED FROM A COMPRESSION CUPLING NEAR THE TAP AT 4" MW MAIN. DUE TO CONFLICTING INFORMATION FROM THE INITIAL INVESTIGATION OF THIS INCIDENT, IT HAS NOT BEEN DETERMINED AT THIS TIME IF THIS LEAK CONTRIBUTED TO THE EXPLOSION OR IF THE EXPLOSION WAS THE CAUSE OF THE LEAK. THERE IS AN ONGOING INVESTIGATION TO DETERMINE THE CAUSE OF THIS INCIDENT. A SUPPLEMENTAL REPORT WILL BE SUBMITTED WHEN THIS INVESTIGATION IS COMPLETED. NOTE ON F3 C & D: NO RECORDS HAVE BEEN LOCATED AS TO NOTIFICATION AND DATES. INVESTIGATION FOUND THE INSERTED CAB SERVICE UNDER TENSION CAUSED BY DAMAGE TO THE STEEL CASING BY THIRD PARTY. THIS EVENTUALLY RESULTED IN SEPARATION OF THE CAB PIPING FROM THE COMPRESSION COUPLING. | 250950 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
721 | 2008-12-03 | MO | sabotage | UNKNOWN (ADAIR COUNTY) | ATMOS ENERGY CORPORATION - KY/MID-STATES (KENTUCKY) | C-COM WAS TRENCHING IN TV CABLE ON 12/03/2008 FOR SMOYER TRENCHING AND CABLE COMPANY. AT APPROXIMATELY 7:30 AM ON THE MORNING OF 12/03/2008, C-COM OPERATOR OF TRENCHING MACHINE HIT AND DAMAGED 6" STEEL MAIN OF ATMOS ENERGY. THIS MAIN LINE SERVED CUSTOMERS IN KIRKSVILLE AND ALL TOWNS SOUTH OF KIRKSVILLE. OPERATING PRESSURE OF PIPELINE AT TIME OF OCCURENCE WAS 130 PSIG. SMOYER TRENCHING AND CABLE COMPANY HAD REQUESTED LOCATE ON OCTOBER 31, 2008, TICKET NUMBER 83040980. THE TIME LIMIT HAD EXPIRED ON THIS REQUEST AND NO OTHER CURRENT LOACATES HAD BEEN REQUESTED. THE LINE WAS STILL FLAGGED ON DECEMBER 3, 2008 FROM THE REQUESTED LOCATE OF 10/31/2008. THE MAIN BLEW TO ATMOSPHERE FROM 7:30 AM UNTIL 11:30 AM, AT WHICH TIME THE UPSTREAM VALVE WAS TURNED OFF TO INTIATE REPAIR. | 89137 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
722 | 2008-11-09 | DE | other | UNKNOWN (NEW CASTLE COUNTY) | DELMARVA POWER & LIGHT COMPANY | NEW CASTLE COUNT POLICE REPORT INVESTIGATIVE SUMMARY (CPL. SOMMERS): PRELIMINARY INVESTIGATION REVEALS THAT FOR UNKNOWN REASONS, POSSIBLY MECHANICAL, VEH-1 (1992 CHEVROLET CAPRICE WHITE IN COLOR WITH DELAWARE REGISTRATION 57903) STRUCK THE FRONT OF THE RESIDENCE OF 712 RYSING DR CAUSING THE GAS METER TO RUPTURE AND SET BOTH THE VEH-1 AND THE RESIDENCE ABLAZE. | 36937 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
723 | 2008-11-01 | GA | sabotage | UNKNOWN (COWETA COUNTY) | ATLANTA GAS LIGHT CO | A CONTRACTOR WORKING FOR COWETA COUNTY STRUCK AND KNOCKED A 2-INCH TEE OFF A 6" HP GAS MAIN ALONG RAYMOND HILL ROAD AT FISHER ROAD WHILE WORKING ON A ROAD WIDENING PROJECT. THE CONTRACTOR WAS ATTEMPTING TO REMOVE AN ABANDON GAS MAIN WITH WITH A TRACK HOE WHEN HE CAUSED THE ABANDONED MAIN TO COLLIDE WITH THE 2-INCH TEE ON THE ACTIVE MAIN. | 61934 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
724 | 2008-12-13 | AK | other | UNKNOWN (MATANUSKA SUSITNA BOROUGH COUNTY) | ENSTAR NATURAL GAS CO | ON SATURDAY, DECEMBER 13, 2008 AT 0958 AN ENSTAR SERVICE TECHNICIAN RESPONDED TO A RESIDENTIAL STUCTURE FIRE AT LOT 6, BLOCK 2 KNIK HIGHLANDS SUBDIVISION NEAR WASILLA, ALASKA TO FIND THE PRESSURE REGULATOR AND METER BURNED AND HDPE SERVICE LINE RISER ON FIRE. THE STRUCTURE WAS UNDER CONSTRUCTION. NO ONE WAS LIVING IN THE BUILING AT THE TIME OF THE FIRE. THE RISER WAS PINCHED OFF AND CAPPED TO CONTROL THE FLOW OF NATURAL GAS. THE CAUSE OF THE FIRE IS UNKWNOWN. NATURAL GAS IS NOT BELEIVED TO HAVE CAUSED OR CONTRIBUTED TO THE FIRE. | 51100 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
725 | 2008-09-19 | WA | sabotage | UNKNOWN (KING COUNTY) | PUGET SOUND ENERGY | THE INCIDENT OCCURRED ON SEPT. 19, 2008, AND PSE RESPONDED TO THE INCIDENT REPORT IMMEDIATELY. THE 3RD PARTY CONTRACTOR, WILDER CONSTRUCTION, DAMAGED A 2" STW GAS DISTRIBUTION MAIN WHILE PLACING A SHORING BOX UNDER A WATER DRAINPIPE. PSE'S FIRST RESPONDER AND SERVICE PROVIDER CONSTRUCTED A TEMPORARY BY-PASS PRIOR TO SQUEEZING THE PIPE TO PREVENT OUTAGES TO COMMERCIAL CUSTOMERS DOWNSTREAM OF THE DAMAGED MAIN. PERMANENT REPAIRS WERE COMPLETED BY THE SERVICE PROVIDER THE NEXT BUSINESS DAY.THE COST OF GAS LOSS FROM THE INCIDENT WAS CALCULATED TO BE $4,542.50, WHILE THE COST OF REPAIR AMOUNT TO $70,326.51. THERE WERE NO PERSONAL INJURIES OR PROPERTY DAMAGES TO ANY WORKERS, EMPLOYEES OR CUSTOMERS EXCEPT FOR THE 2" STW DISTRIBUTION MAIN.THE WRITTEN INCIDENT REPORT WAS SUBMITTED TO THE WASHINGTON UTILITIES & TRANSPORTATION COMMISSION ON OCTOBER 15, 2008. A TELEPHONE NOTIFICATION TO THE NRC WAS MADE ON DEC. 12, 2008. THE DELAY IN REPORTING TO THE NRC WAS DUE TO THE FACT THAT IN PERFORMING ROUTINE MONITORING OF THIS INCIDENT IN PREPARATION FOR CLOSING THE FILE, A NUMBER OF INVOICES FROM SUPPORTING INTERNAL AND EXTERNAL ORGANIZATIONS WERE DISCOVERED TO HAVE EXCEEDED THE FEDERAL REPORTING REQUIREMENT OF $50,000. APRIL 24, 2009 - FINALIZING FORM ON 04/24/09 FOR COMPLETION PURPOSES ONLY. CHANGE MADE ON TOTAL COST - LINE A 5.C AS PROMPTED. CHANGE MADE ON 'PERMANENT MARKINGS' AS PER ORIGINAL NOT CHECKED. - LINE F3.9.DII AS PROMPTED. ENTRY BY HELGE FERCHERT, MANAGER, COMPLIANCE AND REGULATORY AUDITS (PUGET SOUND ENERGY) | 74868 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
726 | 2008-11-27 | OH | leaks and spills | UNKNOWN (CUYAHOGA COUNTY) | COLUMBIA GAS OF OHIO INC | Columbia Gas of Ohio, Inc. (Columbia) has completed its investigation and concluded that the incident was the result of an improperly assembled mechanical compression fitting. The property owner’s representative took possession of the pertinent portions of the customer owned service line during the onsite investigation. The property owner's representative discarded the customer owned service line materials before a laboratory analysis could be completed. Through its third party "cause and origin" experts, and one of its compliance specialists, Columbia conducted an onsite examination of the pipe and fittings and took photographs of the service line materials. The on-site inspections, coupled with the photogrammetric examination, identified the fitting as either a Dresser or a Normac compression elbow and indicated that an improper stiffener had been used in the plastic pipe. The investigation found that the plastic pipe had pulled out of the compression fitting. The plastic pipe did not show any signs of yielding. The stiffener that was used in the plastic pipe did not have a flange (lip) on the outer edge. The flange on the stiffener is a key component for pullout protection in the design of both the Dresser and Normac compression fittings. | 75051 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
727 | 2008-12-12 | VA | sabotage | UNKNOWN (PRINCE WILLIAM COUNTY) | COLUMBIA GAS OF VIRGINIA INC | ON 12/12/08, COLUMBIA GAS OF VIRGINIA SUSTAINED A FACILITY DAMAGE TO A 6" PLASTIC, MEDIUM PRESSURE MAIN ON HEATHCOTE BLVD, GAINESVILLE, VIRGINIA. THE NEAREST CROSS STREET IS HERITAGE HUNT DRIVE. ACCORDING TO STAN PENROD OF TEAM FISHEL, THE MAIN WAS DAMAGED AT APPROXIMATELY 1530. L. SLAGER, CGV CUSTOMER CALL CENTER RECEIVED A CALL REPORTING THE DAMAGE AT 1612. MIKE BOSTON, CGV TECHNICIAN ARRIVED ON SITE AT 1623. THE SITE WAS MADE SAFE AT APPROXIMATELY 2115. SERVICE WAS INTERRUPTED TO 1,818 CUSTOMERS. A 6 INCH GAS MAIN WAS DAMAGED BY REAMER ON PULL BACK FROM DIRECTIONAL DRILL. DUE TO THE PROXIMITY OF THE DAMAGE TO OTHER UNDERGROUND UTILITIES, THE CREW COULD NOT SAFELY INSTALL A REPAIR CLAMP IN ORDER TO AVOID A POTENTIAL OUTAGE. THE CREW WAS THEN DIRECTED BY SUPERVISON ON SITE TO EXCAVATE ACROSS THE STREET ON HEATHCOTE BLVD, DOWN TO THE MAIN. THE CREW UNCOVERED THE CASTING PIPE AND THEN HAD TO EXCAVATE BACK FURTHER. A TAPPING TEE FROM A BYPASS WAS THEN ENCOUNTERED ON THE MAIN SO THE CREW THEN BACKED UP EVEN FARTHER. THE MAIN WAS 72 INCHES DEEP IN THIS LOCATION AND THE MAJORITY OF THIS EXCAVATION WAS HAND DUG DUE TO OTHER UNDERGROUND UTILITIES. THE EXCAVATION HAD TO BE LARGE ENOUGH TO ACCOMMODATE A HYDRAULIC 6" SQUEEZE OFF TOOL WHICH WAS USED TO SHUT DOWN THE FLOW OF GAS. TRAFFIC FLOW WAS RESTORED AT APPROXIMATELY 2130 ON 12/12/08 AND COMPLETE RESTORATION OF SERVICE WAS ACCOMPLISHED AT APPROXIMATELY 2300 ON 12/13/08 WITH THE EXCEPTION OF REALTY COMPANY HELD HOMES SCATTERED THROUGHOUT THE DEVELOPMENT. | 108918 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
728 | 2008-12-16 | AZ | other | UNKNOWN (GILA COUNTY) | SEMSTREAM ARIZONA PROPANE LLC | 1 1/4" ALDYL PIPE APPEARED TO HAVE BEEN PREVIOUSLY SQUEEZED OFF, CAUSING DAMAGE TO THE PIPE. THERE WAS NO SEPERATION BETWEEN THE WATER AND GAS PIPE. INVESTIGATION COMPLETE, FINAL REPORT | 205000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
729 | 2008-12-19 | TN | other | UNKNOWN (DAVIDSON COUNTY) | PIEDMONT NATURAL GAS CO INC | AT 6:58 PM CST, A PIEDMONT CUSTOMER SERVICE REPRESENTATIVE RECEIVED A LEAK CALL FOR 416 MURFREESBORO RD. AT 8:00 PM CST, PIEDMONT RECEIVED A CALL REGARDING AN EXPLOSION AT 416 MURFREESBORO RD. THE COMPANY'S SERVICE TECHNICIAN ARRIVED ON THE SCENE AT APPROXIMATELY 8:45 PM CST. THE FIRE DEPARTMENT WAS ALREADY AT THE SCENE OF THE EXPLOSION AT 420 MURFREESBORO RD. THE FIRE INVESTIGATOR AND PIEDMONT EMPLOYEES DISCOVERED A WIDE OPEN FUEL LINE IN THE BOILER ROOM WHERE THE EXPLOSION OCCURRED. THE FIRE INVESTIGATOR AND PIEDMONT EMPLOYEES ALSO DISCOVERED A THREADED NIPPLE WITH AN END CAP ON IT LAYING ON THE FLOOR NEAR THE WIDE OPEN FUEL LINE. | 65200 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
730 | 2008-12-26 | WA | leaks and spills | UNKNOWN (LINCOLN COUNTY) | AVISTA CORP | ROCK IMPINGEMENT APPEARS TO HAVE CAUSED CRACK IN P.E. PIPE WALL. SNOW AND FROST IN GROUND CAUSED GAS TO MIGRATE TO NEARBY STRUCTURE. GAS ACCUMULATED IN UNDERGROUND AREA OF STRUCTURE AFTER PASSING THROUGH CRACK IN WALL. ONE RESIDENT STATED THAT HE ENTERED GARAGE STRUCTURE AND LIT A CIGARETTE WHICH IS ASSUMED TO BE THE IGNITION SOURCE. | 55200 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
731 | 2009-01-02 | ID | natural disasters | UNKNOWN (KOOTENAI COUNTY) | AVISTA CORP | HEAVY SNOW SLID OFF THE ROOF OF THE BUSINESS BUILDING DAMAGING THE METER SET. THE METER SET BROKE JUST BELOW THE REGULATOR CAUSING THE GAS TO ESCAPE AND MIGRATE INTO THE BUILDING WHICH RESULTED IN IGNITION AND A STRUCTURE FIRE. 6/2/09 CLICKED "FINAL REPORT" BOX - NO CHANGES | 1002024 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
732 | 2008-12-19 | CO | natural disasters | UNKNOWN (PUEBLO COUNTY) | PUBLIC SERVICE CO OF COLORADO | 3/4 INCH CAB SERVICE SEPARATED FROM A MECHANICAL COUPLING, LIKELY DUE TO THERMAL EXPANSION/ CONTRACTION. | 75000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
733 | 2009-01-16 | FL | sabotage | UNKNOWN (ALACHUA COUNTY) | GAINESVILLE REGIONAL UTIL GAS DEPT | CONTRACTOR HAD BUILT A CAMP FIRE TO STAY WARM. THEIR LOCATES WERE OLD AND HAD WASHED AWAY. CONTRACTOR STRUCK 1 1/4 INCH MAIN WITH EXCAVATOR. CAMP FIRE IGNITED NATURAL GAS. NO INJURIES OR FATALITIES. | 2400 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
734 | 2008-12-24 | CA | other | UNKNOWN (SACRAMENTO COUNTY) | PACIFIC GAS & ELECTRIC CO | ON WEDNESDAY, DECEMBER 24, 2008 AT APPROXIMATELY 1335 THE HOUSE AT 10708 PAIUTE WAY, RANCHO CORDOVA EXPLODED, SEVERELY DAMAGING HOUSES ON EITHER SIDE. FIVE PEOPLE, INCLUDING TWO PG&E EMPLOYEES DISPATCHED TO THE SITE, WERE INJURED AND THERE WAS ONE FATALITY. TWO PEOPLE REQUIRED HOSPITALIZATION. MAJOR MEDIA WAS PRESENT AND DAMAGES EXCEED AN ESTIMATED $50K. SACRAMENTO METROPOLITAN FIRE DEPARTMENT AND THE RANCHO CORDOVA POLICE DEPARTMENT WERE ON SCENE. SEVERAL FAMILIES HAVE BEEN TEMPORARILY DISPLACED. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
735 | 2008-12-29 | VA | natural disasters | UNKNOWN (FAIRFAX COUNTY) | WASHINGTON GAS LIGHT CO | WASHINGTON GAS WAS CALLED AT 08:48 BY THE FAIRFAX FIRE BOARD FOR AN ODOR OF GAS. THE LEAK WAS PINPOINTED TO THE INTERSECTION OF BACKLICK ROAD AND INDUSTRIAL ROAD. PRESSURE ON THE LINE WAS REDUCED. UPON EXCAVATION OF THE SITE, THE LEAK WAS FOUND TO BE COMING FROM A CRACKED 12 INCH CAST IRON MAIN. PERMANENT REPAIRS WERE COMPLETED AT 01:45 ON 12/30/2008. | 11000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
736 | 2009-01-12 | CA | other | UNKNOWN (MADERA COUNTY) | PACIFIC GAS & ELECTRIC CO | PG&E RESPONDED TO A CALL FROM THE MADERA FIRE DEPARTMENT REPORTING A STRUCTURE FIRE AT THE PARKWOOD SHOPPING CENTER. THE FIRE DEPARTMENT HAD TURNED OFF THE GAS AT THE METER SET VALVE. AS A RESULT OF THE FIRE THE STRUCTURE FELL ON TO ONE OF THE METERS AFTER IT HAD BEEN SHUT OFF. ACCORDING TO THE FIRE DEPARTMENT PG&E FACILITES DID NOT CONTRIBUTE TO THE FIRE. THIS INCIDENT WAS DETERMINED TO BE REPORTABLE DUE TO DAMAGES EXCEEDING $50,000. THERE WERE NO INJURIES OR FATALITIES AS A RESULT OF THIS INCIDENT AND NO MAJOR MEDIA WAS PRESENT. | 50500 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
737 | 2008-12-24 | NH | other | UNKNOWN (GENIE COUNTY) | NORTHERN UTILITIES, INC. (NH) | DOUBLE METER SET FEEDING TWO UNITS, 5 + 6 AT 86 CHURCH STREET, SNOW WAS PILED ON TOP OF SET CAUSING PRESSURE ON RISER, THE RELEASE OF GAS CAME FROM THIS LOCATION, NIPPLE BETWEEN INLET OF REGULATION AND RISER VALVE. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
738 | 2008-12-28 | NY | maintenance | UNKNOWN (SUFFOLK COUNTY) | KEYSPAN ENERGY DELIVERY - LONG ISLAND | AT 1755 ON DECEMBER 28, 2008, NATIONAL GRID LI RECEIVED A CALL FRO THE AMITYVILLE POLICE DEPARTMENT REPORTING A BURST PIPE AND EVACUATION AT 34 MEADOW LANE, AMITYVILLE. AT 1759, A SECOND CALL WAS RECEIVED INDICATING THAT THE HOUSE HAD "EXPLODED". NATIONAL GRID PERSONNEL ARRIVED ON-SCENE AT 1827 AND FOUND THE HOUSE HAD SUSTAINED SIGNIFICANT DAMAGE AND THE CURB VALVE HAD BEEN CLOSED BY THE FIRE DEPARTMENT PRIOR TO ARRIVAL. THERE WERE NO REPORTED INJURIES. A PRELIMINARY INSPECTION OF THE METER ASEMBLY, LOCATED IN A CRAWL SPACE UNDER THE HOUSE, REVEALED A SEPARATION AT THE SERVICE ADAPTER UPSTREAM OF THE METER COCK. SUBSEQUENT EXAMINATION AND TESTING OF THE ADAPTER DETERMINED FAILURE WAS CAUSED BY GENERAL CORROSION DUE TO PERIODIC FLOODING IN THE CRAWL SPACE. | 300000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
739 | 2008-12-24 | MS | sabotage | UNKNOWN (HINDS COUNTY) | ATMOS ENERGY CORPORATION - MISSISSIPPI | 12/17/2014: THE INVESTIGATION SHOWED THAT THE COATED STEEL SERVICE LINE WAS PROPERLY CONNECTED TO THE GAS MAIN WITH AN APPROPRIATE DRESSER EII COUPLING. ATMOS HAD NO INDICATION OF ANY LEAKS OF THIS STEEL SERVICE PIPE OR THE COMPRESSION COUPLING BEFORE THE DAY OF THE FIRE. THE STEEL SERVICE PIPE WAS IN EXCELLENT CONDITION AND WOULD HAVE PERFORMED WITHOUT LEAKING FOR THE FORESEEABLE FUTURE. THE DRESSER COUPLING WAS ALSO IN EXCELLENT CONDITION; THE GASKET FORMING THE SEAL WITH THE STEEL SERVICE LINE WAS PLIABLE, MOIST AND INTACT, THUS CAPABLE OF CONTINUING TO MAINTAIN A GAS TIGHT SEAL FOR THE FORSEEABLE FUTURE. THE FACT THAT THE EXCAVATOR HAD FAILED TO ADEQUETELY PROTECT THE SERVICE LINE FROM DAMAGE WAS NEITHER KNOWN NOR DETECTED BY ATMOS UNTIL IT WAS REVEALED BY THIS INVESTIGATION. THE ROOT CAUSE OF THE LEAK WAS THE UNFORSEEABLE PLACEMENT OF A HEAVY, RIGID DUCTILE IRON WATER MAIN IN CONTACT WITH THE PROPERLY MARKED GAS SERVICE LINE. THE INVESTIGATION ALSO INDICATED THAT THE ODOR OF GAS WAS STRONG, AS CONFIRMED BY FIRE DEPARTMENT PERSONNEL. FIRE DEPARTMENT PERSONNEL ALSO REPORTED THAT THE INJURED PERSON STATED THAT HE HAD USED A LIGHTER IN AN AREA THAT HAD A READLILY DETECTIBLE GAS ODOR. IT APPEARS THAT A SERVICE TAP WAS LEAKING. MIGRATION OF GAS AWAY FROM THE IMMEDIATE AREA OF THE LEAK WAS DETECTED DURING THE INVESTIGATION AFTER THE INCIDENT OCCURRED. THE ODOR OF GAS WAS STRONG, AS CONFIRMED BY FIRE DEPARTMENT PERSONNEL. FIRE DEPARTMENT PERSONNEL ALSO REPORTED THAT THE INJURED PERSON STATED HE HAD USED A LIGHTER IN AN AREA THAT HAD A DETECTABLE ODOR. THE FIRE DEPARTMENT IS CONTINUING THEIR INVESTIGAION, AS ARE WE. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
740 | 2009-01-17 | TN | other | UNKNOWN (SHELBY COUNTY) | MEMPHIS LIGHT GAS & WATER DIVISION | MEMPHIS LIGHT GAS AND WATER DIVISION, UPON COMPLETION OF INVESTIGATION OF THE HOUSE FIRE AT 1903 THE OAKS AVENUE ON 1/17/09 IN WHICH THE GAS METER AND REGULATOR WERE CONSUMED BY FIRE, HAS DETERMINED THAT OUR FACILITIES DID NOT CREATE THE FIRE BUT THAT OUR FACILITIES WERE DESTROYED AS A RESULT OF THE FIRE. THEREFORE THIS IS NOT A NATURAL GAS REPORTABLE INCIDENT. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
741 | 2009-01-13 | IL | other | UNKNOWN (MCLEAN COUNTY) | NORTHERN ILLINOIS GAS CO | DRIVER LOST CONTROL OF HIS CAR DUE TO SNOW AND ICE AND HIT METER SET TO 1210 ADELAIDE, NORMAL IL. GAS IGNITED. NOTE: THIS INCIDENT WAS ORIGINALLY REPORTED TO THE NRC AS 1210 ADELAIDE, BLOOMINGTON, IL | 336000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
742 | 2009-02-11 | AK | other | UNKNOWN (nan COUNTY) | ENSTAR NATURAL GAS CO | ENSTAR RESPONDED TO A STRUCTURE FIRE AT 13021 ADMIRALTY DRIVE, ANCHORAGE, ALASKA AT 1432 ON 2/11/2009. THE FIRE IS BELIEVED TO HAVE STARTED FROM A CHARCOAL GRILL. HEAT FROM THE STRUCTURE FIRE MELTED ENSTAR'S METER AND PRESSURE REGULATOR,CAUSING A RELEASE OF NATURAL GAS. NATURAL GAS DID NOT CAUSE OR CONTRIBUTE TO THE FIRE. | 51100 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
743 | 2009-01-17 | CA | sabotage | UNKNOWN (ORANGE COUNTY COUNTY) | SOUTHERN CALIFORNIA GAS CO | ON JANUARY 17, 2009, A 3¿ DISTRIBUTION MAIN WAS DAMAGED BY A CONTRACTOR USING POWER EXCAVATING EQUIPMENT TO INSTALL A TRANSMISSION POLE. INVESTIGATION OF THE INCIDENT SHOWED THAT THE CONTRACTOR HAD A CURRENT USA TICKET, AND HAD POTHOLED A STEEL PIPE AT OUR LOCATE MARKS, BUT THAT MARKS WERE APPROXIMATELY 6 FEET AWAY FROM THE ACTUAL LOCATION. NO FIRE OR INJURIES RESULTED FROM THE ESCAPING GAS. REPAIRS AND RESTORES WERE COMPLETED THE SAME DAY. ELECTRONIC LOCATE BALLS WERE INSTALLED ALONG ROUTE OF PIPELINE. FURTHER INVESTIGATION DETERMINED THAT LOCATE WIRE HAD DETERIORATED AT THIS VICINITY, AND LOCATE SIGNAL WAS BEING PULLED TO A NEARBY WATER MAIN. ATLAS SHEETS WERE NOT HELPFUL DUE TO THE LACK OF VERIFIABLE PROPERTY LINES AT THIS LOCATION. THIS INCIDENT BECAME REPORTABLE TO THE TOTAL COSTS ASSOCIATED WITH INCIDENT EXCEEDING $50,000. | 51000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
744 | 2008-12-30 | MO | sabotage | UNKNOWN (ST LOUIS CITY COUNTY) | LACLEDE GAS CO | A PLUMBING COMPANY EXCAVATED AROUND AND UNDERMINED APPROXIMATELY SEVEN FEET OF THE 4-INCH CAST IRON NATURAL GAS MAIN ON OR ABOUT NOVEMBER 19, 2008. THIS EXCAVATION WAS BACKFILLED WITH ROCK AND PAVED ON DECEMBER 24, 2008, WITHOUT PROVIDING SUPPORT TO THE CAST IRON GAS MAIN. THE MAIN CRACKED AT THIS LOCATION SOME TIME AFTER THE BACKFILL. A SECOND EXCAVATION IN THE SIDEWALK AT THE OUTSIDE WALL OF 7527 MICHIGAN AVENUE WAS BACKFILLED AND PAVED ON DECEMBER 30, 2008. A SHORT TIME LATER ON THE SAME DATE, NATURAL GAS MIGRATED INTO THE BASEMENT OF 7527 MICHIGAN AVENUE, WAS IGNITED AND CAUSED A FIRE AT THIS LOCATION. | 37617 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
745 | 2009-01-21 | OK | sabotage | UNKNOWN (TULSA COUNTY) | OKLAHOMA NATURAL GAS CO | CITY OF TULSA WATER DEPARTMENT CREW DAMAGED A 4" POLYETHYLENE MAIN AT THE CORNER OF EAST 11TH AND S. ERIE AVE. THE CITY CALLED IN A LOCATE REQUEST BUT EXCAVATED OUTSIDE OF THE DEFINED WHITE LINE LIMITS OF THEIR REQUEST. THE ONG LINE WAS NOT MARKED OUTSIDE THE SCOPE OF THE TICKET. TULSA & FIRE DEPARTMENTS CLOSED BOTH STREETS TO KEEPS TRAFFIC AT A SAFE DISTANCE. A TOTAL OF 4 EMPLOYEES FROM TWO SMALL USED CAR LOTS WERE EVACUATED. | 52464 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
746 | 2009-01-19 | OK | sabotage | UNKNOWN (OKLAHOMA COUNTY) | OKLAHOMA NATURAL GAS CO | CIMARRON CONSTRUCTION COMPANY DAMAGED ONG'S 6" (INCH) HDPE MAIN WHILE INSTALLING SHORING PYLONS AND SHORE BOXES TO PIT BORE FOR THE RELOCATION OF OKLAHOMA CITY'S WATER LINE. LAPSED TIME IN REPORTING WAS A RESULT OF COLLABORATION OF ENGINEERING AND OPERATIONS GROUP TO DETERMINE THE MOST EFFECTIVE AND APPROPRIATE REPAIR PROCEDURE. UPDATE: FINAL DAMAGE COSTS. | 75924 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
747 | 2009-01-19 | OH | other | UNKNOWN (MUSKINGUM COUNTY) | COLUMBIA GAS OF OHIO INC | A WATER MAIN LEAK ERODED A HOLE IN A COLUMBIA OWNED THREE INCH LOW PRESSURE STEEL GAS MAIN LINE. THE WATER LEAK FORCED WATER INTO AND FILLED THE COLUMBIA OWNED MAIN LINE AND CAUSED A 115 CUSTOMER SERVICE FAILURE (OUTAGE). THE COST OF WATER REMOVAL AND GAS RE-ESTABLISHMENT ASSOCIATED WITH THIS INCIDENT EXCEEDED 50,000 DOLLARS. NOTE. PART A SECTION 8-A WILL ALLOW ONLY WHOLE NUMBERS WITH NO DECIMALS TO BE ENTERED AND THAT 1.0 WAS ENTERED WHILE THE ACTUAL MAOP FOR THIS SYSTEM IS 0.50 PSIG. | 150051 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
748 | 2009-01-27 | IL | natural disasters | UNKNOWN (LAKE COUNTY) | NORTH SHORE GAS CO | ATTACHMENT TO PART G- NARRATIVE DESCRIPTION OF FACTORS CONTRIBUTING TO THE EVENT FROM 5/3/09 REPORT: ON THE EVENING FOLLOWING THE INCIDENT, NORTH SHORE GAS EXCAVATED AND EXPOSED THE 3/4 INCH MILL WRAPPED STEEL SERVICE LINE; FINDING IT BROKEN A FEW INCHES FROM THE INTACT CONNECTION TO THE MAIN. THE CAUSE OF THE BREAK IS STILL UNKNOWN AND UNDER INVESTIGATION. THE INVESTIGATION CONTINUES REGARDING THE CAUSE OF THE EXPLOSION. FOLLOWING ARE FACTS FOUND IN THE SOIL ENVIRONMENT: 1) FROST WAS AT LEAST 40 INCHES DEEP. 2) AN AREA OF SOIL IN AND AROUND THE AREA OF THE BREAK WAS DRY/CRYSTALLINE. 3) NATURAL GAS WAS FOUND TO HAVE MIGRATED ALONG THE SERVICE LINE AND MAIN. IN POST INCIDENT TESTING, THE SERVICE LINE TO THE PREMISE DID NOT LEAK. THE REGULATOR SERVING THE PREMISE FAILED THE LOCK UP AND FLOW TEST, BUT IT IS UNKNOWN IF THE CONDITION WAS CREATED PRE OR POST INCIDENT. 5/17/13 UPDATE: NORTH SHORE GAS COMPANY HAS COMPLETED ITS INVESTIGATION OF THE INCIDENT AT 33842 N. LAKE SHORE DR., GAGES LAKE, IL. ON MARCH 25, 2013, A CONSULTANT TO NORTH SHORE GAS COMPANY ISSUED A REPORT REGARDING HIS INVESTIGATION OF THE INCIDENT AND HIS EXAMINATION OF THE PIPING AND REGULATOR FROM THE RESIDENCE AT 33842 N LAKE SHORE DRIVE. THE INVESTIGATION DEMONSTRATED THAT THE REGULATOR WAS FUNCTIONING PROPERLY. METALLURGICAL ANALYSIS OF THE SERVICE LINE DETERMINED THERE WAS NO EVIDENCE OF A DEFECTIVE OR OUT OF SPECIFICATION PIPE. THERE WAS NO SIGNIFICANT CORROSION OR WALL THINNING OF THE SERVICE LINE AND NO SIGN~ OF GOUGING OR TOOL DAMAGE. THE REPORT NOTED THAT FROST WAS APPARENT IN THE SOIL AT THE LOCATION OF THE MAIN AND CONCLUDED THAT THE LIKELY CAUSE OF THE SERVICE LINE FRACTURE WAS SOIL MOVEMENT. THE EXACT CAUSE OF THE SOIL MOVEMENT IS UNKNOWN BUT PREVIOUS ROAD PAVING AND/OR FROST HEAVE ARE POSSIBLE CONTRIBUTING FACTORS. NORTH SHORE GAS NOW CONSIDERS THIS INCIDENT CLOSED. | 502700 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
749 | 2009-01-24 | NY | maintenance | UNKNOWN (WESTCHESTER COUNTY) | CONSOLIDATED EDISON CO OF NEW YORK | ON SATURDAY, JANUARY 24, 2009 AT 04:20, THE EMERGENCY RESPONSE CENTER (ERC) RECEIVED NOTFICATION OF A BUILDING FIRE AT 4 DRAKE ROAD, CALLED IN BY THE SCARSDALE FD. UPON ARRIVAL AT 04:50, GDS REPORTED THAT THE FD HAD THE FIRE UNDER CONTROL, AND THERE WAS WATER BUBBLING IN THE STREET WITH A STRONG GAS ODOR IN FRONT OF THE HOUSE. THE FD REPORTED THAT WHILE IN THE FIREHOUSE ON THE CORNER OF RT. 22 & POPHAM RD. (A FEW HUNDRED FEET FROM 4 DRAKE ROAD) THEY HEARD AN EXPLOSION. THEY ALSO RECEIVED SEVERAL 911 CALLS FROM PEOPLE REPORTING THEY HEARD AN EXPLOSION AT AN UNKNOWN LOCATION. TWO FIREFIGHTERS AND TWO POLICE OFFICERS WERE TAKEN TO LOCAL HOSPITALS AND TREATED FOR SMOKE INHALATION AND RELEASED. THE OCCUPANT OF THE HOUSE WAS ADMITTED TO WHITE PLAINS HOSPITAL FOR SMOKE INHALATION. AN OUTSIDE LEAK INVESTIGATION REVEALED GAS IN SEVERAL SEWER AND ELECTRIC MANHOLES, AND GAS READINGS IN THE SEWER TRAP, 1.5% IN THE ATMOSPHERE OF THE BASEMENT, AND EVIDENCE OF A FIRE. GDS LEFT THE BUILDING, SHUT OFF THE CURB VALVE, AND PROCEEDED TO CLOSE THREE GAS MAIN VALVES TO ISOLATE THE 3" HP STEEL MAIN, INTERRUPTING GAS SERVICE TO NINE RESIDENTIAL CUSTOMERS. THE SEWER AND ELEXTRIC MANHOLES, AND BUILDINGS VENTED TO ZERO. A GAS CONSTRUCTION CREW AIR TESTED THE SERVICE TO 4 DRAKE RD AT 63 PSI (OPERATING PRESSURE AT THE TIME OF THE INCIDENT) FROM THE CURB VALVE TO THE BUILDING, AND THE TEST PASSED. AT 13:20 CREWS COMPLETED EXCAVATING OVER THE MAIN CONNECTION FOR THE SERVICE SUPPLYING 4 DRAKE ROAD. A STAB END ADAPTER ON THE 1/2" PE SERVICE THAT WAS NOT FULLY SEATED IN THE 1" COMPRESSION COUPLING TYING IT TO THE SERVICE TEE. A 360' SECTION OF MAIN IN FRONT OF 4 DRAKE RD WAS INSERTED WITH 2" PE PLASTIC. THE SERVICE TO 4 DRAKE RD WAS CUT AND CAPPED. SERVICE WAS RESTORED TO ALL AVAILABLE CUSTOMERS AT 21:50. THE LAW DEPT, QUALITY ASSURANCE, ENGINEERING, THE PSC, AND CHANNEL 12 NEWS WERE ALL ON LOCATION. CON EDISON CIG & THE DOT/NRC WERE NOTIFIED. THIS WAS A SERIOUS LEVEL INCIDENT. THE INCIDENT INVESTIGATION HAS BEEN COMPLETED. | 150000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
750 | 2009-01-28 | OH | other | UNKNOWN (LAK COUNTY) | DOMINION EAST OHIO | AT APPROXIMATELY 21:30 HOURS ON JANUARY 28, 2009, A SINGLE FAMILY HOME LOCATED AT 37845 LAKESHORE, EASTLAKE, OHIO SUSTAINED AN EXPLOSION CAUSING SERIOUS INJURY TO THE TWO OCCUPANTS. BOTH PARTIES WERE LIFE FLIGHTED TO METRO HOSPITAL AND WERE PLACED IN THE BURN UNIT. ONE OF THE PARTIES PASSED AWAY ON JANUARY 29, 2009 DUE TO INJURIES SUSTAINED IN THE EXPLOSION. SURVEY OF THE NEIGHBORHOOD REVEALED THAT THE EXPLOSION CAUSED PROPERTY DAMAGE TO APPROXIMATELY 15 PROPERTIES. A LEAK SURVEY OF THE GAS MAIN AND SURROUNDING SERVICE LINES DEMONSTRATED THEM TO BE FREE FROM ANY LEAKAGE. A LEAK SURVEY OF THE PERIMETER OF THE HOUSE REVEALED GAS AT LEVELS RANGING FROM 100% LEL (I.E: 5% GAS TO AIR) TO A NEGLIGIBLE PERCENTAGE GAS ALONG THE LENGTH OF UNDERGROUND HOUSE LINE, THE WEST SIDE OF THE HOUSE, AND BACK WEST CORNER OF THE HOUSE. AN ODOR SURVEY WAS TAKEN AT 37839 LAKE SHORE BLVD., THE PROPERTY NEXT TO AND WEST OF THE SUBJECT PROPERTY, AND WITNESSED BY BOTH THE PUCO AND THE EASTLAKE FIRE MARSHALL DEMONSTRATED THAT ODOR LEVELS WERE WITHIN CODE REQUIREMENTS. A STEEL SERVICE LINE (1 ¼” ) WAS FOUND TO HAVE A 5/8" PLASTIC SERVICE LINE INSERTED. THE PLASTIC SERVICE LINE IS BELIEVED TO BE INSTALLED IN 1975 PER MR. PITCHLER’S DEPOSITION. IN PREPARING THE SERVICE LINE FOR A PRESSURE TEST, A FRACTURE WAS DISCOVERED APPROXIMATELY 200 DEGREES AROUND THE CIRCUMFERENCE OF THE LINE AT THE LOCATION WHERE THE PLASTIC SERVICE LINE COUPLES TO THE METER MANIFOLD RISER UNDERGROUND. A 6" SECTION OF SERVICE LINE (TO INCLUDE THE FRACTURE) ALONG WITH THE RISER WERE REMOVED AND TAKEN BY THE EASTLAKE FIRE MARSHALL TO BE RETAINED AS EVIDENCE FOR FURTHER INVESTIGATION (THEY WERE LATER TRANSFERRED TO DOLENCE ELECTRIC AND THEN TO GTI FOR ALL PARTIES TO TEST AND OBSERVE). THE REMAINING SECTION OF SERVICE LINE WAS TESTED FOR 10 MINUTES AT LINE OPERATING PRESSURE AND WAS FOUND TO BE FREE FROM LEAKAGE. APPROXIMATELY 15' OF UNDERGROUND HOUSE LINE EXTENDED FROM THE MANIFOLD, RAN DUE NORTH AND ENTERED THE FRONT WALL OF THE BASEMENT. A LINE OPERATING PRESSURE TEST OF THE UNDERGROUND HOUSE LINE DEMONSTRATED THE LINE TO BE FREE OF LEAKAGE. DOMINION HAD A FRACTURE ANALYSIS PERFORMED ON THE FAILED METER RISER. THE FRACTURE ANALYSIS CONSISTED OF A SEM (SCANNING ELECTRON MICROSCOPY) ANALYSIS. THE RESULTS INDICATE A RAPID OVERLOAD FAILURE OF THE POLYETHYLENE PIPE OCCURRED AS A RESULT OF HIGH STRESS APPLIED AT THE TIME OF FAILURE, WHICH DOMINION BELIEVES TO BE AN EXCESS OF FORCE APPLIED TO THE METER ASSEMBLY BY A SNOW PLOW. | 1000000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
751 | 2009-01-12 | NM | other | UNKNOWN (CHAVEZ COUNTY) | NEW MEXICO GAS COMPANY | A VEHICLE LOST CONTROL ON6956 OLD DEXTER ROAD AND ROLLED OVER THE METER SET, HIT THE RISER VALVE CAUSING A RELEASE OF GAS. THE METER WAS REMOVED AND THE SERVICE LINE PLUGGED. BECAUSE OF HIPAA PRIVACY RULES, THE COMPANY WAS UNABLE TO VERIFY WHETHER ANYONE INVOLVED IN THE ACCIDENT WERE HOSPITALIZED OVERNIGHT OR THE EXTENT OF INJURIES. | 600 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
752 | 2009-02-11 | MI | leaks and spills | UNKNOWN (MACOMB COUNTY) | CONSUMERS ENERGY CO | AT 0725 ON FEBRUARY 11, 2009, CONSUMERS ENERGY RESPONDED TO AN EMERGENCY CALL AT 21103 BEACONSFIELD, EASTPOINTE, MICHIGAN, AND DETERMINED THAT AN EXPLOSION AND SUBSEQUENT FIRE OCCURRED. THE FIRE DEPARTMENT TURNED OFF THE GAS AT THE METER AT 0830. TWO RESIDENTS WERE TRANSPORTED TO THE HOSPITAL WITH NON LIFE THREATENING INJURIES. THE CAUSE AND LOCATION OF THE EXPLOSION HAS NOT BEEN DETERMINED AT THIS TIME. THE CAUSE OF THIS INCIDENT IS BELIEVED TO BE A LEAKING SADDLE TEE ON THE 6 INCH MEDIUM PRESSURE MAIN. THE SADDLE TEE WAS LOCATED APPROXIMATELY 5 TO 6 FEET FROM THE SERVICE TEE TO 21103 BEACONSFIELD. A COPPER SERVICE TO 21100 AND 21104 BEACONSFIELD WAS PARTIALLY PULLED OUT OF THE SADDLE TEE. | 100150 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
753 | 2009-01-27 | OH | other | UNKNOWN (DELWARE COUNTY) | COLUMBIA GAS OF OHIO INC | AN INVESTIGATION WAS CONDUCTED BY THE PROPERTY OWNER'S INSURANCE CARRIER WHO HAS MAINTAINED POSSESSION OF ALL OF THE CUSTOMERS OWNED MATERIAL. IT IS COLUMBIA'S POSITION THAT ITS OWN INVESTIGATION AND THE INVESTIGATION BY THE PROPERTY OWNER'S INSURANCE CARRIER DID NOT CONCLUSIVELY DETERMINE THE CAUSE OF THIS INCIDENT. THE INVESITGATION DID DISCOVER A CUSTOMER OWNED MECHANICAL JOINT WHICH HAD BEEN IMPROPERLY INSTALLED AND HAD FAILED AT SOME POINT. | 152912 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
754 | 2009-02-07 | AZ | sabotage | UNKNOWN (MARICOPA COUNTY) | SOUTHWEST GAS CORP | NRC REPORT NUMBER 896853 A NATURAL GAS LEAK ON A SOUTHWEST DISTRIBUTION LINE CONTRIBUTED TO A HOUSE FIRE. THE CAUSE OF THE LEAK WAS DUE TO PRIOR THIRD PARTY DAMAGE TO A 1" STEEL SERVICE LINE. THERE WERE NO INJURIES OR A FATALITIES AS A RESULT OF THE INCIDENT. | 585811 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
755 | 2009-02-07 | NY | natural disasters | UNKNOWN (SUFFOLK COUNTY) | KEYSPAN ENERGY DELIVERY - LONG ISLAND | UPDATED BY PHMSA ON 2/9/2016 PER THE OPERATOR'S MARK UP (PART D - MATERIAL SPECIFICATION, ITEM 1 - NOMINAL PIPE SIZE; ITEM 2 - WALL THICKNESS (NOTE: THE .10 IS THE THICKNESS AT THE DAMAGE LOCATION); PART F - APPARENT CAUSE; F2 - NATURAL FORCES, ITEM 6 - TEMPERATURE --> FROST HEAVE). ON SATURDAY, FEBRUARY 7, 2009 AT 1434 HRS, NATIONAL GRID-LI RESPONDED TO A CALL FROM THE SOUTHOLD FIRE DEPARTMENT, REPORTING A FIRE IN PROGRESS AT 895 TOWN HARBOR ROAD, SOUTHOLD. UPON ARRIVAL OF NATIONAL GRID PERSONNEL AT 1506 HRS, IT WAS FOUND THAT THE HOUSE HAD SUSTAINED SIGNIFICANT DAMAGE AND THAT THE SOUTHOLD FIRE DEPARTMENT HAD SECURED THE GAS TO THE CURB VALVE. THERE WERE NO REPORTED INJURIES. A PRESSURE TEST ON THE GAS SERVICE TO THE HOUSE WAS PERFORMED BY NATIONAL GRID PERSONNEL. THE SERVICE FAILED THE PRESSURE TEST DUE TO AN APPARENT LEAK APPROXIMATELY 65 FEET FROM THE CURB VALVE. UPON EXCAVATION, A LEAK WAS DISCOVERED ON A COLD BEND ON THE SERVICE APPROXIMATELY 3 FEET FROM THE HOUSE. THE SECTION OF PIPE WAS REMOVED AND SENT TO LUCIUS PITKIN, INC. FOR TESTING, WHICH REVEALED THAT THE STRESS CRACK, CAUSED THE ULTIMATE FRACTURE AT THE CROUCH OF THE BEND DUE TO FROST LOAD, ALLOWING HP GAS TO ESCAPE INTO THE HOUSE. THE METALLURGICAL AND METALLOGRAPHIC TESTING DETERMINED THAT THE FRACTURE WAS DUE TO BENDING LOADS INDUCED IN THE PIPE DUE TO FROST HEAVE MOVEMENT OF THE PIPE. THE GENERAL MICROSTRUCTURE AND HARDNESS OF THE PIPE WAS CONSIDERED NORMAL AND SATISFACTORY. | 300000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
756 | 2009-02-01 | WI | natural disasters | UNKNOWN (MILWAUKEE COUNTY) | WISCONSIN GAS CO | ON SUNDAY, FEBRUARY 1, 2009, AT 2:17AM, THE CITY OF MILWAUKEE POLIECE DEPARTMENT (MPD) NOTIFIED WE ENERGIES CUSTOMER CONTACT CENTER THAT THERE WAS A GAS LEAK IN THE AREA OF 2435 N.10TH STREET, IN THE CITY OF MILWAUKEE, WISCONSIN. MPD ALSO SAID THAT THE MILWAUKEE FIRE DEPARTMENT (MFD) WAS IN ROUT. WE WNERGIES CUSTOMER CONTACT CENTER TRANSFERRED THE CALL TO THEIR GAS CENTRAL DISPATCH WHO, AT 2:19AM, DISPATCHED A GAS DISTRIBUTION WORKER TO RESPOND TO THE GRADE 1 LEAK. WE ENERGIES GRADE 1 LEAKS REQUIRE IMMEDIATE RESPONSE. AT 2:23AM, GAS CENTRAL DISPATCH RECEIVED A CALL FROM THE MFD THAT THEY WERE ON THE SCENE AND THAT THERE WAS A STRONG ODOR THROUGHOUT THE BLOCK, NOT A SINGLE LOCATION AS ORIGINALLY THOUGHT. THE DISPATCHER REPLIED THAT A RESPONDER WAS EN ROUTE AND ESTIMATED ARRIVAL TIME WOULD BE APPROXIMATELY 20 MINUTES. AT 2:24AM GAS CENTRAL DISPATCH RECEIVED A CALL FROM THE MPD THAT THEY WERE AT THE SCENE AND CONFIRMED A STRONG ODOR OF NATURAL GAS IN THE AREA. THE CALL WAS ALSO TO CONFIRM THAT WE ENERGIES WAS RESPONDING. AT 2:28AM, THE MFD CALLED GAS CENTRAL DISPATCH THAT THE STRONG GAS ODOR WAS COMING FROM A BREAK IN THE STREET. GAS CENTRAL DISPATCH, PROVIDED WITH THE ADDITIONAL INFORMATION REGARDING THE NATURE OF LEAK, DISPATCHED 3 ADDITIONAL GAS DISTRIBUTION WORKERS AND A SUPERVISOR WITHIN THE NEXT 12 MINUTES TO PROVIDE ADDITIONAL RESOURCES. JUST PRIOR TO 2:45AM, THE FIRST WE ENERGIES RESPONDER ARRIVED AT THE SCENE. AT 2:45AM, HE INFORMED GAS CENTRAL DISPATCH THAT EXCAVATION WOULD BE REQUIRED AND REQUESTED ADDITIONAL HELP, AN EMERGENCY HOTLINE LOCATE, AND TO HAVE BARRICADES WITH FLASHERS BROUGHT TO THE SITE. GAS DISPATCH RESPONDED ACCORDINGLY AND DISPATCHED ANOTHER EMPLOYEE AT 2:50AM. AT 3:03AM, THE SECOND WE ENERGIES RESPONDER ARRIVED ON THE SCENE FOLLOWED BY SUBSEQUENT WORKERS AT 3:18AM, 3:23AM AND 3:25AM. THEY ASSISTED IN THE PROCESS OF PROBING FOR GAS LOCATION AND MIGRATION, DETERMINING WHICH VALVES AND THEIR LOCATION TO SHUT OFF THE GAS SUPPLY TO THE AREA, AND CHECKED FOR THE PRESENCE OF GAS AT BUILDINGS IN THE AREA. THE RESULTS OF PROBES AND GAS-IN-AIR MEASUREMENTS ALONG THE GAS MAIN, LEAD THE INVESTIGATION AWAY FROM LOCATION OF THE INCIDENT. THE 2 INCH PVC GAS MAIN WAS UNDER THE PAVEMENT, INSERTED IN AN ABANDONED 4" CAST IRON AND SURROUNDED BY FROZEN SOIL CONTRIBUTING TO THE DIFFICULTY OF LOCATING AND STOPPING THE LEAK. AT APPROXIMATELY 3:26AM, THE FIRST OF TWO AREA VALVES REQUIRED TO SHUT DOWN THE AREA FROM THE SUPPLY OF GAS WAS CLOSED. WITHING ONE MINUTE OF COMPLETING THE VALVE CLOSURE, THE TWO UNIT RESIDENCE AT 2435-37 N. 10TH STREET, EXPERIENCED AN INTERIOR EXPLOSION AND SUBSEQUENT FIRE. THE EXPLOSION AND SUBSEQUENT FIRE RESULTED IN THE COMPLETE DESTRUCTION OF THE BUILDING. TWO OF THE OCCUPANTS WHO WERE IN THE BUILDING AT THE TIME OF THE EXPLOSION INCURRED INJURIES REQUIRING HOSPITALIZATION. THE EXPLOSION ALSO SEVERLY DAMAGED A SECOND SINGLE FAMILY RESIDENCE ADJACENT TO IT. THAT BUILDING IS CONSIDERED TO BE NOT SALVAGEABLE. THERE WAS ALSO MINRO DAMAGE SUCH AS BROKEN WINDOWS TO SERVERAL OTHER BUILDINGS INTHE IMMEDIATE AREA. AT 3:37AM, THE GAS DISTRIBUTION WORKER, WHO HAD JUST COMPLETED CLOSING THE FIRST VALVE, CALLED GAS CENTRAL DISPATCH TO INFORM THEM OF THE EXPLOSION AND TO REQUEST MFD TO RETURN TO THE SCENE FOR ASSISTANCE. WE ENERGIES PERSONNEL AT THE SITE, WITH THE ASSISTANCE OF THE MPD AND THE RETURN OF THE MFD, ASSISTED THE INJURED AND EVACUATED THE SURROUNDING BUILDINGS. APPROXIMATELY 10 MINUTES AFTER THE EXPLOSION, THE 2ND GAS VALVE WAS CLOSED SHUTTING OFF THE GAS SUPPLY TO THE AREA OF THE INCIDENT. THIS RESULTED IN 41 GAS METERS BEING AFFECTED. INCE THE AREA WAS MADE SAFE, WE ENERGIES CREWS, AIDED BY ADDITIONAL PERSONNEL AND EQUIPMENT DISPATCHED TO THE SITE, CHECKED BUILDINGS AND PROBED FOR ANY RESIDUL POCKETS OF GAS. SEVERAL EXCAVATIONS OF PAVEMENT AND FROZEN SOIL OVER THE MAIN REQUIRED BEFORE THE SOURCE OF THE LEAK WAS LOCATED. APPROXIMATELY ONE FOOT FROM A SERVICE TEE AND APPROX IMATELY 4 INCHES INTO THE INSERTED CAST IRON MAIN, THE 2 INCH DIAMETER PVC GAS MAIN WAS FOUND COMPLETELY SEVERED IN A CIRCUMFERENTIAL MANNER. TWO PHOTOGRAPHS ARE ATTACHED TO THIS REPORT TO SHOW IN-SITU CONDITIONS UPON FINDING THE BREAK. IT SHOULD BE NOTED THAT MUCH OF THE INSERTED CAST IRON PIPE HAD BEEN DESTROYED IN THE PROCESS TO LOCATE THE BREAK. THE FAILED PIPE AND SURROUNDING CAST IRON PIPE WERE PRESERVED FOR FURTHER ANALYSIS. A FORMER INCIDENT REVIEW WAS CONDUCTED ON FEBRUARY 10, 2009. PARTICIPANTS IN THE REVIEW INCLUDED THE FIVE GAS DISTRIBUTION WORKERS AT THE SCENE PRIOR TO AND AT THE TIME OF THE EXPLOSION, GAS CENTRAL DISPATCH DISPATCHERS, AND OTHER WE ENERGIES PERSONNEL WHO ASSISTED AT THE SCENE AFTER THE INCIDENT. THE INCIDENT REVIEW WAS ALSO ATTENDED BY PIPELINE SAFETY ENGINEERS WITH THE WISCONSIN PUBLIC SERVICE COMMISSION WHO HAD ALSO INSPECTED THE SITE THE DAY OF THE EXPLOSION. THE REVIEW RECOUNTED THE ACTIONS TAKEN BY EACH PARTICIPANT AND INCLUDED COMMUNICATIONS CONDUCTED WITH EACH OTHER, THE MFD, MPD, AND ANY PUBLIC ENCOUNTERED, PARTICULARLY RESIDENTS OF THE AREA. A TECHNICAL REVIEW AND ANALYSIS WAS ALSO PERFORMED TO DETERMINE THE CAUSE OF THE FAILED PVC PIPE. PRIOR TO THE FAILURE, WISCONSIN WAS EXPERIENCING ITS COLDEST WINTER IN RECENT HISTORY. THE COLD TEMPERATURES RESULTED IN THE FROST LINES EXTENDING TO UNUSUAL DEPTHS, ESPECIALLY UNDER THE STREETS AND ROADS WHERE THE INSULATING AFFECTS OF SNOW COVER IS REMOVED. FROST WAS ENCOUNTERED AT THE DEPTH OF THE INSERTED PVC GAS MAIN WHICH WAS MEASURED AT 5 FOOT, 8 INCHES FROM THE TOP OF PAVEMENT. THE CAUSE OF THE BREAK IN THE PVC PIPE WAS DETERMINED TO BE THE RESULT OF THE FORCE OF THE FROST ON THE GAS MAIN DOWNWARD AND THE DIFFERENTIAL SUPPORT UPWARD OF THE EXPOSED PVC MAIN AND THE ADJACENT INSERTED MAIN ON EACH SIDE. THE PVC PIPE WAS SUPPORTED AT EACH END OF THE INSERTION WITH A GROUT EXTENDING ABOUT 4 INCHES INTO THE OPEN ENDS. THIS CONDITION CREATED A BEAM EFFECT AND RESULTED IN A SHEAR LOCATION AT THE ENDS OF THE BEAM. THE SHEAR FORCE EXERTED ON THE PIPE CAUSED IT TO FAIL IN A BRITTLE MANNER. WE ENERGIES IS IN THE PROCESS OF PERFORMING ADDITIONAL LEAK SURVEYS BEYOND THOSE REQUIRED IN CFR 49, PART 192 AND WILL CONTINUE TO PERFORM THOSE SURVEYS UNTIL WINTER CONDITIONS HAVE CEASED. IT IS ALSO IN THE PROCESS OF ACCELERATING ITS EXISTING PROGRAM TO ELIMINATE PVC GAS MAINS. | 429420 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
757 | 2009-01-25 | MA | natural disasters | UNKNOWN (ESSEX COUNTY) | BOSTON GAS CO | UPDATED BY PHMSA ON 2/9/2016 PER OPERATOR'S MARK UP (PART F - APPARENT CAUSE, F2 - NATURAL FORCES, ITEM 6 - TEMPERATURE --> FROST HEAVE). SIX INCH BROKEN CAST IRON WAS FOUND IN FRONT OF 76 EASTERN AVE, GLOUCESTER, MASSACHUSETTS. CAUSE IS DETERMINED TO BE BENDING LOADS INDUCED IN THE PIPE DUE TO FROST HEAVE MOVEMENT OF PIPE AND BRITTLE BREAKAGE. | 400000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
758 | 2009-01-08 | NV | sabotage | UNKNOWN (CLARK COUNTY) | SOUTHWEST GAS CORP | ON THE MORNING OF JANUARY 8, 2009, SOUTHWEST GAS DISPATCH WAS NOTIFIED OF NATURAL GAS ODORS IN THE VICINITY OF EASTERN AVENUE AND RENO AVENUE IN LAS VEGAS. NATURAL GAS WAS DETECTED DURING THE INITIAL LEAK SURVEY INVESTIGATION IN AN ADJACENT TRAFFIC SIGNAL BOX AND STORM DRAIN SYSTEM. THE EXCAVATOR, A SUBCONTRACTOR ON A PUBLIC WORKS PROJECT, STRUCK AND DAMAGED A 2" PE MAIN AT 4995 SOUTH EASTERN WHILE PERFORMING BORE OPERATIONS SOMETIME IN THE EARLY MORNING HOURS OF JANUARY 8, 2009. THE 2" PE MAIN WAS DAMAGED WHERE IT CROSSED BENEATH A STORM DRAIN MAIN LINE. THE EXCAVATOR HAD A VALID LINE LOCATE TICKET AND THE SOUTHWEST GAS LINE HAD BEEN TIMELY AND PROPERLY MARKED. FACTORS THAT CONTRIBUTED TO THE CAUSE OF THE INCIDENT INCLUDE: THE EXCAVATOR FAILED TO DETERMINE THE EXACT LOCATION OF THE MARKED GAS FACILITIES WITH HAND TOOLS AT THE LOCATION OF THE BORE CROSSING; THE EXCAVATOR FAILED TO MEET WITH THE SOUTHWEST GAS REPRESENTATIVE AS REQUESTED; AND EITHER THE EXCAVATOR FAILED TO ACCOUNT FOR VISIBLE AND OBVIOUS EVIDENCE - MANHOLE COVERS - THAT WOULD HAVE ALERTED A REASONABLE EXCAVATOR TO THE PRESENCE OF AN UNMARKED STORM DRAIN MAIN LINE OR THE EXCAVATOR RECOGNIZED THE PRESENCE OF AN UNMARKED STORM DRAIN MAIN LINE BUT THEN FAILED TO DETERMINE THE EXACT LOCATION OF THE UNMARKED STORM DRAIN MAIN LINE WITH HAND TOOLS AT THE LOCATION OF THE BORE CROSSING. AS A RESULT OF THE INCIDENT, SERVICE WAS TEMPORARILY INTERRUPTED TO AN ESTIMATED 1,751 GAS CUSTOMERS. SERVICE WAS RESTORED TO THE MAJORITY OF AFFECTED CUSTOMERS BY JANUARY 8, 2009 AND THE REMAINING AFFECTED CUSTOMERS BY JANUARY 9, 2009. THERE WAS NO IGNITION OF GAS, INJURIES, OR FATALITIES AS A RESULT OF THE INCIDENT. | 94399 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
759 | 2009-03-04 | TX | sabotage | UNKNOWN (COLLIN COUNTY) | COSEAY GAS | CONTRACTOR DRILLING PEIR HOLES FOR SINGAL LIGHT INSTALLATION DAMAGED A 4" STEEL MAIN. TWO LANES ON A MULTIPLE LANE FM HWY WAS BLOCKED WHILE GAS WAS BROUGHT UNDER CONTROL AND REPAIRS WERE MADE. | 1200 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
760 | 2009-02-22 | WY | other | UNKNOWN (WESTON COUNTY) | SOURCEGAS LLC | A PICKUP TRUCK RAMMED ANOTHER VEHICLE INTO A METER SET APPURTENANCE LOCATED AT THE OUTSIDE BUILDING WALL BREAKING OFF THE PIPE AT THE THREADS JUST BELOW THE METER STOP/SHUT OFF VALVE THE LEAKING GAS IGNITED STARTING A FIRE WHICH DESTROYED THE VEHICLE AND CAUSED SEVERE DAMAGE TO THE BUILDING. THE RISER AT THE SUBJECT METER SET APPURTENANCE WAS A 3/4" ANODELESS RISER (PE 2306 MEDIUM DENSITY). MANUFACTURE AND INSTALLATION DATE ESTIMATED TO BE IN THE 1970 TO 1979 DECADE | 100762 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
761 | 2009-02-27 | AZ | other | UNKNOWN (GILA COUNTY) | SEMSTREAM ARIZONA PROPANE LLC | AT 2:00 AM ON FRIDAY THE 27TH A PICK UP TRUCK WENT OFF THE ROAD AND RAN INTO A TRAILER HOUSE. WHEN IT HIT THE HOUSE, THE TRUCK SHEARED OF THE GAS METER AND THE ELECTRICAL METER. A FIRE ENSUED. THE ELECTRIC CURRENT WAS PASSING THROUGH THE PICK UP TRUCK. THERE WAS NO ONE AT HOME IN THE TRAILER AT THE TIME. THE TWO PEOPLE IN THE TRUCK LEFT THE TRUCK, ONE WAS UNINJURED AND THE OTHER HAD A BROKEN ARM AND SOME OTHER INJURIES THAT CAUSE A LOSS OF BLOOD. HE WAS FLOWN TO A HOSPITAL IN PHOENIX. THE FIRE DEPARTMENT ARRIVED ON THE SCENE AND GOT THE TRUCK MOVED OFF THE ELECTRIC LINE AS WELL AS OUT OF THE FIRE. THEY PINCHED OFF THE BROKEN GAS RISER. AT 2:27 AM THE GAS COMPANY ARRIVED ON THE SCENE AND STARTED TO DIG A HOLE TO ACCESS THE MAIN AND DISCONNECT THE 34 FOOT LONG ¾ INCH SERVICE LINE. THE ACC OFFICE OF PIPELINE SAFETY WAS CALLED AT 7:10 AM (WHEN I ARRIVED AT THE OFFICE). THE FILE NUMBER IS #PL20090449. THE FILE NUMBER AT PHMSA #898643. THE CORNER OF THE OLD PICK UP WAS BURNED, THE TRAILER WAS TOTALED. THE ESTIMATED DAMAGE WAS LESS THAN $10,000. THE ONE UNINJURED INDIVIDUAL THAT FLED THE SCENE HAS BEEN ARRESTED. THERE HAVE BEEN NO FURTHER REPORTS ON THE MAN THAT WAS FLOWN TO THE HOSPITAL IN PHOENIX. | 10430 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
762 | 2009-03-14 | IL | other | UNKNOWN (WABASH COUNTY) | MT CARMEL PUBLIC UTILITY CO | THE ILLINOIS STATE FIRE MARSHAL INVESTIGATOR DETERMINED THAT THE SOURCE OF THE LEAK WAS ON CUSTOMER OWNED, NON-JURISDICTIONAL PIPING. | 47000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
763 | 2009-03-01 | CA | other | UNKNOWN (SAN DIEGO COUNTY) | SAN DIEGO GAS & ELECTRIC CO | ON MARCH 1, 2009, A FIRE ERUPTED INSIDE A RESIDENTIAL HOME, ULTIMATELY SPREADING TO A NATURAL GAS METER THAT MELTED AND IGNITED. AN ELDERLY RESIDENT SUCCUMBED TO FIRE-RELATED INJURIES, AND PROPERTY DAMAGE EXCEEDED $50,000. AS A RESULT, THE INCIDENT WAS REPORTED TO DOT AND CPUC. FURTHER INVESTIGATION DETERMINED THAT THE FIRE WAS STARTED INSIDE THE HOME AWAY FROM THE METER SET ASSEMBLY. ULTIMATELY, THE METER SET ASSEMBLY MELTED FROM THE FIRE, BUT DID NOT CONTRIBUTE TO ANY RESIDENCE DAMAGE OR CUSTOMER INJURIES. IN ADDITION, IGNITED GAS DID NOT HINDER FIREFIGHTING EFFORTS. GAS SERVICE TO THIS DESTROYED HOME HAS BEEN TEMPORARILY ABANDONED. | 1100 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
764 | 2009-03-05 | MT | natural disasters | UNKNOWN (GALLATIN COUNTY) | NORTHWESTERN ENERGY LLC | THIS IS NORTHWESTERN ENERGY’S FINAL REPORT FOR THIS INCIDENT. SINCE LAST UPDATE THE METALLURGY TESTING HAS BEEN COMPLETED AND THE FINAL METALLURGICAL REPORT WAS SUBMITTED TO THE MONTANA PUBLIC SERVICE COMMISSION ON DECEMBER 9, 2009. THE REPORT STATES, IN SUMMARY, THAT THE PRINCIPAL FACTORS INVOLVED IN THE PIPE SEPARATION WERE CHANGES IN THE EXTERNAL ENVIRONMENT OF THE PIPE, WHICH CAUSED UNUSUAL STRESS LOADS ON THE PIPE. THE FRACTURE OCCURRED SUDDENLY AND SHORTLY BEFORE THE ACCIDENT AND APPEARS TO HAVE INITIATED AT A PRE-EXISTING ENVIRONMENTALLY ASSISTED CRACK ON THE LOWER SURFACE OF THE PIPE. THE PUBLIC SERVICE COMMISSION HAS CLOSED ITS INVESTIGATION. END UPDATE 02/23/2010 (CORRECTED DATE ON 02/26/2010) THIS IS NORTHWESTERN ENERGY'S SUPPLEMENTAL REPORT FOR INITIAL PHONE NOTIFICATION 899129 ON 03/05/2009. AT 8:12 AM ON MARCH 5TH, 2009 AN INCIDENT INVOLVING NATURAL GAS OCCURRED IN THE 200 BLOCK OF EAST MAIN STREET IN BOZEMAN MONTANA. AN EXPLOSION AND ENSUING FIRE ENGULFED FIVE BUSINESSES. EMERGENCY RESPONSE HAD THE SITUATION IN CONTROL WITHIN THREE HOURS AND EIGHTEEN MINUTES. THE INCIDENT COMMANDER ORDERED EVACUATION OF A CORDONED OFF AREA. INITIAL REPORTS WERE NO INJURIES, BUT ONE UNACCOUNTED FOR INDIVIDUAL WAS LATER IDENTIFIED AS A RESULTANT FATALITY. INITIAL INVESTIGATIONS BY BOZEMAN FIRE DEPARTMENT, ATF, OPS AND DOT INSPECTORS IDENTIFIED A SMALL SEPARATION ON A 2¿ STEEL GAS SERVICE LINE AT A THREADED COUPLING AS A POSSIBLE SOURCE OF THE GAS INVOLVED. NORTHWESTERN ENERGY OPERATES THAT JURISDICTIONAL SERVICE LINE. THE INVESTIGATION IS CONTINUING INTO THE CUSTOMER OWNED FUEL LINES AND THEIR POTENTIAL FOR INVOLVEMENT. THIS REPORT WILL BE UPDATED AS FURTHER INFORMATION BECOMES AVAILABLE. | 2500000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
765 | 2009-03-20 | AK | other | UNKNOWN (ANCHORAGE COUNTY) | ENSTAR NATURAL GAS CO | ENSTAR RESPONDED TO A HOUSE FIRE AT 5623 DALZELL CIRCLE AT 0615 ON MARCH 20, 2009 AT THE REQUEST OF THE ANCHORAGE FIRE DEPARTMENT. THE METER ASSEMBLY WAS ENGULFED IN FLAMES FROM THE SPREAD OF THE STRUTURE FIRE. ENSTAR CREWS DUG UP THE SERVICE LINE AND PINCHED IT OFF AT 0825 TO SHUT OFF THE FLOW OF NATURAL GAS. THE ORIGIN OF THE FIRE IS UNDER INVESTIGATION. NATURAL GAS IS NOT BELEIVED TO HAVE CAUSED OR CONTRIBUTED TO THE FIRE. | 301100 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
766 | 2009-02-19 | MA | sabotage | UNKNOWN (BRISTOL COUNTY) | NEW ENGLAND GAS COMPANY | THE SECTION OF THE MAIN APPEARS TO HAVE BEEN PHYSICALLY DAMAGED BY A THIRD PARTY CONTRACTOR SOMETIME AFTER IT WAS INSTALLED IN THE 1960'S. THIS MATTER IS STILL UNDER INVESTIGATION AND NEGG MAY AMEND OR SUPPLEMENT THIS REPORT. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
767 | 2009-03-26 | CA | sabotage | UNKNOWN (FRESNO COUNTY) | PACIFIC GAS & ELECTRIC CO | A THIRD PARTY LANDSCAPER STRUCK A 6 INCH STEEL GAS DISTRIBUTION MAIN WHILE PERFORMING TRENCHING WORK CAUSING GAS TO ESCAPE. PG&E PERSONNEL ARRIVED ON THE SCENE AT 0851 HOURS. THE AREA WAS BLOCKED OFF. GAS FLOW WAS STOPPED AT 1017 HOURS; AND PERMANENT REPAIRS WERE COMPLETED AT 1930 HOURS. THERE WERE NO INJURIES OR FATALITIES AS A RESULT OF THIS INCIDENT. GAS SERVICE TO FIVE CUSTOMERS WAS DISRUPTED. THIS INCIDENT BECAME REPORTABLE WHEN IT WAS DETERMINED THAT DAMAGE TO COMPANY PROPERTY WOULD EXCEED $50,000. THE CAUSE OF THIS INCIDENT WAS THE FAILURE OF THE THIRD PARTY CONTRACTOR TO FOLLOW USA PROCEDURES. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
768 | 2009-01-15 | IL | natural disasters | UNKNOWN (TAZEWELL COUNTY) | CENTRAL ILLINOIS LIGHT CO | ON THE MORNING OF JANUARY 15, AMERENCILCO REGULATOR TECHNICIANS INSTALLED A TEMPORARY CATALYTIC HEATER AND A TARP AS A WIND BARRIER TO PROTECT THE PILOTS FROM FREEZING AND RESTORED GAS SERVICE TO A CUSTOMER. LATER THAT MORNING AT 11:20 A.M. AMERENCILCO RECEIVED A CALL THAT THE TARP WAS SMOLDERING AST THE TARP HAD APPARENTLY BEEN IMPACTED BY THE WING AND CAME INTO CONTACT WITH THE HEATER. PRIOR TO THE REGULATOR TECHNICIANS RETURNING TO THE SITE, A FIRE IGNITED. THE FIRE INCREASED IN INTENSITY AND AS THE REGULATOR PILOTS WERE IMPACTED BY THE HEAT, HIGH PRESSURE GAS WAS RELEASED AND IGNITED CAUSING DAMAGE TO THE METERING FACILITIES, CUSTOMER GRAIN DRYING FACILITIES AND THE SIDING ON AND OLD OFFICE. | 50500 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
769 | 2009-03-10 | VA | other | UNKNOWN (RICHMOND COUNTY) | RICHMOND, CITY OF | ALL INDICATIONS FROM THE CITY OF RICHMOND'S FIRE DEPT ARE THAT THE FIRE STARTED ON THE FRON PORC IN A COUCH AND SPREAD TO THE REMAINING STRUCTURE. THE FIRE EVENTUALLY REACHED THE GAS METER CAUSING IT TO FAIL AND IGNITE. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
770 | 2009-03-29 | AK | other | UNKNOWN (MATANUSKA SUSITNA BOROUGH COUNTY) | ENSTAR NATURAL GAS CO | ENSTAR RESPONDED TO A STRUCTURE FIRE AT 901 N. LEATHERLEAF LOO, WASILLA, AK AT 0125 MARCH 29,2009. THE STRUCTURE FIRE MELTED THE HDPE PIPE INSIDE THE SERVICE LINE RISER CAUSING A RELEASE OF NATURAL GAS. THE GAS METER AND REGULATOR WERE CONSUMED IN THE FIRE. THE SERVICE LINE WAS DUG UP AND PINCHED OFF TO CONTROL THE FLOW OF GAS. THE CAUSE OF THE FIRE IS BELIEVED TO BE ARSON AND IS UNDER INVESTIGATION. NATURAL GAS DID NOT CAUSE OR CONTRIBUTE TO THE FIRE. | 51100 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
771 | 2009-02-12 | KY | sabotage | UNKNOWN (OLDHAM COUNTY) | LOUISVILLE GAS & ELECTRIC CO | <P>ATTACHED LG&E REPORT TO THE KPSC REPORT SUBMITTED SIMULTANEOUSLY. </P> <P>CASE SUMMARY: </P> <P>ON FEBRUARY 12, 2009 AT APPROXIMATELY 3:00 P.M., LG&E'S GAS EMERGENCY OPERATIONS CENTER RCEIVED A CALL REPORTING A NATURAL GAS MAIN STRIKE AND LEAK ON HWY 1793 IN GOSHEN, KY. PRELIMINARY INVESTIGATION FOUND THAT LG&E HAD LOST 103 CUSTOMERS, INCLUDING THE OLDHAM COUNTY MIDDLE SCHOOL. DUE TO THE AMOUNT OF CUSTOMERS AFFECTED AND THE EXPECTED TIME NEEDED FOR REPAIRS, IT WAS DETERMINED THAT THIS WOULD BE REPORTABLE. THE KENTUCKY PUBLIC SERVICE COMMISSION WAS NOTIFIED OF THE OUTAGES. THE U.S. DEPARTMENT OF TRANSPORTATION WAS ALSO NOTIFIED. </P> <P>INVESTIGATION:</P> <P>ON FEBRUARY 12, 2009 AT APPROXIMATELY 3:00 P.M., A THIRD PARTY CONTRACTOR, FLYNN BROTHERS CONTRACTING, WAS OPERATING A BORING MACHINE ACROSS HWY 1793. FLYNN BROTHERS CREWS WERE INSTALLING SEWER LINES FOR LONGWOOD LLC. THE FLYNN BROTHERS CREW EXCAVATED AND EXPOSED THE LG&E 4 INCH MEDIUM PRESSURE PLASTIC NATURAL GAS MAIN FOR THE PURPOSES OF VERIFYING ITS LOCATION.</P> <P>ONCE THE BORE JOB WAS COMPLETED, THE OPERATOR ATTEMPTED TO PULL THE BORE-HEAD BACK. WHEN THE BORE-HEAD REACHED THE AREA OF THE NATURAL GAS MAIN, IT STRUCK A ROCK CAUSING THE BORE-HEAD TO GO UPWARD STRIKING THE MAIN. THIS CAUSED A SIGNIFICANT LEAK IN THE MAIN.</P> <P>BILL TROUTMAN, FLYNN BROTHERS FOREMAN, FOUND A MAINLINE VALVE NEARBY AND OPERATED IT TO STOP THE GAS LEAK. WHEN MR. TROUTMAN OPERATED THE VAVLE, HE SHUT DOWN THE MAIN WHICH WAS FEEDING 103 CUSTOMERS INCLUDING THE NORTH OLDHAM COUNTY MIDDLE SCHOOL.</P> <P>SEVERAL LG&E GAS DISTRIBUTION CREWS WERE DISPATCHED TO THE SCENE FOR REPAIRS AND RESTORATION.</P> <P>UNDERGROUND UTILITIES IN THE AREA HAD BEEN LOCATED. LOCATE PAINT MARKS AND FLAGS PROPERLY SHOWED THE LOCATION OF THE DAMAGED GAS MAIN.</P> <P>DATE OF GAS MAIN INSTALLATION - AREA SYSTEM WAS BUILT BETWEEN JUNE 2004 - PRESENT</P> <P>DATE OF LAS LEAK SURVEY - JULY 11, 2008</P> <P>DESCRIPTION OF PIPE - 4" PL | 19940 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
772 | 2009-02-23 | ID | leaks and spills | UNKNOWN (BONNER COUNTY) | AVISTA CORP | THIS IS A REPORTABLE BECAUSE OF THE ACCUMULATED DOLLAR VALUE OF THE INCIDENT. THE INCIDENT WAS DUE TO A FAILED MECHANICAL JOINT THAT WAS IMPROPERLY INSTALLED IN 2005. THE RESIDENCE WAS VACANT AT THE TIME OF THE INCIDENT. THE MAJOR PART OF THE COST WAS DUE TO THE TIME IT TOOK FOR THE GROUND AREA TO VENT TRAPPED GAS FROM AGAINST THE FOUNDATION OF THE ATTACHED GARAGE. IT TOOK 14 DAYS OF MANPOWER AND EQUIPMENT TO EVACUATE THE GAS DUE TO THE CLAY/LOAM TYPE SOIL AND THE FROST CAP. THE PROPERTY DAMAGE RESULTED FROM THE PROBE HOLES FOR THE EVACUATORS AROUND THE FOUNDATION AND AROUND THE YARD AREA. ONCE THE COSTS STARTED TO EXCEED THE THRESHOLD LEVEL OF $50,000, AVISTA DETERMINED THAT IT WAS A REPORTABLE ON MARCH 13TH, 2009. 5/04/2009 NO CHANGE. SUBMITTING AS "FINAL REPORT" | 90488 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
773 | 2009-03-11 | AR | sabotage | UNKNOWN (WASHINGTON COUNTY) | ARKANSAS WESTERN GAS CO | CONTRACTOR WAS DREDGING OUT A DUCK POND AT BEVERLY MANOR APARTMENTS WHEN THEIR EXCAVATOR BECAME STUCK IN SOFT MUD. IN THE PROCESS OF TRYING TO FREE THE EQUIPMENT THEY HOOKED AND PULLED EXISTING 1.250 INCH SERVICE LINE FEEDING 14 METERS OF THE COMPLEX WHICH BROKE THE SERVICE LINE NEAR THE FOUNDATION OF THE STRUCTURE. A SHORT TIME LATER THE GAS WAS IGNITED FROM AN UNDETERMINED SOURCE. | 408000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
774 | 2009-03-04 | FL | sabotage | UNKNOWN (SARASOTA COUNTY) | PEOPLES GAS SYSTEM INC | COUNTY WAS WIDENING THE ROAD. CONTRACTOR HIT OUR PIPE WITH A ROAD MIXER. | 87000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
775 | 2009-03-21 | KY | other | UNKNOWN (DAVIESS COUNTY) | ATMOS ENERGY CORPORATION - KY/MID-STATES (KENTUCKY) | A FORD RANGER PICKUP CRASHED INTO A GAS DISTRIBUTION LOW PRESSUREE REGULATOR STATION LOCATED AT 2ND AND HALE AVENUE. THE PICKUP TRUCK LEFT THE STREET, RAN OVER (3) 4 INCH STEEL BARRICADES AND STRUCK THE REGULATOR STATION ON THE INLET PIPING SEVERING THE INLET PIPING INLET INLET OF A 2" REGULATOR. THIS CAUSED RELEASE OF GAS FROM THE INLET PIPING (PRESSURE ON SYSTEM WAS 40 PSIG), AND THE RELEASING GAS WAS IGNITED CAUSING THE CRASH TO BE FATAL TO THE DRIVER OF THE PICKUP. | 40417 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
776 | 2009-03-23 | TX | sabotage | UNKNOWN (DENTON COUNTY) | COSERV GAS, LTD | INLET BOX FOR STORM DRAIN WAS BEING INSTALLED AND A 4" POLY MAIN WAS DAMAGED. SITE WAS NEAR A DISTRICT REGULATOR STATION AND NOT ALL LINES WERE IDENTIFIED AND MARKED LEAVING THE STATION. | 7300 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
777 | 2009-03-31 | TX | sabotage | UNKNOWN (DENTON COUNTY) | COSERV GAS, LTD | INLET BOX FOR STORM DRAIN WAS BEING INSTALLED AND A 6" POLY MAIN WAS DAMAGED. THIS IS A LARGE PROJECT AND POOR COMMUNICATION WITH EXCAVATOR AND LOCATOR CAUSED THE LINE NOT TO BE MARKED. EXCAVATOR FAILED TO MAKE A SECOND REQUEST | 3972 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
778 | 2009-03-10 | CA | maintenance | UNKNOWN (NEVADA COUNTY) | AMERIGAS PROPANE LP | THE ROOT CAUSE OF THE INCIDENT WAS DUE TO 12 TO 14 FOOT WALL OF SNOW THAT WAS SNOW BLOWN ONTO THE PROPANE TANK THAT IS SET BACK FROM A MAIN DRIVEWAY ENTRANCE TO THE CONDOMINIUM. THE ENTIRE TANK WAS INCASED IN SNOW AND ICE WHEN AMERIGAS BUG OUT THE SNOW AND ICE OUR TECH DISCOVERED THAT THE EXCESS FLOW VALVE WAS SHEERED IN HALF AT THE TREADS THAT WAS SCREWED INTO A UNION. THE FREEZING AND THAWING CAUSE THE VALVE FAILURE. | 688 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
779 | 2009-03-03 | MN | other | UNKNOWN (RAMSEY COUNTY) | NOTHERN STATES POWER CO. OF MINNESOTA | CUSTOMER WAS IN THE PROCESS OF INSTALLING AN EGRESS WINDOW IN BASEMENT AND WAS USING A TORPEDO HEATER TO THAW THE GROUND FROM INSIDE THE HOUSE. THE HEATER MELTED THE GAS SERVICE APPROXIMATELY 10 FEET UPSTREAM FROM THE GAS METER SET, CAUSING A PIPE FAILURE. GAS BLOWING FROM THE PIPE FAILURE IGNITED A FIRE THAT DAMAGED THE CUSTOMERS HOME AND THAT OF A NEIGHBORING RESIDENCE. | 81000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
780 | 2009-02-20 | NJ | other | UNKNOWN (nan COUNTY) | CONSOLIDATED EDISON CO OF NEW YORK | ON 2/20/09 @ 19:01 HRS., A TRANSCO TECHNICIAN NOTIFIED CON EDISON GAS CONTROL OF A STRONG GAS ODOR AT THE MEADOWLANDS HEATERS WITH FIRE DEPT AND POLICE ON LOCATION. CON EDISON PRESSURE CONTROL WAS NOTIFIED TO RESPOND. AN UNKNOWN CONDITION CAUSED A SHUT DOWN OF THE INLET AND OUTLET VALVES OF THE HEATER'S A LINE, WHICH CAUSED A NO GAS FEED CONDITION INTO THE 134 STREET GATE STATION IN MANHATTAN. THE VALVES ARE OWNED AND MAINTAINED BY TRANSCO. CON EDISON GAS CONTROL RAISED PRESSURES AT SEVERAL OTHER GATE STATIONS AND ADVISED CON EDISON POWER GENERATING STATIONS TO SWITCH TO OIL TO COMPENSATE FOR THE LOSS OF GAS. TRANSCO CREWS MANUALLY RE-OPENED THE VALVES AND THE SYSTEM RECOVERED. THERE WERE NO REPORTED INJURIES, MEDIA ATTENTION, OR CUSTOMER IMPACT. THE ROOT CAUSE INVESTIGATION OF THE EVENT DETERMINED AN AUTOMATIC VALVE WAS CLOSED INADVERTANTLY BY TRANSCO. THIS VALVE IS NOT A CONSOLIDATED EDISON OF NEW YORK ASSET. THIS VALVE IS OWNED, OPERATED AND MAINTAINED BY WILLIAMS (TRANSCO)PIPELINE CORPORATION. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
781 | 2009-03-09 | VA | other | UNKNOWN (FAIRFAX COUNTY) | WASHINGTON GAS LIGHT CO | WASHINGTON GAS WAS CALLED BY THE FAIRFAX COUNTY FIRE BOARD TO ASSIST WITH A HOUSE FIRE LOCATED AT 4001 DAVID LANE IN ALEXANDRIA, VA 22312. THE WASHINGTON GAS SERVICE TECH, MR. DONALD FENTON, TURNED THE GAS OFF AT THE CURB VALVE AT 22:50. A LEAK SURVEY WAS PERFORMED OVER THE SERVICE IN THE YARD AND NO LEAK INDICATIONS WERE FOUND. AN ODORANT SAMPLE WAS TAKEN AND FOUND TO BE AT AN ACCEPTABLE LEVEL. A PRESSURE TEST WAS CONDUCTED ON THE SERVICE LINE FROM THE CURB VALVE TO THE INSIDE BUILDING WALL AND THE SERVICE LINE HELD THE PRESSURE TEST. IT IS BELIEVED THAT THE FIRE STARTED ELSEWHERE IN THE HOUSE AND LATER INVOLVED WASHINGTON GAS FACILITIES. THE FIRE IS STILL UNDER INVESTIGATION BY FAIRFAX COUNTY FIRE INVESTIGATORS. | 546100 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
782 | 2009-03-12 | AK | natural disasters | UNKNOWN (ANCHORAGE COUNTY) | ENSTAR NATURAL GAS CO | THIS LEAKING COUPLING WAS EVALUATED AT A FORENSICS LAB AND WAS DETERMINED TO HAVE PULLED APART FROM THE COPPER TUBING DUE TO FROST MOVEMENT. | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
783 | 2009-03-04 | TX | other | UNKNOWN (HARRIS COUNTY) | ENTEX, A NORAM ENERGY COMPANY (FORM. DIV OF ARKLA | 1/2' PLASTIC SERVICE LINE CAUGHT FIRE DUE TO AN AT&T EMPLOYEE MAKING REPAIRS TO PHONE CABLE USING A PROPANE TORCH TO APPLY A HEAT SHRINK SLEEVE. | 2414 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
784 | 2009-03-16 | TX | other | UNKNOWN (HARRIS COUNTY) | ENTEX, A NORAM ENERGY COMPANY (FORM. DIV OF ARKLA | VEHICLE LEFT ROADWAY AND ENTERED DITCH STRIKING AND DAMAGING AN ABOVE GROUND 4" STEEL CROSSING. | 7439 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
785 | 2008-06-18 | IN | sabotage | UNKNOWN (DEARBORN COUNTY) | LAWRENCEBURG GAS CO | CONTRACTOR WAS INSTALLING WATER SERVICES ACROSS BIELBY ROAD/SR 48 (A TWO-LANE STATE HIGHWAY) TO A RECENTLY INSTALLED WATER MAIN. THIS REQUIRED CROSSING THE 8-INCH STEEL GAS FEEDER MAIN OWNED BY THE LAWRENCEBURG GAS COMPANY AT THE LOCATION IN QUESTION. THE CONTRACTOR WAS USING A VERMEER 7X11 DIRECTIONAL BORING MACHINE TO INSTALL THE SERVICE. THE CONTRACTOR HAD PREVIOUSLY ESTABLISHED THE DEPTH OF THE EXISTING GAS MAIN AT OTHER LOCATIONS MORE THAN 200-FEET FROM THIS CROSSING. THE CONTRACTOR UNFORTUNATELY ASSUMED THE GAS MAIN WOULD BE AT THE SAME DEPTH IN THIS LOCATION, AND DID NOT EXCAVATE TO LOCATE THE EXACT DEPTH OF THE GAS MAIN AT THIS PARTICULAR LOCATION BEFORE BORING ACROSS THE GAS MAIN. THE BORING HEAD FOUND THE CENTER OF THE 8-INCH STELL GAS MAIN, AND ONE OF THE ROCK BITS ON THE HEAD BORED A SMALL HOLE INTO THE SIDE OF THE MAIN APPROXIMATELY 0.25 INCHES IN DIAMETER.SINCE THE LINE COULD NOT BE SHUT DOWN COMPLETELY WITHOUT INTERRUPTING SERVICE TO MANY CUSTOMERS, THE PRESSURE ON THE LINE WAS LOWERED TO APPROXIMATELY 40 PSIG SO THAT THE BORING HEAD COULD BE SAFELY REMOVED, AND A STAINLESS STEEL BAND WAS INSTALLED OVER THE HOLE TO ELIMINATE THE ESCAPE OF GAS. AT THIS POINT, A DRESSER REINFORCING SLEEVE WAS WELDED OVER THE BAND TO CREATE A PERMANENT REPAIR, AND TO MAINTAIN THE MAOP OF THE PIPELINE.THIS INCIDENT WAS REPORTED TO THE NRC, BECAUSE AT THE TIME OF THE DAMAGE, IT WAS NOT KNOWN WHAT THE TOTAL DOLLAR AMOUNT OF THE DAMAGE WOULD BE. ALTHOUGH WE ARE STILL WAITING FOR A COUPLE OF ITEMS, WE ARE CERTAIN THAT THE TOTAL DAMAGE WILL BE LESS THAN $20,000. THIS DOES NOT MEET THE REQUIREMENTS FOR A REPORTABLE INCIDENT AT THE FEDERAL LEVEL, BUT DOES MEET THE INDIANA UTILITY REGULATORY COMMISSION DEFINITION. | 8644 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
786 | 2009-03-09 | MA | other | UNKNOWN (nan COUNTY) | CAPE COD GAS CO (DIV OF COLONIAL GAS CO) | THE MASSACHUSETTS FIRE MARSHAL DETERMINED THAT CAUSE OF FIRE WAS THE ARCHING OF ELECTRICAL LINES THAT COMPROMISED GAS SERVICE LINE. | 350000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
787 | 2009-03-27 | NY | other | UNKNOWN (WESTCHESTER COUNTY) | CONSOLIDATED EDISON CO OF NEW YORK | ON FRIDAY, MARCH 27, 2009, AT 13:53, THE CROTON FIRE DEPARTMENT (FD) REPORTED A GAS EXPLOSION AND BUILDING FIRE TO THE GAS EMERGENCY RESPONSE CENTER. CON EDISON GAS DISTRIBUTION SERVICES (GDS) RESPONDED AND THE CROTON FD REPORTED THAT A PRIVATE VEHICLE BACKED INTO AN OUTDOOR GAS METER AND ELECTRIC METER SET AT 21 MOUNT AIRY ROAD. THE VEHICLE DAMAGED THE OUTSIDE GAS SERVICE RISER CAUSING GAS TO ESCAPE AND IGNITE WHEN THE ELECTRIC METER WAS DAMAGED. THE LEAK AND FIRE WERE SECURED BY TURNING OFF MAIN VALVE 36271, INTERRUPTING GAS TO THREE 2-FAMILY HOMES. CON EDISON CONSTRUCTION RESPONDED AND CUT AND CAPPED THE GAS SERVICE TO #21. MAIN VALVE 36271 WAS REOPENED AND GDS RESTORED GAS SERVICE TO THE AFFECTED CUSTOMERS. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
788 | 2009-04-01 | UT | other | UNKNOWN (SALT LAKE COUNTY) | QUESTAR GAS COMPANY | QUESTAR GAS WAS NOTIFIED AT 5:20 AM THAT A DUPLEX WAS ON FIRE. QUESTAR PERSONNEL ARRIVED ON SITE AND FOUND THAT THE FIRE DEPARTMENT HAD SHUT THE SERVICE VALVE. THE DUPLEX WAS TOTALLY DESTROYED AND THE METER AND REGULATOR WERE MELTED AND LEAKED AN UNDETERMINED AMOUNT OF GAS. QUESTAR EMPLOYEES DUG UP AND CAPPED THE RISER. THE CAUSE OF THE FIRE IS STILL UNDER INVESTIGATION BUT THE FIRE DEPARTMENT DOES NOT THINK IT WAS NATURAL GAS RELATED AND ORIGINATED IN THE GARAGE. | 400326 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
789 | 2009-04-06 | CA | sabotage | UNKNOWN (LOS ANGELES COUNTY) | SOUTHERN CALIFORNIA GAS CO | ON APRIL 6, 2009, A 12¿ GAS MAIN WAS PUNCTURED BY A CONTRACTOR USING A TRACKHOE TO REMOVE A BROKEN CONCRETE WATER MAIN. THERE WAS A USA REQUEST FOR THIS AREA, AND FACILITIES WERE PROPERLY MARKED. NO FIRE OR INJURIES RESULTED FROM THE ESCAPING GAS. THE MAIN WAS REPAIRED, AND FIVE CUSTOMERS WERE PUT BACK IN SERVICE. THE LIKELY CAUSE OF THIS INCIDENT WAS FAILURE OF THE CONTRACTOR TO HAND EXCAVATE IN THE VICINITY OF THE PIPELINE. THIS INCIDENT BECAME REPORTABLE TO PHMSA AND THE CPUC WHEN IT WAS DETERMINED THAT ESTIMATED REPAIR COSTS COULD EXCEED $50,000. | 55000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
790 | 2009-02-02 | TX | other | UNKNOWN (TRAVIS COUNTY) | TEXAS GAS SERVICE COMPANY | A NATURAL GAS LEAK OCCURED WITH ACCIDENTAL IGNITION CAUSING A RESIDENTIAL DWELLING TO BURN. THE LEAK WAS DUE TO AN ILLEGAL ACT WHEN A NON-GAS COMPANY EMPLOYEE REMOVED THE VALVE CAUSING AN UNCONTROLLED RELEASE OF GAS. THIS EVENT DID NOT INVOLVE THE FAILURE OF ANY COMPONENT, BUT WAS THE RESULT OF A HUMAN ACT. | 344240 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
791 | 2009-03-17 | TX | other | UNKNOWN (TRAVIS COUNTY) | TEXAS GAS SERVICE COMPANY | AN ACCIDENTAL STRUCTURE FIRE WAS STARTED IN THE GARAGE OF 5210 PINE PLACE. THE RADIANT HEAT FROM SAID FIRE MELTED INTERNAL COMPONENTS OF THE REGULATOR AND METER, CAUSING NATURAL GAS TO BE RELEASED; BECOMING THE SECONDARY FUEL TO THE FIRE. RADIANT HEAT FROM STRUCTURE FIRE CAUSED EXPOSED SURFACES ON STRUCTURE @ 5212 PINE PLACE TO IGNITE. RESULTING FIRE THEN CAUSED DAMAGE TO GAS METER AND REGULATOR AT 5212 PINE PLACE CAUSING A RELEASE. THE AUSTIN FIRE DEPARTMENT EXSTINGUISHED BOTH FIRES AND TGS SQUEEZED OFF GAS FLOW. A SECTION OF THE SERVICE WAS THEN CUT AND CAPPED. | 179581 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
792 | 2009-03-05 | TX | other | UNKNOWN (TRAVIS COUNTY) | TEXAS GAS SERVICE COMPANY | THE FIRE INVOLVED TWO SINGLE FAMILY RESIDENCES. THE FIRE ORIGINATED IN A TRASH REFUSE CART LOCATED BETWEEN THE STRUCTURES. THE HEAT FROM THE FIRE IGNITED THE STRUCTURE AND CAUSED A FAILURE AT THE METER SETS FOR BOTH RESIDENCES. AT THIS JUNCTURE NATURAL GAS BECAME A SECONDARY FUEL SOURCE OF THE FIRE. GAS COMPNAY EMPLOYEES EXPOSED THE SERVICE LINE AT THE PROPERTY LINE, SQUEEZED THE LINE; SHUTTING THE GAS FLOW AND CAPPED IT. | 371910 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
793 | 2009-04-15 | MI | sabotage | UNKNOWN (OAKLAND COUNTY) | MICHIGAN CONSOLIDATED GAS CO (MICHCON) | AT 12:23 ON APRIL 15, 2009, MICHCON RECEIVED A REPORT OF LEAKING GAS AT WEST SUMMIT STREET IN THE CITY OF MILFORD, OAKLAND COUNTY, MICHIGAN. MICHCON PERSONNEL ARRIVED AT THE SCENE AT 12:37 AND DETERMINED THAT A WATER MAIN CONTRACTOR HAD BORED INTO A STEEL GAS DISTRIBUTION MAIN OPERATING AT ABOUT 35 PSIG. AT 13:48 MICHCON SUPERVISION REPORTED THAT THE INTERSECTION OF WEST SUMMIT AND NORTH MILFORD ROAD WAS BEING CLOSED; FOR SAFETY REASONS A CSX TRACK AT CROSSING GRADE IN THE ROAD INTERSECTION WAS CLOSED TO RAIL TRAFFIC (CSX MILE POST 64.41) AT 13:52.MICHCON DETERMINED THAT THE CONTRACTOR'S BORING TOL HAD PENETRATED A 12" STEEL CASING INSTALLED BENEATH THE RAILROAD TRACK AND HAD PUNCTURED THE 8" STEEL MAIN INSIDE. MICHCON FOUND NO EVIDENCE THAT THE WATER CONTRACTOR HAD CONFIRMED DEPTH OR LOCATION OF THE 8" MAIN PRIOR TO BORING. AN EXCAVATION WAS MADE APPROXIMATELY 7 FEET WEST OF THE WEST RAIL TO ALLOW LEAKING GAS TO FREELY VENTILATE TO THE ATMOSPHERE. AT 16:30 PRESSURE IN THE MAIN WAS REDUCED FROM 35 TO 15 PSIG TO LIMIT LEAKAGE; MICHCON CONTINUED TO MONITOR THE ATMOSPHERE IN THE AREA AND REPAIR OPERATIONS COMMENCED AT 17:45.DURING THE EVENING OF THE 15TH AND INTO THE MORNING OF APRIL 16, MICHCON AND MICHCON'S CONTRACTOR INSTALLED A NEW 8" PLASTIC MAIN IN WEST SUMMIT BY BORING UNDER THE CSX TRACK. APPROXIMATELY 261 FEET OF 8" PLASTIC PIPE WAS INSTALLED, CONNECTED, PRESSURE TESTED, AND ACTIVATED OVER THE NEXT SEVERAL HOURS. AT 05:00 ON APRIL 17, MICHCON CREWS REPORTED THE BROKEN 8" STEEL MAIN HAD BEEN SHUT DOWN AND WAS NO LONGER LEAKING. THE CSX TRACK WAS OPENED TO RAILROAD TRAFFIC AT 05:30. SUPPLY TO CUSTOMERS WAS NOT CURTAILED DUE TO THE LEAK OR DUE TO THE PRESSURE REDUCTION DURING THE RECOVERY OPERATION. | 103744 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
794 | 2009-04-25 | CA | other | UNKNOWN (LOS ANGELES COUNTY) | SOUTHERN CALIFORNIA GAS CO | ON APRIL 25, 2009 A 4 INCH STEEL MEDIUM PRESSURE MAIN WAS DAMAGED WHEN A CROSSING WATER SERVICE WAS ELECTRICALLY ENERGIZED. DUE TO THE CLOSE PROXIMITY, ELECTRICITY ARCED FROM THE WATER SERVICE ONTO THE GAS MAIN, BURNING A HOLE IN BOTH THE WATER SERVICE AND THE MAIN (3/8" HOLE IN MAIN). THIS RESULTED IN THE HIGHER PRESSURE WATER ENTERING INTO THE GAS MAIN, CREATING OVER 1,000 CUSTOMER OUTAGES. WATER WAS SHUT OFF AND GAS MAIN REPAIRED. WATER WAS REMOVED FROM GAS MAIN AT NUMEROUS LOCATIONS AND CUSTOMERS RESTORED. THIS INCIDENT BECAME REPORTABLE TO PHMSA ON MARCH 27, 2009 WHEN WATE SETTLED INTO LOW AND END POINTS AND THE EXTENT OF WATER EVACUATION AND RESTORES INDICATED TOTAL COSTS COULD EXCEED $50,000. | 490000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
795 | 2008-05-20 | MN | other | UNKNOWN (COOK COUNTY) | INTERSTATE ENERGY DBA COMO OIL AND PROPANE | FIRE AT CUSTOMER LOCATION, SYSTEM SHUT DOWN. SYSTEM WAS TESTED AND FOUND TO BE LEAK FREE. GAS NOT SUSPECTED AS CAUSE. STATE OF MN REPORTS THAT IT IS A NON-JURISTICTIONAL INCIDENT. SYSTEM WAS RESTARTED ONCE AREA WAS SECURE. | 526000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
796 | 2009-05-25 | AK | other | UNKNOWN (nan COUNTY) | ENSTAR NATURAL GAS CO | ENSTAR WAS NOTIFEID OF A HOUSE FIRE AT 33515, CUMULUS ROAD, EAGLE RIVER, AK AT 0741 ON MONDAY, MAY 25, 2009. ENSTAR'S GAS METER AND SERVICE LINE RISER BURNED IN THE FIRE. THE FIRE DEPARTMENT RESPONDERS PINCHED OFF THE RISER TO STOP THE FLOW OF NATURAL GAS WITHIN 15 MINUTES OF THEIR ARRIVAL ON SITE. ENSTAR PERSONNEL DUG UP AND CAPPED THE LINE SEVERAL HOURS LATER. THE CAUSE OF THE FIRE WAS DETERMINED TO BE FROM THE WOOD STOVE. NATURAL GAS DID NOT CAUSE OR CONTRIBUTE TO THE FIRE. THIS REPORT SHOULD HAVE BEEN MARKED "FINAL" ON THE INNITIAL REPORT. NO ADDITIONAL CHANGES HAVE BEEN MADE. | 51010 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
797 | 2009-05-07 | CA | other | UNKNOWN (SANTA BARBARA COUNTY) | SOUTHERN CALIFORNIA GAS CO | ON MAY 7, 2009 A WILDFIRE BROKE OUT IN THE VICINITY OF TUNNEL ROAD AND SPYGLASS ROAD IN SANTA BARBARA, DAMAGING SERVICES, RISERS AND METER SET ASSEMBLIES. DAMAGE TO SOCALGAS GAS FACILITIES WAS LIMITED TO THESE COMPONENTS. NO DAMAGE TO DISTRIBUTION MAINS OR TRANSMISSION LINES OCCURRED. WHILE GAS ESCAPING FROM THESE FACILITIES DID IGNITE ON OCCASION, IT WAS NOT RESPONSIBLE FOR CAUSING ANY ADDITIONAL DAMAGE OR INJURIES. ALL REPAIRS OF GAS FACILITIES HAVE BEEN COMPLETED. MANY OF THE INVOLVED FACILITIES WERE ATTACHED TO BUILDINGS THAT HAVE BEEN DESTROYED, SO NO RESTORATION IS NECESSARY AT THIS TIME. THE ESTIMATE OF COSTS ASSOCIATED WITH THESE DAMAGES ($50,000) IS FOR RESTORATION OF ALL DAMAGED GAS FACILITIES. IT DOES NOT INCLUDE COSTS ASSOCIATED WITH EMERGENCY RESPONSE, STANDBY, AND GOVERNMENTAL AGENCY SUPPORT. THIS INCIDENT WAS REPORTABLE TO PHMSA DUE TO FACILITY DAMAGE EXCEEDING $50,000, AS WELL AS SIGNIFICANT NATIONAL MEDIA COVERAGE. | 50500 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
798 | 2009-05-31 | FL | other | UNKNOWN (ALACHUA COUNTY) | GAINESVILLE REGIONAL UTIL GAS DEPT | CUSTOMER WAS BURNING A STUMP IN HIS BACK YARD. HE STARTED THE FIRE ON 5/30/09 AND ON THE MORNING OF 5/31/09, WAS STARTLED WHEN THE FIRE HAD BURNED DOWN TO THE GAS SERVICE AND MELTED THE POLY. THE NATURAL GAS IGNITED. THE INCIDENT RESULTED IN NO PERSONAL INJURIES AND ONLY MINOR DAMAGE TO THE YARD (FOR REPAIRS OF THE GAS SERVICE). | 450 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
799 | 2009-05-19 | TX | sabotage | UNKNOWN (COLLIN COUNTY) | COSERV GAS, LTD | 6" POLY MAIN WAS CUT BUT CREW DIRECTIONAL BORING. CUT CAUSE THE INTERSECTION OF ELDERADO AND CUSTER TO BE CLOSED AND TRAFFIC REROUTED. | 7936 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
800 | 2009-05-05 | WA | other | UNKNOWN (YAKIMA COUNTY) | CASCADE NATURAL GAS CORP | DRIVER WAS TRYING TO FLEE FROM THE YAKIMA POLICE DEPARTMENT, MISSED TURN, LOST CONTROL OF CAR AND RAN INTO THE SIDE OF THE HOUSE AT 901 E ARLINGTON ST, RUNNING OVER THE GAS METER CAUSING THE NATURAL GAS TO IGNITE. THE DRIVER AND PASSENGER WERE TAKEN TO THE LOCAL EMERGENCY ROOM TO BE CHECKED OUT AS A RESULT OF THE CAR CRASH. ON JUNE 3, 2009 I WENT BACK IN TO THE DATA BASE TO CLICK THE "FINAL REPORT" BOX. I FAILED TO DO SO ON JUNE 2, 2009 WHEN I INITIALY FILED THIS FINAL REPORT. | 54300 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
801 | 2009-05-30 | AK | other | UNKNOWN (ANCHORAGE COUNTY) | ENSTAR NATURAL GAS CO | ON MAY 30, 2009, AT 2150, ENSTAR WAS NOTIFIED OF A STRUCTURE FIRE AT 11627 CELESTIAL STREET IN EAGLE RIVER, AK. EXTREME HEAT FROM THE FIRE CAUSED THE HDPE TUBING INSIDE THE SERVICE LINE RISER ON A NEARBY DUPLEX (11617 AND 11615 CELESTIAL ST) TO MELT AND RELEASE NATURAL GAS. A SERVICE TECHNICIAN WAS DISPATCHED WHO WITH THE HELP OF THE FIRE DEPARTMENT WAS ABLE TO DIG UP THE RISER AND PINCH IT OFF TO SHUT DOWN THE RELEASE OF NATURAL GAS. A CREW WAS CALLED OUT TO REPLACE THE RISER AND RESTORE SERVICE TO THE DUPLEX WHEN THE FIRE WAS EXTINGUISED NEXT DOOR. NATURAL GAS DID NOT CAUSE OR CONTRIBUTE TO THE FIRE. | 201010 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
802 | 2009-05-07 | MD | other | UNKNOWN (PRINCE GEORGES COUNTY) | WASHINGTON GAS LIGHT CO | AFTER CONSIDERING INFORMATION OBTAINED AND THE OPINIONS OF EXPERTS, THE PREVIOUS SUBMISSIONS ARE REPLACED AS FOLLOWS: WASHINGTON GAS RESPONDED TO A REPORT OF AN ODOR OF GAS AT THE RANGE INSIDE 3432 DONNELL DRIVE IN DISTRICT HEIGHTS, MD. UPON ARRIVAL BY WASHINGTON GAS’ FIRST RESPONDER, THE SERVICE RISER WAS TURNED OFF AND ADDRESSES 3426-3440 DONNELL DRIVE WERE EVACUATED WITH THE ASSISTANCE OF THE FIRE DEPARTMENT. WASHINGTON GAS CONTINUED TO CHECK INSIDE AND OUTSIDE FOR MIGRATION. DURING THESE CHECKS, AN EXPLOSION OCCURRED. TWO FIREFIGHTERS REQUIRED BRIEF IN PATIENT HOSPITALIZATION. A VALVE WAS TURNED OFF NEAR THE INTERSECTION OF MARLBORO PIKE AND LORRING DRIVE TO SHUT OFF THE FLOW OF GAS TO THE STRIP MALL. THE GAS MAIN WAS LATER SQUEEZED OFF AND CAPPED BEHIND 3416 DONNELL DRIVE. A PRESSURE TEST OF THE PIPING DOWNSTREAM OF THE CAPPED OFF LOCATION REVEALED THAT THE PIPE WOULD NOT HOLD PRESSURE AND A BLOWING NOISE COULD BE HEARD COMING FROM THE AREA OF AN ASPHALT PATCH IN THE PAVEMENT. WORKING WITH REPRESENTATIVES OF THE MARYLAND PUBLIC SERVICE COMMISSION AND THE PRINCE GEORGE’S COUNTY FIRE DEPARTMENT AND FIRE MARSHALL, WASHINGTON GAS DID A CAREFUL EXCAVATION, UNCOVERED THE TWO INCH PLASTIC GAS MAIN AND TRACED IT BACK UPSTREAM TO A LOCATION WHERE HOLES WERE FOUND. ELECTRICAL CABLES WERE FOUND TO HAVE BEEN DAMAGED. THE TRACER WIRE FOR THE GAS MAIN WAS FOUND TOUCHING AND IN CLOSE PROXIMITY TO THE HOLES. IT IS APPARENT THAT THE FAULTING ELECTRIC CABLES RELEASED CURRENT WHICH ENERGIZED THE TRACER WIRE, CAUSING IT TO HEAT UP AND MELT THE GAS MAIN IN SPOTS. THE HOLES IN THE GAS MAIN WERE NOT CAUSED BY RADIANT HEAT FROM THE FAULTING ELECTRIC CABLES. GAS ESCAPING FROM THE MAIN MIGRATED INTO THE BUILDING UNTIL AN IGNITION SOURCE IGNITED THE GAS AND CAUSED A LOW ORDER EXPLOSION. AN EXCAVATION OF THE AREA UNDER THE ASPHALT PATCH SHOWED THE LOCATION OF A NEW WATER LINE THAT WAS INSTALLED LONG AFTER THE GAS AND ELECTRIC LINES. THE BACKFILL IN THE VICINITY OF THE WATER LINE WAS INAPPROPRIATE, CHAFED THE ELECTRIC LINE AND PROBABLY THE TRACER WIRE. THE CONTRACTOR WHO INSTALLED THE WATER LINE, GOLDEN SUN CONSTRUCTION, CREATED A SEQUENCE OF EVENTS ENDING IN AN EXPLOSION WHICH WOULD NEVER HAVE OCCURRED IF IT HAD BACKFILLED PROPERLY. BASED ON A REVIEW OF MISS UTILITY RECORDS, GOLDEN SUN DID ITS EXCAVATION WITHOUT GIVING THE REQUIRED NOTICE OF INTENT TO DIG. | 2505500 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
803 | 2009-05-15 | IL | sabotage | UNKNOWN (COOK COUNTY) | NORTHERN ILLINOIS GAS CO | THIRD PARTY EXCAVATOR STRUCK 4" GAS MAIN AND CAUSED 23" LONG BY 1.25" WIDE PUNTURE IN THE MAIN. | 563300 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
804 | 2009-05-19 | MD | other | UNKNOWN (PRINCE GEORGE'S COUNTY) | WASHINGTON GAS LIGHT CO | WASHINGTON GAS RESPONDED TO A HOUSE FIRE REPORTED BY THE PRINCE GEORGE'S COUNTY FIRE DEPARTMENT AT 2616 FELTER LANE IN BOWIE, MD. UPON ARRIVAL, WASHINGTON GAS FOUND THE GAS OFF BY THE FIRE DEPARTMENT AT THE SERVICE RISER LOCATED ON THE OUTSIDE REAR OF THE HOUSE. UPON INVESTIGATION BY THE PRINCE GEORGE'S COUNTY FIRE INVESTIGATOR, IT WAS REPORTED TO WASHINGTON GAS THAT THE FIRE STARTED IN THE REAR OF AN ATTACHED SCREENED PORCH. THE FIRE SPREAD TO THE MAIN STRUCTURE OF THE HOUSE AND INVOLVED THE WASHINGTON GAS FACILITIES. THE SERVICE LINE WAS CUT AND CAPPED OFF AT THE MAIN. | 200200 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
805 | 2009-05-09 | RI | other | UNKNOWN (PROVIDENCE COUNTY) | NEW ENGLAND GAS COMPANY | A HIGH SPEED DRIVES HEADING WEST ALONG RUGBY STREET LEFT THE LANE OF TRAVEL, VEERED RIGHT UP A SLIGHT EMBANKMENT FOR APPROXIMATELY 30 FEET, AND THEN STRUCK AN OUTSIDE METER SET AT 99 RUGBY ST. AS A RESULT OF THE MECHANICAL FORCE CAUSED BY THIS ACCIDENT, AND INTERIOR ELBOW JOINT SEPARATED, CAUSING LOW PRESSURE GAS TO ESCAPE INTO A CONFINED UTILITY CLOSET, WHICH WAS ATTACHED TO AN APARTMENT BUILDING. THREE RESIDENCE FROM THE AJOINING UNIT WERE EVACUATED. THE UTILITY CLOSET IGNITED, &amp; CAUSE OF IGNITION IS UNKNOWN. A FIREMAN &amp; POLICEMAN WERE INJURED BY THE FORCE OF THE EXPLOSION. | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
806 | 2009-06-01 | UT | other | UNKNOWN (SALT LAKE COUNTY) | QUESTAR GAS COMPANY | TRUCK RUNS RED TRAFFIC LIGHT AND CRASHES INTO CAR. DRIVER OF CAR LOOSES CONTROL AND COLLIDES WITH HOME AND GAS METER. IMPACT OF CRASH BREAKS GAS METER CAUSES A NATURAL GAS LEAK. GAS WAS QUICKLY SHUTOFF AT THE SERVICE RISER TO THE METER BY EMERGENCY RESPONDERS. BOTH THE DRIVER OF THE CAR AND A PASSENGER IN THE CAR WERE TAKEN TO LOCAL AREA HOSPITALS FOR INJURIES SUSTAINED DUE TO THE CAR CRASH AND NOT THE RELEASE OF NATURAL GAS. EMERGENCY RESPONDERS DID EVACUATE THE HOME OF THE BROKEN METER AS A SAFETY PRECAUTION, WHICH INVOLVED THREE PEOPLE. STATUS OF THE INJURED CAR DRIVER AND THE PASSENGER IS NOT AVAILABLE. | 10681 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
807 | 2009-05-18 | TN | sabotage | UNKNOWN (CUMBERLAND COUNTY) | UPPER CUMBERLAND GAS UTILITY DISTRICT | A CONTRACTOR USING A 1996 VERMEER 755 TRENCHER WAS INSTALLING A NEW SEWER LINE WHEN HE HIT THE END OF A 2" SDR-11, 3408 STUB APPROXIMATELY 8 FOOT LONG THAT HAD APPARENTLY BEEN PUT IN WHEN THE MAIN WAS INSTALLED IN 1996. THE SHORT STUB WAS NOT ON ANY MAPS AND DIDN'T APPEAR TO HAVE TRACER WIRE LIKE THE MAINS. THE GAS DID IGNITE BUT WAS SHUT OFF AND THE FIRE OUT IN UNDER 30 MINUTES. THERE WEREN'T ANY INJURIES BUT THE CAB AND SOME HOSES ON THE TRENCHER WERE DAMAGED. THE MACHINE DIDN'T LOOK VERY BAD BUT APPARENTLY GETTING PARTS THAT OLD IS HARD TO FIND AND VERY EXPENSIVE. WE WILL UPDATE THIS REPORT WHEN WE GET THE REPAIR COSTS. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
808 | 2009-06-05 | TN | other | UNKNOWN (SHELBY COUNTY) | MEMPHIS LIGHT GAS & WATER DIVISION | AT APPROXIMATELY 0034 HOURS ON FRIDAY, JUNE 5, 2009, A DRIVER FOR ALLIED WASTE SERVICES SET A TRASH DUMPSTER DOWN ON TOP OF OUR GAS METER REGULATOR IN THE REAR OF 5143 QUINCE ROAD. THE IMPACT BROKE THE BODY OF THE REGULATOR OFF AND CAUSED A CATASTROPHIC FAILURE OF THE REGULATOR ALLOWING HIGH PRESSURE GAS OR LINE PRESSURE, EIGHTY EIGHT (88 P.S.I.G.) POUNDS THROUGH THE GAS METER AND INTO THE CUSTOMER¿S FUEL LINE AND APPLIANCES. A 911 CALL WAS PLACED AT THIS TIME BY A SECURITY GUARD WHICH DISPATCHED THE MEMPHIS FIRE DEPARTMENT (MFD). THIS IMPACT ALSO BENT THE ONE AND ONE HALF INCH (1 ½¿) STEEL RISER APPROXIMATELY TEN DEGREES JEOPARDIZING THE INTEGRITY OF THE CUSTOMER¿S FUEL LINE. AT 0102 HOURS THE MFD NOTIFIED MEMPHIS LIGHT GAS AND WATER DIVISION (MLGW) OF A STRUCTURE FIRE WITH GAS ON FIRE ALSO. MLGW ISSUED THE MAINTENANCE AT 0108 HOURS TO THE ON-CALL CREW FOR GAS WITH THE CREW ARRIVING AT 0145 HOURS AND ELIMINATING NATURAL GAS AT 0210 HOURS. AS STATED IN THE MFD¿S INVESTIGATIVE REPORT, INTERVIEWS WITH RESPONDING MLGW EMPLOYEE¿S AND PHYSICAL EVIDENCE NATURAL GAS WAS BURNING FROM THE CUSTOMER FUEL LINE AT THE TOP EDGE OF THE ROOF. | 450575 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
809 | 2009-05-29 | PA | sabotage | UNKNOWN (WASHINGTON COUNTY) | COLUMBIA GAS OF PENNSYLVANIA | ON MAY 29, 2009, AT APPROXIMATELY 5:30 PM, AN EMPLOYEE OF JK FOSTER COMPANY STRUCK A 2 INCH PLASTIC GAS MAIN LINE WHILE EXCAVATING THE AREA TO REPAIR AN UNDERGROUND WATER LINE 121 LAZY-D-TR COURT, ROSCOE, WASHINGTON COUNTY PENNSYLVANIA. THE TRAILER COURT OWNER PLACED AN INSUFFICIENT NON-EMERGENCY PA ONE CALL NOTICE AT 7:08 PM ON MAY 28, 2009. THE EXCAVATION OCCURRED ON MAY 29, 2009 BEFORE THE AREA WAS MARKED FOR UNDERGROUND UTILITIES. COLUMBIA WAS REQUIRED TO MARK THEIR FACILITIES ON JUNE 1, 2009 AND EXCAVATION COULD COMMENCE ON JUNE 2, 2009, UNDER THE PROVISIONS OF PENNSYLVANIA ONE CALL. THE GAS ESCAPING FROM THE DAMAGED MAINLINE MIGRATED TO THE MOBILE HOME, IGNITED, AND DESTROYED THE HOME. | 7123 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
810 | 2009-05-12 | MO | other | UNKNOWN (ST. LOUIS COUNTY) | LACLEDE GAS CO | AN AUTOMOBILE STRUCK THE ABOVE GROUND CASE, INSTRUMENTATION, AND ASSOCIATED SCADA EQUIPMENT OF A PRESSURE LIMITING AND REGULATING FACILITY. THE COLLISION RESULTED IN A MINOR RELEASE OF NATURAL GAS FROM A THERMOPLASTIC NYLON CORE HIGH PRESSURE SENSING LINE HOSE THAT WAS DAMAGED. | 110000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
811 | 2009-05-21 | MD | other | UNKNOWN (WASHINGTON COUNTY) | COLUMBIA GAS OF MARYLAND INC | IN HAGERSTOWN, WASHINGTON COUNTY, MARYLAND A FIRE OCCURRED AT 104 DOUB WAY IN THE AREA OF THE OUTSIDE AIR CONDITIONING UNIT. THE GAS METER AND REGULATOR WERE APPROXIMATELY 2 FEET AWAY. THE HEAT FROM THE FIRE MELTED THE METER AND REGULATOR CAUSING THE GAS TO LEAK OUT AND CONSEQUENTLY FED THE FIRE. SUPPLEMENT SUBMISSION TO ADD INFORMATION FOR PART A #4 | 225001 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
812 | 2009-06-24 | CA | other | UNKNOWN (PLACER COUNTY) | PACIFIC GAS & ELECTRIC CO | A RESIDENTIAL STRUCTURE FIRE STARTED AT APPROXIMATELY 0300 HOURS ON 6/24/09. PG&E WAS NOTIFIED OF THIS INCIDENT BY THE ROCKLIN FIRE DEPARTMENT AT APPROXIMATELY 0338 HOURS, AND PG&E PERSONNEL ARRIVED ON THE SCENE AT 0404 HOURS. GAS FLOW WAS STOPPED AT APPROXIMATELY 0400 HOURS BY THE FIRE DEPARTMENT. ACCORDING TO THE FIRE DEPARTMENT THE FIRE ORIGINATED IN THE GARAGE; THE CAUSE OF THE FIRE IS ARSON. DURING THE FIRE, PART OF THE STRUCTURE FELL AND SEPARATED THE HOUSELINE FROM THE GAS METER, ALLOWING NATURAL GAS TO ESCAPE AND CONTRIBUTE TO THE FIRE. THE METER SET WAS ALSO DAMAGED DUE TO THE HEAT OF THE FIRE. SACRAMENTO TV STATIONS KCRA 3 AND KXTV 10 WERE ON SCENE. THERE WERE NO INJURIES OR FATALITIES FROM THIS INCIDENT AND ONE EVACUATION. | 278000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
813 | 2009-07-06 | CA | other | UNKNOWN (SANTA CLARA COUNTY) | PACIFIC GAS & ELECTRIC CO | A RESIDENTIAL HOUSE FIRE STARTED AT APPROXIMATELY 1030 HOURS ON 7/6/09. PG&E WAS NOTIFIED OF THIS INCIDENT BY THE SAN JOSE FIRE DEPARTMENT AT APPROXIMATELY 1103 HOURS, AND PG&E PERSONNEL ARRIVED ON THE SCENE AT 1141 HOURS. GAS FLOW WAS STOPPED BY THE FIRE DEPARTMENT BY SHUTTING THE SERVICE VALVE OF THE METER SET AT APPROXIMATELY 1130 HOURS. THE CAUSE OF THIS INCIDENT IS UNDETERMINED AS INDICATED BY THE SAN JOSE FIRE DEPARTMENT; INDICATIONS ARE THAT THE FIRE STARTED IN THE VICINITY OF THE METER SET. THE METER SET WAS DAMAGED DUE TO THE HEAT OF THE FIRE RELEASING NATURAL GAS WHICH CONTRIBUTED TO THE FIRE. THERE WERE NO INJURIES OR FATALITIES FROM THIS INCIDENT AND ONE EVACUATION. NO MEDIA WAS PRESENT. | 193000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
814 | 2009-07-06 | CA | other | UNKNOWN (CONTRA COSTA COUNTY) | PACIFIC GAS & ELECTRIC CO | A MOBILE HOME FIRE STARTED AT APPROXIMATELY 1300 HOURS ON 7/6/09. PG&E WAS NOTIFIED OF THIS INCIDENT BY THE CONTRA COSTA FIRE DEPARTMENT AT APPROXIMATELY 1312 HOURS, AND PG&E PERSONNEL ARRIVED ON THE SCENE AT 1336 HOURS. GAS FLOW WAS STOPPED BY THE FIRE DEPARTMENT BY SHUTTING THE SERVICE VALVE OF THE METER SET AT APPROXIMATELY 1330 HOURS. THE CAUSE OF THIS INCIDENT WAS A 3RD PARTY USING A GRINDING WHEEL IN THE VICINITY OF A MOBILE HOME AND A MANIFOLD WITH 5 METERS. THE GRINDING WHEEL STARTED A FIRE IN A STORAGE STRUCTURE ON THE SIDE OF THE MOBILE HOME WHICH IN TURN CAUGHT THE MOBILE HOME ON FIRE. THE FIRE DAMAGED TWO OF THE METERS ON THE MANIFOLD RELEASING NATURAL GAS WHICH CONTRIBUTED TO THE FIRE. THERE WERE NO INJURIES OR FATALITIES FROM THIS INCIDENT AND THREE EVACUATIONS. NO MEDIA PRESENT. | 105000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
815 | 2009-05-29 | GA | sabotage | UNKNOWN (LAURENS COUNTY) | DUBLIN, CITY OF | ON MAY 28,2009, AT APPROXIMATELY 1725 HOURS, I RECEIVED A CALL FROM MR. GARY DUTY, ONE OUR GAS DEPARTMENT'S ON-CALL EMPLOYEES, STATING HE WAS ON JORDAN STREET, IN EAST DUBLIN GA. HE INFORMED ME THAT THE SEWER CONTACTOR FOR THE CITY OF EAST DUBLIN, POPCO INC, HAD CALLED, AND STATED THAT HE HAD HIT A 3/4" GAS SERVICE LINE DURING EXCAVATION. MR. DUTY STATED TO ME THAT HE HAD CHECKED AROUND THE EXCAVATION, USING AN ELECTRONIC CGI, AND HAD NOT DETECTED A GAS LEAK AND THE STEEL SERVICE LINE WAS NOT BROKE. I ADVISED MR. DUTY TO RESURVEY THE AREA AROUND THE HOUSE, OUTSIDE AND INSIDE, AROUND THE STANDPIPE, AND THE SERVICE LINE, AND TO GET WITH THE CONTRACTOR AND SHOW HIM THE RESULTS. I ALSO ADVISED MR. DUTY THAT IF HE FINDS ANY GAS LEAKING, TO CALL ME, SO THAT WE CAN CALL IN A GAS CREW TO SHUTDOWN, AND CUT AND CAP THE SERVICE LINE. APPROXIMATELY 10 TO 15 MINUTES LATER, MR. DUTY CALLED ME BACK, AND STATED THAT HE WAS NOT DETECTING ANY GAS LEAKING. HE ALSO STATED THAT THERE WAS NOT A GAS METER AND THAT THE RISER WAS LOCKED OFF AND CAPPED. MR. DUTY ALSO STATED THAT THE HOUSE WAS LOCKED UP AND THAT NO ONE WAS AVAILABLE TO LET HIM SURVEY FOR LEAKS INSIDE. MR. DUTY STATED THAT THE HOUSE APPEARS TO BE UNDER RENOVATION. MY NEXT CALL FROM MR. DUTY WAS AROURAD 0230 HOURS, ON MAY 29, 2009, STATING THAT HE WAS BACK ON JORDAN STREET AND THE HOUSE WAS ON FIRE. I ARRIVED ON SCENE BY 0300 HOURS AND IDENTIFIED MYSELF TO THE CITY OF EAST DUBLIN'S FIRE DEPARTMENT. I ALSO NOTIFIED THE EAST DUBLIN FIRE DEPARTMENT, THAT WE WERE GOING TO CUT OFF A MAIN GAS VALVE TO REDUCE THE EXISTING 20' PSI MAIN PRESSURE BY APPROXIMATELY 50%) AND THEN WE WILL CUT AND CAP THE SERVICE IN THE STREET TO STOP THE FLOW OF GAS. THE GAS MAIN IS A 2 1/4 " CAST IRON GAS MAIN AND A ONE WAY FEED. THE WORK WAS COMPLETED BY APPROXIMATELY 0445 HOURS, WITH THE FIRE OUT. THE HOUSE WAS A SMALL BLOCK HOUSE THAT APPEARED TO BE ON A CONCRETE SLAB WITH A WOOD ROOF. THE FIRE WAS APPROXIMATELY 3-5 FEET IN FRONT OF THE GAS STAND PIPE, NEXT TO THE HOUSE. THE FLAMES COVERED ABOUT 3 FEET IN DIAMETER, AND REACHED A HEIGHT OF ABOUT 3-4 FEET. THE FIRE DEPARTMENT MAINTAINED A SPRAY OF WATER ON THE FLAME DURING THE SHUTDOWN PROCESS. IN MY CONVERSATION WITH MR. ALLEN, EAST DUBLIN'S FIRE CHIEF, HE STATED THAT TWO PEOPLE WERE AT AND IN THE HOUSE, AND ONE HAD LIT A CIGARETTE, AND THEN THE EXPLOSION HAD OCCURRED, STARTING THE FIRE. BOTH PERSONS WERE TAKEN TO THE LOCAL HOSPITAL, AND THEN TRANSPORTED TO A BURN CENTER IN AUGUSTA, GEORGIA. AFTER AN INITIAL INVESTIGATION TO COLLECT INFORMATION, I CONTACTED MR. BRUCE MORGAN WITH THE PUBLIC SERVICE COMMISSION, WHO IN TURN CONTACTED MR. ROBERT PACE, TO REPORT TO DUBLIN TO BEGIN A STATE INVESTIGATION. AFTER THE INITIAL ONSITE INVESTIGATION WITH MR. ROBERT PACE, I RETURNED TO THE GAS DEPARTMENT OFFICE AND NOTIFIED THE DEPARTMENT OF TRANSPORTATION PIPELINE AND HAZARDOUS MATERIALS SAFETY ADMINISTRATION, AND TALKED TO MS. WILSON, AT 1430 HOURS, NOTIFICATION NUMBER 907006. DURING THE INITIAL INVESTIGATION, THE SERVICE LINE IN FRONT OF THE STAND PIPE, AND AT THE POINT OF THE FIRE, WAS UNCOVERED. THE 3/4" STEEL SERVICE LINE HAD BEEN TRANSITIONED WITH A COMPRESSION COUPLING TO 5/8 ORANGE PE PIPE, AT SOME UNKNOWN PERIOD IN THE PAST. THE COMPRESSION COUPLING WAS SEPARATED FROM THE 3/4" STEEL PIPE, ALLOWING 20 PSI GAS PRESSURE, TO BLOW UNDERGROUND IN SANDY SOIL. AT THIS TIME, WE DO NOT KNOW WHEN THE SEPARATION OF THE COMPRESSION FITTING OCCURRED. FINAL NARRATIVE DESCRIPTION ON SEPTEMBER 17, 2009, THE CITY OF DUBLIN RECEIVED NOTICED FROM THE GEORGIA PUBLIC SERVICE COMMISSION, ON A HEARING IN REFERENCE TO A RULE NISI. THE FIRST MEETING WAS SCHEDULED FOR OCTOBER 22, 2009 IN REFERENCE TO DOCKET #30228 AND DOCKET #30452. THE JOINT CONSENT AGREEMENT WAS SIGNED ON OCTOBER 27, 2009. DUBLIN PAID $30,000.00 IN PENALTIES TO THE PUBLIC SERVICE COMMISSION. PART OF THE CONSENT AGREEMENT WAS FOR DUBLIN TO UPDATE OPERATOR QUALIFICATIONS, USING A THIRD PARTY TRAINER, BY JULY 28, 2010. THE REGULATORY COMPLIANCE SECTION OF THE MUNICIPAL GAS AUTHORITY OF GEORGIA PROVIDED ALL TRAINING. SEE ATTACHMENT ON COMPLETION. DUBLIN'S NATURAL GAS SYSTEM WAS ALREADY UNDER CONTRACT IN THE MANDATED CAST IRON MAIN AND BARE STEEL SERVICES REPLACEMENT. AS OF OCTOBER 31, 2009, APPROXIMATELY 3,340 L.F. OF 2 1/4" CAST IRON GAS MAIN, ON JORDAN STREET, WAS REPLACED WITH 2,640 L.F OF 2” P.E. MAIN. ALL ACTIVE GAS SERVICES WERE ALSO REPLACED WITH 5/8" P.E. PIPING. DURING THIS PROCESS THERE WERE A TOTAL OF 4 INACTIVE SERVICES ABANDONED. THE FINAL SETTLEMENT WAS MADE TO BOTH PARTIES INJURED IN THE HOUSE FIRE ON FEBRUARY 24, 2010. | 54200 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
816 | 2009-07-17 | CA | other | UNKNOWN (NAPA COUNTY) | PACIFIC GAS & ELECTRIC CO | A HOUSE FIRE STARTED APPROXIMATELY 0500 HOURS ON 7/17/09. THE HOUSE IS LOCATED ON HILLY TERRAIN WITH DIFFICULT ACCESS. THE FIRE DEPARTMENT CALLED AT PG&E AT 0605 HOURS. THE PG&E GAS SERVICE REPRESENTATIVE ARRIVED AT 0625 HOURS. GAS CREWS SHUT OFF GAS AT THEVALVE OF THE HIGH PRESSURE REGULATOR NEAR THE STREET AND THE FIRE WAS EXTINGUISHED AT 0828 HOURS. ACCORDING TO THE INVESTIGATION REPORT BY THE FIRE DEPARTMENT THE ORIGIN OF THE FIRE WAS MOST PROBABLY THE BBQ AREA ON THE DECK OF THE HOUSE; THE CAUSE IS UNDETERMINED. THE FIRE CAUSED MORE THAN $50,000 DAMAGE TO THE HOUSE AND DAMGED THE METER SET WHICH IN TURN RELEASED GAS THAT CONTRIBUTED TO THE FIRE. THERE WERE NO INJURIES OR FATALITIES AND NO MEDIA PRESENT. | 53000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
817 | 2009-07-15 | NE | sabotage | UNKNOWN (DOUGLAS COUNTY) | METROPOLITAN UTILITIES DISTRICT | ON JULY 15 2009 A PRIVATE PLUMBING CONTRACTOR HIT THE GAS SERVICE LINE TO 6814 S. 26TH STREET IN OMAHA, DOUGLAS COUNTY, NE 68107 AS THE CONTRACTOR WAS PREPARING TO INSTALL A UPDATED WATER SERVICE AND SEWER LATERAL LINE. WHEN THE GAS SERVICE WAS STRUCK, AT APPROXIMATELY 1405HRS, THE 90 DEGREE FITTING AT THE INSIDE GAS SHUT OFF VALVE WAS STRESSED AND HAD BROKEN OFF FROM THE VALVE AND NATURAL GAS FILLED THE BASEMENT OF THE STATED RESIDENCE. PRIOR TO THE ARRIVAL OF THE METROPOLITAN UTILITES DISTRICT EMPLOYEES THE GAS WAS IGNITED BY AN UNKNOWN SOURCE AND THE HOME EXPLODED AND IS CONSIDERED A COMPLETE LOSS. OUR INVESTIGTION REVEALED THAT THE GAS SERVICE LINE WAS ACCURATELY MARKED AND THAT THE PRIVATE CONTRACTOR THROUGH THEIR ACTIONS AND ERRORS ARE RESPONSIBLE FOR THIS LOSS. MICHAEL CONRAD, CLAIMS ADJUSTER 10/14/2009- TO DATE THERE IS NO EVIDENCE THAT DISPUTES THE METROPOLITAN UTILITIES DISTRICTS INVESTIGATION, THE CAUSE OF THE DAMAGE AND THE REASON FOR THE LOSS LIES WITH PRIVATE CONTRACTOR. THE METROPOLITAN UTILITIES DISTRICT CONSIDERS THIS MATTER CLOSED. MICHAEL CONRAD, CLAIMS ADJUSTER | 150200 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
818 | 2009-04-24 | NY | other | UNKNOWN (QUEENS COUNTY) | CONSOLIDATED EDISON CO OF NEW YORK | ON FRIDAY, APRIL 24, 2009, AT APPROXIMATELY 4:50 P.M., AN EXPLOSION OCCURRED IN A SINGLE FAMILY HOME AT 80-50 260TH STREET, BETWEEN 80TH AND 81ST AVENUES, IN FLORAL PARK, QUEENS. THERE WAS ONE FATALITY; ONE REPORTED INJURY TO A MEMBER OF THE PUBLIC; AND MINOR INJURIES TO NINE FIRE DEPARTMENT OF NEW YORK (FDNY) FIREFIGHTERS AS A RESULT OF THEIR RESCUE EFFORTS. AT 3:2 1 P.M., ON APRIL 24TH A CON EDISON CUSTOMER AT 80-46 260TH STREET REPORTED THAT HE WAS EXPERIENCING PARTIAL LIGHTS IN HIS HOME. AT 3:34 P.M., THE SAME CUSTOMER REPORTED A STRONG ODOR OF GAS OUTSIDE HIS RESIDENCE. A COMPANY MECHANIC WAS DISPATCHED TO THE LOCATION AT 3:56 P.M. AND ARRIVED THERE AT 4:05 P.M. HE THEN BEGAN TESTING THE STREET AREA AND MANHOLES. THE COMPANY MECHANIC FOUND HIGH LEVELS OF NATURAL GAS IN TWO SEWER MANHOLES IN THE VICINITY OF 80-50 260TH STREET, QUEENS; AND HE CALLED FOR ASSISTANCE. CON EDISON DISPATCHED BACKUP MECHANICS AND THEY ARRIVED AT THE SITE AT 4:42 P.M. AT APPROXIMATELY 4:50 P.M., AN EXPLOSION AND FIRE OCCURRED AT THE HOME LOCATED AT 80-50 260TH STREET, WHICH WAS ADJACENT TO 80-46 260 STREET. THE 2 INCH, HIGH-PRESSURE STEEL GAS MAIN, LOCATED ON THE EAST SIDE OF 260" STREET, BETWEEN 80 AVENUE AND 81 AVENUE, WAS ISOLATED BY GAS OPERATIONS AT 5:05 P.M. BY CLOSING FOUR (4) VALVES. THE GAS MAIN ON 259 STREET WAS SHUT DOWN AT THE REQUEST OF THE FDNY DUE TO A FIRE IN THE ADJACENT HOMES AND AT 80-49 259 STREET (THE HOME BEHIND 80-50 260M STREET). AT 5:41 P.M., THE FDNY EVACUATED A11 21 HOMES ON 260TH STREET FOR SAFETY. THE GAS MAIN ON 259TH STREET WAS SHUT DOWN BY GAS OPERATIONS AT 6: 10P.M. BY OPERATING TWO (2) VALVES. AS A RESULT OF THE GAS MAIN ISOLATIONS, FIFTY GAS CUSTOMERS WERE INTERRUPTED. AT 6: 17 P.M., ALL SEWER MANHOLES WERE FOUND TO BE GAS FREE. AT 7:25 P.M., ELECTRIC EMERGENCY CREWS COMPLETED THE ISOLATION OF THE ELECTRIC SUPPLY ON BOTH AFFECTED STREETS. ON SATURDAY, APRIL 25 &, AT 12:01 A.M., THE ELECTRIC SERVICE WAS RESTORED BY THE COMPANY TO ALL CUSTOMERS ON 259 STREET, AS WELL AS TO THE CUSTOMERS ON 260TH STREET, WHOSE HOMES HAD NOT SUSTAINED DAMAGE. THE ELECTRIC SERVICE REMAINED OFF TO THE HOMES AT 80-46, 80-50, AND 80-54 260 STREET. THE ATMOSPHERE IN ALL BUILDINGS ON 259 AND 260TH STREETS WAS RECHECKED BY THE COMPANY TO CONFIRM THAT THERE WAS NO GAS, AND AT 12: 18 A.M. THE EVACUATION WAS ENDED. THERE WAS NEWS MEDIA ON LOCATION. AS PART OF THE INCIDENT INVESTIGATION, THE COMPANY RETAINED THE SERVICES OF LUCIUS PITKIN, INC. (LPI), AN INDEPENDENT, FAILURE ANALYSIS ENGINEERING CONSULTANT. SECTIONS OF THE TWO (2) INCH, HIGH PRESSURE GAS MAIN, THE GAS SERVICE LINE SUPPLYING 80-50 260TH STREET, THE TWO (2) INCH STEEL ELECTRIC CONDUIT AND THE ELECTRIC SERVICE CABLES SUPPLYING 80-46, 80-50, AND 80-54 260TH STREET, WERE EVALUATED. LPI FOUND A DIME-SIZED HOLE AT THE 12 O'CLOCK POSITION ON THE TWO (2) INCH, HIGH-PRESSURE STEEL GAS MAIN. THE GAS MAIN WAS SITUATED APPROXIMATELY FOUR FEET WEST OF THE EAST CURB OF 260TH STREET AN APPROXIMATE DEPTH OF THREE (3) FEET. THE TWO (2) INCH, STEEL ELECTRIC CONDUIT AND THE GAS MAIN WERE FOUND IN CLOSE PROXIMITY WHEN THEY WERE EXCAVATED AND EXPOSED AFTER THE INCIDENT. THE HOLE IN THE GAS MAIN WAS LOCATED AT A POINT WHERE IT PASSED UNDER THE TWO (2) INCH, STEEL ELECTRIC CONDUIT HOUSING THE ELECTRIC SERVICE CABLES SUPPLYING 80-46, 80-50, AND 80-54 260TH STREET. THE STEEL ELECTRIC CONDUIT HAD A CORRESPONDING HOLE IN THE 6 O'CLOCK POSITION WHERE IT CROSSED THE STEEL GAS MAIN, THE ELECTRIC SERVICE CABLES FAILED IN AN AREA APPROXIMATELY 19 FEET WEST (TOWARDS 80-50 260THSTREET) FROM THE LOCATION WHERE THE ELECTRIC CONDUIT AND GAS MAIN CROSSED. THE GAS MAIN, INSTALLED IN 1950, WAS FOUND TO BE IN GOOD CONDITION WITH NO CORROSION, SUITABLE FOR HIGH PRESSURE GAS SERVICE. LPI HAS DETERMINED THAT A FAULT IN THE ELECTRIC SERVICE CABLES MOST LIKELY ORIGINATED IN AN AREA THAT WAS APPROXIMATELY 19 FEET FROM THE LOCATION WHERE THE GAS MAIN AND ELECTRIC CONDUIT PASSED IN CLOSE PROXIMITY. AT THE FAULT LOCATION, THE TWO (2) INCH, STEEL CONDUIT WAS BENT UPWARD AND A COUPLING BETWEEN TWO PIECES OF CONDUIT HAD BEEN COMPROMISED BY CORROSION AND CONDUIT DEFORMATION. THE ELECTRIC FAILURE CAUSED FAULT CURRENT TO FLOW INTO THE STEEL ELECTRIC CONDUIT, WHICH ARCED ONTO THE NEARBY TWO (2) INCH, HIGH-PRESSURE STEEL GAS MAIN. THE ARCING FROM THE CONDUIT TO THE GAS MAIN CREATED HOLES IN BOTH THE ELECTRIC CONDUIT AND THE GAS MAIN. THE ARCING ALSO CAUSED LOCALIZED DAMAGE TO THE INSULATION AND ONE CONDUCTOR OF THE ELECTRIC SERVICE CABLES. IN AREAS UNAFFECTED BY THE ORIGINAL FAULT OR THE ARCING, THE ELECTRIC SERVICE CABLES WERE IN ACCEPTABLE CONDITION, ADEQUATE FOR ELECTRIC SERVICE TO THE HOMES. ONCE THE ARC CREATED THE HOLE IN THE GAS MAIN, THE ESCAPING GAS TRAVELLED THROUGH PREFERENTIAL ROUTES IN THE SOIL AND SUBSURFACE FACILITIES, ULTIMATELY ACCUMULATING IN THE HOUSE. THE EXTERIOR OF THE ELECTRIC CONDUIT EXHIBITED DAMAGE THAT APPEARS TO HAVE RESULTED FROM PAST EXCAVATION ACTIVITIES. WE HAVE LEARNED THAT THE ELECTRIC AND GAS FACILITIES ON 260TH STREET WERE EXPOSED IN 1987 AS PART OF A CONSTRUCTION PROJECT TO INSTALL WATER AND SEWER MAINS BENEATH THE ELECTRIC AND GAS SERVICES. THE ELECTRIC AND GAS SERVICES, LOCATED AT AN APPROXIMATE DEPTH OF THREE (3) FEET, WERE EXPOSED A SECOND TIME IN 2000, WHEN THE ROADWAY ON 260TH STREET WAS EXCAVATED TO APPROXIMATELY A FIVE (5) FOOT DEPTH BY AN INDEPENDENT CONTRACTOR RECONSTRUCTING THE ROADWAY. THE DAMAGE TO THE ELECTRIC CONDUIT IN THE AREA OF THE ORIGINAL FAULT AND THE POSSIBLE MOVEMENT OF THE ELECTRIC CONDUIT AND GAS MAIN IN THE AREA OF CLOSE PROXIMITY WHERE THE ARCING OCCURRED MAY HAVE BEEN CAUSED WHEN THE EXCAVATION WORK WAS PERFORMED IN 1987 OR 2000. | 500000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
819 | 2009-06-24 | IL | sabotage | UNKNOWN (WILL COUNTY) | NORTHERN ILLINOIS GAS CO | A THIRD PARTY EXCAVATOR STRUCK A 3/4" STEEL SERVICE LINE WHILE REPLACING CURBS. A RELEASE OF NATURAL GAS OCCURRED RESULTING IN A FIRE AND POSSIBLE EXPLOSION AT A PRIVATE RESIDENCE. | 253000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
820 | 2009-06-30 | FL | other | UNKNOWN (HILLSBOROUGH COUNTY) | PEOPLES GAS SYSTEM INC | WATER MAIN BROKE WASHING EARTH FROM UNDER CONCRETE DRIVEWAY WHICH THEN COLLAPSED AND BROKE 2 INCH GAS MAIN. | 60000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
821 | 2009-07-11 | AK | other | UNKNOWN (ANCHORAGE COUNTY) | ENSTAR NATURAL GAS CO | ON SATURDAY, JULY 11, 2009, ENSTAR WAS NOTIFED OF A FIRE AT 132 DEETTE CIRCLE IN GIRDWOOD, AK. THE FIRE BURNED THE HDPE SERVICE LINE, METER AND REGULATOR RELEASING NATURAL GAS. THE SERVICE LINE WAS DUG UP AND PINCHED OFF TO STOP THE FLOW OF GAS. THE FIRE WAS BELIEVED TO HAVE STARTED FROM A BBQ GRILL. NATURAL GAS DID NOT CAUSE OR CONTRIBUTE TO THE FIRE. | 101100 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
822 | 2009-06-15 | TX | natural disasters | UNKNOWN (TARRANT COUNTY) | ATMOS ENERGY CORPORATION - MID-TEX | EARTH MOVEMENT ON THE SLOPE OF RAILROAD RIGHT-OF-WAY RELOCATED A 10" HIGH PRESSURE STEEL MAIN, CAUSING PIPE SEPARATION AND RESULTING LOSS OF GAS. | 123577 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
823 | 2009-07-08 | KS | other | UNKNOWN (HARPER COUNTY) | ATMOS ENERGY CORPORATION - COLORADO/KANSAS | RELEASE OF GAS WAS A RESULT OF HEAT APPLIED FROM AN EXTERNAL SOURCE TO THE POLYETHYLENE GAS MAIN THAT RESIDED IN A VOID UNDER THE CONCRETE ALLEY. OPERATOR UNDERSTANDS THAT THE THIRD PARTY SOURCE AND/OR CAUSE OF THE FIRE, WHICH IMPINGED ON OPERATOR’S PE PIPE CAUSING RELEASE OF GAS, ARE STILL UNDER INVESTIGATION BY STATE AND/OR LOCAL INVESTIGATORS. | 601440 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
824 | 2009-07-10 | KS | other | UNKNOWN (SHAWNEE COUNTY) | KANSAS GAS SERVICE | AN ABANDONED HOME AT 5636 NW ROCHESTER RD IN TOPEKA, KS CAUGHT FIRE DUE TO ARSON PER THE FIRE MARSHALLS INVESTIGATION AND BURNT TO THE GROUND ON JULY 10, 2009. BECAUSE OF THE FIRE AN EMPTY (METER REMOVED 3/08) FLEX RISER WITH A PLASTIC SERVICE INSIDE BECAME HOT ENOUGH TO MELT THE PLASTIC PIPE INSIDE THE RISER AND GAS IGNITED. CHECKS COMPLETED BY THE COMPANY AROUND THE STRUCTURE AND ALONG THE SERVICE LINE TO THE MAIN REVEALED NO GAS READINGS EXCEPT AT THE BURNT RISER AND UNDER A CONCRETE SLAB SURROUNDING THE BURNT RISER. THE LAST SCHEDULED LEAK SURVEY PERFORMED ON THE SERVICE TO THE STRUCTURE WAS COMPLETED IN 12/08 AND THERE WERE NO INDICATIONS OF GAS FOUND FROM THAT SURVEY. WE HAVE THEREFORE CONCLUDED THAT THE GAS FOUND UNDER THE SLAB CAME FROM THE RELEASE OF GAS THAT OCCURRED WHEN THE SERVICE INSIDE THE RISER MELTED DURING THE FIRE. OTHER POTENTIAL SOURCES OF IGNITION WERE NOT PRESENT; ELECTRICAL SERVICE WAS ABANDONED 09/08, WEATHER WAS NORMAL. | 102300 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
825 | 2009-07-17 | TX | sabotage | UNKNOWN (NUECES COUNTY) | CORPUS CHRISTI, CITY OF - GAS DIV | THE EIGHT INCH PIPELINE CROSSING WAS LOCATED BY THE GAS DEPARTMENT ON JULY 7, 2009 PER LOCATE REQUEST TICKET 091812909. THE PIPELINE WAS ADEQUATELY MARKED AND THE MARKINGS WERE CLEARLY VISIBLE WHEN THE PIPELINE WAS INITIALLY LOCATED. THE EXCAVATOR WAS FULLY AWARE OF THE LOCATION OF THE PIPELINE AND FAILED TO MAINTAIN THE MARKINGS. AT THE TIME OF THE INCIDENT, THE MARKINGS WERE STILL VISIBLE ON THE WEST SIDE OF DODDRIDGE. EVEN THOUGH THE EXCAVATOR WAS FULLY AWARE OF THE EXISTENCE OF THE LINE CROSSING DODDRIDGE, THEY FAILED TO MAKE A SECOND NOTIFICATION WHEN THEY DID NOT RECEIVE A POSITIVE RESPONSE TO REMARK PER TICKET 091951071 FOR A JULY 16, 2009 START DATE. THE EXCAVATOR FAILED TO PROTECT AND PRESERVE THE PIPELINE MARKINGS. | 2200 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
826 | 2009-06-29 | TX | sabotage | UNKNOWN (BEXAR COUNTY) | CPS ENERGY | THE EXCAVATION AREA WAS MARKED BY A CPS ENERGY LOCATOR RESPONDING TO A LOCATE REQUEST TICKET WHICH WAS CREATED ON JUNE 8, 2009. THE HIT MAIN OCCURRED AT THE BEGINNING POINT OF AN OFFSET AT THE INTERSECTION OF N.W. MILITARY HWY AND GREEN RUN THAT HAD BEEN INSTALLED TO ACCOMODATE A ROAD WIDENING PROJECT. THE MAIN WAS DAMAGED APPROXIMATELY 26-1/2 INCHES AWAY FROM THE LOCATE MARKS THAT WERE VISIBLE AT THE TIME OF THE INCIDENT. THE GAS MAIN WAS BEING POT-HOLED TO DETERMINE ITS EXACT LOCATION JUST TO THE SOUTH OF N.W. MILITARY HWY AND GREEN RUN BY THE EXCAVATOR, HOWEVER AT THE POINT OF THE HIT THE EXCAVATOR DID NOT POT-HOLE THE GAS MAIN BEFORE EXCAVATING. INSUFFICIENT EXCAVATION PRACTICES ALSO CONTRIBUTED TO THE INCIDENT SINCE THE EXCAVATOR WAS MILLING DOWN THE EXISTING GRADE OVER THE GAS MAIN IN EXCESS OF WHAT TXDOT PLANS CALLED FOR IN THAT AREA AND WAS EXCAVATING A WIDER AREA (FURTHER FROM THE STREET CENTERLINE) THAN THE DESIGN PLANS DICTATED. | 385300 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
827 | 2009-06-08 | MO | sabotage | UNKNOWN (BATES COUNTY) | ATMOS ENERGY CORPORATION - COLORADO/KANSAS | PROPERTY OWNER'S BROTHER DROVE A FENCE POST IN THE GROUND AND INTO THE COMPANY'S SERVICE LINE, PUNCTURING THE LINE. | 7000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
828 | 2009-07-17 | UT | other | UNKNOWN (SALT LAKE COUNTY) | QUESTAR GAS COMPANY | GAS FROM THE METER IGNITED AS A RESULT OF THE BUILDING BEING ON FIRE AND MELTED THE METER. | 60600 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
829 | 2009-08-02 | CA | other | UNKNOWN (STANISLAUS COUNTY) | PACIFIC GAS & ELECTRIC CO | A STRUCTURE FIRE STARTED APPROXIMATELY 0000 HOURS ON 8/02/09. THE MODESTO FIRE DEPARTMENT CALLED AT PG&E AT 0045 HOURS. THE PG&E GAS SERVICE REPRESENTATIVE ARRIVED AT 0110 HOURS. A GAS CREW WAS DISPATCHED BECAUSE THE FIRE PREVENTED ACCESS TO THE SERVICE VALVE. THE GAS WAS SHUT OFF AT 0215 BY EXCAVATION AND CUTTING OFF THE SERVICE LINE. ACCORDING TO THE FIRE DEPARTMENT THE CAUSE IS UNDETERMINED. FIRE COMPLETELY DESTROYED THE STRUCTURE, WITH COSTS EXCEEDING $50,000. THE FIRE MELTED SEVERAL METERS AT A METER MANIFOLD SET WHICH IN TURN RELEASED GAS WHICH CONTRIBUTED TO THE FIRE. THERE WERE NO INJURIES OR FATALITIES AND NO MEDIA WAS PRESENT. SERVICE TO EIGHT CUSTOMERS WILL CONTINUE TO BE SHUT OFF UNTIL THE BUILDING IS REBUILT. | 55000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
830 | 2009-07-27 | WA | other | UNKNOWN (KITSAP COUNTY) | CASCADE NATURAL GAS CORP | ARSON FOUND TO BE CAUSE. REPORTS FROM FIRE DEPARTMENT SAY BUILDING WAS ON FIRE WHEN THEY ARRIVED, BUT METER WAS NOT ON FIRE UNTIL LATER. LEAK INVESTIGATIONS OF GAS SERVICE LINE AND BUILDING FOUND NO LEAKS. ODORANT CHECKS THE NEXT MORNING SHOW ADEQUATE ODORIZATION MEETING PART 192 REQUIREMENTS. | 301500 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
831 | 2009-08-01 | OR | other | UNKNOWN (MARION COUNTY) | NORTHWEST NATURAL GAS CO | AT APPROXIMATELY 23:10 P.M. PDT ON AUGUST 1, 2009, NW NATURAL RECEIVED NOTIFICATION OF AN EXPLOSION AND FIRE INVOLVING THE RESIDENCE AT 1501 E. BURNETT STREET, STAYTON, OREGON. THE RESIDENCE WAS COMPLETELY DESTROYED. THE EXPLOSION CAUSED THE WALL OF THE RESIDENCE TO FALL ON THE METER SET, BREAKING THE METER SET OFF AT THE RISER VALVE. NATURAL GAS WAS RELEASED, BUT DID NOT IGNITE. THE NATURAL GAS SUPPLY TO THE HOUSE WAS TERMINATED BY SQUEEZING THE POLYETHYLENE SERVICE LINE NEAR THE PROPERTY LINE. NW NATURAL LEAKAGE PERSONNEL COMPLETED AN INSTRUMENTED LEAKAGE SURVEY OF THE MAIN AND SERVICES IN THE VICINITY OF THE INCIDENT. NO LEAKAGE WAS DETECTED. COMPANY PERSONNEL SUBSEQUENTLY CONDUCTED A TEST OF THE SERVICE REGULATOR AND METER AND FOUND THAT THE REGULATOR AND METER PERFORMED WITHIN ACCEPTABLE SPECIFICATIONS. ALTHOUGH THE INVESTIGATION IS ONGOING, AT THIS TIME NW NATURAL BELIEVES THAT THE ROOT CAUSE OF THE INCIDENT WAS NOT THE RESULT OF THE FAILURE OR LEAKAGE OF JURISDICTIONAL NATURAL GAS PIPING OR APPURTENANCES. THE COMPANY BELIEVES THAT THE INCIDENT WAS CAUSED BY THE THREAT OF “OTHER OUTSIDE FORCES”, COMMONLY KNOWN AS “FIRE FIRST”. | 270200 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
832 | 2009-07-31 | VA | other | UNKNOWN (CALVERT COUNTY) | WASHINGTON GAS LIGHT CO | WASHINGTON GAS RESPONDED TO AN APARTMENT FIRE AT 270 SHORE ACRES WAY IN PRINCE FREDERICK AT THE REQUEST OF THE FIRE DEPARTMENT. UPON ARRIVAL, THE GAS WAS FOUND TO BE OFF AT THE RISER VALVE. THE PIPING ABOVE THE RISER VALVE HAD BEEN DAMAGED BY A VEHICLE WITH A TRAILER THAT HAD BACKED OVER A CURB. THE APARTMENT COMPLEX LATER CAUGHT FIRE. A SUBSURFACE GAS MIGRATION SURVEY WAS CONDUCTED TO VERIFY THE INTEGRITY OF THE UNDERGROUND SYSTEM. THE GAS REMAINS OFF TO 270 SHORE ACRES WAY. | 1001100 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
833 | 2009-08-06 | UT | other | UNKNOWN (WEBER COUNTY) | QUESTAR GAS COMPANY | QUESTAR WAS NOTIFIED AT 7:00 PM ON AUGUST 6TH THAT A HOUSE LOCATED AT 4894 OLD POST ROAD IN OGDEN UTAH WAS ON FIRE. THE FIRE DEPARTMENT INITIALLY CORDONED OFF THE AREA AND DID NOT ALLOW QUESTAR’S CREW ACCESS TO THE PROPERTY. THE FIRE DEPARTMENT TURNED OFF THE GAS AT THE METER PRIOR TO ALLOWING QUESTAR ACCESS. AT 10:40PM QUESTAR WAS ALLOWED ACCESS TO THE PROPERTY AT WHICH TIME THEY CLOSED THE SERVICE VALVE AND SECURED THE SERVICE. THE HOUSE WAS TOTALLY DESTROYED AND THE METER WAS FOUND TO HAVE MELTED AND TO HAVE LEAKED AN UNDETERMINED AMOUNT OF GAS. ACCORDING TO THE FIRE DEPARTMENT, THE FIRE WAS BELIEVED TO HAVE BEEN STARTED BY TREES COMING IN CONTACT WITH ELECTRICAL POWER LINES, CAUSING THE TREES TO IGNITE AND SUBSEQUENTLY THE FIRE TO SPREAD TO THE STRUCTURE. THE INSURED VALUE OF THE HOUSE AND CONTENTS WAS ABOUT $410,000. | 410600 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
834 | 2009-08-04 | CA | other | UNKNOWN (RIVERSIDE COUNTY) | SOUTHERN CALIFORNIA GAS CO | ON AUGUST 4, 2009, A FIRE ERUPTED INSIDE A BUILDING, ULTIMATELY CAUSING BUILDING TO COLLAPSES ON THE METER SET ASSEMBLY, SHEARING OFF THE RISER. A FIREFIGHTER WAS INJURED, BUT HIS INJURY TOOK PLACE PRIOR TO THE COLLAPSE AND RESULTING ESCAPING GAS. FIRE DAMAGES TO PROPERTY EXCEEDED $50,000. AS A RESULT, THE INCIDENT WAS REPORTED TO PHMSA AND CALIFORNIA PUBLIC UTILITIES COMMISSION. FURTHER INVESTIGATION DETERMINED THAT THE FIRE WAS STARTED INSIDE THE BUILDING AWAY FROM THE METER SET ASSEMBLY. ULTIMATELY, THE COLLAPSE SHEARED THE RISER, RESULTING IN ESCAPING GAS WHICH DID NOT CONTRIBUTE TO ANY BUILDING DAMAGE OR INJURIES. IN ADDITION, IGNITED GAS DID NOT HINDER FIREFIGHTING EFFORTS. GAS SERVICE TO THIS DESTROYED PROPERTY HAS BEEN TEMPORARILY ABANDONED. | 201100 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
835 | 2009-08-04 | MN | sabotage | UNKNOWN (OLMSTED COUNTY) | MINNESOTA ENERGY RESOURCES CORPORATION | ROAD CONSTRUCTION WAS READY FOR CONCRETE AND CONTRACTOR DECIDED TO TURN GRAVEL TO DRY OUT WHAT WAS WET. | 61500 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
836 | 2009-08-07 | CA | sabotage | UNKNOWN (VENTURA COUNTY) | SOUTHERN CALIFORNIA GAS CO | ON AUGUST 7, 2009, A 6” PLASTIC MEDIUM PRESSURE PLASTIC MAIN WAS DAMAGED BY A CONTRACTOR USING A BACKHOE TO EXCAVATE FOR A SEWER WORK. THERE WAS USA REQUEST FOR THIS WORK, HOWEVER, LOCATE MARKS PROVIDED WERE NOT ACCURATE. NO FIRE OR INJURIES RESULTED FROM THE ESCAPING GAS. THE MAIN WAS REPAIRED, AND NO CUSTOMERS WERE OUT OF SERVICE. THE INCIDENT WAS DISCUSSED WITH THE LOCATE EMPLOYEE WHO RESPONDED TO THE ONE CALL REQUEST, AND BASED UPON A REVIEW OF THE INCIDENT, IT WAS DETERMINED THAT NOT ALL AVAILABLE RESOURCES WE USED TO ACCURATELY LOCATE AND MARK THIS FACILITY. THIS INCIDENT BECAME REPORTABLE TO PHMSA WHEN ESTIMATED POTENTIAL COSTS REACHED $50,000. INCIDENT TRIGGERED A SIGNIFICANT DOWNTIME CLAIM BY EXCAVATOR. | 52000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
837 | 2009-08-08 | CO | sabotage | UNKNOWN (LARIMER COUNTY) | PUBLIC SERVICE CO OF COLORADO | EXCAVATOR WAS WORKING ON SEWER PROJECT. GAS SERVICE LINE WAS MISLOCATED. EXCAVATOR PULLED STEEL PORTION OF THE SERVICE OUT OF THE GROUND WITH TRACKHOE, AND THE STEEL TO POLYETHYLENE COMPRESSION COUPLING SEPARATED ON THE STEEL SIDE. | 302000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
838 | 2009-08-13 | HI | maintenance | UNKNOWN (nan COUNTY) | THE GAS COMPANY | ACCORDING TO THE HONOLULU FIRE DEPARTMENT (HFD) REPORT, ON 8/12/09 HFD RESPONDED TO A GAS ODOR COMPLAINT AT 235 SOUTH BERETANIA STREET AROUND 10:22 PM. THE REPORT NOTES THAT HFD USED GAS DETECTORS TO CHECK FOR GAS INSIDE THE BUILDING WITH NEGATIVE RESULTS. THE GAS COMPANY RECORDS INDICATE THAT HFD’S FIRST CALL WAS RECEIVED ABOUT 1:45 AM ON 8/13/09 INQUIRING WHETHER 235 SOUTH BERETANIA STREET HAD GAS SERVICE. THE RESPONSE WAS NO. A SECOND CALL FROM HFD WAS RECEIVED AT ABOUT 2:05 AM REQUESTING INFORMATION ON GAS SERVICES TO ADJOINING PROPERTIES TO 235 S. BERETANIA. INFORMATION WAS PROVIDED. ABOUT 2:12 AM, THE GAS COMPANY, ON ITS OWN INITIATIVE, DISPATCHED THE FIRST RESPONDER TO INVESTIGATE. REPORTS IN THE LOCAL NEWSPAPERS INDICATED THAT AN EXPLOSION OCCURRED AT 12:48 AM, BUT THIS INFORMATION WAS NOT COMMUNICATED TO TGC UNTIL THE FIRST RESPONDER REPORTED TO THE SITE. THE BUILDING'S NAME IS LEIOPAPA A KAMEHAMEHA, ALSO KNOWN AS THE STATE OFFICE TOWER. THE GAS COMPANY'S FIRST RESPONDER ARRIVED AT THE SCENE @ ~2:23 AM AND WITH HFD DETERMINED THAT THE LEAK ORIGINATED IN A MANHOLE IN S. BERETANIA STREET FRONTING THE BUILDING. THE GAS COMPANY CREW ARRIVED AROUND 4:40 AM AND CONFIRMED THE LOCATION OF THE LEAK ON THE 4" MAIN IN THE MANHOLE. IT WAS SUSPECTED THAT THE LEAKING GAS MIGRATED THROUGH THE TELEPHONE CONDUITS FROM THIS VAULT AND INTO THE COMMUNICATIONS ROOM IN THE STATE OFFICE BUILDING. AS A SAFETY PRECAUTION, THE HFD DECIDED TO HAVE THE ELECTRIC COMPANY TURN OFF ALL THE POWER TO THE STATE OFFICE TOWER AND SURROUNDING BUILDINGS TO AVOID IGNITION OF ANY RESIDUAL GAS. THE 4” STEEL MAIN WAS INSTALLED IN 1912. IT IS ESTIMATED THAT SOMETIME IN THE 1950’S, THE TELECOMMUNICATIONS COMPANY (NAME ON MH COVER-MTCO) INSTALLED A VAULT AROUND THE GAS LINE. THE GAS LINE WAS EXPOSED ABOUT 8 FEET WITHIN THE VAULT. THE GAS COMPANY HAD NO KNOWLEDGE OF THIS PORTION OF MAIN BEING EXPOSED IN THE VAULT UNTIL IT WAS DISCOVERED SOMETIME BETWEEN 11/5/05 AND 10/2/06. THE MAIN WAS APPROXIMATELY 4 FEET DEEP FROM THE EXISTING GROUND. | 482000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
839 | 2009-08-15 | NM | other | UNKNOWN (BERNALILLO COUNTY) | NEW MEXICO GAS COMPANY | SOLID WASTE VEHICLE HIT METER SET WHILE SETTING DOWN A GARBAGE BIN NEXT TO A BUSINESS. TWO EMPLOYEES FROM THE BUSINESS COMPLAINED OF SMELLING GAS AND WERE TRANSPORTED TO THE HOSPITAL. BECAUSE OF PRIVACY LAWS, IN-PATIENT HOSPITALIZATION COULD NOT BE CONFIRMED. | 2050 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
840 | 2009-08-18 | GA | technical failure | UNKNOWN (FULTON COUNTY) | ATLANTA GAS LIGHT CO | AN AGL EMPLOYEE BROKE A STEEL SERVICE RISER WHILE ATTEMPTING TO LOOSEN A SERVICE REGULATOR WITH PIPE WRENCHES CAUSING A RELEASE OF GAS. A BYSTANDER FELL DOWN SOME NEARBY STAIRS ATTEMPTING TO AVOID EXPOSURE TO THE GAS AND WAS INJURED. THE BYSTANDER ALSO EXPRESSED THE HE WAS HAVING DIFFICULTY BREATHING AND WAS HOSPITALIZED FOR A SHORT TIME AS A RESULT. | 159 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
841 | 2009-08-12 | GA | sabotage | UNKNOWN (FULTON COUNTY) | ATLANTA GAS LIGHT CO | AN AGL CONTRACTOR INSTALLING NATURAL GAS FACILITIES BORED INTO A 2" PLASTIC MAIN. AS A RESULT, A MARTA TRANSIT STATION WAS EVACUATED AND TRANSIT SERVICE WAS TEMPORARILY HALTED. IN ADDITION, A MAJOR THOROUGHFARE WAS CLOSED FOR A PERIOD OF TIME AS A PRECAUTION. AN INVESTIGATION REVEALED THAT MARKING REQUESTS HAD BEEN PROPERLY MADE FOR THE EXCAVATION SITE, BUT THE MAIN WAS IMPROPERLY LOCATED BY THE CONTRACTOR. THE CONTRACTOR IN QUESTION WAS BOTH THE LOCATOR AND EXCAVATOR ON THIS PROJECT. ALL PERSONNEL INVOLVED WERE DRUG AND ALCOHOL TESTED IN ACCORDANCE WITH PHMSA 199.105B. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
842 | 2009-06-24 | AZ | sabotage | UNKNOWN (YAVAPAI COUNTY) | UNISOURCE ENERGY SERVICES | HIGHWAY TECHNOLOGY, A GUARDRAIL COMPANY CONTRACTED BY YAVAPI COUNTY, WAS INSTALLING GUARDRAILS ALONG IRONSPRINGS RD. IN PRESCOTT ARIZONA, HIGHWAY TECHNOLOGY WAS EXCAVATING WITHOUT A VALID BLUE STAKE. THE BLUE STAKE DATABASE HAS BEEN RESEARCHED AND NO VALID BLUE STREAK TICKET HAS BEEN DISCOVERED. HIGHWAY TECHNOLOGY WAS POUNDING A METALLIC I-BEAM GUARDRAIL POST WITH DIMENSIONS OF APPRXIMATELY 4" WIDE BY 6" ACROSS THE I INTO THE GROUND WITHOUT NOTIFYING BLUE STAKE AND WITHOUT POTHOLING FOR EXISTING FACILITIES. THE HYDRAULIC POUNDER ON THE CONTRACTOR'S TRUCK DROVE THE METALLIC POST INTO OUR 3" STEEL NATURAL GAS DISTRIBUTION MAIN. THE POST LODGED INTO OUR PIPELINE. THE ESCAPING NATURAL GAS EVENTUALLY IGNITED AND BURNED THE REAR HALF OF THE CONTACTOR'S VEHICLE. NO INJURIES WERE EXPERIENCED. GAS SERVICE TO THREE RESIDENTIAL CUSTOMERS WAS AFFECTED. THE GAS SERVICE WAS RESTORED UPON COMPLETION OF PERMENANT REPAIRS TO THE 3" STEEL DISTRIBUTION MAIN APPROXIMATELY 24 HOURS LATER. | 160436 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
843 | 2009-01-22 | AL | maintenance | UNKNOWN (BALDWIN COUNTY) | GULF COAST MINERAL, LLC | CORROSION. REASON BELIEVED TO BE CAUSED BY WATER. REPLACING THE SECTION UNDER WATER WITH HIGH PRESSURE "POLY PIPE." | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
844 | 2009-06-01 | TX | sabotage | UNKNOWN (HARRIS COUNTY) | ENTEX, A NORAM ENERGY COMPANY (FORM. DIV OF ARKLA | 3RD PARTY WHILE HAND DIGGING FOR FOUNDATION REPAIR DAMAGED A PROPERLY MARKED 3/4 POLY SERVICE-LINE, ESCAPING GAS IGNITED AND DIRECT FLAME IMPINGEMENT CAUSED STRUCTURE FIRE. | 302588 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
845 | 2009-08-15 | IL | technical failure | UNKNOWN (LASALLE COUNTY) | ILLINOIS POWER CO | THE GAS CONSTRUCTION CREW WAS SCHEDULED TO REBUILD A METER SET REPLACING TWO AL 5000 DIAPHRAGM METERS WITH ROATARY METERS. THE PROJECT WAS SCHEDULED FOR SATURDAY, AUGUST 15TH TO MINIMIZE CUSTOMER IMPACT DUE TO THE OUTAGE REQUIRED TO COMPLETE THIS REBUILD. A WALK THROUGH WAS CONDUCTED ON FRIDAY, AUGUST 14TH TO EVALUATE THE SCOPE OF THE PROJECT AND TO COMMUNICATE THE EXTENT OF THE OUTAGE WITH THE CUSTOMER. THE CONSTRUCTION CREW WOULD DISCONNECT THE FACILITIES FROM THE SOURCE OF SUPPLY AND REBUILD THE METER SET. THE FOLLOWING MONDAY, A REGULATOR TECHNICIAN WAS SCHEDULED TO REESTABLISH GAS TO THE CUSTOMER. THE CREW MET AT THEIR WORK HEADQUARTERS AT 6:30 A.M., LOADED THE MATERIALS AND HEADED FOR THE JOB SITE. ONCE ON SITE, THE CREW CONDUCTED A JOB BRIEFING THAT FOCUSED ON: ENERGY SOURCES - CONTROLLING THE SOURCE OF GAS WITH VALVES WORK PROCEDURES SPECIFICALLY WELDING SPECIAL PRECAUTIONS FIRE EXTINGUISHER, PROPER TOLS, WORK AREA CONDITIONS PPE REQUIREMEMNTS - GLOVES, SAFETY GLASSES, HIGH VIS VESTS, WELDING APPAREL STRAIN HAZARDS ASSOCIATED WITH REMOVING THE AL 5000 GAS METERS THE EXISTING FACILITIES WERE CONSTRUCTED WITH TWO RISERS PROVIDING 90 PSIG GAS TO PARALLEL AL 5000 GAS METERS WITH A SINGLE DOWNSTREAM 461 REGULATOR DELIVERING 55 PSIG GAS TO THE CUSTOMER. THE CREW CLOSED TWO INLET RISER VALVES ISOLATING THE METER SET FROM THE DISTRIBUTION SUPPLY. THE CREW BROKE THE UNIONS DOWNSTREAM OF EACH AL 5000 GAS METER TO BLEED OFF THE GAS. THE RISER VALVES WERE WELD-BY FLANGED GATE VALVES WITH 2" 150 CLASS FLANGE CONNECTIONS DOWNSTREAM OF THE GATE. THE CREW CUT THE PIPING DOWNSTREAM OF THE FLANGE AND REMOVED THE AL 5000 GAS METERS TO HAVE BETTER ACCESS TO REMOVE THE FLANGE BOLTS. THE CREW ORIGINALLY PLANNED TO USE AN IMPACT WRENCH TO REMOVE THE FLANGE BOLTS; HOWEVER, THEY COULD NOT LOCATED A 3/4" X 1/2" IMPACT WRENCH ADAPTER, SO DECIDED TO USE AN OXY-ACETYLENE TORCH TO CUT THE FLANGE BOLTS. THE CREW CHECKED FOR GAS BLEED BY AT THE INLET GATE VALVES TO ENSURE THAT THEY WERE WORKING IN A GAS FREE ENVIRONMENT WITH THE TORCH AND THEN PROCEEDED TO CUT THE EIGHT FLANGE BOLTS. SEVEN OF THE EIGHT FLANGE BOLTS WERE REMOVED WHEN THE FINAL BOLT REQUIRED ADDITIONAL CUTTING TO REMOVE A BURR THAT INHIBITED THE REMOVAL OF THE BOLT. THERE WAS APPROXIMATELY 6 FEET OF SEPARATION BETWEEN THE RISER VALVES AND UNIONS. THIS PIPING DOWNSTREAM OF THE UNIONS HAD BEEN OPEN TO THE ATMOSPHERE FOR APPROXIMATELY 15 MINUTES WHEN THE RESTRICTING ELEMENT ON THE DOWNSTREAM 461 DIRECT OPERATED REGULATOR OPENED ALLOWING THE RELEASE OF CUSTOMER LINE PACK TO THE ATMOSPHERE. THIS LINE PACK CAME INTO CONTACT WITH THE TORCH AND IGNITED, RESULTING IN INJURIES TO AN EMPLOYEE. MEDICAL TREATMENT FOR THE BURN INJURIES WAS PROVIDED AT A LOCAL HOSPITAL. LATER THAT AFTERNOON OR EARLY EVENING, THE EMPLOYEE MADE THE DECISION TO GET ADDITIONAL TREATMENT AT A HOSPITAL IN NORTHERN ILLINOIS WHERE HE WAS ADMITTED OVERNIGHT FOR OBSERVATION AND RELEASED THE FOLLOWING DAY. THE EXTENT OF HIS INJURIES INCLUDED FIRST DEGREE BURNS TO THE SIDE OF HIS FACE AND SECOND DEGREE BURNS TO HIS WRIST BETWEEN HIS GLOVES AND WELDING JACKET. THE APPARENT CAUSE OF THIS INCIDENT IS RELATED TO THE RELEASE OF CUSTOMER LINE PACK DOWNSTREAM OF THE 461 REGULATOR. THE CREW THOUGHT THAT THE GAS DOWNSTREAM OF THE INLET RISER VALVE WAS COMPLETELY BLED OFF WHEN THE TWO UNIONS WERE BROKE AND THE GAS METERS REMOVED. THE GAS IGNITION WAS NOT ORIGINALLY IDENTIFIED AS A REPORTABLE INCIDENT BECAUSE THE SOURCE OF GAS RELEASED WAS CUSTOMER LINE PACK DOWNSTREAM OF THE GAS METERS AND REGULATOR. AMEREN IP DID PROVIDE NOTIFICATION TO THE ILLINOIS COMMERCE COMMISSION (ICC) OF THE IGNITION AND SUBSEQUENT MEDICAL TREATMENT THE FOLLOWING MONDAY, AUGUST 17TH. THE ICC STAFF, IN CONSULTATION WITH PHMSA CENTRAL REGION, STATED THAT THIS GAS IGNITION SHOULD BE REPORTED AS A DISTRIBUTION INCIDENT BECAUSE THE GAS WAS RELEASED THROUGH COMPANY PIPELINE FACILITIES WHEN THE 461 REGULATOR OPENED ALLOWING THE CUSTOMER LI NE PACK TO BLEED OFF TO THE ATMOSPHERE. FOLLOWING THIS DISCUSSION THE INCIDENT WAS REPORTED TO PHMSA AT 11:30 A.M. ON AUGUST 17, 2009. POST INCIDENT ALCOHOL AND DRUG TESTING WAS NOT PERFORMED DUE TO THE 32 HOUR TIME LAPSE. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
846 | 2009-08-19 | WA | sabotage | UNKNOWN (KING COUNTY) | PUGET SOUND ENERGY | <P>THE INCIDENT OCCURED ON AUGUST 19, 2009: PSE'S CONTRACTOR DAMAGED A 6" HP STW MAIN BY PULLING AN UNMARKED 1 1/4" STUB OFF THE MAIN WHILE EXCAVATING WITH A TRACK HOE. PSE'S FIRST RESPONDER CONTROLLED THE FLOW OF GAS BY CLOSING A HP VALVE IN THE VICINITY OF THE DAMAGED MAIN LOCATION. PSE'S SERVICE PROVIDER MADE PERMANENT REPAIRS. THE TOTAL COST OF THE INCIDENT IS CURRENTLY BEING PROCESSED AND IS UNKNOWN AT THIS TIME. THE COST OF GAS LOSS FROM THE INCIDENT WAS CALCULATED TO BE $8,667.00. THE COST OF REPAIR HAS NOT BEEN FIGURED COMPLETELY AND IS ESTIMATED TO BE OVER $50,000. A TELEPHONIC NOTIFICATION OF THIS INCIDENT WAS MADE TO THE WASHINGTON UTILITIES & TRANSPORTATION COMMISSION ON AUGUST 19. A TELEPHONIC NOTIFICATION TO THE NRC WAS MADE ON AUGUST 21, 2009 DUE TO THE TOTAL DAMAGE COST WAS ESTIMATED TO BE OVER $50,000. AS OF OCT 8, 2009, THE TOTAL DAMAGE COST IS CONFIRMED TO BE OVER $50,000. </P> | 108667 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
847 | 2009-09-17 | AK | other | UNKNOWN (ANCHORAGE COUNTY) | ENSTAR NATURAL GAS CO | ON SEPTEBMEER 17, 2009, ENSTAR RESPONDED TO A CALL TO ASSIST THE ANCHROAGE FIRE DEPARTMENT ON A FIRE AT 7316 TANAGA CIRCLE. HEAT FROM THE FIRE DRIED OUT THE GREASE IN THE SERVICE LINE SHUT OFF VALVE CAUSING A SMALL GAS LEAK AT THE VALVE. THE X-TUBE STEEL SERVICE LINE WAS DUG UP AND DISCONNECTED FROM THE GAS MAIN. IT WILL BE ABANDONED AND REPLACED WITH A NEW LINE IF/WHEN THE STRUCTURE IS REBUILT. IT IS BELEIVED THE FIRE STARTED IN A SECOND FLOOR APARTMENT FROM MATCHES AND OR CARELESSLY DISCARDED SMOKING MATERIALS. NATURAL GAS DID NOT CAUSE OR CONTRIBUTE TO THE FIRE. | 101010 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
848 | 2009-08-27 | GA | technical failure | UNKNOWN (FULTON COUNTY) | ATLANTA GAS LIGHT CO | AN AGL CONTRACTOR WAS WELDING ON A 20" STEEL GAS MAIN WITH MECHANICALLY COUPLED JOINTS. DURING WELDING OPERATIONS, THE 20" PIPE SEPARATED FROM A BURIED MECHANICAL COUPLING IN CLOSE PROXIMITY TO THE WORK AREA CAUSING A CONCUSSIVE RELEASE OF GAS. AS A RESULT, FOUR CONTRACTOR PERSONNEL WERE INJURED TWO OF WHICH REQUIRED OVERNIGHT HOSPITALIZATION. CONTRACTOR CREW WAS IN THE PROCESS OF WELDING ON AN END CAP AFTER SETTING A STOPPER FITTING WHEN THE STEEL PIPE SEPARATED FROM A BURIED MECHANICAL COUPLING. THIS SEPARATION WAS DUE TO THRUST FORCES EXERTED UPON THE PIPELINE WHICH EXCEEDED THE RESTRAINT PROVIDED BY THE COUPLING, SOIL, AND ANCHORS SET BY THE CREW. | 143000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
849 | 2006-07-10 | WI | sabotage | UNKNOWN (DOOR COUNTY) | CEDAR GROVE RESORT & HARBOR | ON JULY 10, 2006, AT APPROXIMATELY 2:30 A.M., A SERIES OF EXPLOSIONS OCCURRED IN THE AREA OF CEDAR GROVE RESORT, IN ELLISON BAY, WISCONSIN. THE EXPLOSIONS RESULTED IN THE DEATHS OF TWO RESORT GUESTS, AND INJURIES TO 12 OTHERS, SOME REQUIRING HOSPITALIZATION. THREE BUILDINGS WERE DESTROYED AS A RESULT OF THE EXPLOSIONS, AND TWO OTHERS EXHIBITED EVIDENCE OF FLASH FIRES WITHIN THE CRAWL SPACES. THE EXPLOSIONS OCCURRED AS A RESULT OF AN UNDERGROUND LEAK FROM A PETROLEUM GAS (LP) PIPELINE. THE LEAK OCCURRED AS A RESULT OF MECHANICAL DAMAGE TO THE PIPELINE DURING AN ELECTRICAL CABLE INSTALLATION PROJECT ON JULY 7, 2006. GAS ESCAPING FROM THE DAMAGED PIPELINE MIGRATED UNDERGROUND THROUGHOUT AREAS OF THE RESORT, AND BEYOND. THE POROUS ROCKY SUBSURFACE ALLOWED AN EXPANSIVE AREA TO BE SATURATED WITH LP GAS PRIOR TO THE EXPLOSIONS. THE SPECIFIC IGNITION SOURCE(S) THAT CAUSED THE EXPLOSIONS WAS NOT DETERMINED. THE MECHANICAL DAMAGE OCCURRED WHILE A CABLE INSTALLATION CONTRACTOR WAS PERFORMING A HORIZONTAL DIRECTIONAL DRILLING (HDD) OPERATION ALONG THE WEST SIDE OF CEDAR SHORE ROAD, WITHIN THE CEDAR GROVE RESORT COMPLEX. THE HDD OPERATION WAS BEING PERFORMED TO INSTALL ELECTRICAL CONDUIT, AND CROSSED THE PATH OF AN UNMARKED ½-INCH DIAMETER LP GAS SERVICE LINE WHICH CROSSED CEDAR SHORE ROAD AND PROVIDED GAS TO THE RESORT OFFICE/OWNER’S RESIDENCE. THE RESULTANT LEAK WENT UNDETECTED UNTIL THE EXPLOSIONS ON JULY 10, 2006. | 1400833 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
850 | 2009-09-19 | OR | other | UNKNOWN (JACKSON COUNTY) | AVISTA CORP | A HIGH SPEED IMPACT FROM A VEHICLE STRUCK A DRIVEWAY BRIDGE, KILLING 3 OCCUPANTS. THE IMPACT SEVERED THE GAS SERVICE. 12/3/09 I FINALIZED THIS REPORT WITH NO ADDITIONAL CHANGES. KRIS BUSKO | 102000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
851 | 2009-09-02 | PA | sabotage | UNKNOWN (BEDFORD COUNTY) | UGI CENTRAL PENN GAS, INC | A CONTRACTOR WHILE EXCAVATING A TRENCH TO INSTALL A WATER MAIN STRUCK AND DAMAGED A 4" STEEL HIGH PRESSURE DISTRIBUTION GAS MAIN WHICH RESULTED IN AN ESCAPE OF GAS. | 103000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
852 | 2009-09-07 | IA | leaks and spills | UNKNOWN (HENRY COUNTY) | ALLIANT ENERGY - INTERSTATE POWER AND LIGHT COMPANY | A PICKUP TRUCK LEFT THE ROADWAY AND HIT THE GAS METERSET AT 509 E. MONROE ST. IN MT. PLEASANT, IOWA ON MONDAY SEPTEMBER 7, 2009 AT 1:28 AM. THE FORCE OF THE TRUCK BROKE THE METERSET BETWEEN THE SHUT-OFF VALVE AND THE SERVICE REGULATOR. THE GAS IGNITED AND CAUSED EXTENSIVE DAMAGE TO THE RESIDENCE AND THE TRUCK. A PRESSURE OF 45 PSIG WAS BLOWING FROM THE SET BEFORE THE GAS WAS SHUT-OFF BY THE FIRE DEPARTMENT. INITIAL ESTIMATES PLACED THE TOTAL COST AT OVER $50,000. THE HOUSE WAS VACANT AT THE TIME AND NO INJURIES WERE REPORTED. THE IOWA UTILITY BOARD INVESTIGATED THIS INCIDENT ON SEPTEMBER 9, 2009. NO PROBABLE VIOLATIONS WERE FOUND. | 127646 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
853 | 2009-09-30 | AK | other | UNKNOWN (ANCHORAGE COUNTY) | ENSTAR NATURAL GAS CO | ON WEDNESDAY EVENING, 9/30/2009, ENSTAR WAS NOTIFIED OF A HOUSE FIRE AT 12341 AUDUBON CIRCLE, ANCHORAGE, AK. THE FIRE ORIGINATED ON A DECK NEAR THE GAS METER. HEAT FROM THE FIRE DAMAGED THE RISER AND METER CAUSING A RELEASE OF NATURAL GAS. THE LINE WAS DUG UP AND PINCHED OFF TO STOP THE FLOW OF NATURAL GAS. NATURAL GAS DID NOT CAUSE OR CONTRIBUTE TO THE FIRE. | 502010 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
854 | 2009-08-25 | MO | other | UNKNOWN (SAINT LOUIS CITY COUNTY) | LACLEDE GAS CO | GUNFIRE AT 4724 HIGHLAND AVENUE RESULTED IN A BULLET PUNCTURING A NATURAL GAS METER LOCATED INSIDE A METER CLOSET THAT WAS ACCESSIBLE EXCLUSIVELY THROUGH THE OUTSIDE OF THE BUILDING. THE BULLET PUNCTURE CAUSED NATURAL GAS TO LEAK FROM THE METER AND IGNITE, RESULTING IN A FIRE AT THE ADDRESS. | 101000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
855 | 2009-09-16 | CO | technical failure | UNKNOWN (DENVER COUNTY) | PUBLIC SERVICE CO OF COLORADO | THE CREW FUSED ON A 2" HIGH VOLUME ELECTROFUSION TEE ONTO A 2" PE MAIN. THE CREW WAS USING AN ELECTRIC DRILL TO DRIVE THE TAPPING TOOL THAT CONNECTED TO THE CUTTER. WHEN BACKING OUT THE CUTTER THE TAPPING CHAMBER ALSO WAS REVERSED THEREBY ALLOWING GAS TO BLOW TO THE ATMOSPHERE. THE GAS IGNITED BURNING TWO EMPLOYEES WHICH RESULTED IN ONE OF THE EMPLOYEES BEING HOSPITALIZED OVER NIGHT. THE INDIVIDUAL PERFORMING THE TAP WAS UNDER THE DIRECT SUPERVISION OF AN OQ QUALIFIED PERSON. THE DELAY IN REPORTING THE INCIDENT WAS DUE TO MANAGEMENTS UNDERSTANDING THAT THE INJURED EMPLOYEES WERE TREATED AND RELEASED. THIS IS ALSO THE REASON FOR NO DRUG/ALCOHOL TEST BEING PERFORMED. | 50 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
856 | 2009-10-06 | CA | other | UNKNOWN (SAN JOAQUIN COUNTY) | PACIFIC GAS & ELECTRIC CO | ON 10/6/09 AT APPROXIMATELY 1645 HOURS A VEHICLE STRUCK 1 OF 7 BARRIER POSTS AROUND A MANIFOLD METER SET BENDING THE BARRIER INTO THE MANIFOLD CAUSING GAS TO BE RELEASED. THE VEHICLE ALSO STRUCK AN APARTMENT BUILDING CAUSING SIGNIFICANT DAMAGE. THE DRIVER OF THE VEHICLE WAS ELDERLY AND MISTAKENLY STEPPED ON THE GAS PEDAL INSTEAD OF THE BRAKE CAUSING THE VEHICLE TO STRIKE THE BARRIER. THE INCIDENT RESULTED IN THE LOSS OF SERVICE FOR 25 CUSTOMERS. STOCKTON POLICE AND FIRE DEPARTMENT WERE ON SCENE AND BLOCKED OFF THE AREA. PG&E CREWS WERE ON SCENE AT 1728 HOURS AND HAD SERVICE RESTORED BY 2000 HOURS. NO MEDIA WAS PRESENT. THERE WERE NO FATALITIES OR INJURIES AS A RESULT OF THIS INCIDENT. THIS INCIDENT BECAME REPORTABLE WHEN PROPERTY DAMAGES TO THE BUILDING ARE EXPECTED TO EXCEED $50,000. | 65000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
857 | 2009-10-02 | CA | other | UNKNOWN (RIVERSIDE COUNTY) | SOUTHERN CALIFORNIA GAS CO | ON OCTOBER 2, 2009 A METER SET ASSEMBLY WAS DAMAGED WHEN A VEHICLE LOST CONTROL, LEAVING THE ROADWAY AND STRIKING INTO THE METER SET ASSEMBLY. THE ESCAPING GAS IGNITED, CAUSING A FIRE THAT DAMAGED A BUILDING. DUE TO BUILDING DAMAGE, THIS FACILITY WILL NOT BE RESTORED AT THIS TIME. THE METER LOCATION WAS NOT SUBJECT TO TRAFFIC. THIS INCIDENT BECAME REPORTABLE TO DOT BASED UPON THE ESTIMATE DOLLAR AMOUNT OF FIRE DAMAGE EXCEEDING $50,000. | 101000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
858 | 2009-10-03 | LA | leaks and spills | UNKNOWN (JEFFERSON COUNTY) | ATMOS ENERGY CORPORATION - LOUISIANA | THE 18" STEEL MAIN LINE INVOLVED IN THIS INCIDENT WAS INSTALLED AROUND 1928 AND HAD NO HISTORY OF JOINT FAILURES. THIS SECTION OF THE 18" MAIN LINE IS INVOLVED IN A REPLACEMENT PROJECT WITH 12" PE PIPE. EVENT DESCRIPTION: FAILURE OCCURED UNDERGROUND APPROXIMATELY 2 FEET FROM THE SHORING OF A TIE-IN EXCAVATION. THE 18" MAIN LINE SLIPPED OUT OF A COUPLING DUE TO "POOR CONSTRUCTION PROCEDURES" WHICH INCLUDED THE FOLLOWING: -DID NOT LOCATE THE NEXT COUPLING ON THE MAIN LINE -AT THE EXCAVATION SITE THE EXPOSED 12" PE MAIN LINE AND FITTING COMPONENTS WERE NOT PROPERLY BLOCKED AND SUPPORTED -DID NOT CONSIDER VIBRATION FROM ROAD TRAFFIC -THE EXCAVATION SITE REMAINED OPEN FOR AN EXTENDED PERIOD OF TIME CAUSING THE POTENTIAL FOR THE PIPE TO SAG AND/OR TWIST WHICH COULD RESULT IN A POSSIBLE SEPARATION BETWEEN THE PIPE AND COUPLING. NO FATALITIES OR INJURIES RESULTED FROM THE INCIDENT. THE ROAD WAS CLOSED AT THE INCIDENT SITE AND NEARBY BUILDINGS WERE EVACUATED FOR PRECAUTIONARY PURPOSES. -SOURCE OF IGNITION HAS NOT BEEN CONFIRMED. REMEDIAL ACTION: IN AN EFFORT TO REDUCE THIS TYPE OF FAILURE FROM OCCURING IN THE FUTURE THE FOLLOWING WILL BE PUT INTO PRACTICE. -SURVEY THE LINE TO FIND THE LOCATION OF THE NEXT COUPLING -MAINTAIN A MINIMUM DISTANCE OF 20FT FROM THE NEAREST COUPLING TO THE TIE-IN -SUPPORT AND BLOCK THE PIPE AND FITTINGS AT TIE-IN EXCAVATIONS -UPON ACTIVATION OF THE MAIN LINE; BACKFILL EXCAVATION SITE AT ALL TIE-INS. | 38674 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
859 | 2009-10-04 | MD | other | UNKNOWN (MONTGOMERY COUNTY) | WASHINGTON GAS LIGHT CO | WASHINGTON GAS RESPONDED TO A HOUSE FIRE AT 1226 CLAGETT DRIVE IN ROCKVILLE, MARYLAND ON SUNDAY, OCTOBER 4, 2009, AT THE REQUEST OF THE MONTGOMERY FIRE DEPARTMENT. UPON ARRIVAL, WASHINGTON GAS CONFIRMED THAT THE GAS WAS OFF AT THE INSIDE METER VALVE AND ALSO SHUT OFF GAS AT THE CURB VALVE. WASHINGTON GAS ASSISTED THE MONTGOMERY FIRE INVESTIGATORS AS NEEDED. WASHINGTON GAS CONDUCTED A 360 DEGREE UNDERGROUND MIGRATION SURVEY AROUND THE HOUSE AND OVER THE SERVICE TO THE MAIN. WASHINGTON GAS CAPPED THE ½” COPPER SERVICE OFF AT THE BRANCH TEE. A PRESSURE TEST WAS CONDUCTED AND NO LEAKSWERE FOUND. AN ODORANT SAMPLE WAS ALSO TAKEN AND THE ODORANT WAS FOUND TO BE DETECTABLE AT .17 % GAS IN AIR. THE FIRE IS STILL UNDER INVESTIGATION BUT THE NATURAL GAS RELEASE IS BELIEVED TO BE SECONDARY. | 351100 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
860 | 2009-09-30 | VA | other | UNKNOWN (FAIRFAX COUNTY) | WASHINGTON GAS LIGHT CO | WASHINGTON GAS RESPONDED TO A HOUSE FIRE AT 7651 ROYSTON STREET IN ANNANDALE ON WEDNESDAY, SEPTEMBER 30, 2009, AT THE REQUEST OF THE FAIRFAX FIRE DEPARTMENT. UPON ARRIVAL, WASHINGTON GAS SHUT THE GAS OFF AT THE CURB VALVE. WASHINGTON GAS ASSISTED THE FAIRFAX FIRE INVESTIGATORS AS NEEDED. WASHINGTON GAS CONDUCTED A 360 DEGREE UNDERGROUND MIGRATION SURVEY AROUND THE HOUSE AND OVER THE SERVICE TO THE MAIN. WASHINGTON GAS CAPPED THE ¾” WRAPPED STEEL SERVICE OFF AT THE CURB VALVE. A PRESSURE TEST WAS CONDUCTED FROM THE CAP OFF LOCATION TO THE INSIDE METER VALVE. THIS PRESSURE TEST INDICATED NO LEAKS. AN ODORANT SAMPLE WAS ALSO TAKEN AND THE ODORANT WAS FOUND TO BE DETECTABLE AT .25 % GAS IN AIR. THE FIRE IS STILL UNDER INVESTIGATION BUT THE NATURAL GAS RELEASE IS BELIEVED TO BE SECONDARY. | 301100 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
861 | 2009-10-12 | TX | other | UNKNOWN (EL PASO COUNTY) | TEXAS GAS SERVICE COMPANY | TEXAS GAS SERVICE RESPONDED TO A NATURAL GAS FIRE LOCATED AT 7646 KINGMAN DR. EL PASO, TEXAS 79915. A ONE INCH POLYETHYLENE NATURAL GAS LINE HAD BEEN MELTED AND IGNITED BY A SOLDERING TORCH USED BY A PRIVATE PLUMBING CREW THAT WAS MAKING REPAIRS TO A WATER LINE. TEXAS GAS SERVICE FOUND THIS GAS LINE EXPOSED AND LOCATED APPROXIMATELY FOUR INCHES BENEATH THE WATER LINE BEING REPAIRED BY THE PRIVATE PLUMBING CREW. THE GAS LINE WAS NOT SHIELDED FROM THE SOLDERING PROCESS OF THE WATER LINE. AS A RESULT OF THE GAS LINE NOT BEING SHIELDED, THE LINE MELTED AND IGNITED CAUSING INJURIES TO THE TWO PLUMBING WORKERS PERFORMING REPAIRS ON THE WATER LINE. | 1251 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
862 | 2009-05-03 | TX | other | UNKNOWN (DALLAS COUNTY) | ATMOS ENERGY CORPORATION - MID-TEX | DURING THE INVESTIGATION OF THIS INCIDENT, ATMOS ENERGY DETERMINED THROUGH INDEPENDENT INVESTIGATIONS THAT THE SMALL LEAK FOUND IN THE INVESTIGATION DID NOT CAUSE OR CONTRIBUTE TO THIS INCIDENT. TESTING OF THE STRUCTURE INDICATED THE PRESENCE OF GASOLINE, PROPANE AND BUTANE THAT MAY HAVE CONTRIBUTED TO THIS INCIDENT. | 175000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
863 | 2009-07-16 | IL | sabotage | UNKNOWN (COLES COUNTY) | AMERENCIPS | ON 7/15/09 COLE FARM DRAINAGE OBTAINED AN EMERGENCY JULIE TO REPAIR TILE DUE TO A SINK HOLE IN THE ROAD AND TO LOCATE THE NORTH SIDE OF RT 16. THE TICKET WAS DUE AT 10AM ON 7/16. THE DIRECTIONS SAID APPROXIMATELY 1/4 MILE WEST OF ASHMORE AND 1 MILE EAST FROM THE INTERSECTION OF RT 16 AND 2250 E. THE REQUEST ALSO STATED IT WAS MARKED WITH A RED FLAG. THE LOCATOR RESPONDED TO THE SITE ON THE EVENING OF 7/15. HE DROVE 1 MILE EAST FROM THE ABOVE MENTIONED INTERSECTION WHERE THERE WAS A FIELD ENTRANCE AND COLE'S BACKHOE. THE LOCATOR COULD NOT FIND A SINKHOLE IN THE ROAD AND KNOWING THE NEAREST GAS FACILITY WAS 600'± EAST, CLEARED THE TICKET. THERE WERE FLAGS SCATTERED THROUGHOUT THE FIELD; HOWEVER, BASED UPON THE INFORMATION FROM THE TICKET AND CONDITIONS AT THE SITE, THE LOCATOR DID NOT BELIEVE THAT THE EXCAVATION WAS TAKING PLACE NEAR THE MAIN. ON 7/16 WHILE INSTALLING NEW FIELD DRAINAGE PIPE ACROSS THE FIELD TO THE NORTH OF RT 16, COLE HIT AN UNMARKED 4" STEEL GAS MAIN AT APPROXIMATELY 12:30PM. THE SUBSEQUENT INVESTIGATION HAS DETERMINED THAT COLE WAS EXCAVATING OUTSIDE THE EXTENT OF THE JULIE LOCATE TICKET AND HAD FALSELY OBTAINED AN EMERGENCY LOCATE. THERE WAS NO SINKHOLE FOUND AND THE LOCATION POINTED OUT BY COLE AS A SINKHOLE WAS APPROXIMATELY 380 FEET EAST OF THE DAMAGE LOCATION. THE LOCATION APPEARED TO BE WHERE A SWALE FROM THE FARM FIELD INTERSECTED THE ROAD DITCH AND DID NOT APPEAR TO BE CREATING A HAZARD WITH THE ROAD. THE DAMAGE OCCURRED ABOUT 130 FEET NORTH OF THE APPARENT NORTH ROW OF RT 16 AND OVER 100 FEET FROM THE RED FLAG THAT WAS CLAIMED TO MARK THE LOCATION OF THE REPAIR. COLE CLEARLY EXCAVATED OUTSIDE THE EXTENT DESCRIBED ON LOCATE REQUEST AND DAMAGED THE GAS PIPELINE. AS STATED IN ICC JULIE ENFORCEMENT CASE 0188-09, “EXCAVATING OUTSIDE OF THE EXTENT OF A VALID LOCATE REQUEST IS CONSIDERED THE SAME AS HAVING SUBMITTED NO REQUEST AT ALL”, AND ACCORDING TO THE FINDINGS IN THE AFOREMENTIONED CASE, COLE’S FAILURE TO PROVIDE PROPER NOTICE TO JULIE BEFORE BEGINNING EXCAVATION IN A FARM FIELD ON THE NORTH SIDE OF ILLINOIS ROUTE 16, ¼ MILE WEST OF ASHMORE, ILLINOIS, AND OUT OF THE EXTENT DESCRIBED ON REQUEST #X1961030, IS A VIOLATION OF SECTION 4(D) OF THE ILLINOIS UNDERGROUND UTILITY FACILITIES DAMAGE PREVENTION ACT, 220 ILCS 50. THE ESTIMATED COST AT THE TIME OF THE DAMAGE WAS APPROXIMATELY $35,000 AND THE INCIDENT WAS REPORTED TO THE ILLINOIS COMMERCE COMMISSION. THE ACTUAL COST CALCULATED BY AMEREN CLAIMS FOR 3RD PARTY DAMAGE BILLING WAS LATER FOUND TO EXCEED $50,000. THIS UPDATED COST WAS REPORTED TO THE ILLINOIS COMMERCE COMMISSION JULIE ENFORCEMENT STAFF AND THE NRC WAS NOTIFIED OF THE REPORTABLE INCIDENT ON 09/20/09. | 76907 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
864 | 2009-10-28 | CA | other | UNKNOWN (MARIN COUNTY) | PACIFIC GAS & ELECTRIC CO | A STRUCTURE FIRE STARTED APPROXIMATELY 0100 HOURS ON 8/28/09. THE FIRE DEPARTMENT CALLED AT PG&E AT APPROXIMATELY 0245 HOURS. THE PG&E GAS SERVICE REPRESENTATIVE ARRIVED ON SCENE AT 0330 HOURS. THE GAS WAS SHUT OFF AT APPROXIMATELY 0350 HOURS AT THE SERVICE VALVE AFTER THE FIRE DEPARTMENT MADE THE AREA SAFE. ACCORDING TO THE FIRE DEPARTMENT THE SOURCE OF THE FIRE APPEARED TO BE A BBQ WITH A PROPANE TANK LOCATED APPROXIMATELY 20 FEET FROM THE METER SET. THIS INCIDENT BECAME REPORTABLE DUE TO DAMAGES TO THE STRUCTURE EXCEEDING $50,000. THE FIRE MELTED THE METER SET AND REGULATOR WHICH IN TURN RELEASED GAS WHICH CONTRIBUTED TO THE FIRE. THERE WERE NO INJURIES OR FATALITIES AND NO MAJOR MEDIA WAS PRESENT. SERVICE TO ONE CUSTOMER WILL CONTINUE TO BE SHUT OFF UNTIL THE BUILDING IS REBUILT. | 53000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
865 | 2009-11-19 | TX | sabotage | UNKNOWN (DENTON COUNTY) | COSERV GAS, LTD | CONTRACTOR WAS INSTALLING ELECTRIC SERVICE. LINE HAD BEEN EXPOSED AND DAMAGE OCCURRED WHILE CLEANING OUT BELL HOLE WITH TRACKHOE. | 4200 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
866 | 2009-09-18 | NY | other | UNKNOWN (QUEENS COUNTY) | CONSOLIDATED EDISON CO OF NEW YORK | ON FRIDAY, 9/18/09 AT 13:16, TWO CONSOLIDATED EDISON GAS OPERATIONS EMPLOYEES WERE INJURED AT 6-03 119 ST. QUEENS NY WHEN GAS IGNITED WHILE THEY WERE PREPARING TO INSTALL A CLAMP ON A CORROSION LEAK ON A 1955 - 4" LP UNCOATED STEEL GAS MAIN. BOTH EMPLOYEES RECEIVED FIRST DEGREE BURNS TO THE FACE AND ONE ALSO RECEIVED SECOND DEGREE BURNS TO HIS HANDS. THEY WERE BOTH TRANSPORTED TO JACOBI HOSPITAL BY EMS WHERE THEY WERE TREATED AND RELEASED. ON SATURDAY, 9/19/09, ONE OF THE INJURED EMPLOYEES WAS ADMITTED TO NASSAU UNIVERSITY MEDICAL CENTER WHERE HE WAS TREATED AT THE BURN UNIT, GIVEN PAIN MEDICATION AND ANTIBIOTICS, AND RELEASED ON SUNDAY 9/20/09. CONSTRUCTION CREWS EXCAVATED THREE FIRE BANKS, DROPPED STOPPERS, AND ISOLATED THE SECTION OF MAIN TO CONTROL THE FIRE AND GAS LEAK, INTERRUPTING 12 GAS SERVICES. THE INCIDENT TRIGGERED A RESPONSE BY CITY AGENCIES. NOTIFICATIONS WERE MADE TO THE PSC, DEP AND DOT. NY 1 MEDIA RESPONDED AND REPORTED THE INCIDENT. CONSTRUCTION CREWS REPLACED 12' OF THE 4" LP STEEL MAIN AND RESTORED GAS SERVICE TO THE AFFECTED CUSTOMERS. THIS WAS A SERIOUS LEVEL INCIDENT. THE INCIDENT INVESTIGATION HAS BEEN CONCLUDED. | 84830 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
867 | 2009-10-25 | NY | maintenance | UNKNOWN (WESTCHESTER COUNTY COUNTY) | CONSOLIDATED EDISON CO OF NEW YORK | ON 10/25/2009 AT 00:46 HRS, MOUNT PLEASANT FIRE DEPARTMENT REPORTED A BUILDING FIRE WITH AN ODOR OF GAS AT 376 BRADHURST AVE IN HAWTHORNE, NEW YORK. CON EDISON EMERGENCY PERSONNEL RESPONDED AND FOUND THAT AN UNOCCUPIED GAS STATION ATTENDANT'S BOOTH HAD BEEN DESTROYED BY AN EXPLOSION AND FIRE, AND THERE WAS A STRONG ODOR OF NATURAL GAS IN THE AREA. THERE WERE NO GAS READINGS OF AN EXPLOSIVE LEVEL IN OR NEAR THE STRUCTURE. THE MOUNT PLEASANT POLICE DEPT STATED AT THE SCENE THAT THERE WAS AN ARSON INVESTIGATION UNDERWAY. THE PSC AND DOT/NRC WERE NOTIFIED. ADDITIONAL CON EDISON EMERGENCY PERSONNEL RESPONDED AND INVESTIGATED, AND DETERMINED THAT THE SOURCE OF THE GAS ODOR WAS A LEAKING HP 2" COUPLING IN A GRASS AREA 42" SOUTH OF THE DAMAGED STRUCTURE. THE LEAK WAS LOCATED AND SECURED. AFTER A LENGTHY INVESTIGATION, THE LOCAL MUNICIPAL INVESTIGATORS CONCLUDED THAT THE EXPLOSION WAS THE RESULT OF A NATURAL GAS LEAK. THERE WERE NO REPORTED INJURIES AT THE SCENE. THIS WAS AN UPGRADED LEVEL INCIDENT. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
868 | 2009-11-01 | NM | other | UNKNOWN (CHAVES COUNTY) | NEW MEXICO GAS COMPANY | THERE WERE 2 VEHICLES INVOLVED IN THIS ACCIDENT. THE ACCIDENT OCCURRED NEXT TO AN APPARTMENT COMPLEX. VEHICLE A, WHICH ALSO HAD A HITCHED TRAILER, WAS PARKED CLOSE TO THE METER AND WAS LOADED WITH HOME FURNISHING. VEHICLE B HIT THE TRAILER FROM BEHIND, CLIMBED ON TOP OF THE TRAILER, ROLLED OVER A METER BARRICADE AND BENT THE METER AND THE REGULATOR RELEASED GAS. THE IMPACT CAUSED VEHICLE A TO MOVE FORWARD STRIKING A PERSON. THIS PERSON WAS TRANSPORTED TO THE HOSPITAL. DUE TO HIPPA REGULATIONS, NMGC COULD NOT VERIFY WHETHER THE PERSON WAS ADMITTED (IN-PATIENT) OR RELEASED AFTER TREATMENT. THE AREA WAS PROBED AND NO GAS WAS DETECTED ON THE COMPANY'S PIPELINE FACILITIES. | 11050 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
869 | 2009-10-22 | TX | other | UNKNOWN (HARRIS COUNTY) | ENTEX, A NORAM ENERGY COMPANY (FORM. DIV OF ARKLA | ON JANUARY 11, 2010 THIS OPERATOR WAS NOTIFIED THAT (1) OF THE INDIVIDUALS INJURED AT THE TIME OF THIS INCIDENT, DIED FROM THE INJURIES ON OR ABOUT JANUARY 9TH, 2010. | 129282 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
870 | 2009-11-04 | CA | other | UNKNOWN (SAN JOAQUIN COUNTY) | PACIFIC GAS & ELECTRIC CO | A HOUSE FIRE STARTED APPROXIMATELY 1430 HOURS ON 11/4/09. PG&E WAS NOTIFIED AT APPROXIMATELY 1440 HOURS. THE PG&E GAS SERVICE REPRESENTATIVE ARRIVED ON SCENE AT APPROXIMATELY 1510 HOURS. PG&E CREWS SHUT OFF THE GAS AT 1605 HOURS BY SQUEEZING OFF THE SERVICE LINE AT THE CURB. THE FIRE INVOLVED A LARGE PORTION OF THE HOUSE AND THEN INVOLVED THE METER SET AND REGULATOR WHICH IN TURN RELEASED GAS WHICH CONTRIBUTED TO THE FIRE. THERE WERE REPORTS OF AN EXPLOSION, BUT THE SOURCE OF THE EXPLOSION IS UNKNOWN. ACCORDING TO THE FIRE DEPARTMENT THE ORIGIN OF THE FIRE WAS NOT PG&E FACILITIES. DAMAGES EXCEEDED $50,000. THERE WERE NO INJURIES OR FATALITIES. LOCAL MEDIA WAS PRESENT. | 51000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
871 | 2009-11-23 | NJ | sabotage | UNKNOWN (WARREN COUNTY) | ELIZABETHTOWN GAS CO | EMPCO CONTRACTOR 70-A WASHINGTON AVE, DUMONT, NJ 07628 PH# 201 385-2700, WAS DIGGING FOOTERS FOR BRIDGE AND DAMAGED 4" PE MAIN WITH TRACK HOE. ETG INSTALLED 2" PE BYPASS OVER BRIDGE AND SCHEDULED WITH OUR CONTRACTOR TO REPLACE 4" PE MAIN. COMPLETED ON 11/25/09 INITIAL TOTAL COST ESTIMATE WAS BELOW $50,000, NOTIFIED DOT WHEN IT BECAME KNOW THAT COST EXCEDED $50,000. | 63069 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
872 | 2009-11-12 | MI | sabotage | UNKNOWN (MUSKEGON COUNTY COUNTY) | MICHIGAN CONSOLIDATED GAS CO (MICHCON) | <P>At, 08:29 on November 12, 2009, MichCon received a report of leaking gas on Marquette Avenue east of Harvey Street in the Township of Muskegon, Muskegon County, Michigan. MichCon personal arrived at the scene at 08:40 and determined that a sewer contractor grading for road restoration had torn a 3" service tee from an 8" steel gas distribution main operating at about 10 psig. Approximately 23 person at an elder care facility at 347 Shonat were evacuated as a precaution when indications of combustible gas entering that building were discovered.</P> <P>MichCon installed a pressure control fitting on the 8" main to the east of the damage, and located and squeezed off a section of 8" plastic main to the west of the damage to shut down the main section. Conditions were made safe at 20:24 on November 12, 2009. The remnant of the 3" service tee was removed from the top of the main, and a full-seal stainless steel band clamp was applied over the 2-3/4"-diameter hole to complete the repair at 21:23 the same evening. The residents of the elder care facility were allowed to return at 23:45. </P> <P>Supply to approximately 36 customers was curtailed due to the pressure reduction during the repair operation, and was completely restored early the morning of November 13, 2009. </P> | 69528 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
873 | 2009-11-11 | IN | other | UNKNOWN (LAKE COUNTY) | NORTHERN INDIANA PUBLIC SERVICE CO | DESCRIPTION OF ACCIDENT – ON THE ABOVE DATE AND TIME, NIPSCO WORK MANAGEMENT CENTER RECEIVED A CALL FROM THE HAMMOND FIRE DEPARTMENT INDICATING THERE WAS BLOWING GAS AT THE SUBJECT VALVE STATION AS RESULT OF VEHICULAR IMPACT. BASED ON PUBLIC REPORTS, THE DRIVER OF THE VEHICLE WAS UNDER THE INFLUENCE, LOST CONTROL, CRASHED THROUGH A SECURITY FENCE AND INTO THE VALVE STATION. THE VEHICLE CAME TO REST ON TOP OF A 4” BLOW-OFF FOR A 160 PSI SYSTEM. THE SITUATION WAS SAFELY MONITORED UNTIL THE BLOWING GAS WAS STOPPED BY 10:30 A.M. THAT MORNING, AND REPAIRS WERE COMPLETED BY 8:00 A.M. THE FOLLOWING DAY. THE SUBJECT GAS SYSTEM FED A LARGE INDUSTRIAL CUSTOMER THAT REQUIRED CLOSE COORDINATION BETWEEN THE TIMING OF NIPSCO’S REPAIRS AND THIS CUSTOMER’S NECESSITY TO TRANSITION THEIR OPERATIONS TO ANOTHER GAS SOURCE BEFORE SYSTEM PRESSURE WAS LOWERED. FOLLOWING THE REPAIRS, THE SUBJECT GAS MAIN WAS PUT BACK IN SERVICE AND RELIGHTS OF THE 16 LOST CUSTOMERS WERE COMPLETED BY 2:30 P.M. | 161506 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
874 | 2009-11-28 | CA | other | UNKNOWN (TEHAMA COUNTY) | PACIFIC GAS & ELECTRIC CO | A FIRE AT A MOBILE HOME PARK OCCURRED AT APPROXIMATELY 1145 HOURS ON 11/28/09. THE FIRE DEPARTMENT CALLED AT PG&E AT APPROXIMATELY 1220 HOURS. THE PG&E GAS SERVICE REPRESENTATIVE (GSR) ARRIVED AT 1300 HOURS. THE GSR SHUT OFF THE SERVICE VALVES AT THE METER SETS AT APPROXIMATELY 1445 HOURS. AT LEAST 5 GAS METERS WERE DAMAGED BY THE FIRE RELEASING NATURAL GAS RESULTING IN A SECONDARY IGNITION. ACCORDING TO THE FIRE DEPARTMENT THE FIRE ORIGINATED IN AN UNOCCUPIED MOBILE HOME; THE PRIMARY CAUSE OF THE FIRE HAS NOT BEEN DETERMINED. THE FIRE DAMAGED OR DESTROYED 9 MOBILE HOMES WITH DAMAGES EXCEEDING $50,000. THERE WERE NO INJURIES AND NO FATALITIES. LOCAL REDDING TV CHANNEL 7 WAS PRESENT. | 455000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
875 | 2009-11-18 | NM | other | UNKNOWN (BERNALILLO COUNTY) | NEW MEXICO GAS COMPANY | THE BUILDING AT THE SUBJECT ADDRESS CAUGHT FIRE AND THE BUILDING COLLAPSED ON THE METER CAUSING A RELEASE AND IGNITION OF GAS. THE CAUSE OF THE FIRE WAS UNKNOWN AT THE TIME OF THIS REPORT. THERE WERE NO INDICATIONS OF ANY GAS LEAKS FROM THE OPERATOR'S FACILITIES. PUBLIC/PRIVATE DAMAGES ARE ESTIMATED BECAUSE THE OWNER HAS NOT PROVIDED ANY INFORMATION REGARDING THE ACTUAL DAMAGE TO THE BUILDING. SUPPLEMENTAL: FIRE MARSHALL'S REPORT INDICATES THE FIRE WAS INTENTIONALLY SET. GAS WAS NOT THE CAUSE OF THE FIRE OR THE DAMAGE. DAMAGE TO PRIVATE PROPERTY WAS ESTIMATED AT $250,000. | 252391 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
876 | 2009-11-25 | IL | sabotage | UNKNOWN (MCDONOUGH COUNTY) | BUSHNELL MUNICIPAL GAS UTILITY | <P><FONT face="Times New Roman, Times, serif">BUSHNELL MUNICIPAL UTILITIES, BUSHNELL ILLINIOS ON NOVEMBER 25, 2009, A WATER COMPANY CONTRACTOR WAS INSTALLING A WATER LINE BY THE DIRECTIONAL DRILLING PROCESS, BUSHNELL, IL. THE CONTRACTOR HAD MADE A TIMELY REQUEST FOR UTILITY LOCATIONS AND THE LOCATIONS WERE MARKED, ALSO IN TIMELY FASHION. A 2 INCH DIAMETER, POLYETHYLENE, 50 PSI DISTRIBUTION LINE AND A 6 INCH SEWER LINE WERE LAYING PERPENDICUALAR TO THE ROUTE OF THE WATER PIPE INSTALLATION. THE GAS LINE WAS BURIED APPROXIMATELY 4 FEET BELOW GRADE. THE SEWER LINE WAS BURIED APPROXIMATELY 5 FEET BELOW GRADE. </FONT></P> <P><FONT face="Times New Roman, Times, serif" size=4>The drilling operation passed between the gasline and sewer line without incident. During an expansion and pull back operation, the drill ruptured the gas line on its underside and ruptured the sewer line on its top side, creating a path for pressurized gas to enter the sewer line. The contact occurred at approximately 2:00 p.m. on November 25, 2009.</FONT></P> <P><FONT face="Times New Roman, Times, serif" size=4>A gas odor prompted the excavator to call the gas operator, who imediately responded and began to repair the damage. A few minutes later, a nearby dwelling (about 147 feet from the dig in) exploded. No persons or animals were int he dwelliong at the time of the explosion. There was an ensuing fire that completly destroyed the dwelling. The fire caused moderate damge to one adjacent dwelling and major damage to another adjacent home.</FONT></P> <P><FONT face="Times New Roman, Times, serif" size=4>The dwelling occupant left the dwelling before the explosion as a result of smelling gas in the dwelling. The occupant was not injured.</FONT></P> <P><FONT face="Times New Roman, Times, serif" size=4>The gas distribution line was quickly repaired, but for safety reasons the gas service was cut off for an approximate four block area affecting about 70 homes. The fire was extinguished by approximatel 6:00 p.m. Service restoration began at approximately 8:30 p.m.</FONT></P> | 306000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
877 | 2009-11-24 | TX | sabotage | UNKNOWN (NUECES COUNTY) | CORPUS CHRISTI, CITY OF - GAS DIV | THE EXCAVATOR DAMAGED THE 6 INCH MAIN WHILE DRILLING A HOLE FOR THE INSTALLATION OF A UTILITY POLE. THE CAUSE OF THE INCIDENT WAS THE EXCAVATOR FAILED TO MAINTAIN CLEARANCE BY DRILLING WITH A POWER AUGER INSIDE THE TOLERANCE ZONE OF THE PIPELINE MARKINGS. THE EXCAVATOR WAS AWARE OF THE LOCATION OF THE MAIN PRIOR TO CONDUCTING THE EXCAVATION BECAUSE THE PIPELINE WAS LOCATED AND MARKED BY THE LOCATOR ON NOVEMBER 13, 2009. THE EXCAVATOR DID NOT MAINTAIN CLEARANCE AND HAND DIG WITHIN THE TOLERANCE ZONE OF 21 INCHES. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
878 | 2009-12-06 | AZ | maintenance | UNKNOWN (MARICOPA COUNTY) | SOUTHWEST GAS CORP | 2009-1570 SOUTHWEST GAS SERVICE TECHNICIAN RESPONDED TO AN ODOR COMPLAINT AT 11304 E. SONRISA AVE. AND FOUND 164.917 PSIG IN DISTRIBUTION SYSTEM WITH AN MAOP OF 60 PSIG. OVERPRESSURIZATION WAS DETERMINED TO BE CAUSED BY DEBRIS THAT DAMAGED THE DIAPHRAMS IN THE WORKER AND MONITOR REGULATORS OF DISTRICT REGULATOR STATION #425718 LOCATED AT SIGNAL BUTTE AND GUADALUPE. THE REGULATORS WERE REPAIRED AND THE OPERATING PRESSURE WAS LOWERED TO LESS THAN 60 PSIG AT 1610. THE ENTIRE AFFECTED SYSTEM HAS BEEN LEAK SURVEYED AND APPROPRIATE REPAIRS MADE. 5,667 RESIDENTIAL REGULATORS HAVE BEEN REPLACED. THERE WERE NO INJURIES OR FATALITIES AS A RESULT OF THE OVERPRESSURIZATION. | 500000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
879 | 2009-11-22 | TX | leaks and spills | UNKNOWN (DALLAS COUNTY) | ATMOS ENERGY CORPORATION - MID-TEX | IN RESPONSE TO A FIRE AT 503 MARTINDALE, A NATURAL GAS LEAK ON THE THREE INCH POLY MAIN WAS IDENTIFIED AT THE CORNER OF MARTINDALE AND STEWART. THERE WAS NO EVIDENCE OF A LEAK ON THE MAIN AT ANY TIME BEFORE THE FIRE. BARHOLING IN THE YARD AT 503 MARTINDALE DID NOT REVEAL ANY PATH OF MIGRATION FROM THE LEAK TO THE HOUSE. ATMOS EXCAVATED TO THE LEAK, INSTALLED A BAND CLAMP OVER THE 3 INCH POLY BUTT FUSION, REPLACED THE LEAKING SECTION OF PIPE AND REMOVED IT FOR STORAGE AND ANALYSIS. SUBSEQUENT BARHOLE TESTS DID NOT REVEAL ANY MIGRATION PATH OF GAS TO THE HOUSE. SCENE INSPECTION DATA DID NOT REVEAL ANY OTHER FUEL FOR THE FIRE. AS A RESULT, ATMOS REOPENED THE INVESTIGATION TO DETERMINE THE CAUSE OF THE FAILURE OF THE POLY PIPE. THE ANALYSIS OF THE PIPE REVEALED THAT THE FUSION PERFORMED AND HELD PRESSURE FOR 29 YEARS WITHOUT ANY REPORTED LEAKS. THE LABORATORY EXAMINATION OF THE PIPE INDICATED THAT THE OUTWARD APPEARANCE OF THE PIPE SATISFIED STANDARDS AND PRACTICES FOR THE SIZE OF THE BEAD AS AN INDICATOR OF THE COMPLETENESS OF THE FUSION. THE EXAMINATION OF THE SEPARATED FUSION SURFACE SHOWED ISOLATED AREAS OF INCOMPLETE FUSION. THESE ISOLATED AREAS OF INCOMPLETE FUSION CONTRIBUTED TO THE SEPARATION OF THE PIPE WHEN IT WAS EXPOSED TO AN OUTSIDE FORCE THAT EXCEEDED THE STRENGTH OF THE FUSION. THERE WAS NO EVIDENCE TO INDICATE THAT THE SEPARATION AT THE FUSION OCCURRED AT ANY TIME PRIOR TO THE DATE OF THE INCIDENT. THERE WAS NO EVIDENCE OF A LONG TERM SLOW GROWTH CRACK AT THE FUSION SURFACE. THE APPEARANCE OF THE FUSION SURFACE SUPPORTS THE CONCLUSION THAT IT SEPARATED DUE TO AN OUTSIDE FORCE THAT EXCEEDED THE STRENGTH OF THE FUSION. | 220000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
880 | 2009-12-04 | MS | sabotage | UNKNOWN (RANKIN COUNTY) | ENTEX, A NORAM ENERGY COMPANY (FORM. DIV OF ARKLA | THREE RIVERS CONTRACTORS (THIRD PARTY CONTRACTOR WORKING FOR ATT) DAMAGED OUR (CENTERPOINT ENERGY) NATURAL GAS LINE CAUSING IT TO IGNITE AND BURN A BORING RIG. THE CONTRACTOR CALLED IN THE INITIAL LOCATE AND ACCORDING TO THE STATE DAMAGE PREVENTION LAWS, THE LOCATE TICKET IS GOOD FOR 10 DAYS AND THE EXCAVATOR HAS TO RENEW THE TICKET. THE EXCAVATOR WAS WORKING WITHOUT A VALID LOCATE TICKET WHEN THEY DAMAGED OUR LINE. | 300000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
881 | 2009-12-07 | OH | other | UNKNOWN (MAHONING COUNTY) | DOMINION EAST OHIO | AT APPROXIMATELY 01:57 HOURS ON DECEMBER 7, 2009, A 16” HP DISTRIBUTION MAINLINE OPERATING AT 120# LOCATED ON MIDLOTHIAN RD, YOUNGSTOWN, OHIO RUPTURED. TWO MAINLINE VALVES WERE SHUT AT 03:35 TO ISOLATE THE SEGMENT OF PIPELINE AND MAINTAIN SERVICE TO THE YOUNGSTOWN AREA. INVESTIGATION REVEALED BOTH CIRCUMFRENTIAL AND LONGITUDINAL SEPARATION OF THE PIPE. APPROXIMATELY 49’ OF PIPE WAS REMOVED, PACKAGED AND TRANSPORTED TO A THIRD PARTY LABORATORY FOR FAILURE INVESTIGATION. THIRD PARTY LABORATORY RESULTS INDICATE THE CAUSE OF FAILURE WAS A POORLY-BONDED, LOW-FREQUENCY ERW PIPE SEAM IN CONJUNCTION WITH PREFERENTIAL CORROSION OF THE SEAM. THE LINE SEGMENT INVOLVED WAS PERMANENTLY ABANDONED FROM SERVICE. | 126000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
882 | 2009-12-09 | MS | sabotage | UNKNOWN (HOLMES COUNTY) | MISSISSIPPI RIVER GAS LLC | ELECTRIC POWER CO. HAD A BROKEN POLE THEY NEEDED TO REPLACE AND THEY ASSUMED THEY COULD DRILL A NEW HOLE BESIDE THE BROKEN POLE. WHEN THEY DRILLED, THE AUGER BIT GOUGED INTO THE PIPE. THERE WERE NO STRUCTURES WITHIN 300 FT. OF THE POINT OF DAMAGE. WE WERE GOING TO MAKE REPAIRS UNDER PRESSURE BUT DECIDED THE GAS WOULD HAVE TO BE CUT OFF TO REMOVE THE BIT. THERE WERE LIVE ELECTRIC LINES OVERHEAD ON A BROKEN POLE THAT COULD NOT BE STABILIZED. DUE TO HIGH WINDS BLOWING GAS AWAY, THIS WAS NOT CONSIDERED AN INCIDENT UNTIL THE GAS WAS CUT OFF CAUSING 500 CUSTOMERS TO LOOSE SERVICE, NO SERVICES WERE LOST UNTIL 5:00 P.M. THAT DAY. | 5600 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
883 | 2009-12-11 | CO | technical failure | UNKNOWN (ADAMS COUNTY) | PUBLIC SERVICE CO OF COLORADO | STOPPLES SET AND BYPASS INSTALLED FOR MAIN RENEWAL PROJECT. UN-RESTRAINED 20" MECHANICAL COUPLING SEPARATED DUE TO TENSILE FORCE FROM INTERNAL PRESSURE. BLOWING GAS AND PIPE MOVEMENT CONTRIBUTED TO INJURY. THE GAP REFERENCED IN F6 NUIMBER 23 WAS WORK PERFORMED BY AN ENGINEERING EMPLOYEE. THE PROCEDURE IN QUESTION WAS NOT AN OQ COVERED TASK OR FUNCTION. | 200000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
884 | 2009-11-20 | TX | leaks and spills | UNKNOWN (DALLAS COUNTY) | ATMOS ENERGY CORPORATION - MID-TEX | AFTER FURTHER INVESTIGATION (FLOW RATE TEST) A LEAK WAS FOUND ON THE THREADS OF THE FITTING TO THE SERVICE LINE FEEDING 2502 CATALINA DR. | 145000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
885 | 2009-12-18 | NJ | other | UNKNOWN (UNION COUNTY) | ELIZABETHTOWN GAS CO | A CREWPERSON WAS EXCAVATING BY HAND TO REPAIR A CLASS TWO JOINT LEAK ON A 6” DIAMETER CAST IRON MAIN. THE CREWPERSON WAS USING A PROBE BAR WITH INSULATED SLIDING HANDLE ON TOP. THE BAR CAME IN CONTACT WITH AN UNDERGROUND ELECTRICAL DUCT WHICH HAD NOT BEEN PROPERLY MARKED. THE PROBE BAR PIERCED THE OUTER CASING OF AN ELECTRICAL CONDUIT CAUSING AN ARC AND SHORT CIRCUIT. TWO ELECTRICAL MANHOLES ABOUT 30 AND 100 FEET IN EACH DIRECTION ERUPTED. GAS INVOLVEMENT CANNOT BE RULED OUT. DAMAGE TO ELECTRICAL CABLES AND EQUIPMENT IS ESTIMATED TO BE GREATER THAN $50,000. | 54525 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
886 | 2009-12-09 | TN | other | UNKNOWN (KNOX COUNTY) | KNOXVILLE UTILITIES BOARD |  | 55000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
887 | 2009-12-12 | CA | leaks and spills | UNKNOWN (LOS ANGELES COUNTY) | SOUTHERN CALIFORNIA GAS CO | ON DECEMBER 12, 2009 AN EXPLOSION OCCURRED IN AN ELECTRICAL ROOM AT AN APARTMENT COMPLEX IN CANOGA PARK, CA. THE EXPLOSION DAMAGED THE ELECTRICAL ROOM AND ADJACENT APARTMENT UNITS. NO INJURIES OCCURRED AS A RESULT OF THIS INCIDENT. INITIAL FIELD RESPONSE FOUND NO UNDERGROUND LEAKAGE AT THE TIME OF THE INCIDENT. SUBSEQUENT LEAKAGE SURVEYS WERE PERFORMED, AND ON DECEMBER 14TH LEAK INDICATIONS WERE DISCOVERED. ANALYSIS OF GAS DETERMINED IT TO BE NATURAL GAS. GAS SERVICE WAS CUT AND TESTED, AND DETERMINED TO BE LEAKING AT A TORN OR CRACKED 2” PE ELL FITTING. THE SERVICE WAS REPLACED AND FACILITIES RESTORED. THIS LEAK IS ATTRIBUTED TO A COMBINATION OF FACTORS. THE PRIMARY FACTORS ARE THE LOW STRESS CRACK RESISTANCE OF THE MATERIAL DEMONSTRATED IN THIS PARTICULAR ELBOW ALONG WITH THE BENDING STRAIN TO WHICH THE FITTING WAS SUBJECTED. THE BENDING STRAIN COULD HAVE BEEN INTRODUCED AT THE TIME OF INSTALLATION, OR POST-INSTALLATION DUE TO A NUMBER OF FACTORS SUCH AS OTHER CONSTRUCTION ACTIVITIES. THIS INCIDENT BECAME REPORTABLE TO PHMSA ON DECEMBER 14, 2009 WHEN SOUTHERN CALIFORNIA GAS COMPANY FACILITIES WERE DETERMINED TO BE INVOLVED AND TOTAL PROPERTY DAMAGE WAS DETERMINED TO EXCEED $50,000. | 202000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
888 | 2009-12-11 | VA | sabotage | UNKNOWN (nan COUNTY) | VIRGINIA NATURAL GAS | INFRASOURCE CONSTRUCTION COMPANY WAS INSTALLING AN 8" PLASTIC GAS PIPELINE BY HYDRAULIC DIRECTIONAL DRILL UNDER THE EXISTING 8" STEEL PIPELINE AS A RELOCATION PROJECT. THE UNDERSIDE OF THE EXISTING STEEL PIPELINE WAS DAMAGED DURING THE BACK REAMING OPERATION. THE DAMAGE OCCURRED IN AN ISOLATED AREA OFF THE ROAD AND AWAY FROM ANY BUILDING STRUCTURES. NOTE THAT THE SOIL AT THE DAMAGE SITE WAS SUPER SATURATED FROM THE ABNORMALLY HIGH RAINFALL EXPERIENCED IN THE REGION. AS A RESULT, TRENCH STABILITY, DEWATERING AND SHORING OPERATIONS WERE EXTREMELY CHALLENGING. | 91689 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
889 | 2009-12-20 | LA | natural disasters | UNKNOWN (TERREBONNE PARISH COUNTY) | TERREBONNE PARISH CONSOLIDATED GOVERNMENT | ON DECEMBER 20, 2009, THE TPCG UTILITIES DEPARTMENT GAS DIVISION RESPONDED TO ASSIST THE HOUMA FIRE DEPARTMENT RESPONDING TO A FIRE AND/OR EXPLOSION AT 300 RAILROAD AVE. (LAT 90°43'34.73"W, LONG 29°35'38.34"N). DIVISION PERSONNEL WERE ASKED TO ISOLATE SUPPLY TO THE STRUCTURE. A 2" POLYETHYLENE (PE) MAIN AND A 2" CAST IRON MAIN WERE IN SERVICE IN THE IMMEDIATE VICINITY; BOTH WERE ISOLATED. THE AREA WAS LEAK SURVEYED BY FI; NO GAS WAS DETECTED. THE ODORANT LEVEL WAS TESTED AND FOUND TO BE DETECTABLE. THE FOLLOWING DAY, THE 2" CAST IRON MAIN WAS REACTIVATED AND RESURVEYED BY FI. A LEAK WAS DETECTED AND THE LINE EXPOSED. UPON INSPECTION, THE CAST IRON MAIN WAS FOUND TO BE RESTING ON THE GRAVITY SEWER SERVICE LINE TO THE STRUCTURE AND TO HAVE A CIRCUMFERENTIAL CRACK APPROXIMATELY 8 INCHES FROM THEIR INTERSECTION. AS OF THIS TIME, IT HAS NOT BEEN DETERMINED IF THE INCIDENT WAS CAUSED BY THE CAST IRON MAIN CRACK OR THE CRACK RESULTED FROM THE EXPLOSION. EXISTING CAST IRON GAS LINE WAS DISCOVERED TO BE RESTING ON TOP OF SEWER SERVICE LINE WITH CIRCUMFERENTIAL HAIRLINE CRACK. IT COULD NOT BE DETERMINED THE CONTIBUTING FACTOR OR FACTORS THAT MAY HAVE CAUSED THE GAS LINE TO CRACK. FURTHER INVESTIGATIONS SHOWED THAT THERE WAS NO INIDICATION OF A LEAK FROM THE MAIN PRIOR TO EIGHTY-FOUR MINUTES BEFORE THE EXPLOSION. THE OCCUPANT OF THE HOUSE SMELLED THE ODOR OF GAS EIGHTY-FOUR MINUTES BEFORE THE EXPLOSION BUT FAILED TO NOTIFY EITHER THE GAS DEPARTMENT, TERREBONNE PARISH OR THE FIRE DEPARTMENT. THE WARNING AGENT OF THE ORDORANT WORKED BUT THE OCCUPANT FAILED TO HEED THE WARNING OR NOTIFY TERREBOONE PARISH. THE GAS MAIN IN QUESTION HAD NOT LEAKED IN THE PREVIOUS TEN YEARS BUT WAS NEVERTHELESS SCHEDULED FOR REPLACEMENT. EXCAVATION OF THE CAST IRON PIPE AFTER THE INCIDENT DID NOT REVEAL ANY EVIDENCE OF EXTERNAL CORROSION. | 80010 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
890 | 2009-12-19 | NE | natural disasters | UNKNOWN (nan COUNTY) | BLACK HILLS ENERGY | DAMAGE TO PIPING AND METER SET WAS CAUSED BY LARGE AMOUNT OF SNOW WHICH HAD ACCUMULATED ON ROOF FALLING OFF AT ONE TIME CAUSING STRESS ON THE PIPING SYSTEM AND CAUSING IT TO FAIL. | 150000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
891 | 2009-12-20 | AR | natural disasters | UNKNOWN (PULASKI COUNTY) | RELIANT ENERGY ARKLA, DIV OF RELIANT ENERGY RESOURC | CUSTOMER PHONED LITTLE ROCK FIRE DEPARTMENT TO REPORT AN ODOR OF GAS INSIDE 3501 LONGCOY AT 3:00 A.M. ON 12/20/2009. RESPONDING FIRE DEPT. PERSONNEL EVACUATED THE RESIDENCE, AND CALLED CNP AT 3:15 TO REPORT ODOR OF GAS OUTSIDE. SERVICE TECH ARRIVED AT 4:00 A.M. BAR TESTING INDICATED NO GAS AT FOUNDATION OF HOME, AND HIGH READINGS IN A NARROW CIRCUMFERENCE IN DITCH NEAR STREET. SERVICE TECH ADVISED CUSTOMERS TO REMAIN OUT OF THE HOUSE. CONSTRUCTION CREW HAD BEEN CALLED, AND WAS NEAR THE SITE WHEN EXPLOSION OCCURRED AT 5:56 A.M. THERE WERE NO INJURIES. FIRE CONSUMED ENTIRE STRUCTURE AT 3501 LONGCOY, AND ALSO CAUSED DAMAGE TO 3503 LONGCOY. TWO INCH CAST IRON WAS FOUND TO BE LEAKING FROM A 'COLD BREAK'. POSITION OF THE LEAK WAS UNDER A CULVERT THAT WAS ALLOWING GAS TO MIGRATE UNDER THE DRIVEWAY AND INTO THE STRUCTURE. GAS FLOW IN MAIN WAS STOPPED OFF IN BOTH DIRECTIONS BY 9:45 A.M. | 140956 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
892 | 2009-12-26 | PA | other | UNKNOWN (MONTGOMERY COUNTY) | PECO ENERGY CO | INITIAL CALL FROM MONTGOMERY COUNTY 911 WAS IDENTIFIED AS A HOUSE FIRE CALL. ONCE ON SITE, A LEAK WAS FOUND BY PECO. SOURCE WAS FOUND TO BE A CAST IRON MAIN BREAK UNDER THE ROADWAY ADJACENT TO PROPERTY. GAS WAS IGNITED AND RESULTED IN A LOW LEVEL EXPLOSION IN BASEMENT OF THE HOUSE. NO ONE WAS AT THE PROPERTY AT THE TIME OF THE EVENT. PECO WILL BE PERFORMING A METALLURGICAL TEST ON THE PIPE AND WILL PROVIDE A SUPPLEMENTAL REPORT AFTER THE TEST RESULTS ARE RECEIVED. UPDATE NOVEMBER 22, 2010: BASED ON THE INSPECTION AND TESTING OF THE PIPE FROM SUMMIT STREET, THE CAST IRON MAIN LEAK WAS DUE TO LOCALIZED CORROSION ON THE EXTERIOR OF THE PIPE. | 258120 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
893 | 2009-12-22 | CT | natural disasters | UNKNOWN (FAIRFIELD COUNTY) | YANKEE GAS SERVICES CO | THE STATEMENTS AND CONCLUSIONS WITHIN THIS REPORT ARE BASED ON PRELIMINARY FINDINGS. THE INVESTIGATION INTO THIS INCIDENT IS ONGOING, AND YANKEE GAS SERVICES COMPANY (THE "COMPANY") RESERVES THE RIGHT TO AMEND THIS REPORT. A SUPPLEMENTAL REPORT WILL BE FILED IF APPROPRIATE. ON DECEMBER 22, 2009 AT 9:42 PM THE NORWALK, CONNECTICUT, FIRE DEPARTMENT CONTACTED THE COMPANY TO INFORM THE COMPANY OF A FIRE AT 65 OHIO AVENUE, NORWALK, CONNECTICUT. COMPANY PERSONNEL RESPONDED, ARRIVING ONSITE AT 10:05 PM (THE MECHANIC DID NOT ACKNOWLEDGE HIS ARRIVAL UNTIL SEVERAL MINUTES LATER). A SINGLE FAMILY RESIDENCE WAS ON FIRE. THERE WERE THREE RESIDENTS OF THE HOME, AN ADULT MALE, AN ADULT FEMALE AND AN INFANT. THE ADULT MALE WAS ADMITTED TO THE HOSPITAL WITH INJURIES. COMPANY PERSONNEL BEGAN EXCAVATING TO EXPOSE THE 1" POLYETHYLENE GAS SERVICE SERVICING THE RESIDENCE. THE SERVICE WAS EXPOSED, CUT AND CAPPED. COMPANY PERSONNEL THEN BEGAN EXCAVATING FROM THE FIRST EXCAVATION TO EXPOSE THE GAS MAIN. AS THEY EXCAVATED TOWARD THE MAIN THEY NOTICED WATER ENTERING THE EXCAVATION. THE SOURCE OF THE WATER WAS DETERMINED TO BE A WATER MAIN LEAK LOCATED APPROXIMATELY TWO FEET BELOW AND TWO FEET LATERALLY FROM THE 4" CAST GAS IRON MAIN. THE VOLUME OF WATER PREVENTED COMPANY PERSONNEL FROM EXCAVATING TO EXPOSE THE GAS MAIN. COMPANY PERSONNEL MOVED TO AN UPSTREAM LOCATION SERVING THE GAS DISTRIBUTION SYSTEM AND EXCAVATED AND STOPPED THE FLOW OF GAS IN THE DISTRIBUTION MAIN. THIS INTERRUPTED GAS SERVICE TO TWENTY-FOUR GAS CUSTOMERS. THE WATER COMPANY SHUT OFF THE WATER MAIN SERVING THE AREA WHICH ALLOWED COMPANY PERSONNEL TO EXCAVATE IN FRONT OF THE RESIDENCE. THE DISTRIBUTION MAIN IN FRONT OF THE RESIDENCE WAS EXPOSED UNCOVERING A CRACKED 4" CAST IRON MAIN. A FOUR FOOT SECTION OF THE CAST IRON MAIN INCLUDING THE CRACK WAS REMOVED AND REPLACED WITH POLYETHYLENE PIPE. * PART A.6. THIS IS THE ELAPSED TIME FROM WHEN THE INCIDENT WAS REPORTED TO WHEN THE GAS MAIN WAS SHUT-OFF. | 200100 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
894 | 2009-12-11 | AZ | maintenance | UNKNOWN (MARICOPA COUNTY) | SOUTHWEST GAS CORP | 2009-1718 SOUTHWEST CONSTRUCTION CREW RESPONDED TO A REPORTED LINE BREAK AT 8921 N ARROYO GRANDE AND FOUND GAS BLOWING AT THE SERVICE WITH NO EXCAVATION. THE CREW EXPOSED A 2" X 1" SERVICE SADDLE WITH THE 1" SERVICE PULLED FROM THE SERVICE SADDLE DUE TO AN OVERPRESSURIZATION OF 146.5 PSIG IN A DISTRIBUTION SYSTEM WITH AN MAOP OF 40 PSIG. OVERPRESSURIZATION WAS DETERMINED TO BE CAUSED BY DEBRIS THAT DAMAGED THE DIAPHRAGMS IN THE WORKER AND MONITOR REGULATORS OF DISTRICT REGULATOR STATION #424360 LOCATED AT 32ND STREET AND SHEA BLVD. THE REGULATORS WERE REPAIRED AND THE OPERATING PRESSURE WAS RESTORED TO NORMAL 40 PSIG AT 17:05. THERE WERE NO INJURIES OR FATALITIES AS A RESULT OF THE OVERPRESSURIZATION. SUPPLEMENTAL: THE ENTIRE AFFECTED SYSTEM HAS BEEN LEAK SURVEYED AND APPROPRIATE REPAIRS MADE. 164 UNDERGROUND LEAKS WERE DISCOVERED AND REPAIRED. 702 RESIDENTIAL REGULATORS HAVE BEEN REPLACED. THE CREW EXPOSED A 2" X 1" SERVICE SADDLE WITH THE 1" SERVICE SEPERATED FROM THE SERVICE SADDLE DUE TO AN OVERPRESSURIZATION OF 146.5 PSIG IN A DISTRIBUTION SYSTEM WITH AN MAOP OF 40 PSIG | 934647 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
895 | 2009-12-04 | IL | other | UNKNOWN (COOK COUNTY) | NORTHERN ILLINOIS GAS CO | REGULATOR SET SCREW CAP WAS REMOVED BY UNKNOWN AND UNAUTHORIZED ENTITY. RAIN WATER ENTERED THE TOP OF THE REGULATOR DIAPHRAGM CASE AND FROZE, RESULTING IN PRESSURE PROBLEMS AT THE FURNACE WHICH RESULTED IN A FIRE IN THE STRUCTURE. | 550600 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
896 | 2009-03-29 | AL | other | UNKNOWN (DEKALB COUNTY) | DEKALB - CHEROKEE COUNTIES GAS DISTRICT |  | 170850 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files