## gtgg1986to2001
| Date | State | Cause of Loss | Name of Installation | Name of Owner | Text | Loss Estimated ($) | Link
0 | 1986-01-27 | WY | other | UNKNOWN (CAMPBELL COUNTY) | PHILLIPS 66 NATURAL GAS CO | PIPELINE PRESSURE WAS BEING REDUCED BY VENTING TO THE ATMOSPHERE. SOME UNKNOWN SOURCE IGNITED THE GAS. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1 | 1986-01-17 | IL | other | UNKNOWN (MORGAN COUNTY) | PANHANDLE EASTERN PIPELINE CO | THE OPERATION OF A BACKHOE IN THE VICINITY OF A 2" BRANCH CONNECTION INTRODUCEDSTRESSES IN THE PIPING WHICH CAUSED IT TO BREAK AT THE TAP CONNECTION TO A 16" PIPELINE | 60000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
2 | 1986-01-15 | LA | other | UNKNOWN (OFFSHORE COUNTY) | COLUMBIA GULF TRANSMISSION CO |  | 120000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
3 | 1986-02-10 | AL | maintenance | UNKNOWN (BALDWIN COUNTY) | FLORIDA GAS TRANSMISSION CO | CRACK ON TOP OF GIRTH WELD WAS LEAKING. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
4 | 1986-02-21 | TX | other | UNKNOWN (HARRIS COUNTY) | TRANSWESTERN PIPELINE CO | A BROKEN BOLT IN THE COMPRESSOR CAUSED VIBRATION WHICH CAUSED A 4.5" NIPPLE FROM A SUCTION BOTTLE TO BREAK AROUND A CIRCUMFERENTIAL FILLET WELD. | 117000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
5 | 1986-02-21 | KY | other | UNKNOWN (GARRARD COUNTY) | TEXAS EASTERN GAS PIPELINE CO | THE PIPELINE RUPTURED NEAR THE SOUTH END OF A ROAD CROSSING AT KENTUCKY STATE HIGHWAY #52. THE CAUSE OF THE INCIDENT IS CURRENTLY UNDER INVESTIGATION. | 1300000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
6 | 1986-02-14 | KS | other | UNKNOWN (WALLACE COUNTY) | KN ENERGY INC (KANSAS NEBRASKA NATURAL GAS CO INC) | LEAK REPORT COVERS A NATURAL GAS LEAK THAT OCCURED ON K N ENERGY, INC.'S (K N) 3-INCH TRANSMISSION PIPELINE IN WALLACE COUNTY, KANSAS ON FEBRUARY 14, 1986. IGNITION DID NOT OCCUR. HOWEVER, THE LEAK DID DISRUPT SERVICE TO CITY OF SHARON SPRINGS, KS, FOR APPROXIMATELY TEN HOURS. THE CITY HAS APPROXIMATELY 550 GAS METERS.THE LEAK WAS CAUSED BY AN OUTSIDE PARTY UTILIZING A BACKHOE TO INSTALL A PIPELINE FOR ANOTHER COMPANY UNDER K N'S 3-INCH PIPELINE. IN ADVANCE OF SUCH EXCAVATION, K N WAS NOTIFIED OF THE PLANNED EXCAVATION AND IT EXPOSED THE 3-INCH PIPELINE THAT WAS SUBSEQUENTLY DAMAGED. K N REQUESTED THAT ITS PERSONNEL BE PRESENT WHEN THE UNDERCROSSING WAS TO BE MADE. UNFORTUNATELY, K N RECEIVED NO CALL SO ITSPERSONNEL WAS NOT PRESENT WHEN THE PIPLINE WAS HIT. NO INJURIES OR SIGNIFICANT PROPERTY DAMAGE OCCURRED.THE DAMAGE PORTION OF PIPELINE IS IN A CLASS I LOCATION, MARKED WITHPERMANENT MARKERS. ONE IS A PIPELINE MARKER LOCATED 2,707 SOUTHOF THE INCIDENT WHICH IS CLEARLY VISIBLE FROM THE POINT OF IMPACT. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
7 | 1986-02-13 | WV | other | UNKNOWN (LEWIS COUNTY) | CONSOLIDATED GAS TRANSMISSION CORP | STATION EMPLOYEE OPENED 1" BALL VALVE ON BYPASS WHICH ALLOWED GAS AT 835 PSIG TO ENTER EMCO METER (RATED AT 100 PSIG) RESULTING IN METER CASE RUPTURING. | 600 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
8 | 1986-02-19 | NV | other | UNKNOWN ( COUNTY) | SOUTHWEST GAS CORP | FLOODING OF THE TRUCKEE RIVER NEAR WADSWORTH, NV CAUSED THE 12" STEEL HIGH PRESSURE CARSON LATERAL TO BE WASHED OUT WHERE IT CROSSES THE TRUCKE RIVER.SEE ATTACHED LETTER.INTENSE RAIN STORMS BEG. ON THE 13TH OF FEB. CAUSED FLOODINGOF THE TRUCKEE RIVER. THIS FLOODING SUBSEQUENTLY CAUSED THE WASHOUTOF SOUTHWEST'S 12-INCH HIGH-PRESSURE LINE SERVICING THE COMMUNITIES OFWADSWORTH, FERNLEY, FALLON, YERINGTON, CARSON CITY, MINDEN, GARDNERVILLE, SOUTHAND NORTH LAKE TAHOE, NEVEDA, AND SOUTH AND NORTH LAKE TAHOE CA. THE WASHOUTOCCURRED AT 1515 HOURS ON WED., FEB. 19, 1986. P-2 & P-3 CURTAILMENT WASINITIATED, BUT EVENTUALLY ALL SERV. TO THE NEV. COMMUNITIES WAS LOST,EXCEPT FOR LAKE TAHOE AND FALLON AREAS ON FEB. 19, 1986.RELIGHTS STARTED IN SOUTHWEST'S AREAS AS SOON AS POSSIBLE AFTER THEDISTRIBUTION SYSTEMS WERE PURGED. SNOW MADE RELIGHTS VERY DIFFICULT.RELIGHTS STARTED FEB 24 & COMPLETED MARCH 3RD. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
9 | 1986-02-24 | AR | maintenance | UNKNOWN (NEVADA COUNTY) | ARKANSAS LOUISIANA GAS CO (ARKLA GAS CO) | LINE "S", 20" O.D. PIPELINE BLEW OUT AT 75' SECTION IN THE BODY OF THE PIPE. | 147354 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
10 | 1986-02-23 | CA | other | UNKNOWN (TEHAMA COUNTY) | PACIFIC GAS & ELECTRIC CO | TRANSMISSION MAIN RUPTURED DUE TO STRESS CAUSED BY EXCESSIVE WATER FLOW IN SACRAMENTO RIVER DURING FLOODING. | 1350000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
11 | 1986-03-06 | CA | other | UNKNOWN (PLACER COUNTY) | PACIFIC GAS & ELECTRIC CO | PREVIOUS DAMAGE TO PIPELINE BY CONTRACTOR WAS DISCOVERED BY PG AND E PERSONNEL AND LEAKAGE REPAIRED. CONTRACTOR, WHILE GRADING PROPERTY, STRUCK STEEL PIPELINEWITH A CATERPILLAR TRACTOR ALLOWING GAS TO ESCAPE TO ATMOSPHERE. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
12 | 1986-03-17 | TX | maintenance | UNKNOWN (GALVESTON COUNTY) | CHEVRON PIPELINE CO | EQUIPMENT FAILURE INSIDE A GAS FIRED - WATER FILLED ETHYLENE HEATER. THIS HEATER HAS ETHYLENE PASSING THRU A TUBE COIL ETHYLENE HEATER. ITS TEMPERATURE FOR BETTER MEASUREMENT. IT APPEARS THAT THERE WAS A TUBE FAILURE. UNTIL DOW PIPE LINE COMPLETES THE ANALYSIS OF THEIR EQUIPMENT NO DEFINITE CONCLUSION CAN BE MADE. | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
13 | 1986-03-26 | KY | other | UNKNOWN (KNOX COUNTY) | DELTA NATURAL GAS CO INC | AN EQUIPMENT OPERATOR MINING COAL AT 9:30P.M. GOUGED A HOLE IN THE 6" STEEL PIPELINE. THE AFFECTED SECTION OF THE LINE WAS TAKEN OUT OF SERVICE UNTIL THE NECESSARY REPAIRS WERE MADE. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
14 | 1986-03-09 | CA | other | UNKNOWN (COLUSA COUNTY) | PACIFIC GAS & ELECTRIC CO | IT IS SPECULATED THAT HEAVY WATER RUN-OFF CREATED UNDUE FFORCE ON THE 10" PIPELINE RESULTING IN THE LINE BREAK. | 88000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
15 | 1986-03-02 | TX | other | UNKNOWN (WALLER COUNTY) | TENNESSEE GAS PIPELINE CO |  | 244662 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
16 | 1986-04-03 | NJ | other | UNKNOWN (SALEM COUNTY) | SUNOLIN CHEMICAL CO | DUPONT ADVISED SUN OLIN THAT SOME ELECTRICAL WORK WAS GOING TO BE DONE AT THE UNION CARBIDE CONSTRUCTION SITE IN NEW JERSEY NEAR THE METERING STATION. SUN OLINNOTITIED SUN PIPELINE TO SUPPLY SOMEONE FOR THE JOB. SUN PIPELINE REPRESENTATIVE, JIMMY JACKSON CAME ON SITE TO ADVISE UNION CARBIDE'S ELECTRICAL CONTRACTOR.AT APPROXIMATELY 12 NOON ON THURSDAY, APRIL 3, THE AUGUR DIGGING THE HOLE PUNCTURED A PIPELINE. SUN OLIN WAS NOTIFIED AT 12:05 P.M. SHOWED GREATER THAN 500 PPM CARBON MONOXIDE IN THE AIR, THEREBY CONFIRMING THAT IT WAS THE CARBON MONOXIDEPIPELINE THAT WAS DAMAGED. DUPONT SHUT DOWN THEIR CARBON MONXIDE USER AT THE RIVER WAS CLOSED AT 12:30 P.M. DAVE SCHMIDT OF DUPONT ESTIMATED THE IMMEDIATE AREA WAS SAFE (LESS THAN 50 PPM CARBON MONOXIDE WITHIN A 20 FOOT RADIUS FROM THE LOCATION OF THE HOLE IN THE PIPELINE) AT 1:00 P.M. THE PIPELINE WAS CONSIDERED ESSENTIALLY DEPRESSURED AT 1:30 P.M. AT 3:00 P.M., DUPONT PUT NITROGEN FROM THENITROGEN PRODUCT LINE INTO THE CARBON MONOXIDE PIPELINE WITH 1/2 INCH TUBING. AT 4:12 P.M., SUN OLIN STARTED DEPRESSURING THE CARBON MONOXIDE PRODUCT PIPELINEFROM THE NEW JERSEY RIVER VALVE MANIFOLD TO THE SUN OLIN FLARE. AT 4:15 P.M., SUN OLIN STARTED DEPRESSURING THE CARBON MONOXIDE PRODUCT PIPELINE FROM THENEW JERSEY RIVER VALVE MANIFOLD TO THE SUN OLINE FLARE. AT 4:15 PM, ITWAS DECIDED TO HAND DIG OUT THE AUGUR EQUIPMENT. AT A DEPTH OF ABOUT 4 FEET,THEY COULD SEE THE AUGUR HAD PUNCTURED A TRIANGULAR HOLE WITH A BASE OF ABOUT1 INCH AND ABOUT 1/2 INCH HIGH IN THE SIDE OF THE CARBON MONOXIDE PIPELINE.THE PIPELINE WAS CLAMPED BETWEEN 6-7 PM. AND SHORTLY THEREAFTER, THE NEWJERSEY RIVER VALVE WAS OPENED, THE ENTIRE PIPELINE STARTED TO PURGE BACK TOSUN OLIN WHICH THEN DISPLACED THE REMAINING CARBON MONOXIDE IN THE LINE WITHNITROGEN. AT ABOUT 10:30 PM, IT WAS DECIDED TO PURGE THE PIPELINE THROUGHOUTTHURSDAY AND FRIDAY NIGHT, THEN MAKE ANOTHER GAS ANALYSIS EARLY SATURDAYMORNING. ON SATURDAY MORNING, APRIL 5, THE LINE WAS SAFE AND THE DAMAGEDSECTION OF THE PIPE WAS CUT OUT AND REPLACED WITH A NEW 21-1/2 INCH SECTION OFPIPE. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
17 | 1986-01-23 | LA | other | UNKNOWN (ST JOHN THE BAPTIST COUNTY) | ST JOHN THE BAPTIST PARISH UTILITIES | THE CONTRACTOR WAS IN THE PROCESS OF CONDEMNING AN EXISTING GAS LINE WHEN LEAKING GAS IGNITED. | 15000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
18 | 1986-03-24 | LA | other | UNKNOWN (TERREBONNE COUNTY) | UNITED GAS PIPELINE CO | A CARGO VESSEL (THE GREEN CANYON EXPRESS) TRAVELING IN DENSE FOG, COMPLETELY OUTOF THE CHANNEL, IN THE HOUMA NAVIGATION CANAL, STRUCK THE CANAL CROSSING RISER, SEVERING THE LINE AND IGNITING THE GAS. THE GAS SUPPLY WAS CUT OFF WITHIN MINUTES BY SUPERIOR OIL PERSONNEL NEARBY. | 260000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
19 | 1986-04-01 | LA | other | UNKNOWN (AVOYELLES COUNTY) | UNITED GAS PIPELINE CO | OIL HOLES ON COMPRESSOR BEARING APPARENTLY WERE CLOGGED CAUSING THE BEARING ANDSHAFT TO OVERHEAT AND IGNITE THE OIL AND GAS. | 92906 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
20 | 1986-02-18 | AL | leaks and spills | UNKNOWN (WASHINGTON COUNTY) | COLLET VENTURES INC- COPELAND PLANT | ORIGINAL TESTING SHOWED POSSIBLE MATERIAL DEFECT BUT AFTER EXTENXIVE TESTING ITWAS PROVEN TO BE SULFIDE STRESS DUE TO LACK OF CONSTANT FLOW THROUGH LINE. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
21 | 1986-05-07 | WV | leaks and spills | UNKNOWN (LOGAN COUNTY) | UNION CARBIDE CORP | THE INCIDENT OCCURED IN A 10" NATURAL GAS PIPELINE APPROXIMATELY 40 FEET FROM THE FENCE LINE OF A COMPRESSOR STATION WHICH PUMPS NATURAL GAS. GENERAL EXTERNAL GALVANIC CORROSION ACCELERATED BY THE COMPRESSOR OUTLET TEMPERATURE (90 DEGREES F) IS BELIEVED TO BE THE PRIMARY CAUSE. OTHER POTENTIALLY CONTRIBUTING FACTORS ARE THE LOCAL SOIL CONDITIONS AND POSSIBLY VIBRATIONS FROM THE COMPRESSOR. | 15800 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
22 | 1986-05-03 | MT | leaks and spills | UNKNOWN (POWELL COUNTY) | MONTANA POWER CO | THE RUPTURE ORIGINATED IN A LOCALIZED CORROSION AREA APPROXIMATELY ONE (1) FOOTIN DIAMETER. RUPTURE PROPAGATED TO THE THREE (3) FOOT LENGTH MENTIONED ABOVE. | 160000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
23 | 1986-04-08 | MT | other | UNKNOWN (PARK COUNTY) | MONTANA POWER CO | A SELF POWERED SCRAPPER PUSHED BY A D-7 TRACTOR TORE A VERY LARGE HOLE IN THE PIPE RESULTING IN A RAPID LOSS OF GAS TO THE ATMOSPHERE. | 30300 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
24 | 1986-04-21 | CO | other | UNKNOWN (MESA COUNTY) | ROCKY MOUNTAIN NATURAL GAS CO INC | CHANGING ORIFACE IN A "DANIELS ORIFACE FITTIN" GAS ESCAPED AND SOME IGNITION, POSSIBLE SPARK FROM STATIC ELECTRICITY FROM STEEL TOOLS OR CLOTHING UNABLE TO DETERMINE EXACTLY. VERY LITTLE EXPLOSION - FLASH BURN UNDER PRESSURE PROBLEM. | 6000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
25 | 1986-04-11 | KS | leaks and spills | UNKNOWN (STAFFORD COUNTY) | NORTHERN NATURAL GAS CO |  | 150000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
26 | 1986-04-24 | KS | other | UNKNOWN (PHILLIPS COUNTY) | KN ENERGY INC (KANSAS NEBRASKA NATURAL GAS CO INC) | 2 3/8" BURIED LINE WAS DAMAGED BY J B FIELD, HIRED MAN FOR NELSON FARMS, LONG ISLAND, KANSAS, WHILE CHISELING GROUND. NO PRIOR NOTIFICATION TO K N THAT WORK WAS GOING TO BE DONE. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
27 | 1986-04-17 | LA | maintenance | UNKNOWN (JACKSON COUNTY) | UNITED GAS PIPELINE CO | WILL BE FILLED IN AFTER METALURGICAL INVESTIGATION IS COMPLETE; ON SUPPLEMENTAL | 431224 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
28 | 1986-05-06 | KY | other | UNKNOWN (CHRISTIAN COUNTY) | WESTERN KENTUCKY GAS CO | DOZER OPERATOR HIT LINE WHILE MAKING A DRAINAGE WATERWAY ACROSS FARM LAND. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
29 | 1986-04-23 | CA | other | UNKNOWN (RIVERSIDE COUNTY) | SOUTHERN CALIFORNIA GAS CO | TWO FISHER MODEL 472-AC 6" RELIEF VALVES AT WHITEWATER STATION "FAILED" IN THE OPEN POSITION WHEN COMPANY PERSONNEL MISTAKENLY CLOSED A 2" CONTROL VALVE DURINGA PIGGING OPERATION. | 132260 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
30 | 1986-03-31 | OK | leaks and spills | UNKNOWN (BECKHAM COUNTY) | NATURAL GAS PIPELINE CO OF AMERICA | RUPTURE OCCURED DUE TO INTERNAL CORROSION. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
31 | 1986-05-31 | TX | maintenance | UNKNOWN ( COUNTY) | BLACK MARLIN PIPELINE CO |  | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
32 | 1986-05-31 | TX | leaks and spills | UNKNOWN (PANOLA COUNTY) | UNITED GAS PIPELINE CO |  | 250000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
33 | 1986-05-28 | LA | maintenance | UNKNOWN ( COUNTY) | ANR PIPELINE CO (AMERICAN NATURAL RESOURCE) | LEAK LOCATED AT LONGITUDINAL SEAM. SEAM LOCATED NEAR TOP OF PIPE AT THE 10:30 POSITION. | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
34 | 1986-04-30 | AZ | other | UNKNOWN (MARICOPA COUNTY) | EL PASO NATURAL GAS CO | BLUESTAKE REQUIRES UPDATE OF MARKINGS IF OVER 10 DAYS AND NO CONSTRUCTION ACTIVITY ON PAVED AREAS AND 5 DAYS ON DIRT SURFACES. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
35 | 1986-05-11 | CO | other | UNKNOWN (GARFIELD COUNTY) | NORTHWEST PIPELINE CORP |  | 47200 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
36 | 1986-05-09 | CA | other | UNKNOWN (CONTRA COSTA COUNTY) | STANDARD PACIFIC GAS LINE INC |  | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
37 | 1986-05-07 | IA | maintenance | UNKNOWN (HARRISON COUNTY) | NORTHERN NATURAL GAS CO |  | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
38 | 1986-04-08 | TX | other | UNKNOWN (POLK COUNTY) | UNITED TEXAS TRANSMISSION CO |  | 63687 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
39 | 1986-06-09 | GA | other | UNKNOWN (ROCKDALE COUNTY) | TRANSCO GAS PIPELINE CORP |  | 150000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
40 | 1986-06-17 | MO | other | UNKNOWN (PLATTE COUNTY) | NORTHWEST CENTRAL PIPELINE CORP |  | 30000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
41 | 1986-06-03 | NE | other | UNKNOWN (DAWSON COUNTY) | KN ENERGY INC (KANSAS NEBRASKA NATURAL GAS CO INC) |  | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
42 | 1986-07-04 | NE | other | UNKNOWN (MADISON COUNTY) | KN ENERGY INC (KANSAS NEBRASKA NATURAL GAS CO INC) |  | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
43 | 1986-07-12 | AL | other | UNKNOWN (AUTAUGA COUNTY) | SOUTHERN NATURAL GAS CO |  | 1300000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
44 | 1986-08-05 | LA | other | UNKNOWN (ASSUMPTION COUNTY) | ACADIAN GAS PIPELINE SYSTEM |  | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
45 | 1986-07-18 | MS | other | UNKNOWN (ADAMS COUNTY) | MID - LOUISIANA GAS CO |  | 130000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
46 | 1986-07-09 | LA | other | UNKNOWN (ASSUMPTION COUNTY) | ACADIAN GAS PIPELINE SYSTEM |  | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
47 | 1986-06-24 | TX | other | UNKNOWN (LIBERTY COUNTY) | ENSERCH GAS TRANSMISSION CO | A VACUUM TRUCK HIT OUR LINE. TRHE IMPACT BROKE THE WELD SADDLE OFF OF THE 16' LINE CAUSING THE PIPE TO RUPTURE AND THE GAS WAS IGNITED BY THE TRUCK ENGINE. THERESULTING FIRE KILLED THE DRIVER AND COMPLETELY DESTROYED ALL EGT MEASUREMENT AND ODORIZATION FACILITIES AT THIS LOCATION.! **** LONE STAR GAS SUBMITTED REPORT FOR SAME INCIDENT. SEE 860152 | 311590 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
48 | 1986-07-06 | OK | other | UNKNOWN (CLEVELAND COUNTY) | NORTHWEST CENTRAL PIPELINE CORP |  | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
49 | 1986-08-12 | AZ | maintenance | UNKNOWN (COCONINO COUNTY) | EL PASO NATURAL GAS CO | ON AUGUST 12, 1986, AT 8:35 AM, A CRANKCASE EXPLOSION OCCURED AT WILLIAMS COMPRESSOR STATION THAT RESULTED IN THE INJURY OF THREE (3) EPNG EMPLOYEES. SUBSEQUENT INVESTIGATION REVEALED A FRACTURE OF THE #2 BEARING CAP AND THE RESULTANT MELTING OF THE BEARING BABBITT INTO THE CRANKCASE OIL AS THE CAUSE OF THE EXPLOSION.THE INVESTIGATION COMMITTEE HAS CONCLUDED THAT THE CAUSE SHALL BE CLASSIFIED ASA MECHANICAL FAILURE. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
50 | 1986-08-04 | WV | leaks and spills | UNKNOWN (PENDLETON COUNTY) | COLUMBIA GAS TRANSMISSION CORP | PIPE SECTION HAS BEEN SUBMITTED FOR METALLURGICAL ANALYSIS TO ASCERTAIN CAUSE. | 135000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
51 | 1986-07-16 | TX | maintenance | UNKNOWN (SAN PATRICIO COUNTY) | NATURAL GAS PIPELINE CO OF AMERICA | 30" MAINLINE RUPTURED AT A 6" COLD TAP. | 103226 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
52 | 1986-06-27 | AR | leaks and spills | UNKNOWN (MILLER COUNTY) | TEXAS EASTERN GAS PIPELINE CO | THE PIPELINE WAS OUT OF NORMAL OPERATING SERVICE AT THE TIME OF THE FAILURE. THE MAINLINE VALVE DOWNSTREAM OF THE POINT OF RUPTURE WAS CLOSED FOR PIPE REPLACEMENT ACTIVITIES IN PROGRESS IN THE DOWNSTREAM VALVE SECTION. THE PIPELINE SEGMENTWHICH FAILED WAS CONNECTED TO THREE LATERALS CONNECTING FOUR WELLS TO THE MAINLINE TO ACCUMULATE ENOUGH GAS FOR A REVERSE FLOW PIGGING OPERATION. NO DIRECT PRESSURE MEASUREMENT EQUIPMENT WAS IN SERVICE ON THE MAINLINE AT THE TIME OF FAILURE, THEREFORE THE EXACT PRESSURE ON THE MAINLINE CANNOT BE DETERMINED. THE SETTING OF THE ONLY RELIEF VALVE ON THE MAIN LINE SEGMENT WAS VERIFIED AT 847 PSIG ON MAY 19, 1986 PRIOR TO THE INCIDENT AND WAS CERTIFIED AFTER THE INCIDENT AT 850 PSIG. THIS RELIEF VALVE DID NOT RELIEVE. TWO OF THE RELIEF VALVES ON THE LATERALSWERE SET AT 848 PSIG AND THE THIRD SET AT 840 PSIG. AFTER THE INCIDENT THE LATERAL RELIEF VALVE SETTINGS WERE CERTIFIED AT 830 PSIG, 848 PSIG, AND 875 PSIG. THE RELIEF VALVES CERTIFIED AT 830 PSIG DID NOT. THE PIPELINE HAD BEEN SHUT-IN FORAPPROXIMATLY 25 HOURS, SO THE PRESSURES IN THE SEGMENT OF PIPELINE WERE AT OR NEAR STEADY STATE. | 531000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
53 | 1986-08-20 | TX | leaks and spills | UNKNOWN (EAST ADDITION COUNTY) | ANR PIPELINE CO (AMERICAN NATURAL RESOURCE) |  | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
54 | 1986-08-05 | LA | other | UNKNOWN (CAMERON COUNTY) | NATURAL GAS PIPELINE CO OF AMERICA | PIPELINE WAS GOUGED AND DENTED BY THIRD PARTY EQUIPMENT WHICH CAUSED A CRACK THAT LEAKED.ON AUGUST 6, 1986 AT 0730 HOURS, BUBBLING WAS REPORTED ON THE RIGHT OF WAY OF NATURAL GAS PIPELINE COMPANY OF AMERICA'S #1-30" LOUISIANA MAINLINE. THE INCIDENTSITE IS IN THE SALTWATER BARRIER CANAL ON THE EAST SIDE OF CALCASIEU LAKE, CAMERON PARISH, LA. THE LEAK RESULTED FROM A CRACK BY A GOUGE AND DENT BY AN UNKNOWNTHIRD PARTY. NO INJURIES OR FIRE RESULTED FROM THE LEAK. THE AFFECTED SECTION OF PIPE WAS REMOVED AND REPLACED, AND THE PIPELINE WAS RETURNED TO SERVICE. THE INCIDENT REPORT FORM IS ATTACHED. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
55 | 1986-08-28 | NM | other | UNKNOWN (SAN JUAN COUNTY) | EL PASO NATURAL GAS CO | ON AUGUST 28, 1986 AT 10:05 P.M. DURING NORMAL PIGGING OPERATIONS, AN EXPLOSIONAND FIRE OCCURRED AT THE PIGGING FACILITY ON THE CHACO-LINDRITH FIELD LINES WHICH RESULTED IN INJURY TO TWO(2) EPNG EMPLOYEES. SUBSEQUENT INVESTIGATION REVEALED THAT VAPORS WHICH HAD ACCUMULATED IN A LOW AREA FROM AN OPEN PIT RECEIVING THEPIGGING LIQUIDS OR POSSIBLY FROM A LEAK IN THE GAGE GLASS AREA WERE APPARENTLY IGNITED BY A VEHICLE WHICH WAS BEING DRIVEN BY ONE OF THE INJURED INDIVIDUALS. THE OTHER INJURED INDIVIDUAL WAS OBSERVING THE LIQUID LEVEL IN THE GAGE GLASS ANDWAS IN RADIO CONTACT WITH THE PERSON DRIVING THE VEHICLE WHEN THE EXPLOSION ANDFIRE OCCURRED. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
56 | 1986-09-01 | NM | other | UNKNOWN (SAN JUAN COUNTY) | EL PASO NATURAL GAS CO | ON SEPTEMBER 1, 1986 AT 4:00 P.M. AN EXPLOSION OCCURRED AT THE PIGGING FACILITYON THE CHACO-LINDRITH FIELD LINE WHICH RESULTED IN INJURY TO THREE (3) EPNG EMPLOYEES; HOWEVER, ONLY ONE REQUIRED HOSPITALIZATION. THE INCIDENT OCCURRED WHILE A CREW WAS PREPARING TO REPLACE THE SECTION OF 34-INCH PIPE RESERVOIR WHICH HAD BEEN DAMAGED IN THE EXPLOSION AND FIRE WHICH HAD OCCURRED ON AUGUST 28, 1986. ASA WELDER STARTED TO TACK WELD THE PIPE, THE EXPLOSION OCURRED INJURING THE EMPLOYEES. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
57 | 1986-09-09 | WY | other | UNKNOWN (CONVERSE COUNTY) | PHILLIPS PETROLEUM CO | AVAILABLE MEANS OF RELEASING PRESSURE FROM SPHERE RECEIVER NOT USED. RECEIVER UNDER PRESSURE WHEN EMPLOYEE TRIED TO REMOVE CAP. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
58 | 1986-09-10 | MI | other | UNKNOWN (KALKASKA COUNTY) | CONSUMERS POWER CO | LIGHTNING STRUCK A TREE 36 FEET AWAY FROM THE 12" PIPELINE AND TRAVELED TO THE PIPELINE VIA THE TREE'S ROOTS. THIS RESULTED IN A PINHOLE LEAK ON THE TOP OF THE | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
59 | 1986-10-01 | WV | other | UNKNOWN (LEWIS COUNTY) | CONSOLIDATED GAS TRANSMISSION CORP | BOTTOM BARRELL OF STEP LADDER DRIP (12" SECTION) SEPARATED IN SEAM. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
60 | 1986-10-28 | WA | other | UNKNOWN ( COUNTY) | CASCADE NATURAL GAS CORP |  | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
61 | 1986-10-06 | CA | other | UNKNOWN (SAN BERNARDINO COUNTY) | SOUTHERN CALIFORNIA GAS CO | REGULATOR MALFUNCTION | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
62 | 1986-10-10 | TX | maintenance | UNKNOWN (GRAY COUNTY) | WESTAR TRANSMISSION CO | CRACK IN SEAM OF PIPE OPENED CAUSING RUPTURE. THIS FAILURE WAS IN A DRAW APPROXIMATELY 12' DEEP AND 80' WIDE. BAD SEAM IN JOINT OF PIPE. NUMEROUS COROSION PITSUNRELATED TO PIPE FAILURE WERE NOTED. | 78000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
63 | 1986-11-02 | AR | maintenance | UNKNOWN (CLARK COUNTY) | ARKLA ENERGY RESOURCES | A SECTION OF 20" PIPE ON AN OVERHEAD CROSSING BLEW OUT, PIPE HAD APPARENTLY BEEN DAMAGED BY PIG IN 45 DEGREE E11. | 185988 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
64 | 1986-10-29 | TX | other | UNKNOWN (RUSK COUNTY) | SESCO PRODUCTION CO | CONSTRUCTION CREW (CHAPARRAL GENERAL CONSTRUCTION CO., INC.) RUPTURED PIPELINE WITH FRONT-END LOADER WHILE ESCAVATING FOR STREET CONSTRUCTION. | 500 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
65 | 1986-10-30 | IL | maintenance | UNKNOWN (LIVINGSTON COUNTY) | NATURAL GAS PIPELINE CO OF AMERICA | LEAK CAUSED BY INCOMPLETE FUSION OF THE LONGITUDINAL SEAM. | 62300 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
66 | 1986-10-31 | NJ | other | UNKNOWN (HUNTERDON COUNTY) | TEXAS EASTERN GAS PIPELINE CO | ON OCTOBER 31, 1986 AT 9:34 A.M. E.S.T. A SCHEDULED ROUTINE BLOW-DOWN OF TEXAS EASTERN'S 36" LINE NO. 27 WAS INITIATED JUST EAST OF THE DELAWARE RIVER HUNTERDON COUNTY, NEW JERSEY. THE PRESSURE ON LINE NO. 27 WAS 850 PSIG AT THE TIME THE BLOW-DOWN WAS STARTED THROUGH THE 10" X 8" BLOW-DOWN VALVE. AT 1:25P.M. E.S.T. AFTER THE PRESSURE HAD BEEN REDUCED TO APPROX. 50 PSIG, THE ESCAPING GAS IGNITED AND BURNED TWO HIGH VOLTAGE POWER LINES. THE CAUSE OF THE IGNITION HAS NOT BEEN DETERMINED AT THIS TIME. THE POWER LINES WERE LOCATED APPROX. 48' NORTH OF THE BLOW-DOWN STACK. THIS INCIDENT DID NOT RESULT IN ANY POWER OUTAGE. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
67 | 1986-11-13 | TX | other | UNKNOWN (HUTCHINSON COUNTY) | PANHANDLE EASTERN PIPELINE CO | A CONTRACTOR'S EMPLOYEE WAS STEAMING A FROZEN DRAIN LINE FROM A NATURAL GAS CONDENSATE STORAGE TANK, LIQUID WAS RELEASED THROUGH AN OPEN VALVE, AND VAPOR FROM THE LIQUID WAS IGNITED BY THE OPEN FLAME ON THE CONTRACTOR'S STEAMER TRUCK. | 750000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
68 | 1986-11-05 | KY | other | UNKNOWN (MADISON COUNTY) | TENNESSEE GAS PIPELINE CO | A SMALL 11/16" TAPERED DRILLED HOLE WAS PARTIALLY DRILLED INTO MAIN BODY OF PIPE AT THE 7 O'CLOCK POSITION. LEAK DID NOT START UNTIL AFTER HYDROSTATICALLY TESTED ON 9/30/86. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
69 | 1986-12-02 | OK | other | UNKNOWN (MUSKOGEE COUNTY) | OKLAHOMA NATURAL GAS CO | THE LINE THAT FAILED WAS INSTALLED IN JUNE 1986. THIS PROJECT WAS A RELOCATION REQUIRED DUE TO HIGHWAY CONSTRUCTION. THE PIPELINE WAS DESIGNED, INSTALLED, AND TESTED IN ACCORDANCE WITH THE ASME B31.8-1968 EDITION CODE FOR "GAS TRANSMISSIONAND DISTRIBUTION PIPING SYSTEMS." THE LINE PIPE MATERIAL WAS 12 3/4" O.D.,27.20#(0.203"),API-5LX., X-42 ERW MANUFACTURED BY LONE STAR STEEL. THE LINE WAS HYDROSTATICALLY TESTED TO 1100 PSIG FOR FOUR HOURS, WHICH ESTABLISHED AN MAOP OF 720 PSIG IN A CLASS 2 LOCATION. DUE TO THE SUPPLY TO THIS SYSTEM AND NO NEED FOR THE720 PSIG PRESSURE TO SERVE MARKET, THE PIPELINE HAS OPERATED AT 300 TO 350 PSIGSINCE INSTALLATION. THE NEED FOR 50O PSIG MAXIMUM OPERATING PRESSURE ON THIS PIPELINE IS NOW REQUIRED TO SERVE MARKET. SINCE THE LINE HAD NOT OPERATED HIGHER THAN 350 PSIG. IT WAS DECIDED TO GO THROUGH AN UPRATING PROCEDURE. A WRITTEN PLANWAS PREPARED AS PER SUBPART K OF THE D.O.T. RULES. THE PRESSURE IS TO BE INCREASED IN 100 PSIG INCREMENTS TO 750 (500 X 1.5) WITH A FLAME-IONIZATION LEAK SURVEY DURING THE 24-HOUR HOLD PERIOD. THE LINE RUPTURED AT 55O PSIG, WHICH WAS THE SECOND STEP OF THE PRESSURE INCREASES. THE 550 PSIG WAS ATTAINED AT ABOUT 1600 HOURS ON DECEMBER 2, 1986, AND THE LINE FAILED AT 1930 HOURS ON DECEMBER 2, 1986. NO FIRE, NO FATALITIES. AND NO INJURIES RESULTED FROM THE RUPTURE. SERVICE WAS IN | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
70 | 1986-12-06 | MS | other | UNKNOWN (RANKIN COUNTY) | UNITED GAS PIPELINE CO | THERE IS NO APPARENT CAUSE FOR THE RUPTURE, BUT A METALLURGICAL INVESTIGATION IS UNDERWAY ON SAMPLES OF THE RUPTURED PIPE TO DETERMINE THE CAUSE OF RUPTURE. UNITED HAS TWO 30" LINES CROSSING PELAHATCHIE BAY. A VALVE SITE IS LOCATED ON EACHSIDE OF THE BAY WHERE THE LOOP TERMINATES WITH A CROSSOVER AND VALVE TYING INTOTHE 30" MAIN LINE. THE LOOP LINE, AT HTE NORTH VALVE SITE RUPTURED IN THE BODY OF THE PIPE 2'-11 1/2" FROM THE LONGITUDINAL SEAM AT A POINT 8'-4' SOUTH OF THE CROSSOVER AND VALVE PIPING OUT OF THE TOP OF THE TEE AT THE 30" MAIN LINE TIE-INPOINT. | 685000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
71 | 1986-11-24 | LA | other | UNKNOWN ( COUNTY) | SEA ROBIN PIPELINE CO | A SHRIMP BOAT HUNG A NET IN THE LINE, DAMAGING A 2 INCH TAP VALVE. | 90000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
72 | 1986-12-06 | OK | other | UNKNOWN (BECKHAM COUNTY) | EL PASO NATURAL GAS CO | ON DECEMBER 12, 1986, AT 1:10 P.M. AN EXPLOSION OCCURRED ON THE 6-5/8" O.D. NONJURISDICTIONAL LINE TO APACHE CORP. - PUCKETT WELL #1-16, THAT RESULTED IN THE DEATH OF A BULLDOZER OPERATOR EMPLOYED BY APACHE CORP. THE OPERATOR WAS KILLED WHEN. WHILE MOVING THE BULLDOZER FROM ONE LOCATION TO ANOTHER, THE BULLDOZER SANK IN THE WET SOIL AND STRUCK AND RUPTURED OUR LINE. THE LINE HAD APPROXIMATELY 4 FEET OF COVER. THE FORCE OF THE EXPLOSION THREW THE OPERATOR FROM THE BULLDOZER AND CAUSED HIS DEATH. UNDER THE REGULATIONS ISSUED BY THE DEPARTMENT OF TRANSPORTATION IN THE CODE OF FEDERAL REGULATIONS, TITLE 49, SUBTITLE B, CHAPTER 1, PART 191, EL PASO NATURAL GAS COMPANY SUBMITS THE REPORTS COVERING THE INCIDENT WHICHOCCURRED ON DECEMBER 6, 1986, ON EL PASO NATURAL GAS COMPANY'S LINE TO APACHE CORPORATION'S PUCKETT WELL #1-16 IN EL PASO'S SOUTH ZYBACH GATHERING SYSTEM. EVENTHOUGH THIS FACILITY IS NONJURISTICTIONAL, DUE TO THE DEATH OF A BULLDOZER OPERATOR EMPLOYED BY APACHE CORPORATION, WE TELEPHONICALLY REPORTED THIS INCIDENT TOTHE DEPARTMENT OF TRANSPORTATION. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
73 | 1986-11-26 | LA | leaks and spills | UNKNOWN ( COUNTY) | STINGRAY PIPELINE CO | NONE KNOWN AT THIS TIME. | 200000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
74 | 1986-11-10 | AR | other | UNKNOWN (CRAWFORD COUNTY) | ARKLA ENERGY RESOURCES |  | 75000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
75 | 1986-12-12 | NJ | other | UNKNOWN (MIDDLESEX COUNTY) | TEXAS EASTERN GAS PIPELINE CO | A BACKHOE WAS WORKING NEAR A REGULATOR PIT WHEN THE BACKHOE BUCKET STRUCK A BLEED OFF ASSEMBLY CAUSING A 1" THREADED PIPE NIPPLE TO BE STRIPPED FROM A THREAD-O-LET FITTING. ALL PERSONNEL WERE REMOVED FROM THE VICINITY OF THE LEAK AND THE AREA WAS SECURED BY TEXAS EASTERN AND AUTHORITIES. THE AREA WAS SECURED WITHIN 30MINUTES AFTER THE INCIDENT OCCURRED. THE SOURCE OF GAS CONTINUED AND SECURITY OF THE AREA WAS MAINTAINED UNTIL THE LEAK WAS STOPPED. THE PIPELINE WAS BLOWN DOWN AND A PIPE PLUG WAS INSTALLED TO STOP THE LEAK. THIS INCIDENT DID NOT CAUSE ANY PERSONAL INJURIES OR FIRE. VERY MINOR MATERIAL DAMAGE RESULTED FROM THE INCIDEN | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
76 | 1986-11-12 | LA | other | UNKNOWN (WINN COUNTY) | UNITED GAS PIPELINE CO | WILL BE FILLED IN AFTER METALLURGICAL INVESTIGATION IS COMPLETE, ON SUPPLEMENTAL REPORT. | 221665 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
77 | 1986-10-14 | TX | maintenance | UNKNOWN ( COUNTY) | HOUSTON PIPELINE CO | IN OUR LETTER OF SEPTEMBER 12, 1986, WE REPORTED THAT THIS INCIDENT WAS ORIGINALLY REPORTED IN ERROR AN AUGUST 27, 1986 AS IT HAD BEEN DETERMINED THAT THE ORIGIN WAS NOT A PART OF OUR DISTRIBUTION SYSTEM. AFTER FURTHER INVESTIGATION, IT HASBEEN DETERMINED THAT THE INCIDENT WAS REPORTABLE. INITIAL FIELD TEST REPORTS INDICATED REGULATOR ALLOWED EXCESSIVE PRESSURE ON CUSTOMER PIPING. FURTHER LABORATORY TESTS INDICATED REGULATOR FUNCTIONED PROPERLY. AFTER FURTHER REVIEW OF FIELDDOCUMENTATION OF EVENTS, IT WAS DISCOVERED THAT SEVERAL FIELD TESTS WERE ACTUALLY PERFORMED INDICATING MALFUNCTION OF SERVICE REGULATOR. SUBSEQUENTLY, WE ARE SUBMITTING AN INCIDENT REPORT. WE REGRET ANY INCONVENIENCE THIS MAY HAVE CAUSED. | 5000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
78 | 1986-12-30 | TX | other | UNKNOWN (ARANSAS COUNTY) | VALERO TRANSMISSION CO | PIPELINE WAS HIT BY MARINE VESSEL. WE DO NOT KNOW WHO WAS RESPONSIBLE FOR DAMAGE. APPEARS THAT A BARGE HIT PIPE CAUSING DAMAGE. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
79 | 1986-12-15 | ND | maintenance | UNKNOWN (BILLINGS COUNTY) | WILLISTON BASIN INTERSTATE PIPELINE CO | LEAK OR CRACK OCCURRED IN A FIBERGLASS WASTE LIQUED TANK OR IN PLASTIC PIPE LEADING TO TANK. EXACT LOCATION UNKNOWN. FIRE DESTROYED FACILITIES. | 350000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
80 | 1986-07-11 | PA | maintenance | UNKNOWN (ELK COUNTY) | NATIONAL FUEL GAS SUPPLY CORP | TWO INCH & FOUR INCH PIPE WAS TO BE LAID IN THE GATHERING SYSTEM OF BELMOUTH STORAGE FIELD, A REMOTE AREA IN ELK COUNTY, PA. WHEN TESTED, A TOTAL OF FIVE FAILURES WERE FOUND, ALL BELOW 2000 PSIG, 4 IN 4", AND 1 IN 2". FURTHER INVESTIGATIONREVEALED THAT AT LEAST SOME OF THE PIPE WAS ACTUALLY STRUCTURAL TUBING SHIPPED AND BILLED AS PRIME ERW PIPE. ALL 4" PIPE HAS BEEN REPLACED. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
81 | 1986-12-10 | TX | leaks and spills | UNKNOWN (DALLAS COUNTY) | DELHI GAS PIPELINE CORP | INCIDENT OCCURRED DURING THE REPAIR OF A LEAK IN A 6" PIPELINE. THE LINE HAD BEEN BLOWDOWN & ISOLATED FOR THE REPAIR PROCEDURES. DURING THE REMOVAL OF THE LEAKING PIPELINE SEGMENT, A SUDDEN, SHORT DURATION GAS FLOW WAS EXPERIENCED. LINE WAS INTERNALLY INHIBITED. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
82 | 1987-02-13 | LA | leaks and spills | UNKNOWN ( COUNTY) | STINGRAY PIPELINE CO | LINE WAS BLOWN DOWN TO INSTALL REPAIR CLAMP ON LEAK AND WAS BEING REPRESSURED FOR SERVICE WHEN RUPTURE OCCURRED. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
83 | 1987-02-02 | LA | maintenance | UNKNOWN ( COUNTY) | ANR PIPELINE CO (AMERICAN NATURAL RESOURCE) |  | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
84 | 1987-02-01 | LA | leaks and spills | UNKNOWN ( COUNTY) | STINGRAY PIPELINE CO |  | 200000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
85 | 1987-02-17 | TX | other | UNKNOWN (MARTIN COUNTY) | WESTAR TRANSMISSION CO | FARMER WAS DEEP PLOWING & HIT AN ABONDONED TAP THAT EXTENDED 9 INCHES ABOVE PIPELINE (PIPELINE HAD 21 INCHES OF COVER) FARMER ALSO FAILED TO NOTIFY ANYONE UNTIL THE NEXT DAY. | 10000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
86 | 1987-02-11 | NV | other | UNKNOWN ( COUNTY) | SOUTHWEST GAS CORP | WHILE ATTEMPTING TO LOCATE A CULVERT, CONTRACTOR DUG INTO 8" HIGH PRESSURE TRANSMISSION LINE. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
87 | 1987-03-29 | IL | other | UNKNOWN (WASHINGTON COUNTY) | ILLINOIS POWER CO | SUBSIDENCE INA COAL MINE ABADONED IN 1948 CAUSED A LEAK IN THE I.,P.C. #2 GAS GAS STORAGE WELL IN ILLINOIS POWER'S TILDEN GAS STORAGE FIELD. AS ARESULT OF THISSUBSIDENCE, THE 5 1/2" O.D PRODUCTION CASING AND 8 5/8" O.D. MINE CASING WERE DAMAGEED AND GAS ESCAPED INTO THE ABANDONED COAL MINE.THREE ILLINOIS POWER OBSERVATION WELLS COMPLETED IN THE ABANDONED MINE WERE USEDTO VENT THE ESCAPING GAS TO ATMOSPHERE WITHIN THREE HOURS TO CONTROL THE PRESSURE IN THE ABANDONED MINE. NUMEROUS ATTEMPTS TO PUMP FLIUD DOWN THE WELL FAILED TO KILL THE WELL AND STOP THE FLOW OF GAS. A COILED TUBING UNIT WAS ALSO UTILIZED IN ATTEMPTS TO KILL THE WELL WITH FLUID WERE UNSUCCESSFUL. ARIG WAS THEN UTILIZED TO MILL OUT APPROXIMATELY 12.5 FEET OF DAMAGED CASING TO ALLOW FLUID TO BEPUMPED INTO THE WEL TO STOP THE FLOW OF GAS. THE DAMAGE I.P.C #2 WELL WAS THENPLUGGED WITH CEMENT | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
88 | 1987-01-13 | TX | leaks and spills | UNKNOWN ( COUNTY) | NATURAL GAS PIPELINE CO OF AMERICA | THERE ARE 2 LEAKS ON THE 12" PIPELINE DUE TO INTERNAL CORROSION | 150000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
89 | 1987-04-06 | TX | leaks and spills | UNKNOWN (JEFFERSON COUNTY) | AMOCO GAS CO | THE PIPE IS ON PILINGS PARRALLELING KEITH LAKE BRIDGE. CORROSION STARTED UNDERTHE COATING, CAUSING A SMALL PIT AND A RESULTING LEAK. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
90 | 1987-02-13 | KS | other | UNKNOWN (LINCOLN COUNTY) | NATURAL GAS PIPELINE CO OF AMERICA | CONTRACTOR OPERATOR GOUGEED 18" PIPELINE WITH 235 CAT BACKHOE BUCKET WHILE CLEANING DRAINAGE DICTH. PIPELINES WERE FLAGGED, PRODDED AND DEPTH RECORDED ON FLAGS ON 1/7/87. COMPANY INSPECTORS WERE PRESENT AND WITNESSED THE DAMAGE. | 70545 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
91 | 1986-12-01 | TX | leaks and spills | UNKNOWN (MIDLAND COUNTY) | PHILLIPS PETROLEUM CO | FOR APPROXIMATELY ONE YEAR, THE GENERAL AREA WHERE THE LEAK ACCURRED HAS BEEN UNDER WATER DUE TO EXCESSIVE AMOUNT OF RAINFALL AND IRRIGATION BY LANDOWNER. AREA REQUIRED DRAINAGE. | 90000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
92 | 1987-03-02 | TX | leaks and spills | UNKNOWN (JEFFERSON COUNTY) | UNITED TEXAS TRANSMISSION CO | LINE WAS LEAKING UNDER PAVED COUNTY ROAD (GENTRY ROAD). COMPANY PERSONAL MONITORED THE LEAK CONTINUALLY FROM TIME OF VERIFATION UNTIL THE LINE WAS SHUT DOWN. | 147232 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
93 | 1987-02-04 | TX | other | UNKNOWN (ZAVALA COUNTY) | VALERO TRANSMISSION CO | 4" PIPELINE WAS HIT BY TENNESSEE PIPELINE CONSTRUCTION COMPANY WHILE EXCAVATING. | 1000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
94 | 1987-03-06 | TX | leaks and spills | UNKNOWN (KLEBERG COUNTY) | VALERO TRANSMISSION CO | THIS IS A RESULT OF A CORROSION LEAK IN A TRANSMISSION LINE. THE LEAK DEVELOPED IN A RURAL AREA AND PRESENTED NO HAZARD. IT IS BEING REPORTED BECAUSE IT EXCEEDS THE PROPERTY DAMAGE LIMIT | 18000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
95 | 1987-05-13 | CA | other | UNKNOWN (ORANGE COUNTY) | EXXON CO USA | AT 1:40 PM ON MAY 13, 1987, THE LONG BEACH FIRE DEPT REPORTED AN OIL SPILL 500 YARDS OFFSHORE SEAL BEACH, CALIF. 10 BARRELS OF CRUDE OIL LEAKED OUT OF AN EIGHTINCH EMULSION PIPELINE CONNECTING EXXON'S BELMONT ISLAND PRODUCTION FACILITY WITH CRUDE OIL PROCESSING FACILITES AT EXXON'S SEAL BEACH SEPARATION CENTER. PRODUCTION FROM BELMONT ISLAND WAS IMMEDIATELY SHUT-IN TO MINIMIZE THE EXTENT OF THE SPILL. CLEAN-UP OPERATIONS WERE PROMPTLY INITIATED WITH THE NOTIFICATION OF CLEAN COASTAL WATERS AND INTERNATIONAL TECHNOLOGY CORP. THE NATIONAL RESPONCE CENTERWAS NOTIFIED AT 2:04 PM (NRC REPORT #5573). APPROXIMATELY TWO BARRELS OF CRUDE OIL WASHED ASHORE ALONG A FOUR MILE STRETCH OF SEAL BEACH AND LONG BEACH. CLEAN-UP OPERATIONS WERE COMPLETED BY 7:30 PM ON MAY 15, 1987. AN UNDERWATER INSPECTION OF THE EIGHT INCH EMULSION PIPELINE REVEALED A 5/8" DIA. HOLE. THIS HOLE WAS CAUSED BY INTERNAL CORROSION IN THE 32 YEAR OLD PIPELINE. AN INSPECTION OF THE ADJACENT THREE INCH PURCHASE GAS PIPELINE REVEALED A 1/4" DIA HOLE. THIS HOLE WAS THE RESULT OF EXTERNAL EROSION AS THE CRUDE OIL EMULSION AND ENTRAINED SAND EXITED THE EIGHT INCH EMULSION PIPELINE. AN UNKNOWN, BUT RELATIVELY SMALL QUANTITY OF NATURAL GAS ESCAPED FROM THE TREE INCH GAS PIPELINE AND BUBBLED TO THE OCEAN SURFACE. ALL HOLES WERE SUBSEQUENTLY CLAMPED BY DIVERS. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
96 | 1987-07-10 | TN | other | UNKNOWN (SHELBY COUNTY) | MEMPHIS LIGHT GAS & WATER DIVISION | CONTRACTOR WAS TRENCHING ACROSS ROAD AND HIT GAS MAIN, CAUSING A FIRE THAT DAMAGED TRENCHER AND BURNED OPERATOR AN ARM AND NECK. | 16500 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
97 | 1987-06-30 | MD | other | UNKNOWN (FREDERICK COUNTY) | COLUMBIA GAS TRANSMISSION CORP | LIGHTNING STRUCK AN INDIRECT WATER BATH HEATER OWNED AND OPERATED BY WASHINGTONGAS LIGHT (WGL) AT BRINK STATION. A FIRE ENSUED AND SPREAD TO THEIR BUILDING. THE BUILDING WAS DESTROYED, DROPPING THE ROOF ONTO COLUMBIA'S MEASURING STATION AND OTHER WGL FACILITIES AS LOCATED THEREIN. THIS DESTROYED COLUMBIA'S ROCKWELL T-18 TURBINE METER SETTING AND DAMAGED RELATED 6"PIPE (ALONG WITH OTHER WGL FACILITIES). | 45000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
98 | 1987-07-08 | TX | leaks and spills | UNKNOWN (SAN PATRICIO COUNTY) | FLORIDA GAS TRANSMISSION CO | CORROSION WAS EXTERNAL, ON THE BOTTOM OF THE PIPE. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
99 | 1987-06-30 | VA | other | UNKNOWN (FAIRFAX COUNTY) | WASHINGTON GAS LIGHT CO | ON THE EVENING OF JUNE 30, 1987, LIGHTING STRUCK A GATE STATION WHICH DELIVERS NATURAL GAS FROM COLUMBIA TRANSMISSION COMPANY TO WASHINGTON GAS LIGHT COMPANY. A LINE HEATER VALVE WAS THE POINT OF STRIKE, WAS BURNED THROUGH AND IGNITION OCCURRED. THE FLAMES INTENSIFIED UNTIL THE ENTIRE STATION WAS FULLY INVOLVED. MUTUALEFFORTS OF COLUMBIA AND WASHINGTON GAS LED TO THE CLOSING OF THE STATION INLET AND OUTLET VALVES WHICH ALLOWED THE FIRE TO EXTINGUISH ITSELF. | 500000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
100 | 1987-06-10 | TX | leaks and spills | UNKNOWN (DALLAS COUNTY) | LONE STAR GAS CO | CORROSION IN A MAIN LINE DRIP ON LINE OS-8". | 5483 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
101 | 1987-06-08 | TX | leaks and spills | UNKNOWN (NUECES COUNTY) | DELHI GAS PIPELINE CORP | PIPELINE WAS PURCHASED FROM SUN OIL CO. IN 1971. PRIOR RECORDS INDICATE THAT SUN HAD CATHODIC PROTECTION ON PIPELINE PRIOR TO DELHI'S PURCHASE. THIS LINE IS SCHEDULED FOR REPLACEMENT ON 7/14/87 | 5441 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
102 | 1987-05-24 | LA | other | UNKNOWN (ST LANDRY COUNTY) | TRANSCO GAS PIPELINE CORP | PART B AS A RESULT OF THE GATES BEING CLOSED AT THE OLD RIVER DIVERSION STATION, THERE WAS A DROP IN THE LEVEL OF THE ATCHAFALAYA RIVER IN A SHORT PERIOD OF TIME . IT IS SURMISED THAT THIS CONDITION CONTRIBUTED TO THE SLOUGHING OF THE EAST BANK.PART 3 INCIDENT OCCURRED ON EAST BANK OF ATCHAFALAYA RIVER. THE PIPELINE PULLED APART AT A GIRTH WELD BECAUSE OF STRESSES CAUSED BY THE SLOUGHING OF THE EAST BANK. CURRENT PLANS ARE FOR THIS PIPELINE TO BE ABANDONED IN PLACE. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
103 | 1987-05-26 | CO | maintenance | UNKNOWN (RIO BLANCO COUNTY) | NORTHWEST PIPELINE CORP | PART C #4 3/4 - INCH CRACK IN LONGSEAM | 24000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
104 | 1987-05-25 | OH | other | UNKNOWN (CUYAHOGA COUNTY) | COLUMBIA GAS TRANSMISSION CORP | PART B #3INCIDENT RESULTED FROM A MOTORCYCLE TRAFFIC ACCIDENT; SEE ATTACHED COPY OF OHIOTRAFFIC ACCIDENT REPORT NO. 87-4172 BY STRONGSVILLE POLICE DEPT. THE MOTORCYCLEBROKE VALVE LOOSE FROM 1" PIPE, CAUSING GAS TO ESCAPE. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
105 | 1987-05-28 | OK | other | UNKNOWN (JEFFERSON COUNTY) | LONE STAR GAS CO |  | 350000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
106 | 1987-04-22 | TX | other | UNKNOWN (CRANE COUNTY) | LONE STAR GAS CO | BULLDOZER OPERATOR WORKING ON A WELL FOR ANOTHER COMPANY HIT LONE STAR'S 36" LINE. THE OPERATOR WAS NOT AWARE OF THE LINE. PIPELINE DID NOT RUPTURE BUT WAS DAMAGED. | 47500 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
107 | 1987-04-29 | TX | other | UNKNOWN (NAVARRO COUNTY) | LONE STAR GAS CO | EMPLOYEES ATTEMPTED TO RE-LIGHT THE TITARTOR, EXPLOSION AND FIRE DESTROYED THE BUILDING AND ALL THE EQUIPMENT. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
108 | 1987-05-12 | TX | leaks and spills | UNKNOWN (WEBB COUNTY) | VALERO TRANSMISSION CO | REASON FOR FAILURE IS UNKNOWN AT THIS TIME. METALLURGICAL INVESTIGATION IS BEINGCONDUCTED. | 200000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
109 | 1987-05-27 | TX | leaks and spills | UNKNOWN (NAVARRO COUNTY) | TEXAS UTILITIES FUEL CO | SMALL LEAK ABOUT 200 YARDS WEST OF MILES MARKER K-15 OFF OF COUNTY RD. LT-2-87 | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
110 | 1987-08-13 | MN | leaks and spills | UNKNOWN (ROSEAU COUNTY) | INTER - CITY GAS MINNESOTA PIPELINES LTD | CORROSION LEAK WAS DISCOVERED DURING LEAK SURVEY. CORRODED SECTION WAS REPLACEDWITH PRETESTED PIPE (1392 PSIG) - COMPLETED AUGUST 24, 1987 | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
111 | 1987-08-06 | KY | other | UNKNOWN (PENDLETON COUNTY) | COLUMBIA GAS TRANSMISSION CORP | PART 3:HOLLOWAY CONSTRUCTION WAS CROSSING PIPELINE WITH HEAVY EARTH MOVING EQUIPMENT (SCRAPER PANS AND DOZERS) WHEN A PAN STRUCK THE PIPELINE, AFTER REMOVING FIVE (5)FEET OF EARTH COVER. PART B # 3:THE PIPELINE HAD BEEN RELOCATED FOR CONSTRUCTION OF THE A-A HIGHWAY, AND A STATE INSPECTOR, WHO KNEW THE PIPELINE LOCATION, WAS ON THE JOB SITE AT THE TIME OF THE INCIDENT. ALSO, THE CONSTRUCTION SUPERINTENDENT WAS AWARE OF THE PIPELINE LOCATION AND HAD DISCUSSED THE HAZARDS WITH EQUIPMENT OPERATORS. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
112 | 1987-07-17 | MT | other | UNKNOWN (BEAVERHEAD COUNTY) | MONTANA POWER CO | PIPE CONTAINED MULTIPLE DENTS IN A SPACE OF 6 FEET. THERE WAS ALSO EVIDENCE OF BENDING UPWARD WHICH RESULTED IN A TENSION FAILURE IN A GIRTH WELD | 11900 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
113 | 1987-07-22 | TX | leaks and spills | UNKNOWN (CHAMBERS COUNTY) | UNITED TEXAS TRANSMISSION CO | COMPANY PERSONNEL MONITORED LEAK CONTINUALLY FROM TIME OF INITIAL NOTIFICATION ON 7/21/87 UNTIL THE LINE WAS SHUT DOWN FOR REPAIR ON 7/23/87. TELEPHONIC NOTIFICATION TO THE RRC WAS MADE WHEN LEAK WAS CONFIRMED TO BE ON UTTCO FACILITIES ON 7/22/87 | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
114 | 1987-09-16 | TX | other | UNKNOWN ( COUNTY) | VALERO TRANSMISSION CO | LOCATION MARKED WITH PIPELINE MARKERS WITH COMPANY NAME AND 24-HOUR EMERGENCY NUMBER. | 20000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
115 | 1987-09-11 | LA | other | UNKNOWN ( COUNTY) | TENNESSEE GAS PIPELINE CO |  | 111000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
116 | 1987-09-14 | TX | other | UNKNOWN (WARD COUNTY) | WESTAR TRANSMISSION CO | WESTAR SUPERVISOR REMAINED ON SITE UNTIL CONTRACTOR FINISHED EXPOSING & CROSSING PIPELINE. AFTER WESTAR SUPERVISOR LEFT CONTRACTOR BEGAN SHAVING TOP WALLS OF DITCH & HIT PIPELINE WITH BACKHOE BUCKET. CONTRACTOR FOR CHEVRON PUNCTURED WESTARLINE #4000 WITH BACKHOE. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
117 | 1987-09-24 | TX | other | UNKNOWN (FAYETTE COUNTY) | CLAJON GAS CO | THE GRADALL VEHICLE WAS WEST BOUND ON 2981 WHEN THE DRIVER MR. LUNA LOST CONTROLON A DOWN HILL SLOPE-RAN OFF THE ROAD TO THE LEFT, CROSSED THE DITCH, THE FENCEAND HIT THE PIPELINE TAP-PASSING OVER THE TAP AND CAME TO REST APPROX. 10' WESTOF THE TAP. MR. LUNA DROVE THE VEHICLE AWAY FROM THE FIRE AT THE TAP-BACK ACROSS FM 2981. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
118 | 1987-07-27 | TN | other | UNKNOWN (WASHINGTON COUNTY) | EAST TENNESSEE NATURAL GAS CO |  | 18000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
119 | 1987-09-03 | PA | maintenance | UNKNOWN (ELK COUNTY) | NATIONAL FUEL GAS SUPPLY CORP | HORIZONTAL FAILURE. LINE C WAS LAID IN 1908. IN 1947 THE PIPE WAS PICKED UP, RECONDITIONED AND PUT BACK IN THE GROUND. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
120 | 1987-08-09 | TX | other | UNKNOWN (JIM WELLS COUNTY) | C B GAS GATHERING INC | SMALL LEAK IN STARTING GAS SYSTEM WHICH POSSIBLY IGNITED FROM ELECTRICAL SYSTEMAND BURNED 125# START GAS HOSE IN HALF TO FEED FIRE. | 33000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
121 | 1987-09-09 | TX | other | UNKNOWN (HARRIS COUNTY) | TEXAS SOUTHEASTERN GAS CO | PEANUT FARMER HIT OUR PIPELINE WITH HIS HARVESTING MACHINE. | 4000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
122 | 1987-08-20 | LA | leaks and spills | UNKNOWN ( COUNTY) | ANR PIPELINE CO (AMERICAN NATURAL RESOURCE) |  | 82000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
123 | 1987-08-13 | AR | leaks and spills | UNKNOWN (CLARK COUNTY) | ARKLA ENERGY RESOURCES | A SECTION OF 20" PIPE IN CREEK CROSSING RUPTURED. | 70352 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
124 | 1987-09-02 | MA | other | UNKNOWN (NORFOLK COUNTY) | ALGONQUIN GAS TRANSMISSION CO | LINE WITH A FRONT END LOADER, STRUCK AND PUNCTURED THE PIPELINE. THE LOCATION OF THE PIPELINE HAD BEEN ERRONEOUSLY MARKED. LOCATION OF PIPELINE HAD BEEN ERRONEOUSLY MARKED. | 38175 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
125 | 1987-08-25 | TX | other | UNKNOWN (EASTLAND COUNTY) | SOUTHWESTERN GAS PIPELINE INC | WELL SITE BEING CONSTRUCTED BY A PRODUCING COMPANY. DID NOT CALL TO HAVE PIPELINES LOCATED. IGNORED POSTED LINE MARKERS IN THE VICINITY INDICATING PIPELINES ARE PRESENT. | 251939 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
126 | 1987-08-21 | TX | other | UNKNOWN ( COUNTY) | HOUSTON PIPELINE CO | DURING THE GAS PURGE OF THE LINE, LIQUID HYDROCARBON SPRAYED FROM THE BLOWDOWN RISER. THE PURGING OPERATION WAS SHUTDOWN IMMEDIATELY BUT ABOUT 10 MINUTES LATERTHE GAS/LIQUID PHASE CAUGHT FIRE. | 10000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
127 | 1987-10-08 | TX | other | UNKNOWN ( COUNTY) | DELHI GAS PIPELINE CORP | DURING EXCAVATION OF DELHI'S FARM SYSTEM 12" A LEAK WAS DISCOVERED IN THE THREADS OF A 1" PIPELINE TAP. THE LEAK WAS DUE TO EXTERNAL FORCE OF MESQUITE TREE ROOTS WHICH HAD GROWN AROUND THE 1" FITTING AND VALVE. THE TAP WAS INACTIVE AND THEVALVE WAS PLUGGED. | 9000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
128 | 1987-10-10 | TX | other | UNKNOWN (FAYETTE COUNTY) | CLAJON GAS CO | PRELIMINARY INDICATIONS POINT TO THE CARBURATION IN THE FUEL SYSTEM. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
129 | 1987-11-04 | KY | maintenance | UNKNOWN (FLOYD COUNTY) | KENTUCKY - WEST VIRGINIA GAS CO | PIPE BROKE IN 45DEGREE MITER WELD. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
130 | 1987-10-27 | FL | leaks and spills | UNKNOWN (SANTA ROSA COUNTY) | FLORIDA GAS TRANSMISSION CO | EXTERNAL CORROSION OVER ABOUT A 15 INCH AREA WITH PITTING AS DEEP AS 0.170" IS THE APPARENT CAUSE OF THE FAILURE. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
131 | 1987-08-28 | CA | other | UNKNOWN (SOLANO COUNTY) | PACIFIC GAS & ELECTRIC CO | CONTRACTOR EXCAVATING FOR NEW SUBDIVISION STRUCK LINE WITH A TRACTOR, ALLOWING GAS TO ESCAPE TO ATMOSPHERE. BUILDINGS WERE EVACUATED AND TRAFFIC REROUTED. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
132 | 1987-09-10 | LA | other | UNKNOWN ( COUNTY) | STINGRAY PIPELINE CO | SHRIMP BOAT WAS REPORTED IN AREA OF DAMAGE AT TIME OF LEAK. | 200000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
133 | 1987-09-15 | IL | leaks and spills | UNKNOWN (FRANKLIN COUNTY) | TRUNKLINE GAS CO | FAILURE OCCURRED IN INACTIVE CORROSIVE BLOTCH. | 60000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
134 | 1987-08-05 | TX | leaks and spills | UNKNOWN (HIDALGO COUNTY) | RIO GRANDE VALLEY GAS CO | OUR INITIAL REPORT STATED THE FAILURE OCCURRED AT 530 PSIG. HOWEVER, ATTACHED IS A COPY OF A PRESSURE CHART TAKEN FROM THE METER STATION JUST UPSTREAM OF THE RELIEF VALVE WHICH IS CALIBRATED IN PSIA. THIS CHART SHOWS THE FAILURE OCCURRED AT518 PSIA. THE DIFFERENCE IN ABSOLUTE AND GAUGE PRESSURE IN HIDALGO COUNTY IS 14.65 WHICH MEANS THE FAILURE OCCURRED AT APPROXIMATELY 503 PSIG. CONSIDERING THE CHART ACCURACY AND THE FACT THAT THE RELIEF VALVE FUNCTIONED PROPERLY DURING THETEST THE MORNING OF THE INCIDENT, WE HAVE CONCLUDED THE FAILURE OCCURRED JUST PRIOR TO THE RELIEF VALVE GOING OPEN. | 40000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
135 | 1987-08-24 | PA | leaks and spills | UNKNOWN (FOREST COUNTY) | NATIONAL FUEL GAS SUPPLY CORP | GENERAL CORROSION REDUCED WALL THICKNESS OF PIPE. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
136 | 1987-10-28 | MI | other | UNKNOWN ( COUNTY) | MICHIGAN CONSOLIDATED GAS CO (MICHCON) | OPERATOR IN PREPARING TO REMOVE PIG BALL FROM LINE ASSUMED THAT HE COMPLETELY BLEW DOWN RECEIVER. PRESSURE REMAINED IN THE RECEIVER AND THE CAP WAS REMOVED WITH PRESSURE REMAINING IN THE RECIEVER BODY. THE CAP BLEW OFF RESULTING IN INJURY OF TWO COMPANY PERSONNEL. ONE EMPLOYEE WAS RELEASED ON THE DAT OF THE ACCIDENT, THE OTHER WAS HOSPITALIZED UNTIL 10/31/87. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
137 | 1987-10-24 | AR | leaks and spills | UNKNOWN ( COUNTY) | ARKLA ENERGY RESOURCES | A SECTION OF "8" PIPE RUPTURED. | 12150 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
138 | 1987-10-14 | NM | other | UNKNOWN (SAN JUAN COUNTY) | EL PASO NATURAL GAS CO | ON WEDNESDAY, OCTOBER 14, 1987, AT 7:30 P.M. THE BLANCO "C" #2 TURBINE CONTROL CAB EXPLODED, WRECKING THE CONTROL SYSTEM WIRING, THE UNIT MOTOR FROM VARIOUS SYSTEM COMPONENTS RESULTED IN AN UNCONTROLLED LEAKAGE OF GAS FROM THE COMPRESSOR CASE THROUGH THE SEAL OIL SYSTEM INTO THE LUBRICATION OIL RESERVOIR UNDERNEATH THE ACCESSORY CAB WHERE GAS MIGRATED INTO THE CONTROL CAB AND IGNITED. | 500000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
139 | 1987-10-22 | TX | other | UNKNOWN (GULF OF MEXICO COUNTY) | TRANSCO GAS PIPELINE CORP | A LARGE TRAWLING NET AND CABLES WERE FOUND WRAPPED AROUND A 2" TAP VALVE. IT IS ASSUMED THAT THE NET WAS DRAGGED ACROSS THE PIPELINE AND DISLODGED THE 2" VALVE AND WELD-O-LET. | 66700 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
140 | 1987-11-18 | VA | other | UNKNOWN (SUFFOLK COUNTY) | COMMONWEALTH GAS PIPELINE CORP | FAILURE OCCURED WHILE D-6 DOZER WAS BEING OPERATED OVER THE PIPELINE. PIPE MAYHAVE BEEN HIT BY TRACK CLEAT. | 5000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
141 | 1987-10-27 | KY | other | UNKNOWN (FLOYD COUNTY) | COLUMBIA GAS TRANSMISSION CORP | A CONTRACTOR'S CONSTRUCTION CREW WAS REMOVING COVER FROM THE LINE. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
142 | 1987-11-02 | TX | other | UNKNOWN ( COUNTY) | ANR PIPELINE CO (AMERICAN NATURAL RESOURCE) |  | 500000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
143 | 1987-11-06 | WY | other | UNKNOWN (LINCOLN COUNTY) | NORTHWEST PIPELINE CORP | PROJECTS WERE NEARING COMPLETION TO REPLACE THE CONCRETE FOUNDATIONS AND INSTALLNEW PULSATION BOTTLES ON THE TWO REFRIGERATION COMPRESSORS, #1 CLARK AND #2 CLARK. A SCHEDULED, ONE DAY MAINTENANCE SHUT DOWN OF THE OIL PLANT BEGAN A 6:45AMON NOVEMBER 6,1987. NORTHWEST PIPELINE EMPLOYEES WERE PERFORMING MAINTENANCE ON THE #2 CLARK. TWO CONTRACTORS, ARROW INDUSTRIES, INC. AND ITS SUBCONTRACTOR TED MILLER CO., INC. WERE FINISHING WORK ON THE #1 CLARK. THEIR WORK INCLUDED POURING A GROUT CAP UNDER THE #1 CLARK AND REINSTALLING BLOCK VALVES IN THE BASEMENT OF THE #1 CLARK. AT 9:33AM, GAS RELEASED BY A SPARK FROM A VACCUM CLEANER NEAR THE BASEMENT. THE RESULTING FLASH FIRE INJURED SIX PERSONS, FOUR REQUIRING HOSPITALIZATION, AND MINOR DAMAGE TO THE BUILDING AND EQUIPMENT. ONE OF THE INJURED IS STILL HOSPITALIZED. THE MAIN FIRE WAS TWO INITIAL FLASHES THAT LASTED JUST SECONDS. ALL THE INJURIES OCCURRED DURING THESE FIRST FEW SECONDS. OTHER, SMALLER FIRES WERE EXTINGUISHED BY PLANT PERSONNEL WITHIN A FEW MINUTES. THE SOURCE OF THE GAS IS UNDER INVESTIGATION, BUT THOUGHT TO BE FROM LINES THAT WERE HABING BLINDS REPLACED BY VALVES FOLLOWING CONSTRUCTION WORK. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
144 | 1987-11-03 | TX | leaks and spills | UNKNOWN (NUECES COUNTY) | VALERO TRANSMISSION CO | AN EXTERNAL CORROSION PIT DEVELOPED IN THE CARRIER PIPE LOCATED INSIDE A CASING. LEAK WAS IN AN AREA OF DAMAGED COATING. THE PIPELINE WASA TAKEN OUT OF SERVIOCE AND A NEW SECTION OF PIPE WAS INSTALLED IN THE EXISTING CASING. | 10000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
145 | 1988-01-13 | NE | other | UNKNOWN (SHERIDAN COUNTY) | KN ENERGY INC (KANSAS NEBRASKA NATURAL GAS CO INC) | THE ATTACHED INCIDENT REPORT COVERS A LEAK THAT OCCURRED ON K N ENERGY, INC.'S (K N'S) 4-INCH TOP-OF-GROUND TRANMISSION PIPELINE IN SHERIDAN COUNTY, NEBRASKA ON JANUARY 13, 1988. IGNITION DID NOT OCCUR AND THERE WERE NO INJURIES OR FATALITIES AS A RESULT OF THE LEAK. SERVICE WAS TEMPORARILY INTERRUPTED TO 109 DOMESTIC AND 13 COMMERCIAL CUSTOMERS IN THE COMMUNITY OF GORDON, NEBRASKA AND ON THE RURAL ROUTES.THE LEAK WAS CAUSED BY AN OUTSIDE PARTY OPERATING SNOW REMOVAL EQUIPMEWNT. THEDAMAGED PROTION OF THE PIPELINE IS IN A CLASS I LOCATION AND WAS MARKED WITH PERMANENT LINE MARKERS. THE DAMAGED PORTION WAS PART OF A PIPELINE PATROL CONDUCTED ON APRIL 15, 1987. A PERMANENT REPAIR WAS ACCOMPLISHED BY REPLACING 20 FEET OF THE DAMAGED PIPELINE WITH PRETESTED PIPE OF EQUAL OR GREATER SPECIFICATIONS.TELEPHONIC REPORT OF THE ABOVE LEAK WAS TRANSMITTED TO ENSIGN CHERRY OF THE DEPARTMENT OF TRANSPORTATION AND TO MARGARET HARDER WITH THE NEBRASKA STATE FIRE MARSHAL'S DISTRICT OFFICE AT NORTH PLATTE, NEBRASKA AT 11:50 A.M. CDT ON JANUARY 13, 1988. UPDATED TELEPHONIC REPORTS WERE TRANSMITTED TO THE NEBRASKA STATE FIREMARSHAL'S OFFICE AT 3:30 P.M. CDT ON JANUARY 14, 1988 AND TO DOT AT 3:15 P.M. ON THE SAME DATE. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
146 | 1987-12-05 | WV | other | UNKNOWN (LEWIS COUNTY) | EQUITABLE GAS CO | CONTRACTOR CUT GAS SERVICE LINE WHILE TRENCHING TO INSTALL ELECTRIC CABLE. GASIGNITYED AND DESTROYED THE TRENCHING MACHINE. ( NO SECOND COPY).GE FIELD POOL LOCATED IN THE STONEWALL JACKSON LAKE PROJECT, LEWIS COUNTY, WESTVIRGINIA. THIS PROJECT IS UNDER THE AUSPICES OF THE U.S. ARMY CORPS OFF ENGINEERS, OHIO RIVER DIVISION. NATURAL GAS BLEW FOR APPROXIMATELY THIRTY-SIX HOURS UNTIL IT WAS DISCOVERED AT 0930 HOURS ON DECEMBER 7, 1987, AT WHICH TIME THE STORAGE POOL WAS SHUT-IN.A PRESSURE TRANSMITTER RELAYED THE PRESSURED DROP AT THE COPLEY RUN COMPRESSOR STATION LOCATED APPROXIMATELY FOUR MILES FROM THE RUPTURE. THE TWO OPERATING UNITS AND DEPARTMENT DIRECTLY INVOLVED TRANSPORTATION OPERATIONS, TRANSMISSION DEPARTMENT AND THE GAS CONTROL DEPARTMENT.INTERDEPARTMENTAL INVESTIGATION AND DISCUSSIONS ENSUED IMMEDIATELY AFTER DISCOVERY OF THE PRESSURE DROP. IT WAS ERRONEOUSLY DECIDED, AT THAT TIME, THAT THE PRESSURE DROP WAS DUE TO A FAULTY PRESSURE TRANSMITTER. THIS TRANSMITTER HAS HAD A HISTORY OF OPERATION AND MAINTENANCE PROBLEMS AND WAS SCHEDULED TO BE REPLACED.OTHER FACTORS CONTRIBUTING TO THE EXTENDED RESPONSE TIME WERE:1. REMOTE LOCATION. SINCE THE RUPTURE IS LOCATED IN A U.S. GOVERNMENT CONTROLLED AREA, THERE WERE NO PUBLIC ROADS OPEN OR HOUSES IN THE GENERAL VICINITY - NO ONE COULD HEAR OR SEE THE ESCAPING NATURAL GAS.2. THE NATURAL GAS DIDNOT IGNITE.3. THE RUPTURE OCCURED IN THE EVENING DURING THE MIDDLE OF THE WEEDEND. THERE WERE NO EQUITABLE PERSONNEL NOR DAM CONSTRUCTION WORKERS IN THE AREA TO HEAR OR WITNESS THE ESCAPING NATURAL GAS. ALSO, SINCE DEER HUNTING SEASON CLOSED THE EVENING OF DECEMBER 5, 1987, THERE WERE NO HUNTERS IN THE AREA.4. THE CAUSE OF THE WELD FAILURE IS CURRENTLY UNDER INVESTIGATION. ALL OXY-ACETYLENE WELDED PIPE IN THE SKIN CREEK STORAGE POOL IS SCHEDULED TO BE REPLACED ASSOON AS POSSIBLE.CONSTRUCTION IS CURRENTLY UNDERWAY TO REPLACE ALL OXY-ACETYLENE PIPE IN THE POOL. FURTHER, AN INVESTIGATIVE TASK FORCE HAS ALREADY SUBMITTED APRELIMINARY REPORT ON THE INCIDENT AND ADDITIONAL, INTERNAL RECOMMENDATIONS WILL BE FORTHCOMING PROMPTLY. | 128000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
147 | 1987-12-04 | OK | other | UNKNOWN ( COUNTY) | OKLAHOMA NATURAL GAS CO | COUNTY CUTTING NEW ROAD PUNCTURED GAS LINE. GRADER BURNED. OPERATOR WAS TREATED AND RELEASED FROM LOCAL HOSPITAL. | 25549 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
148 | 1987-12-14 | TN | other | UNKNOWN (SEVIER COUNTY) | EAST TENNESSEE NATURAL GAS CO | PROPERTY OWNER THOUGHT THE PIPELINE WAS DEEPER AND FAILED TO FOREWARN THE BULLDOZER OPERATOR OF THE EXISTENCE OFTHE PIPELINE. EXISTING STRUCTURE COUSING NATURAL GAS TO BLOW INTO CELLAR AREA AND EVENTURALLY WAS IGNITED AND EXPLODED. THE GAS COMPANY WAS NOTIFIED BY SOUTH HADLEY POLICE. | 25000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
149 | 1987-12-14 | CO | maintenance | UNKNOWN (ADAMS COUNTY) | PUBLIC SERVICE CO OF COLORADO | 1/2" NIPPLE USED FOR PRESSURE TAP BROKE AT PIPE THREADS BELOW VALVE. ESCAPING GAS WAS IGNITED BY AN UNKNOWN SOURCE RESULTING IN A FIRE THAT DESTROYED THE REGULATOR/METER STATION. CAUSE OF RUPTURE AND FIRE IS UNDER INVESTIGATION.PART C- 1/2" NIPPLE CRACKED AND BROKE AT PIPE THREAD. THE CAUSED OF FAILURE ISUNDER INVESTIGATION. NIPPLE WAS INSTALLED IN PRE-TESTED, FABRICATED STATION PIPING AFTER FIELD INSTALLATION. | 102000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
150 | 1987-12-11 | TX | leaks and spills | UNKNOWN (HARRIS COUNTY) | EXXON CO USA | INTERNAL CORROSION CAUSED BY SULFATE REDUCING BACTERIAL GROWTH.PART A- A CONTINUOUS CORROSION INHIBITOR INJECTION PROGRAM IS CURRENTLY IN PLACE. THIS PROGRAM WILL BE MIDIFIED TO INCLUDE BACTERIAL BATCH TREATMENT. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
151 | 1988-01-09 | TX | other | UNKNOWN (BURLESON COUNTY) | CLAJON GAS CO | VIBRATION OF TUBING CAUSED METAL FATIGUE & BREAKAGE IN SUPPLY TUBING & WAS IGNIGHTED BY FIRE IN REBOILER | 500 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
152 | 1988-01-09 | OK | other | UNKNOWN (BEAVER COUNTY) | COLORADO INTERSTATE GAS CO | ICE BUILD-UP ON THE OFFICE BUILDING WALL PLUGGED THE VENT ON THE REGULATOR SUPPPLYING GAS TO THE BUILDING (HEAT & HOT WATER). 26.7 PSIG GAS WENT TO THE FURNACE& HOT WATER HEATER, RESULTING IN AN EXPLOSION WHICH DESTROYED THE 33' X 58' SINGLE STORY BUILDING. THERE WERE NO PERSONNEL IN THE BUILDING AT THE TIME OF THE EXPLOSION. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
153 | 1987-12-30 | TX | other | UNKNOWN (WHEELER COUNTY) | PALO DURO PIPELINE CO | PIPELINE RUPTURED AT 100 PSIG WHILE BEING PRESSURED UP AFTER TIE-IN SHUTDOWN ATWHEELER COMPRESSOR STATION II. | 36000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
154 | 1987-12-23 | IL | other | UNKNOWN (CLINTON COUNTY) | NATURAL GAS PIPELINE CO OF AMERICA | PENDING METALLURGICAL ANALYSIS OF FAILED SECTION. FRACTURE OCCURRED AT A WELD CONNECTING AN 8" X 30" SADDLE TO A REINFORCING SLEEVE OF A BRANCH CONNECTION ASSEMBLY | 160000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
155 | 1987-07-24 | LA | other | UNKNOWN (ACADIA COUNTY) | FLORIDA GAS TRANSMISSION CO | TWO CONTRACTOR EMPLOYEES WORKING WITH A TORCH WERE BURNED WHEN THEIR TORCH IGNITED GAS VENTING FROM A SCRUBBER WASTE STORAGE TANK'S VENT LINE AT FGT'S COMPRESSOR STATION.. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
156 | 1988-01-05 | PA | leaks and spills | UNKNOWN (PIKE COUNTY) | COLUMBIA GAS TRANSMISSION CORP |  | 150000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
157 | 1988-01-27 | PA | maintenance | UNKNOWN (CAMERON COUNTY) | NATIONAL FUEL GAS SUPPLY CORP | NO REMARKS GIVEN. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
158 | 1988-01-09 | IL | maintenance | UNKNOWN (COOK COUNTY) | PEOPLES GAS LIGHT & COKE CO | FOR UNKNOWN REASONS, A SEGMENT OF H.P. STEEL PIPE EXPOSED ON A STRUCTURE OVER R.R. TRACKS, RUPTURED. THE PIPELINE SUPPLIES TWO LARGE CUSTOMERS. THE ONE SUPPLYTO THIS LINE CONTAINS AN AUTOMATIC VALVE WHICH COLSED AND SHUT OFF THE FOW OF GAS. THE GAS DID NOT IGNITE AND THERE WERE NO INJURIES. PRELIMINARY RESULTS FROM METALURGICAL EXAMINATIONS INDICATE THAT THE SECTION OF PIPE IN QUESTION HAS A HIGHER THAN SPECIFICATION CARBON CNTENT. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
159 | 1988-01-12 | TX | other | UNKNOWN (BRAZORIA COUNTY) | UNITED TEXAS TRANSMISSION CO | AFTER ISOLATING THE LINE, WE DUG UP THE PIPELINE LEAK AND OBSERVED A 3 FT. GOUGE AT APPROXIMATELY 11:00 ON THE DOW 20" LINE, APPARENTLY CAUSED BY A THIRD PARTYCONTRACTOR WORKING OVER OUR PIPELINE SYSTEM. A 4"X1/8" PORTION OF THE 3 FT. GOUGE ACTUALLY PENETRATED THE PIPELINE, CAUSING NTRUAL GAS TO ESCAPE. UNITED TEXAS IS PRESENTLY CONDUCTING AN INVESTIGATION INTO THE EVENTS SURROUNDING THIS LEAK. | 75000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
160 | 1988-01-14 | LA | maintenance | UNKNOWN (CAMERON COUNTY) | TENNESSEE GAS PIPELINE CO |  | 130000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
161 | 1988-01-27 | TX | leaks and spills | UNKNOWN (CHAMBERS COUNTY) | AMOCO GAS CO | BOLTS CONNECTING A 2" TAP VALVE TO 16" TRANSMISSION LINE HAD DETERIORATED AND ALEAK HAD OCCURRED.MAIN LINE UNDER CATHODIC PROTECTION. TAP VALVE LINE WAS NOT ON IDLE. | 5850 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
162 | 1988-01-19 | FL | other | UNKNOWN (PINELLAS COUNTY) | FLORIDA GAS TRANSMISSION CO | THE ENCLOSED INCIDENT REPORT FOR FLORIDA GAS TRANSMISSION CO. DESCRIBES A DIG-IN BY AN OUTSIDE PARTY WHICH OCCURRED JANUARY 19, 1988. AT TRHE TIME OF OCCURRENCE THIS APPEARED NOT TO BE REPORTABLE NOTIFIED ONJANUARY 19, 1988 AS A COURTESY.AS COSTS OF MAKING A PERMANENT REPAIR ACCRUED AND THE ESTIMATED GAS LOSS WAS CALCULATED, IT BECAME APPARENT THAT THE $50,000 CRITERIA HAD BEEN EXCEEDED. TELEPHONIC NOTICE TO THE NATIONAL RESPONSE CENTER WAS MADE FOLOWING THIS DTERMINATION. | 250000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
163 | 1988-02-11 | LA | other | UNKNOWN (ST CHARLES COUNTY) | BRIDGELINE GAS DISTRIBUTION CO | THE SEGMENT THAT FAILED WAS IN A CROSSING OF THE MISSISSIPPI RIVER. THE SEGMENTWAS ISOLATED WITH APPROXIMATELY 450 PSIG PRESSURE WHEN FAILURE OCCURRED. NO INSPECTION OF THE LINE TO DETERMINE CAUSE OF FAILURE IS POSSIBLE UNTIL THE RIVER REACHES A LOWER STAGE. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
164 | 1988-02-08 | CO | other | UNKNOWN (GARFIELD COUNTY) | NORTHWEST PIPELINE CORP | THE DELAY IN TELEPHONIC REPORTING WAS DUE TO ORIGINAL COST ESTIMATE BEING LESS THAN $50,000. | 87000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
165 | 1988-01-07 | OH | other | UNKNOWN (SUMMIT COUNTY) | EAST OHIO GAS CO |  | 90000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
166 | 1988-01-23 | PA | other | UNKNOWN (CAMBRIA COUNTY) | TEXAS EASTERN GAS PIPELINE CO | THE INCIDENT CONSISTED OF A LUBRICATING OIL FIRE IN A TURINE UNIT AT THE COMPRESSOR STATION. THE CAUSE OF THE INCIDENT IS UNDER INVESTIGATION. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
167 | 1988-02-21 | IL | other | UNKNOWN (WILL COUNTY) | ANR PIPELINE CO (AMERICAN NATURAL RESOURCE) | A RUNAWAY 18-WHEELED SEMI STRUCK AND DISLODGED TWO ABOVEDGROUND 12" FLANGED JOINTS AND IGNITED ESCAPING GAS. THE FIE CAUSED A SECONDARY PIPELINE FAILURE. A HOUSE LOCATED APPROXIMATELY 165' FROM TH FIE CENTER, CAUGHT FIRE AND WAS DESTROYED. THE DRIVER OF THE TRUCK DIED, BUT WE DO NOT KNOW WHETHER THIS OCCURRED BEFORE OR AT THE TIME OF THE ACCIDENT. | 750000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
168 | 1988-03-11 | TX | other | UNKNOWN (LUBBOCK COUNTY) | POWER TEX JOINT VENTURE | PRESSURE REGULATOR THAT IS PILOT OPERATED FAILED OPEN DUE TO THE FAILURE IN A DIAPHRAM IN THE CONTROL PILOT AND THUS CAUSE TEH DOWNSTREAM RELIEF VALVE TO GO OFF. A FIRE WAS STARTED BY STATIC ELECTRICITY OR SOME FOREIGN MATTER MOVING THROUGH THE RELIEF AND STRIKING METAL TO CAUSE A SPARK. | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
169 | 1988-03-11 | WV | leaks and spills | UNKNOWN (KANAWHA COUNTY) | CONSOLIDATED GAS TRANSMISSION CORP |  | 189600 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
170 | 1988-01-17 | KS | other | UNKNOWN (SEDGWICK COUNTY) | WILLIAMS NATURAL GAS CO |  | 4256 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
171 | 1988-03-11 | LA | other | UNKNOWN ( COUNTY) | ANR PIPELINE CO (AMERICAN NATURAL RESOURCE) |  | 200000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
172 | 1988-02-15 | LA | maintenance | UNKNOWN (JEFFERSON DAVIS COUNTY) | TENNESSEE GAS PIPELINE CO | PINHOLE LEAK IN LONGITUDINAL SEAM DUE TO MATERIAL DEFECT. | 67000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
173 | 1988-02-08 | CO | other | UNKNOWN (LOGAN COUNTY) | NATURAL GAS PIPELINE CO OF AMERICA | SEISMIC CREW USING A 5" AUGER GOUGED THE 36" PIPELINE. THERE WAS NO RELEASE OFGAS TO ATMOSPHERE. OPERATOR HAS REPLACED DAMAGED SECTION.TWO YEAR OLD "ONE CALL" SYSTEM EXISTS IS COLORADO. NATURAL HAS BEEN A MEMBER FOR ONE ONE-HALF YEARS. | 85000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
174 | 1988-03-21 | TX | leaks and spills | UNKNOWN (GALVESTON COUNTY) | ANR PIPELINE CO (AMERICAN NATURAL RESOURCE) |  | 130000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
175 | 1988-03-15 | TX | other | UNKNOWN (SMITH COUNTY) | LONE STAR GAS CO | CONTRACTOR EXCAVATING AND HAULING FILL DIRT FOR PROPERTY OWNER STRUCK LINE SEVERAL TIMES IN A 12 FT. SEGMENT ULTIMATELY CUTTING 1 1/4 & 3 3/4 HOLE IN PIPE WITHFRONT END LOADER.LINE MARKED AT HWY. 155 APPROX. 300' S.E. OF DAMAGE AREA. CONTRACTOR WORKING FOR PROPERTY OWNER WHO MUST HAVE BEEN AWARE OF LINE ON PROPERTY. | 16000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
176 | 1988-03-11 | TX | other | UNKNOWN (LUBBOCK COUNTY) | CABOT GAS SUPPLY CORP | DAMAGE RESULTED FROMFIE OF THRID PARTY'S FACILITIES. | 40000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
177 | 1988-03-22 | TX | maintenance | UNKNOWN (MATAGORDA COUNTY) | VALERO TRANSMISSION CO | CAUSE FO RUPTURE PENDING METALLURGICAL REPORT RESULTS. | 120000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
178 | 1988-04-01 | MO | other | UNKNOWN (CASS COUNTY) | PANHANDLE EASTERN PIPELINE CO | MOVEMENT OF THE BANK OF A RAIN-SWOLLEN CREEK ALLOWED A JOINT OF PIPE TO PARTIALLY SLIP OUT A COUPLING. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
179 | 1988-05-16 | OK | other | UNKNOWN (CADDO COUNTY) | DELHI GAS PIPELINE CORP | PIPELINE WAS BEING DERPESSURED DURING PIGGING OPERATION IN A ONTROLLED AND MONITORED PROCEDURE. AN ACCUMULATION OF NATURAL GAS WAS IGNITED BY AN UNKNOWN SOURCE, RESULTING IN A FLASH FIRE AND SEBSEQUENT EXPLOSION THEREBY CAUSING BOCILY INJURY AND PROPETY DAMAGE. | 30000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
180 | 1988-05-07 | MS | maintenance | UNKNOWN (DE SOTO COUNTY) | ANR PIPELINE CO (AMERICAN NATURAL RESOURCE) | FIVE FOOT LONG LAMINATION AT THE 9:00 POSITION. | 57000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
181 | 1988-04-27 | NM | other | UNKNOWN (SAN JUAN COUNTY) | EL PASO NATURAL GAS CO | ON APRIL 27, 1988, AT 8:50 A.M., AN EXPLOSION OCCURRED AT BLANCO "C" PLANT IN THE OIL SUMP OF THE #2 TURBINE. THIS TURBINE HAD NOT BEEN IN USE SINCE THE EXPLOSION AND FIRE THAT OCCURRED ON OCTOBER 17, 1987. SINCE THAT DATE, THE TURBINE HAD BEEN COMPLETELY OVERHAULED, THE COMPRESSOR SHAFT REPAIRED AND REBALANCED, ANDA NEW CONTROL SYSTEM INSTALLED. PRIOR TO RELEASING THE #2 TURBINE TO PLANT OPERATIONS, A 48-HOUR TEST RUN WAS TO BE COMPLETED. ATTEMPTS HAD BEEN MADE TO START THE TURBINE APRIL 26, 1988, BUT WERE NOT SUCCESSFUL. AFTER DEBUGGING OF CONTROLS, ETC., ANOTHER ATTEMPT WAS SCHEDULED FOR THE FOLLOWING MORNING. THE MORING OF APRIL 27, 9188, THE TURBINE HAD BEEN PLACED IN RATCHETING MODE. FOLLOWING APPROXIMATELY 25 MINUTES OF RATCHETING, THE EXPLOSION OCCURRED. THE FORCE OF THE EXPLOSION BLEW THE OIL SUMP HATCH DOOR OPEN AND OFF THE HINGES. A FLASH FIRE FOLLOWED THE EXPLOSION ESCAPING OUT OT THE SUMP THROUGH THE ACCESSORY CAB ON THE EAST AND WEST SIDES. EMPLOYEES OF EL PASO NATURAL GAS COMPANY AND FISH EMOLPYEES,ONE RECEIVED FIRST DRGREE BURNS TO HIS FACE AND THE OTHER A CONTUSED EARDRUM AND STRAINED MUSCLES IN THE NECK AND BACK. THESE INJURIES WEE OT LOST TIME INJURIES. THIS EXPLOSION IN CURRENTLY UNDER STUDY BY AN ACCIDENT INVESTIGATION TEAM.THE SOURCE OF IGNITION AD THE SOURCE OF FUEL HAVE NOT BEEN DETERMINED AT THIS TIME. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
182 | 1988-05-24 | ID | other | UNKNOWN (BANNOCK COUNTY) | NORTHWEST PIPELINE CORP | DIG IN BY FARMERS CONTRACTOR LANDLEVELING. | 75000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
183 | 1988-06-07 | KY | other | UNKNOWN (FLOYD COUNTY) | KENTUCKY - WEST VIRGINIA GAS CO |  | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
184 | 1988-06-10 | TX | leaks and spills | UNKNOWN ( COUNTY) | BLUE DOLPHIN PIPELINE CO | 250# ZINC BRACELETS ON 1/4 MILE SPACING USED DURING INITIAL CONSTRUCTION AND LINE WS BURIED FOUR FEET DEEP. RECTIFIER AND ANODE ADDED ON "A" PLATFORM IN 1969. RECTIFIER FUNCTION CHECKED OK 2-16-88. CABLES REPLACED 3/19/88.OFFSHORE OIL SHEEN REPORTED BY AMOCO TO MMS WAS REPORTED FOR INVESTIGATION TO IVORY PRODUCTION CO WHO OPERATES BLUE DOLPHIN PIPELINE FROM GA-288 TO FREEPORT, TX. INVESTIGATION REVEALED A CORROSION PIT WHICH WAS REPAIRED BY INSTALLING A SPLIT SLEEVE BOLT-ON, PLIDCO CLAMP, RATED 1000 PSI WP. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
185 | 1988-05-25 | LA | other | UNKNOWN ( COUNTY) | TENNESSEE GAS PIPELINE CO | PIPELINE IS LOCATED IN A KNOWN MUDSLIDE AREA. IT APPEARS THAT A MUDSLIDE CAUSED LEAK. | 60000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
186 | 1988-01-20 | NJ | other | UNKNOWN (BERGEN COUNTY) | TRANSCO GAS PIPELINE CORP | ON JANUARY 20, 1988 AN INCIDENT OCCURRED AT TRANSCONTINENTAL GAS PIPE LINE'S STATION 240 LNG PLANT THAT CAUSED DEFORMATION OF THE COLD BOX STRUCTURAL STEEL. AFTER THIS INCIDENT, AN INSPECTION OF THE PROCESS PIPING AND VESSELS INSIDE THE COLD BOX RESULTED IN THE DISCOVERY OF FOUR SMALL LEAKS IN AN ALUMINUM PLATE-FIN EXCHANGER(E-13). ADDITIONALLY, A CHEMICAL ANALYSIS F THE ATMOSPHERE INSIDE TH COLD BOX WAS MADE AFTER THE INCIDENT, BUT PRIOR TO THE INTERNAL INSPECTION. THIS ANALYSIS SHOWED THAT IN SOME PARTS OF THE COLD BOX THAT THERE WERE SUFFICIENT AMOUNTS OF OXYGEN (FROM AIR), ETHYLENE AND NATURAL GAS CONSTITUENTS PRESENT TO SUPPORT A LIMITED REGION OF COMBUSTION. IT IS BELIEVED THAT ADDITIONAL CONTRIBUTING FACTORS WERE NATURAL GAS INTERMITTENLY LEAKING FROM FLANGES ON EXCHANGERS E-8AND /OR E-9 IN THE COLD BOX AND AIR ENTERED THE COLD BOX DUE TO POOR PERFORMANCE OF THE NITROGEN PRUGE SYSTEM. ALTHOUGH THERE IS NO DIRECT EVIDENCE AS TO WHAT CAUSED THE DAMAGE TO THE COLD BOX,ANALYSIS SHOWS THAT A DEFLAGRATION OR MILD EXPLOSION PROBABLY OCCURRED IN A SMALL PORTION OF THE COLD BOX SPACE. HYPOTHETICALLY, THE SEQUENCE OF EVENTS WAS: 1) LOW LEAKAGE RATES OF EHTYLENE, 2) INTERMITTENT LEAKAGE OF NATURAL GAS, 3) PRESENCE OF OXYGEN (AIR), 4) A FLOW OF A GAS WHICH CREATED AN ELECTROSTATIC CHARGE, 5) A SPARK AND 6) COMBUSTION. | 85000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
187 | 1988-05-20 | TX | other | UNKNOWN (BROOKS COUNTY) | VALERO INTERSTATE TRANSMISSION CO | STRUCTURE PIPE FAILURE DUE TO POSSIBLE STRESS CORROSION, NO TEST RESULT YET. | 230000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
188 | 1988-06-16 | TX | leaks and spills | UNKNOWN (ECTOR COUNTY) | PHILLIPS PETROLEUM CO | THIS LINE WAS PURCHASE FROM EL PASO NATURAL GAS IN JANUARY, 1987. AT THAT TIME,CATHODIC PROTECTION WAS ON THE LINE AN IS PROTECTED AT THIS TIME.LOCALIZED PITTING DUE TO INTERNAL CORROSION RESULTED IN RUPTURE. H2S EMISSION FORCED EVACUATION OF 11 OCCUPANTS AT TEXACO'S PENWELL FIELD OFFICE. NO INURIES OCCURRED OR HOSPITALIZATION REQUIRED. | 11500 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
189 | 1988-06-02 | TX | other | UNKNOWN (FRIO COUNTY) | VALERO TRANSMISSION CO | THIS INCIDENT WAS THE RESULT OF A ROAD GRADER HITTING THE PIPELINE AND SERVERING IT. THIS SECTION OF PIPE WAS REMOVED AND A NEW SECTION OF PIPE WAS INSTALLED.THE PIPELINE HAS BEEN RETURNED TO SERVICE. | 1500 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
190 | 1988-07-25 | TN | other | UNKNOWN (SHELBY COUNTY) | MEMPHIS LIGHT GAS & WATER DIVISION | CONTRACTOR DAMAGED SERVICE LINE WHILE BACKFILLING A DITCH THAT WAS CUT TO FACILITATE THE INSTALLATION OF A 66" WATER TRANSMISSION MAIN.HE BUILDING WAS OF DOUBLE BRICK WALL CONSTRUCTION WITH WOOD RAFTERS AND SHEETING, AND ASPHALT ROOF. THE BUILDING FIRE DAMAGED INSTRUMENT LINES AND FITTINGS ENTERING THE SOUTH GABLE, CAUSING GAS TO ESCAPE FROM THESE LINE AND FUELING THE FIRE. THE HEAT FROM THE BLAZE EXPANDED THE FLANGE BOLTS IN THE REGULATOR RUNS AND DESTROYED THE GASKET MATERIAL, ALLOWING MORE GAS TO ESCAPE AND FUEL THE FIRE FURTHER. ULTIMATELY, A 6" WELDED ELBOW ON AN INLET STUB RUPTURED, BLOWING OUT THE SOUTH WALL OF THE BUILDING AND GREATLY INTENSIFYING THE FIRE. FLAME AND HEAT FROM THE REGULATOR STATION FIRE WERE DIRECTED TOWARD METERING FACILITIES OWNED AND OPERATED BY TEXAS GAS TRANSMISSION CORP (TGT), CAUSING A 10" RISER TO FAIL AND RUPTURE. THE HEAT FROM THE METER STATION FIRE CAUSED AN 8" RUN-AROUND PIPE ON A TGTBLOCK VALVE TO FAIL AND ALLOW ADDITIONAL GAS TO ESCAPE. THE CONFLAGRATION COMPLETELY DESTROYED THE STATION'S METERING AND REGULATING FACILITIES AND ASSOCIATED INSTRUMENTATION EQUIPMENT. THERE WERE NO INJURIES OR FATALITIES. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
191 | 1988-07-25 | TN | other | UNKNOWN (SHELBY COUNTY) | TEXAS GAS TRANSMISSION CORP | LIGHTNING STRUCK THE POWER SUPPLY AND/OR REGULATOR BUILDING OWNED BY MEMPHIS, LIGHT, GAS AND WATER (MGL&W). BUILDING WAS DOUBLE BRICK WALL WITH WOOD RAFTERS, WOOD SHEETING AND ASPHALT ROOFING. HEAT OR FALLING MATERIAL FROM ROOF STRUCTURECAUSED STEEL TUBING FITTINGS FOR CONTROL LINE TO EXPAND, LEAK, AND FUEL THE FIRE. THE ADDED HEAT EVENTUALLY RELAXED THE FLANGE BOLTS AND NUTS, AND CAUSED THE FLANGE GASKETS TO LEAK AND FUEL THE FIRE MORE. A 6" PIPE ELL INSIDE THE REGULATOR BUILDING RUPTURED. WHEN THE 6" ELL FAILED, THE BUILDING WAS DESTROYED BY ANEXPLOSION. HEAT FROM MLGW'S REGULATOR STATION WAS DIRECTED TOWARD A 10" RISER ON TEXAS GAS'S METER STATION AND CAUSED IT TO EXPAND AND FAIL. THE HEAT FROM THETXG METER STATION WAS DIRECTED TOWARD THE BLOCK VALVE AREA AND CAUSED THE 8" RUN-AROUND PIPE AND THE VALVE EXTENSION TO FAIL. | 500000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
192 | 1988-07-20 | TX | other | UNKNOWN (BEXAR COUNTY) | VALERO TRANSMISSION CO | ALAMO CEMENT COMPANY CONSTRUCTING ROAD BESIDE RIGHT-OF-WAY. D-9 DOZER HIT 6" PIPELINE CAUSING 12" RIP IN PIPE; ALSO DAMAGING OVER 20 FEET OF PIPE WITH RIPPER. | 11500 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
193 | 1988-08-03 | OK | other | UNKNOWN (LATIMER COUNTY) | OZARK GAS PIPELINE CORP | SOME OF THE PIPELINE MARKER FLAGS WERE PULLED UP OR DAMAGED BY LIVESTOCK IN THEAREA. INITIAL NOTIFICATION TO OZARK WAS DELAYED THREE HOURS DUE TO CONFUSION BY THE DRILLING CREW AND NOTIFICATION TO THE WRONG PIPELINE COMPANY.OZARK 20" TRANSMISSION LINE WAS PUNCTURED BY CGG SEISMIC DRILLING RIG. THE DRILL CREW MISTAKENLY DRILLED AT THE WRONG LOCATION BY MISREADING NUMBERS ON THEIR SURVEY FLAGS. THE CREW DID NOT SEE OZARK'S PIPELINE MARKER FLAGS WHICH WERE NEARBY. (SOME FLAGS HAS BEEN PULLED UP BY LIVESTOCK IN THE AREA). | 45000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
194 | 1988-09-03 | LA | other | UNKNOWN ( COUNTY) | ACADIAN GAS PIPELINE SYSTEM |  | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
195 | 1988-07-25 | TX | other | UNKNOWN (STARR COUNTY) | VALERO TRANSMISSION CO | FARM TRACTOR PLOWING FIELD HIT LINE WITH PLOW. GAS LINE WAS VERY SHALLOW AND EXPOSED DUE TO EROSION. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
196 | 1988-08-19 | LA | other | UNKNOWN (CAMERON COUNTY) | TEXAS GAS TRANSMISSION CORP | TEXAS GAS 6" LAKESSIDE-MALLARD BAY PIPELINE PARALLELS THE SOUTH SIDE OF THE INTRACOASTAL CANAL IN LOUISIANA AND CROSSES A CHANNEL FROM THE INTRACOASTAL CANAL TO GRAND LAKE. APPARENTLY THE PROP FROM A TUGBOAT PUSHING A HEAVY LOAD THROUGH THE CHANNEL HIT OUR PIPELINE, WHICH HAD APPROXIMATELY THREE FEET OF COVER. THE GOUGE WAS APPROXIMATELY 14" LONG AND .200" DEEP. THE PIPE FAILED LATER, AND THE RUPTURE WAS ABOUT 2 FEET LONG. LIGHTNING SET THE GAS ON FIRE, BUT NO ONE WAS NEAR, SO THERE WERE NO INJURIES OR OUTSIDE PROPERTY DAMAGE. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
197 | 1988-08-13 | PA | other | UNKNOWN (BERKS COUNTY) | TEXAS EASTERN GAS PIPELINE CO | SEVERAL MODIFICATIONS WERE BEING MADE TO UPGRADE TURBINE UNIT NO. 1 AT BERNVILLE COMPRESSOR STATION WHEN THE INCIDENT OCCURED. THE STATION WAS OUT OF SERVICE AND ALL GAS HAD BEEN VENTED FROM THE COMPRESSOR UNIT PIPING. A GAUGE PANEL WAS BEING CUT AWAY FROM THE TURBINE SKID AT THE TIME OF THE INCIDENT. THE AREA AROUNDTHE GAUGE PANEL WAS CHECKED FOR THE PRESENCE OF NATURAL GAS PERIODICALLY PRIOR TO CUTTING AND NO GAS WAS INDICATED. A SMALL EXPLOSION OCCURRED, PROBABLY IN ORNEAR A NON-FLAMMABLE LUBE OIL RESERVOIR TO WHICH THE GAUGE PANEL WAS ATTACHED.UNDETECTED GAS IS SUSPECTED AS THE CAUSE. | 45000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
198 | 1988-09-11 | LA | other | UNKNOWN ( COUNTY) | SOUTHERN NATURAL GAS CO | ON SEPTEMBER 8, 1988, THE MAIN PASS 77 STRUCTURE WAS SHUT- IN AND EVACUATED FORHURRICAN "FLORENCE". ON SEPTEMBER 11, 1988, THE PLATFORM WAS REMANNED. AN ATTEMPT TO BRING THE GAS LINE IN-SERVICE WAS ABORTED DUE TO LEAKAGE IN THE RISER. SUBSEQUENTLY, THE GULF WAS RE-EVACUATED FOR HURRICANE "GILBERT". AFTER THE HURRICANE " GILBERT" THREAT WAS OVER, SURVEYS AND DIVING INVESTIGATIONS WERE MADE WHICH INDICATE A MUDSLIDE ON THE OCEAN FLOOR OCCURRED NEAR THE MAIN PASS 77 STRUCTURE. THIS MUDSLIDE LATERALLY DISPLACED AOUT 2500'+ OF THE 10-INCH LINE AND PROVIDED THE NECESSARY FORCE TO BREAK THE RISER ATTACHED TO THE PLATFORM. THE PRESSURE ON THIS LINE,WHICH WAS NOT IN SERVICE AT THE TIME OF THE INCIDENT WAS 1050 PSI(+),FURTHER INVESTIGATIONS HAVE VERIFIED A CHECK VALVE INSTALLED IN THE LINE ATTHE BASE OF THE RISER CONTANED THE PRESURE ON THE PIPELINE AND THE ONLY DISCHARGE CAME FROM THE ISOLATED RISER PIPING. | 3389000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
199 | 1988-09-10 | TX | leaks and spills | UNKNOWN (WATERS COUNTY) | ANR PIPELINE CO (AMERICAN NATURAL RESOURCE) |  | 75000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
200 | 1988-09-17 | LA | other | UNKNOWN ( COUNTY) | TENNESSEE GAS PIPELINE CO | THE VALVE GUARD WAS PULLED OFF OF THE SIDE VALVE ASSEMBLY, POSSIBLY BY A CABLE FROM A PASSING BOAT. THE VALVE GUARD HUNG ON THE OPERATOR ON THE 12" CHECK VALVE, SHEARING OFF THE OPERATOR AND BREAKING THE 1/2" NIPPLE. | 97000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
201 | 1988-08-31 | NE | other | UNKNOWN (GAGE COUNTY) | NATURAL GAS PIPELINE CO OF AMERICA | TORCH IGNITED NATURAL GAS THAT HAD LEAKED INTO THE ENGINE CRANKCASE THROUGH THE COMPRESSOR PACKINGS. EMPLOYEES WERE USING A TORCH TO HEAT SPROCKET HUBS FOR REMOVAL FROM CRANKCASE. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
202 | 1988-09-02 | LA | leaks and spills | UNKNOWN (ST CHARLES COUNTY) | TEXACO INC | PINHOLE, ISOLATED LEAK DUE TO EXTERNAL CORROSION BELIEVED TO HAVE BEEN CAUSED BY STRAY CURRENT. | 12000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
203 | 1988-09-04 | TX | leaks and spills | UNKNOWN (REFUGIO COUNTY) | FLORIDA GAS TRANSMISSION CO | THE ENCLOSED INCIDENT REPORT FOR FLORIDA GAS TRANSMISSION CO. DESCRIBES A RUPTURE WHICH OCCURRED ON SEPTEMBER 4TH, 1988. AFTER CALCULATIONS HAD BEEN MADE TO DETERMINE THE AMOUNT OF NATURAL GAS RELEASED TO THE ATMOSPHERE, IT WAS DETERMINED THAT THE $50,000 CRITERIA HAD BEEN EXCEEDED. TELEPHONIC NOTICE TO THE NATIONAL RESPONSE CENTER WAS MADE FOLLOWING THIS DETERMINATION. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
204 | 1988-09-01 | TX | maintenance | UNKNOWN ( COUNTY) | TENNESSEE GAS PIPELINE CO | 6" CRACK IN SADDLE PAD SIDE VALVE. | 200000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
205 | 1988-08-17 | OH | other | UNKNOWN (HANCOCK COUNTY) | COLUMBIA GAS TRANSMISSION CORP | PIPELINE PULLED-OUT OF UNDETECTED ORIGINAL COUPLING AFTER COMPLETING REPLACEMENT PIPELINE TIE-IN AND PRESSURIZING LINE. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
206 | 1988-09-01 | NM | other | UNKNOWN (SAN JUAN COUNTY) | GAS CO OF NEW MEXICO | FAILURE OF THE DEPARTMENT OF ENERGY (D.O.E.) MAINLINE, PRIMARILY A BARE LINE, WAS CAUSED BY EXTENSIVE CORRISIVE IN A SECTION OF WRAPPED PIPE. SEVERAL SCRATCHES WERE FOUND ON THIS SECTION WHICH HAD RESULTED IN EXTENSIVE COATING DAMAGE AND ACCELERATED CORROSION REDUCING THE PIPE WALL TO PAPER THICKNESS. THE DEEPEST GROOVE CONTAINED A ONE INCH (1") PORTION THAT HAD CORRODED COMPLETELY THROUGH THE PIPE WALL CAUSING THE RUPTURE. IT IS APPARENT THAT THESE GROOVES AND SCRATCHES WERE ACTUALLY CLAW MARKS CAUSED BY A BACKHOE, THIRD PARTY DAMAGE THAT WENT UNREPAIRED.FURTHER INVESTIGATION REVEALED THAT THE D.O.E., OWNER OF THE MAINLINE, HAD HAD A CLOSE INTERVAL CATHODIC PROTECTION SURVEY DONE WITH A SUBSEQUENT INSTALLATIN OF ANODES AND/OR TEST STATIONS ON THIS LINE IN 1984. IT IS ASSUMED THAT THE DAMAGE TO THE MAINLINE OCCURRED THEN. | 72367 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
207 | 1988-08-16 | TX | leaks and spills | UNKNOWN (HARRIS COUNTY) | AMOCO GAS CO | LEAK WAS CAUSED BY ATMOSPHERIC CORROSION AT A COATING HOLIDAY ON CARRIER PIPE IN THE CASING. | 1760 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
208 | 1988-08-24 | TX | maintenance | UNKNOWN (HARRIS COUNTY) | UNITED TEXAS TRANSMISSION CO | DISCOVERED LEAK HAD OCCURRED IN RUBBER OF DRESSER COUPLE ON 8-24-88, INITIALLY THOUGHT COULD BE REPAIRED WITH A BAND CLAMP. ON EVENING OF 8/24, DECIDED LINE NEEDED TO BE SHUT IN FOR REPAIR. | 5000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
209 | 1988-09-12 | TX | other | UNKNOWN (FOARD COUNTY) | LONE STAR GAS CO | SERVICE METER 200 FEET WEST OF WHERE LINE WAS DAMAGED PERMANENT LSG MARKER 2000FEET OF WHERE LINE WAS DAMAGED. | 8260 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
210 | 1988-09-29 | LA | other | UNKNOWN (WASHINGTON COUNTY) | FLORIDA GAS TRANSMISSION CO | LIGHTNING STRIKE BROKE STAINLESS STEEL TUBING GAUGE LINE AND IGNITED GAS. PIPELINE FACILITIES DAMAGED BY FIRE; ELECTRONIC FACILITIES DAMAGED BY ELECTRICAL DISCHARGE. | 51500 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
211 | 1988-08-06 | TX | other | UNKNOWN (FORT BEND COUNTY) | UNITED TEXAS TRANSMISSION CO | LANDOWNER WAS PLOWING FIELD AND STRUCK OUR PIPELINE CAUSING GOUGE IN PIPE. | 7500 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
212 | 1988-10-16 | TX | other | UNKNOWN (DENTON COUNTY) | LONE STAR GAS CO | LAND OWNER WAS CLEARING BRUSH ON PROPERTY WITH A TRACK LOADER AND PUNCTURED PIPELINE. INFLICTED 4" DIAMETER HOLE IN PIPELINE. REPAIR MADE BY TAKING LINE OUT OF SERVICE AND REPLACING DAMAGED PIPE. | 9500 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
213 | 1988-10-06 | TX | other | UNKNOWN (CANTON COUNTY) | LONE STAR GAS CO | 3- INCH PIPELINE HIT BY TP&L POWER DIGGER DIGGING PIER HOLES TO INSTALL H-FRAM POWER LINES CUTTING 2"X6" HOLE IN TOP QUARTER OF PIPE. | 15000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
214 | 1988-08-28 | TX | leaks and spills | UNKNOWN (WEBB COUNTY) | VALERO TRANSMISSION CO | THIS INCIDENT WAS THE RESULT OF INTERNAL CORROSION ON OUR RURAL GATHERING PIPELINE. THE LINE WAS TAKEN OUT OF SERVICE AND THIRTY (30) FEET OF PIPE WAS REPLACED. THE LINE WAS RETURNED TO SERVICE. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
215 | 1988-10-30 | TN | leaks and spills | UNKNOWN (PERRY COUNTY) | TENNESSEE GAS PIPELINE CO | EXTERNAL GENERAL CORROSION APPROXIMATELY 24" LONG X .180" - .230" DEEP. APPROXIMATELY AT THE 5:00 POSITION. | 150000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
216 | 1988-10-22 | TX | leaks and spills | UNKNOWN (SAN JACINTO COUNTY) | TENNESSEE GAS PIPELINE CO | THE INCIDENT WAS CONCLUDED TO BE CAUSED PRIMARILY BY STRESS CORROSION CRACKING (SCC). A SMALL CLUSTER OF CRACKS WHICH APPEARS TO BE SCC WAS FOUND ON A BURNED PIECE OF RUPTURED PIPE. | 120000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
217 | 1988-11-21 | TX | other | UNKNOWN (ECTOR COUNTY) | PHILLIPS PETROLEUM CO | 18" U GAS PIPELINE WAS BEING CLEANED BY PIGGING OPERATION. TWO RIVERS CONSTRUCTION CO., THE CONTRACTOR THE PROJECT, ALLOWED 6-INCH DRAIN LINE TO THE FRAC TANKTO COME LOOSE. SIDRO MORENO WAS HOSPITALIZED W/BROKEN FOREARM AND CUT ON FOREHEAD. ALBERT GARZA WAS GIVEN A BREATHING TREATMENT AND RELEASED. ISREAL LUNA WAS GIVEN BREATHING TREATMENT AND HOSPITALIZED OVERNIGHT FOR OBSERVATION. THE LOCATION OF THE INCIDENT IS NOT JURISDICTIONAL; HOWEVER, A PORTION OF THE LINE IS JURISDICTIONAL. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
218 | 1988-11-08 | IL | other | UNKNOWN (WILL COUNTY) | ANR PIPELINE CO (AMERICAN NATURAL RESOURCE) | LOW PRESSURE INSTRUMENT GAS VENTING FROM TRANSDUCERS IN CONTROL PANEL INSIDE THE METER BUILDING FOUND ITS WAY THROUGH ELECTRICAL CONDUIT INTO THE COMPUTER ROOM, IGNITED AND CAUSED A SMALL FIRE. | 125000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
219 | 1988-08-20 | LA | leaks and spills | UNKNOWN (PLATFORM COUNTY) | CHEVRON USA INC | THE 20" RISER WAS PROTECTED IN THE SPLASH ZONE VIA 26" CASING WITH TEH ANNULUS FILLED WITH COCRETE. THE 26" CASING TERMINATED ROUGHLY 10' ABOVE THE WATERLINE.THE CONCRETE WAS NOT ISOLATED FROM THE ENVIRONMENT AT THE 26" TERMINATION POINT. CONTINUAL WETTING OF THE CONCRETE RESULTED IN TEH CONCRETE BECOMING CHANNELED, THUS TRAPPING WATER NEXT TO THE 20" RISER. THE RISER SUFFERED SEVERE PITTING ALONG THE CHANNEL, AND SUBSEQUENT SANDBLASTIG CREATED A HOLE AT THIS AREA. | 70000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
220 | 1988-10-26 | WA | other | UNKNOWN (GRANT COUNTY) | NORTHWEST PIPELINE CORP |  | 24000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
221 | 1988-11-09 | IL | other | UNKNOWN (COOK COUNTY) | NORTHERN ILLINOIS GAS CO | WHILE PURGING GAS FROM A PIPELINE PRIOR TO A TIE - IN, THE GAS WAS IGNITED BY AN UNKNOWN SOURCE ( SUSPECTED STATIC ELECTRICITY). THE HEAT MELTED OVERHEAD ELECTRIC LINES CAUSING THEY TO FAIL AND FALL TO THE GROUND. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
222 | 1988-09-23 | TX | other | UNKNOWN (JIM WELLS COUNTY) | VALERO INTERSTATE TRANSMISSION CO |  | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
223 | 1988-10-20 | IL | other | UNKNOWN (LAKE COUNTY) | NORTH SHORE GAS CO | CONTRACTOR GRADING SITE FOR ANEW PARKING AREA PIERCED 24" STEEL MAIN WITH TOOTHOF BULLDOZER. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
224 | 1988-10-22 | WV | other | UNKNOWN (RANDOLPH COUNTY) | COLUMBIA GAS TRANSMISSION CORP | THE DEHYDRATION PLANT EXPLOSION AND RESULTING FIRE WHICH DESTROYED TWO GLYCOL HEATER; A GAS/GLYCOL SEPARATOR; A GLYCOL ACCUMULATOR TANK; FOUR GLYCOL PUMPS; ALLASSOCIATED PIPING, VALVES, REGULATORS AND FITTINGS; AND THE EQUIPMENT ENCLOSUREMADE DETERMINING THE ACTUAL CAUSE IMPOSSIBLE. THE PRESUMED CAUSE IS THAT DIRT OR FOREIGN MATTER CAUSED AN AUTOMATIC FLOAT DRAIN ASSEMBLY ON A BALSTON A-60 FILTER TO MALFUNCTION IN THE OPEN POSITION. THE FILTER WAS USED TO REMOVE GLYCOL, NOT REMOVED BY THE FUEL SCRUBBER, FROM GAS SCAVANGED VIA OF THE OF TEH GAS/GLYCOL SEPARATOR FOR THE GLYCOL HEATER FUEL GAS. (SEE FIGURE 1) THIS ALLOWED ALL THEGLYCOL TO BLOW FROM THE FILTER DRAIN, AND THEN 30 PSIG GAS TO ESCAPE. THE ESCAPING GAS THEN ACCUULATED IN THE EQUIPMENT ENCLOSURE UNTIL IT WAS IGNITED BY THE HEATER PILOTS. THE RESULTING HEAT FROM THE EXPLOSION AND FIRE MELTED THE NITRILE SEAT ND DEAPHRAM IN A FISHER 630 NREGULATOR ALLOWING 760 PSIG GAS TO FEED THE FIRE. | 250000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
225 | 1988-11-12 | LA | other | UNKNOWN (STATE WATERS COUNTY) | TENNESSEE GAS PIPELINE CO | CONDITION OF PIPE INCIDATES A DREDGE OR DRILLING RIG HIT PIPELINE AND DAMAGED OVER 50 FEET, 37 FEET OF WHICH WAS CAUSED WHEN PIPE RUPTURED. THE RESPONSIBLE PARTY HAS NOT BEEN LOCATED. | 80000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
226 | 1988-10-24 | TX | other | UNKNOWN (DIMMIT COUNTY) | VALERO TRANSMISSION CO | DOZER OPERTOR DID NOT NOTIFY US BEFORE DIGGING, BUT STATED HE WAS AWARE PIPE WAS THERE BECAUSE OF SIGNS. HE ASSUMED LINE WAS BURIED DEEPER. | 1200 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
227 | 1988-11-28 | TX | other | UNKNOWN (GALVESTON COUNTY) | PHILLIPS PETROLEUM CO | DOZER WITH HYDRAULIC EXTENDED MOWER STRUCK NEARBY PROPANE LINE WHICH INGITED. HEAT FROM ORIGINAL RUPTURE CAUSED 10" ETHYLENE LINE TO EXPLODE AND BURN. | 70000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
228 | 1988-11-25 | AR | leaks and spills | UNKNOWN (OUACHITA COUNTY) | ARKLA ENERGY RESOURCES | TRANSMISSION LINE RUPUTURED AT CREEK CROSSING. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
229 | 1988-11-29 | LA | other | UNKNOWN (BIENVILLE COUNTY) | BEAR CREEK STORAGE CO |  | 54900 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
230 | 1988-12-09 | NE | other | UNKNOWN (THAYER COUNTY) | KN ENERGY INC (KANSAS NEBRASKA NATURAL GAS CO INC) | THE PIPELINE WS HIT BY AN OUTSIDE PARTY OPERATING A BULLDOZER. THE DAMAGED PORTION OF THE PIPELIN IS IN A CLASS I LOCATION AND WAS MARKED WITH PERMANENT LINE MARKER. A PERMANENT REPAIR WAS COMPLETED BY REPLACING FIVE (5) FEET OF THE DAMAGED PIPELINE WITH PRETESTED PIPE OF EQUAL OR GREATER SPECIFICATION. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
231 | 1988-11-17 | TX | other | UNKNOWN ( COUNTY) | ANR PIPELINE CO (AMERICAN NATURAL RESOURCE) |  | 1785 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
232 | 1988-11-10 | CA | maintenance | UNKNOWN (LOS ANGELES COUNTY) | SOUTHERN CALIFORNIA GAS CO |  | 72000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
233 | 1988-12-06 | IN | other | UNKNOWN (OWEN COUNTY) | TEXAS GAS TRANSMISSION CORP | ON DECEMBER 6, 1988, AT 8:47AM., A CONTRACTOR WAS GRINDING UP TREE BRANCHES ON TEXAS GAS RIGHT-OF-WAY WITH HYDRO-AX EQUIPMENT AND HIT OUR ABOVEGROUND PIPE. THE BLADE ON THE HYDRO-AX PUT A 4 1/2" BY 1 1/2" HOLE IN THE PIPELINE. NO ONE WASHOSPITALIZED, AND ONLY 36 CUSTOMERS WERE WITHOUT GAS UNTIL 7:00 PM. OF DECEMBER6, 1988. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
234 | 1988-12-07 | LA | leaks and spills | UNKNOWN ( COUNTY) | NATURAL GAS PIPELINE CO OF AMERICA | A WORK CREW FLYING BACK FROM A PLATFORM HAD OBSERVED BUBBLING, I.E. A RELEASE OF GAS. THE LINE HAS BEEN SHUT-IN, BUT INCLEMENT WEATHER IS DELAYING REPAIRES. THEREFORE, WE ARE ISSUING THIS REPORT BASED ON PRELIMENARY INFORMATION. ADDITIONAL INFORMATION WILL BE PROVIDED TO YOU AS SOON AS POSSIBLE. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
235 | 1988-11-28 | TX | other | UNKNOWN (GALVESTON COUNTY) | VALERO TRANSMISSION CO | AT APPROXIMATELY 2:00 PM. A TRACTOR MOWER STRUCK A PHILLIPS PETROLEUM PIPELINE WHICH CAUSED EXPLOSION WHICH IN TURN CAUSED OTHER PIPELINES TO RUPTURE AND EXPLODE. THIS CAUSED OUR PIPELINE TO RUPTURE. | 110000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
236 | 1988-08-26 | WY | leaks and spills | UNKNOWN ( COUNTY) | WESTERN TRANSMISSION CORP | WHEN THE PIPE WAS INITIALLY INSTALLED INTO THE DITCH, WHAT APPEARS TO HAVE OCCURRED WAS THAT THE APING MACHINE MALFUNCTIONED IN THIS AREA AND DID NOT OVERLAP THE TAPE WHICH LEFT BARE PIPE OF APPROXIMATELY 1/4/ INCH WIDE THE ENTIRE CIRCUMFERENCE OF THE PIPE--APPROXIMATELY 50 FEET LONG. AT THE EXACT POINT OF THE CORROSION LEAK, THE PIPE CRADLE APPEARED TO HAVE DAMAGED THE COATING WHILE NEGOTIATINGA BEND. BOTH PROBLEMS ATTRIBUTED TO THE LEAK. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
237 | 1988-12-15 | TX | other | UNKNOWN (COLLIN COUNTY) | GARLAND, CITY OF | BLOW DOWN NEW PIPELINE PRIOR TO FLOWING GAS. | 1600 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
238 | 1988-04-18 | LA | leaks and spills | UNKNOWN (ST MARY COUNTY) | LOUISIANA INTRASTATE GAS CORP | PIPELINE WAS SHORTED TO ANOTHER LINE IN THE SAME RIGHT OF WAY AND WAS RECIEVINGINADEQUATE CATHODIC PROTECTION AT THAT LOCATION. | 15000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
239 | 1988-12-23 | LA | other | UNKNOWN (LA SALLE COUNTY) | LOUISIANA INTRASTATE GAS CORP | TIMBER CUTTING CREW WAS USING A DOZER TO PREPARE ROAD IN THE IMMEDIATE VICINITYOF THE PIPELINE. DOZER OPERATOR ALLOWED BLADE TO GOUGE PIPELINE. | 5000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
240 | 1988-12-31 | MS | other | UNKNOWN (NOXUBEE COUNTY) | SOUTHERN NATURAL GAS CO | CONTINUED RAIN CAUSED THE GROUND SURROUNDING THE PIPELINE TO BECOME SATURATED AND ALLOWED THE PIPE TO SHIFT, RESULTING IN THE PIPE PULLING OUT OF THE MECHANICAL COUPLING. | 220000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
241 | 1989-01-11 | TX | other | UNKNOWN (PALO PINTO COUNTY) | SOUTHWESTERN GAS PIPELINE INC | CONTRACTOR PLOWING IN TELEPHONE CABLE FOR SUTHWESTERN BELL TELEPHONE CO. FAILEDTO OBSERVE PIPELINE MARKING OF PAINTED CROSS FENCE AND DID NOT CALL OPERATOR FOR LINE LOCATION AND DEPTH. THREE FENCE POSTS PAINTED WITH THE COMPANIES COLORS WERE 10 FEET 6 INCHES FROM WHERE PIPELINE WAS HIT. PIPELINE WAS IN CONSOLIDATEDROCK IN A CLASS 1 LOCATION 23 INCHES DEEP. | 3919 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
242 | 1989-01-20 | LA | leaks and spills | UNKNOWN ( COUNTY) | TENNESSEE GAS PIPELINE CO | LEAK WAS DISCOVERED ON 20" RISER AT +6' MEAN LOW GULF (MLG) UNDER A RISER CLAMP. RISER IS ATTACHED TO PLATFORM SUPPORT SYSTEM VIA CLAMPS. CORRODED PART OF PIPELINE WAS EXPOSED TO ATMOSHPERE AND, THEREFORE, RELIED ON COATINGS, NOT CATHODIC PROTECTION, FOR CORROSION CONTROL. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
243 | 1989-02-01 | MI | other | UNKNOWN (CHARLEVOIX COUNTY) | GREAT LAKES GAS TRANSMISSION CO | ON FEBRUARY 1, 1989, A FIRE CAUSED EXTENSIVE DAMAGE IN THE INSIDE OF A COMPRESSOR BUILDING AT GREAT LAKES GAS TRANSMISSION COMPANY'S BOYNE FALLS, MICHIGAN COMPRESSOR STATION. THE EXTERNAL APPURTENANCES OF THE COMPRESSOR PACKAGE WAS DAMAGED AS WELL AS THE BUILDING STRUCTURE. THE STATION WAS UNMANNED AT THE TIME OF IGNITION THEREFORE NO INJURIES WERE SUSTAINED. THE FIRST EMPLOYEE AT THE SCENE EXTINGUISHED THE MAJORITY OF THE FIRE. THE PROBABLE CAUSE OF THE FIRE WAS A STEEL REINFORCED FLEX LINE/FITTING FAILURE THAT SPRAYED NATRUAL GAS AND SEAL OIL ONTO THE HOT POWER TURBINE SECTION OF THE COMPRESSOR. THIS VIEW IS SUPPORTED BY THE PATTERN OF DESTRUCTION. THE MOST SEVERE DAMAGE OCCURRED ON THE WEST SIDE OF THE EXHAUST STACK BETWEEN THE POWER TURBINE & GAS COMPRESSOR. THE ESAST HALF OF THE SEAL OIL TANK WAS SEVERLY CHARRED. AT THAT TANK, THE REFERENCE GAS LINE TO THE SEAL OIL LEVEL SWITCH WAS FOUND SEPERATED.IT WAS AS IF THE FLEX LINE SEGMENT PULLED OUT OF ITS OWN CONNECTOR. IF SO, THE UPPER OPENING RELEASED HIGH PRESSURE GAS AND THE LOWER OPENING RELEASED THE SEAL OIL. BOTH MEDIA WOULD HAVE SPILLED DIRECTLY ON THE STILL HOT,POWER TURBINE CASING. IT SHOULD BE NOTED, THAT EVEN THOUGH THE UNIT WAS SHUT DOWN AT THE TIME OF IGNITION OF THE FIRE, THE SEALOIL WAS STILL BEING PUMPED AND GAS WAS STILL IN THE UNIT PIPING, AND THE POWERTURBINE EXTERNAL SHIELD MAY HAVE BEEN AS HOT AS 1500F. THE ESD SYSTEM EVACUATED THE GAS WITHIN THE COMPRESSOR STATION YARD AND BUILDINGS. ALL OTHER CRITICAL EMERGENCY DEVICES AND PROCEDURES FUNCIONED AS DESIGNED.MATERIAL SPECIFICATIONS UNDER INVESTIGATION. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
244 | 1989-01-11 | LA | leaks and spills | UNKNOWN ( COUNTY) | CHEVRON USA INC | COATING FAILURE IN THE RISER SECTION ALLOWED SALTWATER TO COME IN CONTACT WITH THE PIPE AND CAUSED LOCALIZED PITTING. | 250000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
245 | 1989-01-27 | WY | other | UNKNOWN (WASHAKIE COUNTY) | WILLISTON BASIN INTERSTATE PIPELINE CO |  | 20000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
246 | 1989-01-15 | MN | other | UNKNOWN (DAKOTA COUNTY) | NORTHERN NATURAL GAS CO | DECEASED WAS ASPHYXIATED BY NATURAL GAS WHILE ATTEMPTING TO CLOSE VALVES IN A REGULATOR BUILDING TO ISOLATE A LEAK CAUSED BY THE FAILURE OF A REGULATOR CONTROLLINE. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
247 | 1989-01-13 | KS | other | UNKNOWN ( COUNTY) | KANSAS POWER & LIGHT CO | LANDOWNER WAS FARMING AT 16" TO 18" DEPTH & HIT 4" PIPELINE, PULLING ONE JOINT OF PIPE OUT OF MECHANICAL COUPLING. AVERAGE DEPTH IS 24", DEPTH WAS 17" AT LOCATION OF INCIDENT. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
248 | 1988-11-02 | CA | leaks and spills | UNKNOWN (LOS ANGELES COUNTY) | SOUTHERN CALIFORNIA GAS CO | THE REGULATOR AND METER PERSONNEL MADE AN IMMEDIATE CHECK OF THE 26,000 FEET OF 4" AND 6" STEEL HIGH PRESSURE TAPLINE AND UPSTREAM REGULATOR STATION. ALL EQUIPMENT WAS FOUND TO BE FUNCTIONING PROPERLY AND NO LINE BREAKS WERE EVIDENT. PRESSURES TAKEN ALONG THE HIGH PRESSURE PIPELINE INDICATED NORMAL PRESSURES. IT WAS DETERMINED THAT THE PRESSURE LOSS RESULTED FROM AN EQUIPMENT PROBLEM AT THE SANTAQUIN #1 DISTRICT REGULATOR STATION. THE HIGH PRESSURE BLOCK VALVE AT THE STATION INLET HAD NORMAL PRESSURE INDICATED. THE COMPLETE LOSS OF PRESSURE IN THEDISTRIBUTION PIPING NECESSITATED AT TOTAL SHUTDOWN OF 659 COMMERCIAL AND RESIDENTIAL REGULATOR AND METER SETS. NATURAL GAS WAS TURNED BACK INTO THE DISTRIBUTION PIPING SYSTEM AT 2:16 AM. FEBRUARY 9, SIX HOURS AND 16 MINUTES AFTER THE INITIAL DISCOVERY OF SERVICE INTERRUPTION. THE PRESSURE IN THE SYSTEM WAS CONTROLLED BY MONITORING THE BYPASS VALVE AT THE STATION VALVE ASSEMBLY. A SUBSEQUENT CHECK OF THE STATION EQUIPMENT FOUND AN INLINE 2" - 300 ANSI STRAINER-FILTER TO BECOMPLETELY PLUGGED WITH VALVE GREASE WHICH MOVED INTO THE STRAINER AS A RESULT OF THE VERY HIGH STATION GAS FLOWS DUE TO EXTREMELY LOW TEMPERATURES. THE INLINE FILTER WAS REMOVED AND NORMAL REGULATING CAPABILITIES WERE RESUMED AT 10:00 AM. FEBRUARY 9, 1989. | 160000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
249 | 1989-02-13 | TX | other | UNKNOWN (CRANE COUNTY) | WARREN PETROLEUM CO (NEW MEXICO GAS PIPELINE) | AFTER BEING FRACTRUED, THE CROSSHEAD WAS FORCED INTO THE COMPRESSOR CYLINDER HOUSING BY THE CONNECTING ROD WHICH HAD ENOUGH FORCE TO BREAK THE CYLINDER ANCHOR BOLTS AND DISCHARGE PIPING ALLOWING GAS TO ESCAPE. THE IGNITION SOURCE WAS A SPARK CAUSED BY THE METAL TO METAL COLLISION. | 200000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
250 | 1989-02-24 | TX | leaks and spills | UNKNOWN ( COUNTY) | BLUE DOLPHIN PIPELINE CO | COAST GUARD NOTIFIED US OF SPILL REPORTED IN GA 286 ABOUT 1420 HRS ON 02-24-89 BOUY DROPPED HELICOPTER 1630 HRS; LINE SHUT IN 1725 HRS; ZERO LINE PRESSURE 2400HRS; INSTALLED 1500 WP 20" BOLT-ON, SPLIT SLEEVE PLIDCO CLAMP 1432 HRS ON 02-27-89; TESTED 450 PSI, 0215 HRS 02-28-89. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
251 | 1989-02-06 | NJ | other | UNKNOWN (BERGEN COUNTY) | TRANSCO GAS PIPELINE CORP | A SMALL CRACK WAS FOUND IN A TUBE IN THE COIL OF THE H-4B VAPORIZER AT THE LNG FACILITY. METALLURGISTS NOW HAVE THE TUBE SECTION CONTAINING THE CRACK AND ARE IN THE PROCESS OF INVESTIGATING REPORT, A SUPPLEMENTAL REPORT WILL BE SENT TO DOT ALONG WITH A COPY OF THE REPORT. | 300000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
252 | 1989-01-27 | MS | maintenance | UNKNOWN (MARSHALL COUNTY) | TENNESSEE GAS PIPELINE CO | THE CAUSE OF THE LEAK WAS DETERMINED TO BE DUE TO A MANUFACTUING DEFECT IN THE LONGITUDINAL WELD. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
253 | 1989-02-02 | MA | other | UNKNOWN (ESSEX COUNTY) | TENNESSEE GAS PIPELINE CO | A SUPPLEMENTAL REPORT WILL FOLLOW ONCE THE INDEPENDENT LAB REPORT DETERMINES THE CAUSE OF THE PIPE FAILURE. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
254 | 1989-02-16 | AL | other | UNKNOWN (RUSSELL COUNTY) | SOUTHEAST ALABAMA GAS DISTRICT | CONTRACTOR HAD FOUND UNACCEPTED SOIL ON STATE OF ALABAMA HIGHWAY PROJECT NO. 1246-6 AND FAILED TO NOTIFY GAS COMPANY THAT HE HAD RUN INTO THIS CONDITION. COROSS SECTION OF THIS AREA DID NOT SHOW ANY CUTTING OF EXISTING GRADE NECESSARY AT STATION 100 + 00. WHILE REMOVEING THIS UNACCEPTABLE SOIL, OPERATORS EQUIPMENT (PAN TYPE EARTH MOVER) STRUCK AND DAMAGED 8" TRANSMISSION GAS MAIN. | 7894 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
255 | 1989-02-03 | NV | maintenance | UNKNOWN (STOREY COUNTY) | SOUTHWEST GAS CORP | A TRANSMISSON CREW WAS DISPATCHED FROM CARSON CITY. THE PRESSURE WAS LOWERED IN THE LINE. AFTER THE LINE WAS UNCOVERED, IT WAS DETERMINED THAT A 16" T.D. WILLIAMSON STOPPLE FITTING HAD A 9"-10"-LONG CRACK ON A FILET WELD. THE WELD WAS REPARIED AND THE LINE WAS PUT BACK IN SERVICE AT APPROXIMATELY 4:45 AM. ON FEBRUARY 4, 1989. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
256 | 1989-02-20 | TX | leaks and spills | UNKNOWN (JEFFERSON COUNTY) | UNITED TEXAS TRANSMISSION CO |  | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
257 | 1989-03-08 | TX | other | UNKNOWN (LAMB COUNTY) | CABOT GAS SUPPLY CORP | AT APPROXIMATELY 11:45PM ON TUESDAY, MARCH 7, 1989 LIQUID FLOWED FROM THE MAPLE PLANT X PIPELINE INTO THE CABOT GAS SUPPLY, LUBBOCK TO FARWELL 8" +MAINLINE AT THE CABOT/MAPLE INTERCONNECT, LOCATED THREE MILES WEST OF AMHERST. APPROXIMATELY TWO WEEKS AGO, (EXACT DATE NOT KNOWN) MAPLE PUT A PIG IN THEIR PLANT-X PIPELINE. THE PIG DIDN'T COME IN AND GAS CONTINUED TO FLOW. ON MARCH 7TH,ACCORDING TO CABOT INSTRUMENTS AT THE INTERCONNECT, LIUID BEGAN FLOWING INTOTHE CABOT SYSTEM. THE DUMP LINES ON MAPLE'S SCRUBBER (AT THE INTERCONNECT), HAD BEEN DISCONNECTED AT A PREVIOUS TIME, LEAVING THE MAINLY CONDENSATE MIXTURE NO WHERE TO DISCHARGE OUTSIDE THE SYSTEM. ON WEDNESDAY MORNING, MARCH 8, 1989 CABOT AND ENERGAS EMPLOYEES WERE DISPATCHED TO VARIOUS LOCATIONS ALONG THE CABOT MAINLINE TO START DRAINING LIQUID AND VENTING GAS. AN INVESTIGATION IS STILL UNDER WAY TO DETERMINE THE AMOUNT OF LOSS. AN UNDETERMINED AMOUNT OF POSITIVE METERS WERE DAMAGED AND AN INDETERMINED NUMBER OF CUSTOMERS WERE SHUT IN. WE NOTIFIED THE TRRC ON MARCH 9, 1989. | 45000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
258 | 1989-02-28 | LA | other | UNKNOWN ( COUNTY) | SOUTHERN NATURAL GAS CO | ANCHOR CABLE FROM A CONSTRUCTION BARGE BECAME TANGLED IN AN UNDERWATER BYPASS VALVE ASSEMBLY. VALVE ASSEMBLY WAS BROKEN OFF OF PIPELINE. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
259 | 1989-03-05 | LA | other | UNKNOWN (TERREBONNE COUNTY) | TEXAS EASTERN GAS PIPELINE CO | PREPARATIONS WERE BEING MADE FOR THE INSTALLATION OD A VARIABLE SPEED MOTOR CONTROLLER FOR AN ELECTRIC MOTOR DRIVEN GAS COMPRESSOR AT THE POINTE AU CHEINFACILITY. THE LOAD BREAKER SUPPLYING ELECTRICAL POWER TO THE ELECTRIC MOTOR DRIVEN GAS COMPRESSOR HAD BEEN REMOVED. THE EMPLOYEES PERFORMING THE WORK INSTALLED A GROUNDING CONDUCTOR ONTO A TERMINAL OF THE SURGE CAPACITOR, WHICH ISCONNECTED TO THE ENERGIZED SIDE OF THE 4160 VOLT BUS. DURING THIS WORK AN ELECTRIC ARC OCCURED BETWEEN THE MAIN BUS AND THE GROUNDING CONDUCTOR. ONE EMPLOYEE RECEIVED SCOND AND THIRD DEGREE BURNS ON FIFTY TO SIXTY PERCENT OF HIS BIODY. TWO EMPLOYEES EACH RECEIVED FIRST AND SECOND DEGREE BURNS TO THE FACE AND CHEST. THESE THREE EMPLOYEES WERE ADMITTED AS IN-PATIENTS TO HOSPITALS IN NEW ORLEANS AND HOUMA, LA., RESPECTIVELY. AN ADDITIONAL EMPLOYEE RECEIVED FIRST AND SECOND DEGREE BURNS ON HIS LEFT HAND AND WAS TREATED AND RELEASED ON MARCH 6. NO NATURAL GAS WAS INVLOVED IN THIS INCIDENT; HOWEVER IT IS BEING REPORTED UNDER THE CRITERIA FOR AN INCIDENT IN 49 CFR PART 191.3 AS AN EVENT THAT IS SIGNIFICANT IN THE JUDGEMENT OF THE OPERATOR. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
260 | 1989-04-20 | OK | other | UNKNOWN (MAJOR COUNTY) | RINGWOOD GATHERING CO | A DIFFERENTIAL PRESSURE CONTROLLER ESCAPED THE LOCATED CLOSED POSITION AND PERMITTED A PNEUMATIC VALVE OPERATOR OPEN WHILE THE INJURED MEN WERE OPENING THE ORIFICE METER FLANGES PREPARATORY TO MAKING A ROUTINE INSPECTION OF THE ORIFICE PLATE. THE RESULTING ESCAPE OF GAS WAS IGNITED BY AN APPARENT SPARK. | 40000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
261 | 1989-03-31 | IL | maintenance | UNKNOWN (CHAMPAIGN COUNTY) | ILLINOIS POWER CO | ON 3/31/89 AT APPROXIMATELY 2:00 P.M., A 12" TRANSMISSION MAIN UNDER 300 PSI OFPRESSURE SEPARATED WHERE A PLIDCO SPLIT AND SLEEVE FITING HAD BEEN INSTALLED. THE FITTING JOINTED THE ENDS OF A REPLACED SECTION OF THE MAIN AND THE EXISTING PORTION OF THE PIPELINE. THE OPERATING PRESSURE OF 700 PSI WAS BEING RESTORED IN100 INCREMENTS PRIOR TO THE ACCIDENT. BECAUSE OF THIS INCIDENT, AN ILLINOIS POWER EMPLOYEE, WHO WAS ADJACENT TO THE ABOVE DESCRIBED FITTING IN THE EXCAVATION, WAS FATALLY INJURED. THE CAUSE OF THIS OCCURRENCE IS UNDER INVESTIGATION BY ILLINOIS POWER.SUPPLEMENT : THE INVESTIGATION OF THIS INCIDENT BY ILLINOIS POWER CO IS NOT YETCOMPLETE. ARNOLD BLOCKMAN, ATTORNEY FOR ILLINOIS POWER CO WILL BE DISCUSSING THIS MATTER WITH HIS CONSULTANT AS TO THE CAUSE OF THIS INCIDENT. AFTER THAT INPUT, ILLINOIS POWER CO WILL BE BETTER ABLE TO DETERMINE ANY NEEDED FURTHER COURSE OF INVESTIGATION TO DETERMINE CAUSE. WE SHALL KEEP YOU ADVISED.FINAL UPDATE: THE INVESTIGATION OF THE INCIDENT BY ILLINOIS POWER CO IS COMPLETE. THE INCIDENT WAS CAUSED BY VAGUE, AMBIGUOUS AND MISLEADING INFORMATION SUPPLIED BY THE MANUFACTURER OF THE MECHANICAL CONNECTOR. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
262 | 1989-03-19 | LA | other | UNKNOWN ( COUNTY) | SOUTHERN NATURAL GAS CO | ON THE MORNING OF SUNDAY, MARCH 19, 1989, PIPELINES UNLIMITED SERVICES (PLUS),SOUTHERN'S INDEPENDENT CONTRACTOR, ARRIVED AT ARCO'S SOUTH PASS BLOCK 60 "B"PLATFORM. AT APPROXIMATELY 7:00 PM, A SUBCONTRACTOR SELECTED BY PLUS INITIATEDCOLD CUTTING OF THE 18" PIPELINE AT APPROXIMATELY THE +15 FOOT LEVEL BELOW ACLOSED VALVE AT APPROXIMATELY THE +20 FOOT LEVEL. THE COLD CUTTING DEVICE WASBEING OPERATED BY AN AIR COMPRESSOR ON A BOAT MOORED ADJACENT TO THE PLATFORMAND DIRECTLY UNDER THE RISER. WHEN TOTAL PENETRATION WAS FIRST MADE INTO THELINE, GAS AND LIQUID OOZED FROM THE CUT UNDER PRESSURE. THE SUBCONTRACTOR THENRE-RIGGED THE CUTTING DEVICE TO ALLOW THE COLD CUTTER TO BE OPERATED FROM THEWORK BOAT. CUTTING WAS RESUMED WITHOUT THE PREMISSION OF ANY REPRESENTATIVE OFSOUTHERN. SHORTLY THEREAFTER, THE LINE WAS COMPLETELY SEVERED AND GAS ANDLIQUIDS WERE EXHAUSTED FROM THE PIPELINE. THE GAS WAS IGNITED, CREATING A FIRE;SEVERAL OTHER PIPELINESTHEREAFTER EXPLODED, ENGULFING THE PLATFORM IN FLAMES.EXACT CAUSE OF THIS INCIDENT AND THE FACTORS THAT CONTRIBUTED TO IT ARE UNDERINVESTIGATION. ALTHOUGH THE INVESTIGATION HAS NOT BEEN COMPLETED, IT IS APPARENTTHAT ARCO, THE PLATFORM OPERATOR, HAD NOT PROPERLY BLED THE LINE DOWN IN ORDERPROPERLY TO RELIEVE IT OF PRESSURE. SUPPLEMENTAL REPORT 12/15/94 INDICATESTHAT LINE WAS OUT OF SERVICE... PLATFORM OPERATOR WAS TO HAVE RELIEVED LINE OFPRESSURE. CAUSE CHANGED FROM OTHER, TO DAMAGE BY OUTSIDE FORCES.. SUBMITTED BYERIC THOMAS (205) 325-7632. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
263 | 1989-02-03 | TX | maintenance | UNKNOWN (COTTLE COUNTY) | LONE STAR GAS CO | THERE IS NO RECORDED TEST PRESSURE ON THIS SEGMENT OF PIPE. LINE 71-5-2-1 WAS PURCHASED FROM UNITED GAS COMPANY IN 1967 AN MAXIMUM ALLOWABLE OPERATING PRESSURE WAS EXTABLISHED IN ACCORDANCE WITH 49 CFR 192.619(A)(3). | 20654 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
264 | 1989-03-02 | TX | leaks and spills | UNKNOWN (VICTORIA COUNTY) | DELHI GAS PIPELINE CORP |  | 24000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
265 | 1989-03-08 | TX | leaks and spills | UNKNOWN (MCLENNAN COUNTY) | TEXAS UTILITIES FUEL CO | SHORTED CASING, LOCALIZED EXTERNAL PITTING. SMALL LEAK. | 3000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
266 | 1989-02-23 | MI | other | UNKNOWN (GRATIOT COUNTY) | MICHIGAN CONSOLIDATED GAS CO (MICHCON) | CONTRACTOR PLOWING INFIELD TILE ON JULY 15, 1988,STRICK AND DAMAGED LINE, DID NOT REPORT DAMAGE. | 300000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
267 | 1989-04-11 | CT | other | UNKNOWN (LITCHFIELD COUNTY) | TENNESSEE GAS PIPELINE CO | OUTSIDE PARTY/THIRD PARTY CONTRACOTR'S BACKHOE SEVERED LINE. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
268 | 1989-04-02 | LA | other | UNKNOWN (CADDO COUNTY) | GULF STATES PIPELINE CORP | THE CAUSE IS UNKNOWN AS IT OCCURRED UNDER HIGH WATERS AND IS STILL INACCESSIBLE. ACCORDING TO THE RECORD, 1988 AND 1989 HAVE SEEN THE HIGHEST BAYOU FLOOD LEVELS SINCE THE LINE WAS COMPLETED, MAY 9, 1974. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
269 | 1989-03-02 | CO | leaks and spills | UNKNOWN (LA PLATA COUNTY) | EL PASO NATURAL GAS CO | A RUPTURE OCCURRED ON THE INTERCONNECTING LINE TO A DRIP ASSEMBLY ON LATERAL 4A-41. THE 90 DEGREE "L" OF THE DRIP SHOWED SEVERE INTERNAL CORROSION DUE TO ACCUMULATION OF WATER IN THE DRIP ASSSEMBLY. THE SOURCE OF IGNITION HAS NOT BEEN DETERMINED. | 334149 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
270 | 1989-03-08 | TX | maintenance | UNKNOWN ( COUNTY) | ANR PIPELINE CO (AMERICAN NATURAL RESOURCE) |  | 130000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
271 | 1989-03-21 | SD | other | UNKNOWN (MCCOOK COUNTY) | NORTHERN NATURAL GAS CO | MEASUREMENT TECHNICIAN CONNECTED A 125 PSIG RATED DIFFERENTIAL PRESSURE TEST APPARATUS TO PIPING OPERATING AT 700 PSIG. THE TEST APPARATUS FAILED AND A RELEASE OF GAS OCCURRED FOR A FEW SECONDS. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
272 | 1989-06-02 | MD | other | UNKNOWN (BALTIMORE COUNTY) | BALTIMORE GAS & ELECTRIC CO | AT APPROXIMATELY 1450 HOURS ON JUNE 2, 1989, THE PRINCIPAL GAS SYSTEM OPERATOR AT THE SPRING GARDENS GAS CONTROL CENTER NOTED AN INSTANTANEOUS INCREASE IN GAS FLOW AT THE OWINGS MILLS GATE STATION ON TYHE INSTRUMENTATION ON THE CONTROL PANEL. A CORRESPONDING PRESSURE DROP FROM 310 PSI TO 235 PSI WAS ALSO NOTED. AT 1510 HOURS, GAS CONTROL RECIEVED A REPORT OF A GAS LEAK AT 10426 REISTERSTOWN ROAD, OWINGS MILLS, MD. COMPANY CREWS WERE DISPATCHED TO THE SITE AND FIRE AND POLICE DEPARTMENTS WERE NOTIFIED. COMPANY REPRESENTATIVES DISCOVERED A SEVERE LEAKIN A 20 INCH GAS TRANSMISSION PIPELINE. THE UPSTREAM VALVE AT THE OWINGS MILLSGATE STATION WAS OPERATED AT 1520 HOURS. THE DOWNSTREAM MAIN LINE VALVE WAS OPERATED 1555 HOURS. THE LEAKING NATURAL GAS DID NOT EXPLODE OR IGNITE. THERE WERE NO INJURIES NOR FATALITIES. NO BUILDINGS OR STRUCTURES WERE DAMAGED OTHER THAN THE GAS PIPING. THE INCIDENT RESULTED FROM THE PIPE PULLOUT OF A 20 INCH COMPRESSION COUPLING. RELOCATION OF THE PIPELINE HAD RECENTLY BEEN PERFORMED 52 FEET DOWNSTREAM OF THE LEAK. THE COUPLING WAS NOT UNCOVERED FOR THE WORK. IT IS DEDUCED THAT THE CONSTRUCTION WORK UNKNOWINGLY DISTURBED THE PIPELINE ANCHORING SUFFICIENTLY TO ALLOW THE COUPLING TO PULL OUT. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
273 | 1989-05-03 | MS | leaks and spills | UNKNOWN (ITAWAMBA COUNTY) | ITAWAMBA INDUSTRIAL GAS CO | THE LEAK WAS A VERY SMALL PIN HOLE ON THE BOTTOM OF THE PIPE AND APPEARED TO BESOMETHING THAT WOULD RESULT FROM ELECTROYSIS CAUSED BY DAMAGE TO A SMALL AREA OF THE COATING. THE REPAIR WAS ACCOMPLISHED USING A SPLIT SADDLE MADE FROM A PIECE OF FOUR INCH .250 WALL STEEL PIPE ABOUT TWELVE INCHES LONG. THIS SPLIT SLEEVE WAS THEN WELDED LONGITUDINAL AND CIRCUMFERENTIAL ON THE PIPE TO COVER THE PIN HOLE OPENING IN THE PIPE. ALL WELDS WERE FILLET TYPE WITH WORK PERFORMED BY A QUALIFIED WELDER WITH CURRENT QUALIFICATION DOCUMENTS. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
274 | 1989-03-20 | TX | leaks and spills | UNKNOWN (MCLENNAN COUNTY) | TEXAS UTILITIES FUEL CO | LOCALIZED EXTERNAL PITTING. SMALL LEAK. | 20000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
275 | 1989-03-17 | TX | maintenance | UNKNOWN (VICTORIA COUNTY) | HOUSTON PIPELINE CO | DURING ORIGINAL CONSTRUCTION A 4" TAP WAS MADE ON THE 18" MAINLINE USING A WELD-O-LET. A THROUGH-WALL CRACK DEVELOPED IN THE 18" LINE UNDER THE TOE OF THE FILLET WELD. | 25000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
276 | 1989-04-28 | TX | other | UNKNOWN (DAWSON COUNTY) | RED RIVER PIPELINE CORP | THE LEAK WAS A 9" X 1.25" CRESCENT SHAPE CRACK ON THE 10" DISCHARGE PIPING OF COMPRESSOR UNIT #30006 ALONG AND NEAR THE AREA OF A 3" WELD-O-LET SERVING AS THE INLET TO A RELIEF VALVE. THE CRACK WAS CAUSED BY EXTERNAL FORCE ON THE 10" PIPING WHEN THE 3" X 6" RELIEF VALVE OPENED AT APPROXIMATELY 1190 PSIG. THE MAJOR CONTRIBUTING FACTOR WAS THE FAILURE OF THE THREADS OF A FLANGE BOLT ON THE RELIEF VALVE OUTLET FLANGE WHICH CONNECTED THE RELIEF VALVE OUTLET SUPPORT. WITHOUT SUPPORT THE FORCE OF GAS FLOW THROUGH THE RELIEF VALVE AND ITS DISCHARGE BLOWDOWN PIPE ACTED ON THE 10" DISCHARGE PIPE. | 13000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
277 | 1989-04-29 | KS | other | UNKNOWN (SHAWNEE COUNTY) | WILLIAMS NATURAL GAS CO |  | 10000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
278 | 1989-06-05 | LA | leaks and spills | UNKNOWN (CADDO COUNTY) | J - W OPERATING CO |  | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
279 | 1989-03-21 | TX | other | UNKNOWN (DONLEY COUNTY) | LONE STAR GAS CO |  | 35000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
280 | 1989-04-21 | TX | leaks and spills | UNKNOWN ( COUNTY) | HOUSTON PIPELINE CO |  | 43000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
281 | 1989-04-16 | TX | leaks and spills | UNKNOWN (FORT BEND COUNTY) | MOBIL VANDERBILT-BEAUMONT PIPELINE CO |  | 42000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
282 | 1989-04-14 | TX | leaks and spills | UNKNOWN (NUECES COUNTY) | DELHI GAS PIPELINE CORP | EXTERNAL CORROSION. | 9909 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
283 | 1989-04-30 | TX | leaks and spills | UNKNOWN (FORT BEND COUNTY) | MOBIL VANDERBILT-BEAUMONT PIPELINE CO | ON APRIL 30, 1989, A LEAK WAS REPORTED AT MP 68 ON THE VANDERBILT TO BEAUMONT NATURAL GAS PIPELINE. THE PIPELINE WAS SHUT DOWN FROM THR ORIGIN STATION AT VANDERBILT TO MP 71 AND THE PRESSURE REDUCED. A FLAME IONIZATION INSPECTION WAS CONDUCTED OVER THIS SEGMENT OF THE PIPELINE. ADDITIONAL LEAKS WERE FOUND AT MP 65.8, ON MAY 2, 1989, AND AT MP 58.1 ON MAY 3, 1989. ONLY MINIMALS WERE REPAIRED BY INSTALLING THREE SECTIONS OF NEW LINE PIPE. | 75000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
284 | 1989-07-29 | LA | leaks and spills | UNKNOWN (ST HELENA COUNTY) | TRANSCO GAS PIPELINE CORP |  | 60000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
285 | 1989-06-09 | OH | other | UNKNOWN (HANCOCK COUNTY) | COLUMBIA GAS TRANSMISSION CORP | CONTRACTOR OPERATING FIELD TILING/TRENCHING MACHINE PUNCTURED LINE RESULTINGIN AN APPROXIMATE 2" DIA. HOLE. | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
286 | 1989-06-22 | NE | other | UNKNOWN (LINCOLN COUNTY) | K N ENERGY INC(KANSAS NEBRASKA GAS CO) | OPERATOR ACCIDENTALLY OPENED DISCHARGE ESD VALVE, ALLOWING GAS TO ESCAPE FROM OPEN DISCHARGE HEADER. | 300000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
287 | 1989-06-18 | LA | leaks and spills | UNKNOWN (NATCHITOCHES COUNTY) | LOUISIANA INTRASTATE GAS CORP |  | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
288 | 1989-05-16 | TX | leaks and spills | UNKNOWN (BEXAR COUNTY) | VALERO TRANSMISSION CO | TWO SMALL LEAKS IN SADF WEST, MEDINA RIVER SECONDARY CROSSING. BOTH LEAKS UNDERWATER REPAIRED BY CUTTING AND CAPPING SECONDARY CROSSING. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
289 | 1989-07-26 | TX | leaks and spills | UNKNOWN ( COUNTY) | BLUE DOLPHIN PIPELINE CO | MMS NOTIFIED US OF OIL SLICK 0930 HOURS ON 7-26. WE DROPPED BUOY 1330 HOURS AND STARTED SHUTDOWN. LIFT BOAT ON LOCATION 2030 HOURS 7-27. DIVER FOUND LEAK 1830 HOURS 7-28. SET CLAMP 2045 HOURS 7-29. TEST 450 PSIG OK. RESUMED GAS SALES 0700 HOURS 7-30. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
290 | 1989-06-25 | TX | other | UNKNOWN (ANGELINA COUNTY) | NATURAL GAS PIPELINE CO OF AMERICA | A FIRE WAS APPARENTLY CAUSED BY LUBE OIL ESCAPING FROM THE CHIP DETECTOR PIPING OF THE #10 UNIT. THE OIL WAS IGNITED BY AN UNKNOWN SOURCE. HYDRAULIC OIL AND AMBITROL SUBSEQUENTLY FUELED THE FIRE AS VALVES IN THOSE SYSTEMS MELTED. NATURAL GAS WAS NOT A FACTOR IN THE INCIDENT. | 4000000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
291 | 1989-07-04 | IA | other | UNKNOWN (MUSCATINE COUNTY) | NATURAL GAS PIPELINE CO OF AMERICA | A SALES METER WAS DAMAGED BY A FIRE FUELED BY NATURAL GAS. THE CAUSE OF THEINCIDENT IS UNDER INVESTIGATION. | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
292 | 1989-06-29 | TX | other | UNKNOWN (GALVESTON COUNTY) | CHEVRON PIPELINE CO | RELEASE WAS FROM A CRACK WHICH RESULTED FROM A DENT IN THE PIPELINE FROM AN UNKNOWN SOURCE AT AN UNDETERMINED TIME. LEAK WAS FOUND BY A SMALL AMOUNT OF PRODUCT BUBBLING UP THROUGH STANDING WATER. LINE WAS SHUT DOWN, PRUGED AND REPAIRES MADE. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
293 | 1989-07-09 | TX | maintenance | UNKNOWN (HARRIS COUNTY) | MOBIL VANDERBILT-BEAUMONT PIPELINE CO | FRACTURE FAILURE OF WELD NECK FLANGE DUE TO A MANUFACTURING DEFECT. HYSTOSTATIC TEST PRESSURE COULD HAVE FURTHER INDUCED WEAKENING IN THE AREA OF THE DEFECT PRIOR TO THE FAILURE. | 6200 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
294 | 1989-07-27 | LA | maintenance | UNKNOWN ( COUNTY) | TRANSCO GAS PIPELINE CORP | DURING A ROUTINE UNDERWATER INSPECTION USING A REMOTE OPERATED VEHICLE, BUBBLES WERE OBSERVED NEAR THE BOTTOM OF THE RISER ON THE A-4 LEG OF BLOCK 20-A PLATFORM. A VIDEO TAPE OF THE FACILITIES IN THIS AREA INDICATED THAT A LEAK WAS LOCATED APPROXIMATELY 10 FEET PAST THE TUBE TURN ON THE UPSTREAM 12" FLANGE ON THE B.I.M.S. SLIP JOINT CONNECTION. LEAK IS COMING FROM THE 12" RING JOINT GASKET. DEPTH OF WATER AT THIS LOCATION IS APPROXIMATELY 500 FEET. | 375000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
295 | 1989-08-02 | NE | other | UNKNOWN (HAMILTON COUNTY) | K N ENERGY INC(KANSAS NEBRASKA GAS CO) | THE PIPELINE WAS HIT BY AN OUTSIDE PARTY OPERATING A WEED CUTTER. THE DAMAGED PORTION OF THE PIPELINE IS IN A CLASS I LOCATION AND WAS MARKED WITH PERMANENT LINE MARKERS. A PERMANENT REPAIR WAS COMPLETED BY REPLACING TWELVE (12) FEET OF THE DAMAGED PIPELINE WITH PRETESTED PIPE OF EQUAL OR GREATER SPECIFICAT | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
296 | 1989-07-28 | TX | leaks and spills | UNKNOWN ( COUNTY) | ANR PIPELINE CO (AMERICAN NATURAL RESOURCE) |  | 65000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
297 | 1989-05-16 | TX | other | UNKNOWN (SOMERVELL COUNTY) | LONE STAR GAS CO | WATER WASHED DAM OUT. PIPELINE CROSS CREEK IN DAM. | 26595 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
298 | 1989-08-02 | TX | other | UNKNOWN (WISE COUNTY) | LONE STAR GAS CO |  | 5000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
299 | 1989-07-26 | TX | other | UNKNOWN (CAMERON COUNTY) | RIO PIPELINE LP | FOREMOST PAVING HIT OUR LINE AT FM 803 AND SH 100 AT APPROXIMATELY 11:15 AM.WE BLEW THE LINE DOWN TO ATMOSPHERE AT 12:15 PM. THE LINE WAS REPAIRED AND PUT BACK IN SERVICE BY 4:30 PM. | 5000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
300 | 1989-08-14 | WV | other | UNKNOWN (HARDY COUNTY) | COLUMBIA GAS TRANSMISSION CORP | BACKHOE OPERATOR LOST CONTROL OF BACKHOE WHICH RAN INTO AND DESTROYED A MEASUREMENT & REGULATION STATION. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
301 | 1989-09-04 | LA | other | UNKNOWN ( COUNTY) | CHEVRON USA INC | BREAK APPARENTLY CAUSED BY ANCHOR RECOVERY OPERATIONS FROM A YET UNKNOWN COMPANY. THE PIPE WAS COMPLETELY SEPARATED WITH SIGNIFICANT MARKINGS CAUSED BY ANCHOR SCRAPINGS. | 500000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
302 | 1989-07-25 | NC | other | UNKNOWN (WAYNE COUNTY) | NORTH CAROLINA NATURAL GAS CORP | A LOCATION REQUEST TICKET WAS RECIEVED FROM U.L.O.C.O. ON 7/18/89. THE LOCATION ON THE TICKET WAS GIVEN AS THE INTERSECTION OF S.R. 1107 & MUSGRAVE ROAD. THE ACTUAL LOCATION WAS S.R. 1007 & MUSGRAVE RD. N.C.N.C. DOES NOT HAVE ANY FACILITIES ON OR NEAR S.R. 1107 IN WAYNE COUNTY, N.C.HERRING & RIVENBARK (CONTRACTOR) WAS TRENCHING TO INSTALL WATER LINES. TRENCHERSTRUCK 10" GAS LINE CAUSING A HOLE IN THE PIPELINE. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
303 | 1989-08-10 | TX | leaks and spills | UNKNOWN (JACKSON COUNTY) | HOUSTON PIPELINE CO | THE BREAK OCCURRED IN A SUBMERGED CROSSING OF A WATER FILLED DITCH. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
304 | 1989-08-28 | LA | other | UNKNOWN (BIENVILLE/QUACHITA PARISH COUNTY) | SOUTHERN NATURAL GAS CO | ON AUGUST 28, 1989, EXPLOSIVE DEVICES WERE DETECTED AT THREE LOCATIONS ON SOUTHERN'S HIGH PRESSURE INTERSTATE NATURAL GAS TRANSMISSION PIPELINE SYSTEM INBIENVILLE AND QUACHITA PARISHES, LOUISIANA. TWO DEVICES COMPOSED OF TWO FOUR-POUND STICKS OF FUSED DYNAMITE (EACH CHARGE) WERE VISUALLY DETECTED AND REMOVED. ONE DEVICE A LOCATION #2 HAD DETONATED PRIOR TO DISCOVERY BY COMPANY PERSONNEL. ALTHOUGH UNDER FEDERAL INVESTIGATION, NO ARREST HAVE BEEN MADE TO DATE.SUPPLEMENTAL REPORT INDICATES THAT INCIDENT RESULTED FROM VANDALISM. AFURTHER DESCRIPTION OF THE THREE LOCATIONS FOLLOWS: LOC #1 SOUTHERN'S SUGARBOWL #1 METER STATION LOGANSPORT LINE - MP 54.7 BIENVILLE PARISH, LA 71008DEVICE DETECTED AT 11 AM 8/28/89 DEVICE WAS ATTACHED TO 12" PIPE RISER DEVICEREMOVED BY AUTHORITIES. LOCATION #2 - SOUTHERN'S HWY 101 BLOCK GATE VALVELOGANSPORT LOOP LINE MP 53.103 1 1/2 MI. EAST OF LOC #1 BIENVILLE PARISH, LA71008 DEVICE EXPLODED PRIOR TO DETECTION. DISCOVERY BY COMPANY PERSONNEL1:00PM. DAMAGE WAS TO 20" VALVE EXTENSION. ESTIMATED DAMAGE TO EXTENSION$5000.00. NO GAS ESCAPED THE PIPELINE. LOC. #3- SOUTHERN'S QUACHITA RIVERCROSSING LOGANSPORT LINE. MP 8.322 (45 MI. EAST OF LOC #1). QUACHITA PARISH,LA. 71280. DEVICE DETECTED AT 5:40PM. DEVICE WAS ATTACHED TO 4" BLOWOFF RISER.DEVICE REMOVED BY AUTHORITIES. INVESTIGATION OF THE INCIDENT CONTINUES, ANDSOUTHERN HAS OFFERED A $10,000 REWARD. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
305 | 1989-09-15 | LA | other | UNKNOWN (WINN COUNTY) | LOUISIANA INTRASTATE GAS CORP | COMPANY MAINTENANCE CREW DAMAGED SIDE TAP VALVE WHILE PERFORMING ROUTINE MAINTENANCE ON PIPELINE. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
306 | 1989-09-09 | LA | other | UNKNOWN (PLAQUEMINES COUNTY) | SOUTHERN NATURAL GAS CO | THIRD PARTY WAS USING BARGE AND DRAGLINE TO DIG OUT ALONG RIVER BANK FOR FUTURE BARGE ACCESS. THE BUCKET HIT THE UNDERWATER RIVER LINE. SUBSEQUENT DIVER INSPECTION INDICATED VERY MINOR DAMAGE TO THE PIPE. APPROXIMATELY SIX DAYSLATER THE PIPELINE RUPTURED. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
307 | 1989-08-21 | TX | leaks and spills | UNKNOWN (HIDALGO COUNTY) | VAL GAS CO | THIS FAILURE WAS LOCATED IN A WET AREA NEAR A SEWER POND DRAINAGE. EXTERNALCORROSION OCCURRED DUE TO COATING DISBONDMENT. VOLUME LOST BASED ON VALLEY COMPLEX SYSTEM LINE PACK LOST, PRODUCTION FLOWING FOR ONE HOUR AND 3.2 MILES OF 8" PIPE BLOWN TO "0" ON BLOWOUT SECTION. | 14000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
308 | 1989-08-29 | TX | maintenance | UNKNOWN (FREESTONE COUNTY) | TEXAS UTILITIES FUEL CO | LEAK OCCURRED AT HEAT AFFECTED ZONE ADJACENT TO A GIRTH WELD. | 20500 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
309 | 1989-09-13 | LA | other | UNKNOWN (ST LANDRY COUNTY) | TRANSCO GAS PIPELINE CORP | A CONTRACTOR WAS WORKING FOR TRANSCO ON WELL#44 AT PAD 18 REMOVING SAND FROMTHE PERFORATED ZONE OF THE WELL AND HAD INSTALLED A COIL TUBING UNIT AND ANINJECTOR ASSEMBLY ON THE WELL. DURING THE DESANDING OPERATION, THE CONTRACTOR'S TUBING UNIT (#2148) DEVELOPED A PROBLEM IN THE UNIT'S HYDRAULIC SYSTEM.A SECOND TUBING UNIT (#2140) WAS BROUGHT IN NEXT TO UNIT #2148. CONTRACTOR INTERCONNECTED THE TWO UNIT'S HYDRAULIC SYSTEMS AND CONTINUED THE OPERATION.BOTH UNITS WERE APPROXIMATELY 3-5 FEET FROM THE WELLHEAD WITH TWO CONTRACTORCREWMAN IN THE CONTROL HOUSE OF EACH UNIT. THE CONTRACTOR COMPLETED THE DESANDING AND WAS WITHDRAWING TUBING FROM WELL. TUBING WAS APPROACHING THE TOP OF THE WELL WHEN THE INJECTOR ASSEMBLY BROKE LOOSE AT THE 4 1/2" X 3" SWAGE, CAUSING GAS TO BLOW FROM THE WELL. WITHIN SECONDS THE GAS IGNITED, SENDING FLAMES 40 TO 50 FEET IN THE AIR. BOTH TUBING UNITS ALSO CAUGHT ON FIRE. TRANSCO EMPLOYEES, CALLED TO THE SITE,ISOLATED AND BLEW DOWN CONNECTING PIPELINES, AND WITH ANSUL 39 LB. DRY CHEMICAL EXTINGUISHERS, EXTINGUISHED THE TWO TUBING UNIT TRUCKS AND THE WELLHEAD FIRES AND SHUT THE VALVE. A TOTAL OF FOUR CONTRACTOR EMPLOYEES WERE INJURED. ALL FOUR WERE TRANSPORTED TO THE HOSPITAL. ONE EMPLOYEE WAS TREATED AND RELEASED; THE OTHER THREE WERE TRANSFERRED TO BURNCENTERS. THE 4 1/2" X 3" SWAGE IS A CONNECTION ASSEMBLED IN THE CONTRACTOR'S MECHANCIAL SHOP. THE ENTIRE ASSEMBLY, INCLUDING ALL VALVES, CONNECTIONS AND COIL TUBING WAS TESTED TO 4500 PSI AFTER ASSEMBLY ON THE WELLHEAD. THE TEST WAS PERFORMED BY THE CONTRACTOR PERSONNEL AND WITNESSED BY TRANSCO PERSONNEL | 568920 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
310 | 1989-09-28 | VA | other | UNKNOWN (LOUDOUN COUNTY) | COLUMBIA GAS TRANSMISSION CORP | DURING LAND CLEARING OPERATION, A BACKHOE DIGGING HOLES TO BURY STUMPS PUNCTRUED PIPELINE, PRODUCING A 2-INCH BY 3-INCH HOLE. | 112000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
311 | 1989-10-05 | TX | leaks and spills | UNKNOWN ( COUNTY) | ANR PIPELINE CO (AMERICAN NATURAL RESOURCE) |  | 152000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
312 | 1989-10-02 | NM | other | UNKNOWN (LEA COUNTY) | LLANO INC | INSPECTION OF THE CRYOGENIC PLANT COMPRESSION FACILITIES INVOLVED IN THE INCIDENT REVEALED THE ABSENCE OF A 1 5/8" "JACK BOLT" FROM AN INBOARD, DISCHARGEVALVE CAP ON A COMPRESSOR CYLINDER. DURING DISMANTLING OF THAT COMPRESSION CYLINDER, PARTICULARLY THAT VALVE ASSEMBLY, THE CENTER THROUGH BOLT WHICH HOLDS THE VALVE COMPONENTS TOGETHER WAS FOUND TO BE BROKEN. THE "VALVE CHAIR" WA S FOUND TO HAVE IMPACT DAMAGE FROM STRIKING THE JACK BOLT, OFF CENTER. THESEFINDINGS SUGGEST THE VALVE THROUGH BOLT FAILURE LED TO A "COCKING" OF THE VALVE CHAIR WHICH IN TURN STRUCK THE JACK BOLT. THE JACK BOLT, THROUGH JARRING CAUSED BY THE IMPACTING OF THE CHAIR, "BACKED OUT" OF ITS THREAD PROFILE. GAS LEAKAGE, AT 1000 PSIG, AROUND THE JACK BOLT BEGAN DURING THIS PROCESS. FAILURE OF THE JACK BOLT STARTING THREAD, APPROXIMATELY 270*, AND THE FIRST THREAD IN THE VALVE CAP SUGGEST A FORCEFUL REJECTION OF THE JACK BOLT FROM ITS PROFILE. GAS HAVING ACCUMULATED UNDER THE COMPRESSOR FACILITIES COVER, A 20'X40'X20' OPEN SKIRTED BUILDING, WAS SUBSEQUENTLY IGNITED. SOURCE OF IGNITIONCOULD HAVE BEEN SPARKS CREATED BY EXITING OF THE CARBON STEEL JACK BOLT OR FROM NUMEROUS, NORMAL HOT SPOTS ON THE INTERNAL COMBUSTION ENGINE WHICH WAS DRIVING THE COMPRSSOR. THE ENSUING NATURAL GAS FIRE WAS RESPONSIBLE FOR CAUSING A FIRE OF COMPRESSOR LUBRICATION OIL. | 600000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
313 | 1989-09-24 | TX | leaks and spills | UNKNOWN ( COUNTY) | ANR PIPELINE CO (AMERICAN NATURAL RESOURCE) |  | 400000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
314 | 1989-09-18 | TX | other | UNKNOWN (ANDERSON COUNTY) | LONE STAR GAS CO | ROAD GRADER GRADING LOGGING ROAD STRUCK PIPELINE CAUSING 3 1/4" TRIANGULAR HOL | 10142 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
315 | 1989-10-05 | TX | other | UNKNOWN (WARD COUNTY) | CABOT GAS SUPPLY CORP | INDEPENDENT CONTRACTOR HIT PIPELINE WITH A BACK HOE WHILE DITCHING TO LAY A WATER LINE. | 42000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
316 | 1989-09-22 | TX | leaks and spills | UNKNOWN (ZAVALA COUNTY) | VALERO TRANSMISSION CO | THIS INCIDENT WAS CAUSED BY AN EXTERNAL CORROSION LEAK ABOUT FOUR (4) MILES NORTH OF CRYSTAL CITY. THREE (3) CUSTOMERS AND ONE (1) PRODUCER WERE WITHOUTSERVICE FOR THREE (3) HOURS WHILE THE LINE WAS BLOCKED IN FOR REPAIR. | 3500 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
317 | 1989-10-24 | CO | other | UNKNOWN (ARCHULETA COUNTY) | WESTERN GAS SUPPLY CO | THE MICRO LOCK BRAKES FAILED ON A TOW TRUCK PARKED ON THE ROAD BEHIND THE METER STATION. THE TRUCK ROLLED DOWN THE HILL THROUGH THE STATION FENCE, STRIKING THE ABOVE GROUND PIPING. A 3" ANSI 150 PLUG VALVE RUPTURED. THE STATION PIPING ABOVE AND BELOW GROUND WAS TWISTED BY THE FORCE OF THE IMPACT. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
318 | 1989-10-23 | NJ | leaks and spills | UNKNOWN (GLOUCESTER COUNTY) | SUN REFINING & MARKETING CO | THE SIX INCH LINE UNDER RACCOON CREEK AT BRIDGEPORT, NEW JERSEY, DEVELOPED ALEAK FROM INTERNAL LOW POINT ACQUIOUS CORROSION. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
319 | 1989-10-03 | TX | other | UNKNOWN ( COUNTY) | NATURAL GAS PIPELINE CO OF AMERICA | FISHING BOAT STRUCK PIPELINE APPROXIMATELY 1/2 MILE OFFSHORE. | 750000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
320 | 1989-10-18 | AZ | other | UNKNOWN (MARICOPA COUNTY) | EL PASO NATURAL GAS CO | LAND OWNER HAD BEEN TOLD NOT TO MAKE CUTS OR REMOVE COVER FROM OUR PIPELINE.A CONTRACTOR HIRED BY LAND OWNER WAS GRADING WITH A BULLDOZER AND HIT AND RUPTURED OUR 16" LINE #2039. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
321 | 1989-10-21 | WV | other | UNKNOWN (KANAWHA COUNTY) | COLUMBIA GAS TRANSMISSION CORP | A DOZER CONSTRUCTING AN ACCESS ROAD HIT AND SEPARATED THE PIPELINE RESULTING IN AN EXPLOSION AND FIRE. | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
322 | 1989-11-01 | LA | leaks and spills | UNKNOWN ( COUNTY) | NATURAL GAS PIPELINE CO OF AMERICA | LEAK WAS CAUSED BY INTERNAL CORROSION.REPAIRED BY INSTALLING A PLIDCO LEAK CLAMP. | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
323 | 1989-11-30 | KY | other | UNKNOWN (ROWAN COUNTY) | TENNESSEE GAS PIPELINE CO | UNIT HAS BEEN DOWN SINCE 1983. RECENT OVERHAUL AND NEW CONTROLS WERE BEING VERIFIED AND ACCEPTED. POWER TURBINE FAILED. CAUSED OIL LEAK WHICH RESULTEDIN FIRE. THE FIRE DESTROYED THE UNIT WALL, ASSOCIATED WALLS, FLOOR, AND CEILING. | 3000000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
324 | 1989-11-14 | TX | other | UNKNOWN (PANOLA COUNTY) | TEJAS GAS CO | CONTRACTOR USING A D-7 DOZER STRUCK PIPELINE WHILE CONSTRUCING A RESERVE PITFOR A NEW PENZOIL WELL LOCATION. | 5000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
325 | 1989-11-13 | OH | leaks and spills | UNKNOWN (HOCKING COUNTY) | COLUMBIA GAS TRANSMISSION CORP | NO KNOWN OUTSIDE FACTORS. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
326 | 1989-11-10 | LA | maintenance | UNKNOWN (CAMERON COUNTY) | NATURAL GAS PIPELINE CO OF AMERICA | LEAK DUE TO LAMINATION IN PIPE WALL. | 130000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
327 | 1989-12-16 | LA | other | UNKNOWN (CADDO COUNTY) | J - W OPERATING CO |  | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
328 | 1989-12-02 | LA | other | UNKNOWN ( COUNTY) | COLUMBIA GULF TRANSMISSION CO | THE EXISTING 12" PIPELINE FROM PENNZOIL PLATFORM "A" IN SOUTH PASS BLK. 57 TO A CONNECTION IN TENNESSEE GAS' 26" PIPELINE IN SOUTH PASS BLK. 77, A DISTANCE OF APPROXIMATELY 3.85 MILES, WAS PULLED OUT OF ITS ORIGINAL POSITION APPROXIMATELY 1800 TO 2400 FEET. THE PIPELINE SUSTAINED CONSIDERABLE DAMAGE, WITHA LEAK DEVELOPED IN SOUTH PASS BLK. 77. PLANS FOR THE REPAIR AND/OR REPLACEMENT OF THE DAMAGED PIPELINE ARE BEING FORMULATED. | 4702000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
329 | 1989-11-29 | MN | other | UNKNOWN (DAKOTA COUNTY) | NORTHERN NATURAL GAS CO | A 1/2" NPS NIPPLE ON THE #4 COMPRESSOR RELIEF VALVE SENSING LINE FAILED RESULTING IN THE COMPRESSOR PLANT (FIVE COMPRESSORS) EMERGENCY SHUT DOWN SYSTEM ACTIVATING.SUPPLEMENTAL : AN UNNECCESSARY, UNPLANNED ACTIVATION OF THE COMPRESSOR PLANT (5UNITS) EMERGENCY SHUTDOWN SYSTEM OCCURRED. ONE INLET VALVE DID NOT CLOSE, RESULTING IN HIGH GAS LOSS. | 91700 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
330 | 1989-11-25 | MS | other | UNKNOWN ( COUNTY) | ANR PIPELINE CO (AMERICAN NATURAL RESOURCE) | PRELIMINARY CONCLUSION: ELECTRICAL MALFUNCTION OF TURBINE CONTROL SYSTEMS COUPLED WITH LUBE OIL AND GAS LEAK APEAR TO HAVE CAUSED THE FIRE. INVESTIGATION IS STILL IN PROGRESS. | 1000000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
331 | 1989-12-27 | TX | leaks and spills | UNKNOWN ( COUNTY) | BLUE DOLPHIN PIPELINE CO | HELICOPTER LINE SURVEY FOLLOWING CLAMP #5 AND GAS TEST PRESSURE APPLIED TO PIPELINE LOCATED BUBBLES IN BLOCK GA 286; SO DIVER BOAT WAS MOVED THERE AND CLAMP WAS SET BY 1502 HOURS ON 12/29/89 AND 400 PSI GAS PRESSURE TEST WAS SUCCESSFUL. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
332 | 1989-12-21 | TX | leaks and spills | UNKNOWN ( COUNTY) | BLUE DOLPHIN PIPELINE CO | SLICK OBSERVED BY ARMS PERSONNEL IN HELICOPTER WAS REPORTED BY RADIO/TELEPHONE; SO A MARKER BOUY WAS DROPPED. PRODUCERS SHUT DOWN GAS DELIVERY WITHIN TWO HURS BUT REPAIR WAS WAS DELAYED BY HIGH SEAS AND RECORD COLD. SET PLIDCO, SPLIT SLEEVE, BOLT-ON, 1500 WP CLAMP BY 1000 HOURS 12/27/89; THEN 140 PSI TEST PRESSURE CREATED GAS BUBBLE EVIDENCE OF LEAK NO. 6 WHICH IS REPORTED SEPARATELY. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
333 | 1989-11-21 | TX | other | UNKNOWN (PECOS COUNTY) | VALERO TRANSMISSION CO | WHILE PERFORMING SCHEDULED MAINTENANCE WORK, TWO WORKERS WERE BURNED WHEN AFLASH FIRE ERUPTED. THE WORKERS WERE ATTEMPTING TO WELD A 24" END CAP TO A 24" PIPE IN THE WAHA COMPRESSOR YARD PIPING. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
334 | 1989-12-23 | AR | maintenance | UNKNOWN (GRANT COUNTY) | ARKANSAS LOUISIANA GAS CO (ARKLA GAS CO) | A CRACK DEVELOPED IN A WRINKLE BEND. CRACK FOLLOWED WRINKLE AND PIPE SPLIT, 22" LONG, WIDEST OPENING 1/4". | 176000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
335 | 1989-12-19 | PA | leaks and spills | UNKNOWN (WASHINGTON COUNTY) | COLUMBIA GAS TRANSMISSION CORP | NO OUTSIDE CONTRIBUTING FACTORS. | 101000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
336 | 1989-12-29 | NY | other | UNKNOWN (BRONX COUNTY) | CONSOLIDATED EDISON CO OF NEW YORK | FIRE AT RUPTURED 30" HIGH PRESSURE STEEL GAS MAIN. INVESTIGATION IS CONTINUING; SUPPLEMENTAL REPORT TO FOLLOW.SUPPLEMENT - AN EXPLOSION OCCURED IN TWO ELECTRIC MANHOLES, CAUSED BY THE IGNITION OF A GAS OF UNDETERMINED ORIGIN. THE EXPLSION IN THE MANHOLES SENT APRESSURE WAVE THROUGH THE SOIL WHICH RUPTURED AN ADJOINING MAIN. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
337 | 1989-12-28 | LA | other | UNKNOWN ( COUNTY) | UNITED GAS PIPELINE CO | CAUSE OF DAMAGE IS NOT CONFIRMED, BUT PRELIMINARY EVIDENCE INDICATES THAT THE DAMAGE WAS CAUSED BY A SHELL DREDGE. | 120000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
338 | 1989-12-22 | TX | other | UNKNOWN (MONTGOMERY COUNTY) | MORGAS CO | EMPLOYEES WERE ATTEMPTING TO OPEN CITY GATE BY-PASS. EXCESSIVE PRESSURE REACHED POSITIVE DISPLACEMENT. METER EXPLODED. | 7500 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
339 | 1990-01-21 | TX | leaks and spills | UNKNOWN (BRAZORIA COUNTY) | BLUE DOLPHIN PIPELINE CO | HELICOPTER INVESTIGATION OF REPORTED OIL SLICK VERIFIED 100' WIDE X 5 MILES LONG COMING FROM BUBBLES IN GA-275; DROPPED BOUY 1000 HR ON 1/21; COMMENCED TELEPHONE REPORTS, FIELD SHUT IN, MOBILIZATION OF DIVERS, FABRICATION OF CLAMP BY TEAM IN ALVIN; DELIVERED 1600 HR ON 1/23; ACQUIRED HYDRO-TORC; CLAMP TIGHT 1500 HR 1/24 ; TESTED LINE 400 PSI GAS PRESSURE OK. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
340 | 1990-01-20 | MS | other | UNKNOWN (YAZOO COUNTY) | MUSTANG FUEL CORP OF MISSISSIPPI | GROUND SHIFTING | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
341 | 1990-01-03 | NM | other | UNKNOWN (EDDY COUNTY) | GAS CO OF NEW MEXICO | A JETCO 7332 TRENCHER OWNED BY B & H CONSTRUCTION, P.O. BOX 977, EUNICE, NM 88231 AND OPERATED BY B.J. PILKENTON HIT AND SEVERED AN 8" GAS TRANSMISSION LINE. CONTRACTOR REQUESTED LINE LOCATE AND THEN BEGAN EXCAVATION BEFORE LINE WAS LOCATED BY OPERATOR. | 150000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
342 | 1990-01-11 | TN | maintenance | UNKNOWN (MCNAIRY COUNTY) | TENNESSEE GAS PIPELINE CO | RUPTURE OCCURRED IN WRINKLE (SAG) BEND. THERE WAS NO FIRE AND THE ONLY DAMAGE WAS TO THE PIPE INCLUDING GAS LOST. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
343 | 1989-12-23 | TX | other | UNKNOWN (AZLE COUNTY) | LONE STAR GAS CO |  | 32200 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
344 | 1989-11-12 | TX | other | UNKNOWN (JEFFERSON COUNTY) | UNITED TEXAS TRANSMISSION CO | BACK HOE HIT 2" DUMP LINE ON TRANSMISSION MAIN WHILE EXCAVATING FOR A VALVE REPLACEMENT. | 26761 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
345 | 1990-01-19 | NE | maintenance | UNKNOWN (NUCKOLLS COUNTY) | K N ENERGY INC(KANSAS NEBRASKA GAS CO) | TOWN METERING CHART (1.5 MILES AWAY FROM LEAK ARE) INDICATED A DROP IN SUPPLY PRESSURE OCCURRED ABOUT 5 A.M. ON 1/19/90. LEAKAGE INCREASED OVER THE NEXTFEW DAYS UNTIL A FEW CUSTOMER SERVICES WERE LOST IN TOWN. LEAKAGE INVESTIGATION CREW LOCATED DEFECTIVE PIPE SHORTLY AFTERWARDS AND MADE REPAIR. EXTENT AND LOCATION OF LEAK CAUSED GAS SERVICE TO NELSON, NE CUSTOMERS TO BE INTERRUPTED UNTIL REPAIRS WERE COMPLETED. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
346 | 1990-01-12 | OK | other | UNKNOWN (PAYNE COUNTY) | ONG TRANSMISSION CO | CONTRACTOR CONSTRUCTING WELL LOCATION PUNCTURED PIPELINE WITH DOZER. LOST TOWNS OF PAWNEE AND INGALLS, OKLAHOMA; APPROXIMATELY 1350 CUSTOMERS. | 52200 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
347 | 1989-12-01 | TX | leaks and spills | UNKNOWN ( COUNTY) | COASTAL STATES GAS TRANSMISSION CO |  | 10000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
348 | 1990-01-13 | TX | leaks and spills | UNKNOWN (LEON COUNTY) | TEXAS UTILITIES FUEL CO | PINHOLE LEAK IN 8 INCH PIPELINE BETWEEN MILE MARKER BVA65 AND BVA68 IN LEON CO.ON THE GRAPELAND - OLETHA PIPELINE. PINHOLE LEAK DUE TO CORROSION. | 28000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
349 | 1989-01-18 | TX | other | UNKNOWN ( COUNTY) | LONE STAR GAS CO | RUPTURED PIPE TO BE TESTED BY A METALLURGIST AT A LATER DATE FOR FURTHER INFORMATION ON CAUSE OF RUPTURE. PIPE TO SOIL READINGS AT THE SIGHT WERE NO. END:.87 SO. END:.91 WITH A SOIL POTENTIAL OF NEUTRAL. | 15000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
350 | 1990-02-05 | OH | maintenance | UNKNOWN (ATHENS COUNTY) | TEXAS EASTERN GAS PIPELINE CO | IMPELLER WHEEL IS A PART OF THE AERO ASSEMBLY WHICH IS THE INTERNAL MAKE-UP OF THE CENTRIFUGAL COMPRESSOR.PART 3 - THE FAILURE OF THE COMPRESSOR UNIT WAS CAUSED BY THE DISINTEGRATION OFTHE RIVETED IMPELLER IN THE CLARK COMPRESSOR, RESULTING IN A VIBRATION WHICH BENT THE COMPRESSOR SHAFT, BROKE UP THE BEARING HOUSING IN THE COMPRESSOR PEDESTALAND BREACHED THE COMPRESSOR GAS SEAL. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
351 | 1990-02-22 | TX | leaks and spills | UNKNOWN (BRAZORIA COUNTY) | BLUE DOLPHIN PIPELINE CO | 0745 HRS SHEEN REPORTED BY COASTAL HELICOPTED MARKED BY OUR BUOY 1150 HRS. DIVE BOAT ARRIVED 2/24/90, 0600 HRS; LEAK LOCATED 1716 HRS; CLAMP SET 2131 HRS; TESTED OK 400 PSI GAS, 2/25/90 0001 HRS; CHECKED BLACK LIGHT = OK, 0702 HRS 2/25/90, STARED GAS SALES. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
352 | 1990-02-07 | TX | other | UNKNOWN ( COUNTY) | LONE STAR GAS CO | WHILE DIGGING OUT CONCRETE DRAIN PIPE, TRACK MOUNTED LOADER OPERATOR STRUCK AND PUNCTURED 6" STEEL PIPELINE. | 9700 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
353 | 1990-02-26 | TX | other | UNKNOWN (CASTRO COUNTY) | WESTAR TRANSMISSION CO | FARMER HIT WHILE DEEP PLOWING. THIS PORTION OF LINE RUNS DOWNHILL INTO AN OLD LAKE BED. SOIL EROSION TOOK COVER FROM PIPELINE. | 5500 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
354 | 1990-02-23 | LA | maintenance | UNKNOWN ( COUNTY) | UNITED GAS PIPELINE CO | LEAK OCCURRED DUE TO THE FAILURE OF AN 0-RING SURROUNDING A DUST COVER ON THE EXTENDED ARM ( SEE ATTACHED SKETCH). THE 0-RING IS MADE OUT OF VITON "A" MATERIAL.SUPPLEMENT: AT 1610 HOURS ON 4/20/90 A PLIDCO CLAMP WAS INSTALLED TO FINALIZETHE REPAIRS. | 98249 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
355 | 1990-02-10 | LA | other | UNKNOWN (PLAQUEMINES COUNTY) | UNITED GAS PIPELINE CO | LARGE SHIP, ATTEMPTING TO ANCHOR IN THE MISSISSIPPI RIVER, CAUGHT ANCHOR ON PIPELINE. IN ATTEMPTING TO FREE HIMSELF, PIPELINE WAS RUPTURED. PIPELINE CROSSING ALSO LISTED ON NOAA NAVIGATIONAL CHARTS OF MISSISSIPPI RIVER DELTA NO.11361. | 500000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
356 | 1990-02-14 | LA | other | UNKNOWN ( COUNTY) | TENNESSEE GAS PIPELINE CO | LOCATION OF INVOLVED FACILITIES LIMITS MARKING OF PIPELINE; HOWEVER, DETAILED CONSTRUCTION DRAWINGS EXIST FOR EXACT FACILITY COORDINATES.CONSTRUCTION BARGE WORKING IN THE EUGENE ISLAND BLOCK 338 AREA DRUG AN ACHOR ACROSS EXISTING VALVE ASSEMBLY SHEARING A 2" BLOWOFF VALVE FROM THE FABRICATED ASSEMBLY AT A DEPTH OF 250 FT. | 200000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
357 | 1990-02-16 | CT | maintenance | UNKNOWN (LITCHFIELD COUNTY) | TENNESSEE GAS PIPELINE CO | TGP'S 4" TORRINGTON LATERAL RUPTURED NEAR YAKMOSHUK ROAD IN BARKHAMSTED, CONNECTICUT. THERE WAS NO LOSS OF SERVICE TO CUSTOMERS. ORIGINATED AT A DENT AND 5" GOUGE. | 5000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
358 | 1990-03-11 | AR | maintenance | UNKNOWN (HOT SPRING COUNTY) | ARKLA ENERGY RESOURCES | SEAM FAILURE, PIPE TO BE ANALYZED BY BATTELLE. MOP REDUCED TO 332 PSIG UNTIL BATTELLE RECOMMENDATINS ARE RECEIVED. | 51000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
359 | 1990-03-12 | LA | leaks and spills | UNKNOWN (FEDERAL WATERS COUNTY) | ANR PIPELINE CO (AMERICAN NATURAL RESOURCE) |  | 63000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
360 | 1990-03-01 | KS | other | UNKNOWN (LABETTE COUNTY) | WILLIAMS NATURAL GAS CO |  | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
361 | 1990-03-12 | TX | leaks and spills | UNKNOWN (BRAZORIA COUNTY) | BLUE DOLPHIN PIPELINE CO | OIL SLICK OBSERVED BY COASTAL HELICOPTER REPORTED TO US. WE DROPPED BUOY MARKER AND ORDERED OUT LOCAL DIVERS ON BOAT FROM LOUISIANA WHICH ARRIVED 1400 HRS. 13 MAR., BUT WAS FORCED OFF LOCATION BY WEATHER 14 MAR. AND RETURNED 15 MAR. TO INSTALL A CLAMP, TIGHTENED 1950 HRS, 15 MARCH. THEN TESTED OK W/BLACKLIGHT AND 400 PSI GAS PRESSURE. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
362 | 1990-02-25 | LA | leaks and spills | UNKNOWN (ST HELENA COUNTY) | TRANSCO GAS PIPELINE CORP | THE RUPTURE BLEW OUT APPROXIMATELY 27 FEET OF THE PIPELINE. MEASUREMENTS MADE ALONG TEH SEAM WELD OF THE RECOVERED PIECES SHOWED THAT ALL THE MISSING PIPE FROM THE LINE HAD BEEN FOUND. THE RESULTS OF THE FIELD AND LABORATORY EXAMINATIONS SHOWED THAT THE FAILURE WAS THE RESULT OF WALL THINNING CAUSED BY EXTERNAL CORROSION OF THE PIPE BODY. THE TENSILE PROPERTIES AND THE CHEMICAL COMPOSITION OF THE FAILED PIPE MET THE REQUIREMENTS OF API SPECIFICATION 5L FOR GRADE X52. THE CAUSE OF THE CORROSION WAS NOT DETERMINED. SEE ATTACHED ADDITIONAL COMMENTS. | 150000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
363 | 1990-03-14 | LA | leaks and spills | UNKNOWN ( COUNTY) | NATURAL GAS PIPELINE CO OF AMERICA | THE PIPELINE HAD BEEN SHUT-IN FOR TWO YEARS PRIOR TO LEAK. THE PIPELINE HASNOW BEEN FILLED WITH WATER IN PREPARATION FOR ABANDONMENT. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
364 | 1990-03-22 | TX | other | UNKNOWN (JACKSON COUNTY) | LONE STAR GAS CO | ONE MARKER 110 FEET AND THE OTHER MARKER IS 1957' FROM DAMAGE AREA. | 17485 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
365 | 1990-03-20 | FL | other | UNKNOWN (ESCAMBIA COUNTY) | UNITED GAS PIPELINE CO | ESCAMBIA COUNTY MAINTENANCE DEPARTMENT ROAD GRADER HIT LINE WHILE GRADING ROAD DITCH. | 10700 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
366 | 1990-03-19 | KY | maintenance | UNKNOWN (ROWAN COUNTY) | TENNESSEE GAS PIPELINE CO | A FLEXIBLE (STEEL BRAIDED) FUEL GAS LINE TO THE #3 ENGINE BROKE AND IGNITED. THE FIRE BURNED THROUGH A RUBBER OIL DRAIN BOOT CAUSING OIL TO IGNITE AND SPREAD THE FIRE ON ONE SIDE OF THE #3 UNIT AND IMMEDIATELY UNDER THE UNIT AT BASEMENT LEVEL. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
367 | 1990-03-23 | TX | other | UNKNOWN ( COUNTY) | CHANNEL INDUSTRIES GAS CO | COMPANY'S CONTRACTOR WAS WORKING IN WET SOIL CONDITIONS WHICH CAUSED BACKHOETO PUSH SOIL AGAINST NIPPLE AND SIDE VALVE, CAUSING NIPPLE TO BREAK. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
368 | 1990-04-02 | LA | other | UNKNOWN ( COUNTY) | TENNESSEE GAS PIPELINE CO | RUPTURE OCCURRED IN APPROXIMATELY THE MIDDLE OF THE RED RIVER CROSSING. EXISTING HEAVY FLOODING CONDITIONS AND RESULTING STRONG CURRENTS AND RIVERBED WASHING WAS THE CAUSE OF THE INCIDENT. | 1000000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
369 | 1990-04-03 | LA | other | UNKNOWN (PLAQUEMINES COUNTY) | TENNESSEE GAS PIPELINE CO | MISSISSIPPI RIVERBED WASHIING FROM FLOODING AND STRONG CURRENTS PROBABLY CAUSED PIPELINE FAILURE. ACCESSIBILITY IS LIMITED UNTIL CURRENT FLOODING CONDITIONS SUBSIDE. THE LINE HAS BEEN TAKEN OUT OF SERVICE. | 800000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
370 | 1990-04-06 | IL | maintenance | UNKNOWN (MERCER COUNTY) | ANR PIPELINE CO (AMERICAN NATURAL RESOURCE) | THIS INCIDENT OCCURRED WHILE THE PIPELINE SEGMENT WAS BEING INSPECTED WITH ALINALOG DEVICE. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
371 | 1990-04-25 | TX | other | UNKNOWN (GAINES COUNTY) | NORTHERN NATURAL GAS CO (ENRON) | LOSS OF AC POWER DUE TO LIGHTNING ACTIVATED STATION EMERGENCY SHUTDOWN SYSTEM. SUCTION SIDE VALVE FAILED TO OPERATE WHICH ALLOWED GAS TO VENT THROUGH STATION BLOWDOWNS UNTIL MANUALLY CLOSED (75 MIN.). | 210000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
372 | 1990-04-22 | TX | leaks and spills | UNKNOWN (BOWIE COUNTY) | NATURAL GAS PIPELINE CO OF AMERICA | THE COVER BOLTS ON A 2" CHECK VALVE IN SOUR GAS SERVICE FAILED. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
373 | 1990-04-13 | AR | other | UNKNOWN (LONOKE COUNTY) | MISSISSIPPI RIVER TRANSMISSION CORP |  | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
374 | 1990-05-09 | OR | maintenance | UNKNOWN (KLAMATH COUNTY) | NORTHWEST PIPELINE CORP | THERE WERE SEVERAL PINHOLE LEAKS IN THE LONG SEAM. THE LEAK WAS DISCOVERED DURING THE ANNUAL LEAK SURVEY. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
375 | 1990-05-06 | AR | maintenance | UNKNOWN (LAWRENCE COUNTY) | MISSISSIPPI RIVER TRANSMISSION CORP | THE INITIAL REPORT FROM AN INDEPENDENT LABORATORY SUGGESTS THAT A GOUGE IN THE PIPE WAS THE ORIGIN OF FAILURE. | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
376 | 1990-06-01 | TX | leaks and spills | UNKNOWN ( COUNTY) | ANR PIPELINE CO (AMERICAN NATURAL RESOURCE) |  | 170000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
377 | 1990-06-06 | LA | other | UNKNOWN (CADDO COUNTY) | TEXAS GAS TRANSMISSION CORP | NO REMARKS SHOWNED. | 1586450 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
378 | 1990-06-10 | TX | other | UNKNOWN (LAMAR COUNTY) | NATURAL GAS PIPELINE CO OF AMERICA | THE RUPTURE INITIATED AT A 12" LONG GOUGE THAT WAS POSITIONED BETWEEN 3 O'CLOCK AND 6 O'CLOCK. PIPE WAS GOUGED A PERIOD OF TIME BEFORE THE INCIDENT OCCURRED. | 600000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
379 | 1990-06-25 | MN | other | UNKNOWN (KANDIYOHI COUNTY) | NORTHERN NATURAL GAS CO (ENRON) | MINNESOTA BRANCHLINE MNB 75601 WAS SEVERED BY A SCRAPER DOING EXCAVATION WORK FOR RECONSTRUCTION OF A COUNTY ROAD. | 61000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
380 | 1990-06-25 | LA | other | UNKNOWN ( COUNTY) | SEA ROBIN PIPELINE CO | A CREW OF THREE (3) MEN WERE ATTEMPTING TO REMOVE A SPHERE FROM A PIG RECEIVER. AFTER BELIEVING THE PIGTRAP WAS "BLOWNDOWN" THEY ATTEMPTED TO OPEN THE PITTRAP DOOR. TRAPPED PRESSURE EJECTED BOTH THE PIG AND CLOSURE. THREE (3) MEN WERE INJURED, WITH TWO (2) REQUIRING INPATIENT HOSPITALIZATION. (NOTE: THEBLOWDOWN SYSTEM WAS A CLOSED SYSTEM TO A COMMON VENT ACROSS A BRIDGE ON A TRIPOD PLATFORM. NORMALLY, ALL VALVES BETWEEN THE BLOWDOWN VENT AND THE PIG RECEIVER WOULD BE OPENED TO ACHIEVE BLOWDOWN TO ATMOSPHERE. PRELIMINARY INVESTIGATIONS INDICATE THAT AT LEAST ONE OF THESE VALVES WAS NOT OPENED TO ALLOW THE PIG RECEIVER TO VENT PROPERLY.) | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
381 | 1990-07-03 | OH | other | UNKNOWN (MUSKINGUM COUNTY) | TEXAS EASTERN GAS PIPELINE CO | MOVEMENT OF A LANDSLIDE CAUSED TEXAS EASTERN TRANSMISSION'S 24" PIPELINE TO FAIL. THIS PIPELINE IS LOCATED IN A MAJOR LANDSLIDE AREA THAT ENCOMPASSES MOST OF THE PIPELINE RIGHT-OF-WAY. THIS LANDSLIDE IS TYPICAL OF MANY IN THIS REGION OF OHIO, BEING CHARACTERIZED AS OLD AND VERY SPASMODIC, INTERMITTENT, AND UNPREDICTABLE. THEY CAN BE TRIGGERED BY RAINFALL, CHANGES TO THE TERRAIN, OR BY NATURAL CAUSES. TEXAS EASTERN IS CURRENTLY BUILDING A 36" PIPELINE THROUGH THE SAME SLIDE REGION, PARALLEL TO OUR EXISTING RIGHT-OF-WAY. TO VOID THIS TYPE OF FAILURE ON THE NEW LINE, ITS BEING BURIED TO A GREATER DEPTH, PLACING IT WELL BELOW THE BASE OF SLIDE MOVEMENT. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
382 | 1990-06-27 | LA | leaks and spills | UNKNOWN ( COUNTY) | NATURAL GAS PIPELINE CO OF AMERICA | THE ATTACHED REPORT CONCERNS AND INCIDENT THAT OCCURRED OFFSHORE OF LOUISIANA. ON JUNE 30,1990, A LEAK WAS CONFIRMED ON THE WC-551 LATERAL IN WEST CAMERON BLOCK 552. THE LEAK WAS REPAIRED THE SAME DAY BY INSTALLING A CLAMP ON THE PIPE. NATURAL GAS PIPELINE COMPANY OF AMERICA OWNS AN INTEREST IN AND OPERATES THE JOINT INTEREST LATERAL. | 90000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
383 | 1990-07-03 | TX | maintenance | UNKNOWN (SCHLEICHER COUNTY) | HANOVER ENERGY INC | SYSTEM PURCHASED FROM BP AMERICAN OCTOBER 1, 1988. OUR KNOWLEDGE IS LIMITEDDUE TO THE INFORMATION RECEIVED BY BP AMERICA. DURING CONSTRUCTION A JOINT OF .125 WALL X-42 WAS USED INADVERTENTLY. | 350000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
384 | 1990-07-18 | NY | other | UNKNOWN (WYOMING COUNTY) | CNG TRANSMISSION CORP | LANDSLIDE PARALLEL TO PIPELINE CAUSED PIPE TO BUCKLE AND EVENTUALLY CRACK LONGITUDINALLY ALONG THE BUCKLE. FAILURE OCURRED UNDER TONAWANDA CREEK. | 217000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
385 | 1990-07-10 | LA | leaks and spills | UNKNOWN ( COUNTY) | TENNESSEE GAS PIPELINE CO |  | 221000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
386 | 1990-08-17 | IL | other | UNKNOWN (LA SALLE COUNTY) | ILLINOIS POWER CO | ON AUGUST 17, 1990, AT APPROXIMATELY 7:50AM, A FIRE WAS REPORTED AT THE LASALLE #2 DELIVERY STATION WHICH RECEIVES NATURAL GAS FROM NGPL. THE FIRE WAS REPORTED BY A NEIHBOR WHO NOTED A LIGHTENING STRIKE IN THE IMMEDIATE VICINITY & NOTED TWO DISTINCT FIRES. THE FIRST FIRE WAS NOTED AS A GLOW INSIDE A CONTROL VALVE BUILDING, FOLLOWED BY A BALL OF FIRE IN THE STATION. (NO EXPLOSION OCCURED, BUT FIRE/HEAT WAS THE SOURCE OF ALL DAMAGE). THE INITIAL INVESTIGATION THERORIZES THAT LIGHTEDING WAS THE SOURCE OF IGNITION TO A RELIEF VALVE BLOWING. FURTHER INVESTIGATION IS BEING PERFORMED AS TO THE CAUSE OF THIS OCCURRENCE. | 70000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
387 | 1990-08-12 | IL | other | UNKNOWN (CHAMPAIGN COUNTY) | PEOPLES GAS LIGHT & COKE CO | A FRACTURE OCCURED IN A COMPRESSOR ROD AT THE POINT WHERE THE ROD ATTACHES TO THE COMPRESSOR PISTON. THIS FAILURE IN TURN CAUSED THE CYLINDER HEAD TO FAILAND THE COMPRESSOR FLANGE, HEAD AND PISTON WERE BLOWN OFF AND OUT OF THE COMPRESSOR. AUTOMATIC EQUIPMENT PERFORMED AN EMERGENCY SHUTDOWN OF THE UNIT ANDSHUT-IN THE GAS SUCTION AND DISCHARGE PIPING WITHOOUT FURTHER INCIDENT. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
388 | 1990-07-30 | WV | maintenance | UNKNOWN (RANDOLPH COUNTY) | COLUMBIA GAS TRANSMISSION CORP | A PRELIMINARY INVESTIGATION INDICATED THAT THE RUPTURE INITIATED IN A 26 X 24 INCH OD, SADDLE REINFORCED BRANCH CONNECTION INSTALLED IN '51. THE PIPE MATERIALS USED HAVE BEEN DESCRIBED IN THE REPORT FORM. AT THE TIME OF THE RUPTURE THERE WAS CONTRUCTIONIN THIS AREA REQUIRED TO CONNECT A CROSSOVER TO ANOTHER PIPELINE. THE BACKFILL OVER THIS BRANCH CONNECTION HAD BEEN REMOVED. THE LOCATION OF THIS FAILURE RELATIVE TO THE FILES CREEK COMNPRESSOR STATION IN SHOWN IN FIGURE 1. VISUAL EXAMINATION OF THE FRACTURE SURFACES SHOWED EVIDENCE OF A LONG, PRE-EXISTING CRACK AT THE EDGE OF THE FILLET WELD TOE ON THE OUTSIDE SURFACE. THIS FRACTURE APPEARED TO BE PRIMARILY BRITTLE. IT IS POSSIBLE THAT THIS CRACK WAS FORMED FROM SMALL WELD FLAWS THAT WERE A RESULT FO THE ORIGINAL FABRICATION WELDING. PRESSURE FLUCTUATIONS OVER THE SERVICE LIFE CREATED A CYCLIC STRESS LOADING THAT CAUSED GROWTH AND LINKAGE TO FORM NEAR CRITICAL CRACK DIMENSIONS. THIS PARTICULAR LOCATION NEAR THE ASSUMED ORIGIN IS ONE OF THE HIGHEST STRESS IN SUCH A BRANCH CONNECTION. A DRAWING OF THIS RUPTURE IS ATTACHED AS FIGURE 2. ANY STRESS IMPOSED THAT WAS INCIDENTAL OF A NEW FORGED TEE IN THE 26" OD PIPELINE AND ASSOCIATED CROSSOVER PIPING MAY HAVE CONTRIBUTED TO ADDITIONAL CRACK GROWTH. THE RELATIVE LOCATION OF THE NEW TEE TO THE SUPTURE LOCATION IS SHOWN IN FIGURE 3. THE O TO 800 PSI PRESSURE INCREASE MAY HAVE ALSO CAUSED SOME GROWTH. A FOUR FOOT LONG SECTION OF THE BACK SIDE OF THE BRANCHCONNECTION WAS EJECTED FROM THE DITCH. THE LOCATION OF THIS SECTION HAS BEEN INDICATED IN FIGURE 3. | 150000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
389 | 1990-07-24 | TX | other | UNKNOWN (BRAZORIA COUNTY) | HOUSTON PIPELINE CO | PIPE ON COMPRESSOR DISCHARGE HEADER FAILED, RESULTING IN A FIRE. | 300000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
390 | 1990-07-19 | OK | other | UNKNOWN (CADDO COUNTY) | FORT COBB FUEL IRRIGATION AUTH | THE INCIDENT WAS A FIRE SUPPORTED BY ESCAPING NATURAL GAS DURING ROUTINE LINE MAINTENANCE. THE SPECIFIC TASK BEING PERFORMED WAS THE REPLACEMENT OF AN APPROXIMATE 390 FOOT SEGMENT OF 2" PVC DISTRIBUTION LINE TO PERMIT LOWERING OF THIS SEGMENT. THE SEGMENT HAD BEEN EXPOSED AT ABOVE GROUND LEVEL BY FLASH FLOODING DURING EARLIER HEAVY RAINFALLS. SEE ACCOMPANYING PHOTO #1 SHOWING EXPOSED LINE SEGMENT AND REPLACEMENT. PER STATEMENTS FROM ONE OF THE INJURED INDIVIDUALS, MR. WILLIS MCGARRAH, FLOWING GAS FROM THE UPSTREAM (EAST) END OF THE SEGMENT OF LINECARRIED SOME FOREIGN PARTICLES. THESE WERE GREY/WHITE DUST OF DIRT IN APPERANCE FROM THE OPEN END OF THE LINE. THIS APPEARED TO HAVE CONTRIBUTED TO OR CAUSEWD THE INCIDENT BY STATIC ELECTRICITY SPARK IGNITION OF THE VENTING GAS STREAM. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
391 | 1990-08-09 | NM | other | UNKNOWN (MCKINLEY COUNTY) | EL PASO NATURAL GAS CO | A CONTRACTOR, WHILE REMOVING A CONCRETE VAULT FROM AROUND A DRIP THAT WAS BEING REMOVED FROM AROUND A DRIP THAT WAS BEING REMOVED FROM OUR 30-INCH PERMIAN - SAN JUAN LINE NO. 1300, ACCIDENTLY KNOCKED OFF A 1-INCH NIPPLE DIRECTLY CONNECTED TO THE LINE, CAUSING GAS TO ESCAPE. THE LINE BLEW FOR APPROXIMATELYTHREE HOURS WHILE A 2-INCH BYPASS WAS INSTALLED TO PREVENT CURTAILMENT OF SERVICE TO THE TOWN OF THOREAU, NEW MEXICO. STATE HIGHWAY 57/412 WAS TEMPORARILY CLOSED DUE TO THE 2-INCH BYPASS BEING LAID ACROSS THE HIGHWAY WHILE REPAIRS WERE BEING MADE. THE LINE WAS REPAIRED AND BACK IN SERVICE BY 10:00 PM. MDT THE SAME DAY (08/09/90). | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
392 | 1990-08-28 | NM | other | UNKNOWN (LEA COUNTY COUNTY) | LLANO INC | LLANO EMPLOYEES HAD INSTALLEDNEW PRESURE PACKING ON A FIRST STAGE COMPRESSORCYLINDER. THE DISTANCE PIECE INSPECTION DOOR HAD BEEN REPLACED AND RE-PRESSURING OF THE COMPRESSOR CYLINDER INITIATED. GAS LEAKING BY THE NEW PRESSURE PACKING EXCEEDED THE CAPACITY OF THE DISTANCE PIECE VENT AND CAUSED AN PRESSURE BUILD-UP IN THE DISTANCE PIECE. THE PRESSURE BUILD-UP CAUSED THE DISTANCEPIECE INSPECTION DOOR TO FRAGMENT. THE CAST IRON FRAGMENTS FROM THE INSPECTION DOOR STRUCK AN EMPLOYEE IN THE FACE CAUSING SEVERE FACIAL INJURIES. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
393 | 1990-08-03 | OK | maintenance | UNKNOWN (BECKHAM COUNTY) | CAPROCK PIPELINE CO | A VENT ON A POSITIONER VALVE WAS CLOGGED. NATURAL GAS SEEPAGE THROUGH THE CONDUIT, ENTERED THE INSTRUMENTATION BUILDING. THE GAS IGNITED AND A FLASH FIRE ENSUED. | 8500 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
394 | 1990-08-31 | LA | maintenance | UNKNOWN ( COUNTY) | SOUTHERN NATURAL GAS CO | THE BOLTED BONNET COVER UTLITZES A RUBBER O-RING TYPE GASKET SEAL. APPARENTLY THE RUBBER GASKET HAS CRACKED OR DETERIORATED IN SEVERAL PLACES.PART 3 - DIVERS WERE INSPECTING A 12" RUTURE TAP AND DISCOVERED SLOW RELEASE OFBUBBLES FROM EXISTING CRACKS IN CONCRETE COATING. THE COATING WAS REMOVED AND IT WAS DETERMINED THAT THE LEAK WAS FROM TH BONNET ON THE CHECK VALVE. THE CHECK VALVE IS IN 234' OF WATER. | 200000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
395 | 1990-08-30 | PA | other | UNKNOWN (ALLEGHENY COUNTY) | PEOPLES NATURAL GAS CO | CONTRACTOR HIT TP-7575 WITH BULLDOZER. LINE HAD BEEN LOCATED AND MARKED BY THE PEOPLES NATURAL GAS COMPANY. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
396 | 1990-08-04 | CA | other | UNKNOWN (LOS ANGELES COUNTY) | SOUTHERN CALIFORNIA GAS CO | USA TICKET INDICATED WORK TO BE DONE ON 8/3/90. SURVEILLANCE PERSON WENT TOJOB SITE, MARKED PIPELINE IN INTERSECTION, NO ONE WAS AT JOB SITE.ADDITIONAL - ON AUGUST 4, 1990, AT APPROXIMATELY 1:55PM THE LOS ANGELES FIRE DEPT. NOTIFIED OUR COMPANY OF BLOWING GAS AT SEPULVEDA AND CHURCH LANE/OVADA PLACE. THE DAMAGE TO THE LINE WAS CAUSED BY A STREET CONSTRUCTION MACHINE OPERATED BY THE CITY OF LOS ANGELES, DEPT. OF PUBLIC WORKS, BUREAU OF STREET MAINTENANCE. REPAIRS WERE MADE BY INSTALLING TWO 26" WELD CAPS. FOUR CUSTOMERS WERE AFFECTED BUT NO EVACUATIONS WERE NECESSARY. THERE WERE NO FIRES OR INJURIES ASSOCIATED WITH THIS INCIDENT. ESTIMATED COSTS ASSOCIATED WITH THIS INCIDENT WERE $68,000, WHICH INCLUDES GAS LOSSES ESTIMATED TO BE 4,781 MCF. | 68000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
397 | 1990-09-08 | KS | maintenance | UNKNOWN (JOHNSON COUNTY) | WILLIAMS NATURAL GAS CO | VALVE SEPARATION - MAIN BODY SEPARATED FROM FLANGE ALLOWING GAS ESCAPE. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
398 | 1989-12-16 | LA | other | UNKNOWN (ACADIA COUNTY) | TRANSCO GAS PIPELINE CORP | ON DECEMBER 16, 1989 AT 1:30 A.M. TRANSCO FIELD PERSONNEL NOTICED A LOSS OF PRESSURE IN LINE A OF THE CENTRAL LOUISIANA LATERAL WHICH HAD BEEN OPERATING AT A PRESSURE OF 840 PSI. AS TRANSCO BEGAN SHUTTING IN THE AFFECTED PIPELINE SECTION, AT 1:40 A.M., HOUSTON DISPATCH RECEIVED A TELEPHONE CALL FROM THE ACADIA PARISH SHERIFF'S DEPARTMENT RELAYING A FARMER'S REPORT THAT HE HAD HEARDA LOUD NOISE IN A FIELD CLOSE TO HIS HOUSE. THE LOCATION OF THE LEAK WAS THEN NARROWED DOWN TO A SECTION OF LINE A BETWEEN THE VALVE SITES AT MILE POSTS23.61 AND 36.94. THE AFFECTED SECTION OF PIPELINE WAS ISOLATED BY MANUALLY CLOSING THESE VALVES. THREE HOURS AND FIFTEEN MINUTES AFTER THE LOSS OF PRESSURE WAS DETECTED THE AREA WAS MADE SAFE. THERE WAS NO FIRE AND DAMAGE WAS LIMITED TO A SECTION OF TRANSCO PIPELINE APPROXIMATELY 165 FEET LONG LOCATED IN A FARMERS FIELD. THE FIELD WAS NOT CULTIVATED AT THE TIME OF THE INCIDENT. | 140000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
399 | 1990-08-23 | CA | other | UNKNOWN (SAN BERNARDINO COUNTY) | SOUTHERN CALIFORNIA GAS CO |  | 21200 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
400 | 1990-09-20 | KS | other | UNKNOWN (JOHNSON COUNTY) | WILLIAMS NATURAL GAS CO | ACCIDENTLY STRUCK 1" TAP WHILE PERFORMING MAINTENANCE ACTIVITY | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
401 | 1990-10-03 | TX | other | UNKNOWN (HARDIN COUNTY) | HOUSTON PIPELINE CO | LIQUIDS WERE BEING REMOVED FROM A PIPELINE (16", ACCT. 1136) BY PIGGING. REMOVED LIQUIDS AND VENTING GAS WERE BEING DISCHARGED INTO A 500 BBL. TANK OPENTO THE ATMOSPHERE. IT IS SURMISED THAT HEAVY HYDROCARBON VAPORS VENTING FROM THE TANK, COLLECTED NEAR GRADE LEVEL IN THE AREA AND WERE IGNITED BY A SOURCE WHICH HAS NOT YET BEEN CONFIRMED. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
402 | 1990-09-21 | OK | maintenance | UNKNOWN (CARTER COUNTY) | ONG TRANSMISSION CO |  | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
403 | 1990-09-23 | TX | leaks and spills | UNKNOWN (SOUTH ADDITION COUNTY) | ANR PIPELINE CO (AMERICAN NATURAL RESOURCE) |  | 202500 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
404 | 1990-09-19 | PA | other | UNKNOWN (TIOGA COUNTY) | CNG TRANSMISSION CORP | A 1" REGULATOR ON THE PILOT LINE TO THE 6" STATION BLOWOFFS FAILED CAUSING THE PILOT LINE TO DRAIN AND OPENING THREE BLOWOFF VALVES AT SABINSVILLE COMPRESSOR STATION | 143000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
405 | 1990-09-20 | NM | other | UNKNOWN (GRANT COUNTY) | EL PASO NATURAL GAS CO | EPNG'S 6 5/8" LINE NO. 2010 WAS HIT BY A GRADER OWNED BY PHELPS DODGE, CAUSING AN 18 INCH TEAR.NEW MEXICO ONE-CALL SYSTEM IS PRESENTLY BEING IMPLEMENTED | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
406 | 1990-10-02 | NM | other | UNKNOWN (SAN JUAN COUNTY) | EL PASO NATURAL GAS CO | A MAINTAINER BEING OPERATED BY BROKEN HILLS PROPRIETARY COMPANY WAS GRADING ADITCH PARALLELING OUR 24-INCH PIPELINE WHEN IT HIT AND RUPTURED THE PIPELINE. THERE WAS NO FIRE OR EXPLOSION BUT THE FORCE | 209210 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
407 | 1990-09-30 | NM | other | UNKNOWN (BLANCO COUNTY) | EL PASO NATURAL GAS CO | A FIRE INVOLVING TWO MERIDIAN OIL COMPANY TRUCKS WHICH WERE UNLOADING LIQUIDDRIP, OCCURRED AT THE BLANCO STORAGE TANKS LOCATED BETWEEN THE BLANCO AND CONOCO PLANTS. THE FIRE STARTED WHEN VAPORS FROM THE DOME HATCH OF THE TRUCK MIGRATED TO THE AIR INTAKE OF THE ENGINE ON THE OTHER TRUCK, CAUSING THE ENGINE TO START DIESELING (RUN AWAY) AND IT BACKFIRED. THIS BACKFIRE STARTED A FIRE WHICH DESTROYED TWO TRACTORS, A TWO HUNDRED BARREL TANK TRAILER, AN EQUIPMENT SHACK, AND INSTRUMENTATION ON A DRIP SYSTEM. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
408 | 1990-09-25 | TX | other | UNKNOWN (MOORE COUNTY) | NATURAL GAS PIPELINE CO OF AMERICA | WHILE PERFORMING MAINTENANCE INSIDE AN ABSORBER TOWER, 4 EMPLOYEES WERE BURNED BY A FLASH FIRE. TWO EMPLOYEES WERE HOSPITALIZED, AND 2 WERE TREATED AND RELEASED. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
409 | 1990-10-02 | CO | maintenance | UNKNOWN (ARAPAHOE COUNTY) | COLORADO INTERSTATE GAS CO | FACTORS CONTRIBUTING TO THIS INCIDENT INCLUDE THE EXTREMELY LOW GAS FLOWS ANDA LOSS OF SENSITIVITY IN THE CONTROL SYSTEM, RESULTING IN INACCURATE READINGSBEING SUPPLIED TO PERSONNEL CONTROLLING THE GAS/AIR BLENDING SYSTEM. THE VOLUME DEMAND THROUGH THE GAS/AIR MIXER WAS REDUCED TO A LEVEL BELOW WHICH CONTROLS FOR THE MIXING EQUIPMENT FUNCTION AUTOMATICALLY, WHICH THEN REQUIRED SWITCHING THE CONTROLS TO A MANUAL BLENDING OPERATION. THE OPERATOR CONTROLS THE BLENDING BY THE READINGS ON TWO THERM-TITRATORS. IT IS PROBABLE THAT THE THERM-TITRATOR WAS NOT READING A REPRESENTATIVE SAMPLE OF THE GAS DUE TO A BROKEN THERM-TITRATOR PROBE. THE INSERTION PROBE ON THE THERMTITRATOR WAS BROKENOFF. THIS RESULTED IN THE MEASUREMENT OF A NON_REPRESENTATIVE SAMPLE OF GAS.TNE CAUSE OF THE BROKEN PROBE IS UNKNOWN | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
410 | 1990-09-13 | TX | other | UNKNOWN (BURLESON COUNTY) | CLAJON GAS CO | D THE BELLHOLE. WHEN WELDERS STARTED WELDING, THE VAPORS IGNITED IN FLASH FI | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
411 | 1990-10-16 | LA | leaks and spills | UNKNOWN (UNKNOWN COUNTY) | NATURAL GAS PIPELINE CO OF AMERICA | AT 6:15 PM ON OCTOBER 16, 1990, BUBBLING WATER WAS OBSERVED ABOUT 0.5 MILES FORM THE ARCO 212C PLATFORM. THE LEAK WAS CONFIRMED AT 9:17 AM ON OCTOBER 17AND REPAIRED WITH A LEAK CLAMP ON OCTOBER 20. NATURAL GAS PIPELINE COMPANY OF AMERICA OPERATES AND SHARES OWNERSHIP OF THE PIPLEINE. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
412 | 1990-10-22 | CA | other | UNKNOWN (KERN COUNTY) | SOUTHERN CALIFORNIA GAS CO | THE PIPELINE WAS HIT BY A RIPPER THAT WAS SUBSOILING TO REPLANT A FIELD. | 55000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
413 | 1990-10-17 | LA | other | UNKNOWN (BOSSIER COUNTY) | TEXAS EASTERN GAS PIPELINE CO | TRACTOR WAS DISKING THE FIELD WHEN PRODUCERS PIPING WAS HIT BY A DISK. THE 2" WELDOLET WAS TORN FROM THE PIPELINE AND APPROXIMATELY 30 FEET OF PIPE SPLIT OPEN. | 90000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
414 | 1990-10-16 | LA | other | UNKNOWN (BIENVILLE COUNTY) | UNITED GAS PIPELINE CO | AN EXPLOSIVE ATMOSPHERE DEVELOPED OVER AN OPEN OIL AND WATER PIT AT BISHTINEAU COMPRESSOR SATION. THE EXPLOSIVE ATMOSPHERE IGNITED DUE TO CONSTRUCTION AT THE PIT. THE RESULTING "FLASH" CAUSED 2 MEN TO SUSTAIN BURN INJURIES REQUIRING HOSPITALIZATION. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
415 | 1990-11-07 | CA | other | UNKNOWN (RIVERSIDE COUNTY) | SOUTHERN CALIFORNIA GAS CO | THE SOCALGAS OPERATES AND MAINTAINS AN UNDERGROUND 30-INCH NATURAL GASTRANSMISSION PIPELINE (LINE 2000) PARALLEL TO THE AT&SF TRACK IN THE GENERALAREA OF THE COLLISION SITE. THE DISTANCE FROM OUR PIPELINE TO THE RAILROADTRACKS VARIES FROM 60 TO 70 FEET, WITH THE CLOSEST DEBRIS FROM THE COLLISIONTO OUR PIPELINE BEING APPROXIMATELY 30 FEET. THE PIPELINE WAS INSPECTED INACCORDANCE WITH PRUDENT OPERATING PROCEDURES AND IT WAS DETERMINED THAT THEINTEGRITY OF THE PIPELINE WAS NOT COMPROMISED AT ANY POINT AS A RESULT OF THEFREIGHT TRAIN INCIDENT. ON NOVEMBER 7, 1990, AT APPROXIMATELY 10:30 P.M., WEWERE INFORMED BY AT&SF THAT HEAVY CRANE EQUIPMENT WOULD BE USED OVER OURPIPELINE FOR REPAIR AND CLEANUP PURPOSES. DUE TO THE UNCERTAINTY OF THEPLACEMENT OF THE EMERGENCY RAILROAD EQUIPMENT, THE LINE WAS TAKEN OUT OFSERVICE AND BLOWN DOWN. THIS BLOWDOWN OPERATION TOOK APPROXIMATELY TWO HOURSTO COMPLETE. IN ORDER TO ALLEVIATE AGENCY CONCERNS REGARDING THE INTEGRITY OFOUR LINE 2000 IN THE AREA OF THIS INCIDENT, THE SECTION IN QUESTION WASPOTHOLED AND HYDROSTATICALLY TESTED TO 90 PERCENT OF SMYS WHICH REVERIFIED THEINTEGRITY OF THE PIPELINE. SUPPLEMENTAL REPORT 10/03/94 INDICATED THAT THEINCIDENT HAS BEEN RECLASSIFIED AS "DAMAGE BY OUTSIDE FORCE." THE INCIDENT WASA RESULT OF A TRAIN COLLISION/DERAILMENT. THE OUTSIDE/THIRD PARTY WAS THEATCHISON, TOPEKA AND SANTA FE RAILROAD (AT&SF). | 210000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
416 | 1990-11-01 | LA | other | UNKNOWN (ST MARY COUNTY) | TENNESSEE GAS PIPELINE CO | SUSPECT MARIN VESSEL CAUSED DAMAGE AND SUBSEQUENT RUPTURE. | 500000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
417 | 1990-11-10 | AZ | leaks and spills | UNKNOWN (LA PAZ COUNTY) | EL PASO NATURAL GAS CO | GENERAL PIPE CORROSION IN THE IMMEDIATE AREA CAUSED THE PIPELINE TO RUPTURE AND THE FRICTION OF THE PIPELINE RIPPING IGNITED THE GAS. | 300000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
418 | 1990-11-24 | TX | leaks and spills | UNKNOWN (REFUGIO COUNTY) | FLORIDA GAS TRANSMISSION CO |  | 150000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
419 | 1990-11-27 | KY | other | UNKNOWN (JESSAMINE COUNTY) | DELTA NATURAL GAS CO INC | AT APPROXIMATELY 8:55 A.M. NOVEMBER 27, 1990, DELTA'S NICHOLASVILLE OFFICE RECEIVED A TELEPHONE CALL REPORTING A LINE BREAK ON THE NICHOLASVILLE BY-PASS NEAR KIMBERLY HEIGHTS SUBDIVISION. BILL GARDNER, DELTA'S NICHOLASVILLE/WILMORE DISTRIBUTION SUPERVISOR, AND JOE PEEL AND LAWRENCE RILEY, BOTH CUSTOMER SERVICE REPRESENTATIVES IN THE NICHOLASVILLE SYSTEM, ARRIVED AT THE SCENE IN APPROXIMATELY TEN MINUTES. THEY FOUND THAT DRIFTWOOD INC., A CONTRACTOR FOR GTE, HAD AUGERED THROUGH THE SIX-INCH STEEL TRANSMISSION LINE FEEDING WILMORE. THE PIPELINE HAD A TWO-INCH OPENING THAT WAS BLOWING GAS. BILL GARDNER SHUT IN THE VALVE AT THE NICHOLASVILLE TOWN BORDER STATION DISRUPTING NATURAL GAS SERVICE TO APPROXIMATELY 900 CUSTOMERS IN THE WILMORE SYSTEM. TWENTY-FOUR CUSTOMER SERVICE REPRESENTATIVES FROM DELTA'S NORTHERN & SOUTHERN DIVISIONS WERE DISPATCHED TO WILMORE IN ORDER TO EXPEDITE RESTORATION OF NATURAL GAS SERVICE TO THE AFFECTED CUSTOMERS. THE CUSTOMER SERVICE REPRESENTATIVES TURNED THE GAS OFF AT EACH METER. DELTA'S NORTHERN CONSTRUCTION CREW REPAIRED THE PIPELINE BY REPLACING A TWO FOOT SECTION OF SIX-INCH STEEL PIPE. REPAIRS WERE COMPLETE BY 2:30 P.M. THE PIPELINE WAS THEN PURGED AND ENERGIZED. NATURAL GAS SERVICE HAD BEEN RESTORED TO APROXIMATELY 800 CUSTOMERS BY 11:00 P.M. THAT EVENING. THE REMAINING 100 CUSTOMERS WERE RELIT THE NEXT DAY BEGINNING AT 7:00 A.M. GTE WAS INSTALLING AN ANCHOR FOR A TELEPHONE POLE WHEN THEY HIT WHATTHEY THOUGHT WAS ROCK. THEY CONTACTED DRIFTWOOD INC. FOR ASSISTANCE. DRIFTWOOD DRILLED THROUGH OUR PIPELINE WITH A CARBIDE TIP AUGER. GTE DID NOT CALLDELTA'S OFFICE FOR LINE LOCATION. DELTA HAD LINE MARKER POSTS ON EACH SIDE OF THE HIGHWAY MARKING THE ROAD CROSSING UNDER THE BY-PASS. THE FIRST LINE MARKER POST WAS LOCATED APPROXIMATELY 100 FEET FROM WHERE GTE WAS WORKING.SEVERAL OF DELTA'S YELLOW FLAGS WERE PRESENT WHERE THE LINE HAD BEEN PREVIOUSLY LOCATED IN KIMBERLY HEIGHTS SUBDIVISION. THERE WERE NO INJURIES OR FATALITIES ATTRIBUTABLE TO THIS INCIDENT. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
420 | 1990-11-20 | LA | maintenance | UNKNOWN ( COUNTY) | SOUTHERN NATURAL GAS CO | THE BOLTED BONNETT COVER UTILIZES A RUBBER O-RING GASKET SEAL. APPARENTLY THE RUBBER GASKET HAS CRACKED OR DETERIORATED IN SEVERAL PLACES.PART 3 - DIVERS WERE INSPECTING AN UNUSED UNDERWATER 12" TAP AND DISCOVERED A SLOW RELEASE OF BUBBLES FROM EXISTING CRACKS IN CONCRETE COATING. THE CONCRETE COATING WAS REMOVED AND THE BONNETT GASKET ON THE 12" CHECK VALVE WAS FOUND LEAKING. THE CHECK VALVE IS LOCATED IN 195' OF WATER. | 160000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
421 | 1990-11-26 | TX | other | UNKNOWN (WEBB COUNTY) | VALERO TRANSMISSION CO | REASON FOR FAILURE IS UNKNOWN AT THIS TIME. METALLUGICAL INVESTIGATION IS BEING CONDUCTED. | 105630 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
422 | 1990-11-24 | NY | other | UNKNOWN (RICHMOND COUNTY) | TEXAS EASTERN GAS PIPELINE CO | BARGE OR TUG BOAT APPARENTLY HIT THE PIPELINE UNDER THE AUTHUR KILL RIVER, CAUSING A PUNCTURE THAT ALLOWED GAS TO BLOW TO ATMOSPHERE. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
423 | 1990-12-07 | NM | maintenance | UNKNOWN (TORRANCE COUNTY) | EL PASO NATURAL GAS CO | BELEN COMPRESSOR STATION EXPERIENCED A LOW SUCTION PRESSURE ALARM AT 9:10 PMON DECEMBER6, AND AN ESD AT 9:15 PM. LINCLON COMPRESSOR STATION REPORTED LOWREADINGS AND AT 9:30 PM PERSONNEL WERE DISPATCHED TO PATROL THE PIPELINE TO DETERMINE IF THERE HAD BEEN A PIPELINE FAILURE. THE RUPTURE WAS CONFIRMED AT 12:15 AM WHEN IT WAS DISCOVERED THAT APPROXIMATELY 85 FEET OF PIPELINE HAD BLOWN OUT. THE PIPELINE WAS ISOLATED AT ABOUT 12:45 AM. THERE WAS NO FIRE. NO LAW ENFORCEMENT OR FIRE DEPARTMENTS WERE INVOLVED. THE PIPELINE WAS BLOWN DOWNFROM VALVE 21 TO VALVE 23 (APPRO. 20 MILES).PART C - THE FRACTURE WAS NOT ASSOCIATED WITH A LONGITUDINAL SEAM OR A GIRTHWELD. THE FRACTURE FACE EXHIBITED BRITTLE FEATURES (FLAT FRACTURE WITH CHEVRON MARKINGS) THAT POINTED BACK TO AN AREA APPROXIMATELY 5 INCHES LONG, APPROXIMATELY 9 FEET FROM THE UP STREAM FRACTURED END. THIS AREA MAY HAVE BEEN THE INITIATION SITE, SINCE THE PIECE WAS CLEARLY BENT WITH A RUPTURED AND TORN HOLE ON THE OUTSIDE OF THE BEND. THE PIECE CONTAINED A WRINKLE BEND ON ITS UPSTREAM SIDE THAT EITHER WAS IN THE ORIGINAL PIPELINE OR WAS CAUSED BY TH RUPTURE. THE WRINKLE EXHIBITED A BRITTLE FRACTURE SURFACE WITH MANY CRACKS IN AND AROUND THE BEND. ULTRASONIC, MAGNETIC PARTICLE AND HARDNESS TESTS WERE PERFORMED ON THE POSSIBLE INITIATION SITE. THESE TESTS CONFIRMED A WALL THICKNESSOF .345 TO .350 INCHES. THERE WAS NO EVIDENCE OF INTERNAL OR EXTERNAL CORROSION. HARDNESS TESTING VERIFIED THAT THE AREA AROUND THE POSSIBLE RUPTURE INITIATION SITE WAS 38 HRC INDICATING THAT HYDROGEN STRESS CRACKING OF THE "HARDSPOT" WAS THE CAUSE OF THE FAILURE. | 370299 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
424 | 1990-12-04 | WV | leaks and spills | UNKNOWN (BOONE COUNTY) | CNG TRANSMISSION CORP | RUPTURE OCCURRED IN STREAM CROSSING. ESCAPING GAS IGNITED RESULTING IIN DAMAGE TO DWELLINGS NEAR PIPELINE. | 150000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
425 | 1990-12-16 | MS | other | UNKNOWN (PANOLA COUNTY) | TENNESSEE GAS PIPELINE CO | COMPRESSOR OPERATOR SUFFERED BURNS WHEN GAS LEAKING FROM COMPRESSOR PACKINGIGNITED FROM UNKNOWN SOURCE. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
426 | 1990-12-10 | LA | maintenance | UNKNOWN (IBERVILLE COUNTY) | SOUTHERN NATURAL GAS CO | EMPLOYEES WERE REMOVING MOTOR AND GEARBOX ASSEMBLY FROM COMPRESSOR STATION #3 SCRUBBER. AS THE GEARBOX ASSEMBLY WAS REMOVED, THE SHAFT WAS BLOWN OUT OF THE SCRUBBER INJURING ONE EMPLOYEE. THE APPARENT CAUSE WAS AN INTERNAL BEARING FAILURE WHICH RESULTED IN SHAFT WEAR WHICH BROKE DUE TO ROTATION AGAINST THE BEARING SUPPORTS. THE INJURED EMPLOYEE IS EXPECTED TO RECOVER FULLY. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
427 | 1990-12-06 | LA | other | UNKNOWN (UNKNOWN COUNTY) | TRUNKLINE GAS CO | UNION RIG KEYS #303 DRUG LEGS ACROSS PIPELINE WHILE PREPARING TO SET UP ON UNOCAL SS 253 PLATFORM. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
428 | 1990-12-10 | MS | maintenance | UNKNOWN (COVINGTON COUNTY) | TRANSCO GAS PIPELINE CORP | MECHANICAL WEAR IN BRONZE COMPRESSOR ROD PACKING CAUSED GAS TO ESCAPE AND PASS BY IGNITION TRANSFORMERS. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
429 | 1990-11-17 | NY | other | UNKNOWN (NEW YORK COUNTY) | CONSOLIDATED EDISON CO OF NEW YORK | PRESSURE REGULATORS AT A TRANSMISSION METER STATION LOST CONTROL, ALLOWING DELIVERY PRESSURE TO INCREASE. FURTHER INVESTIGATION DISCLOSED THAT OVERRIDE SYSTEM OPERATED PROPERLY AND MAOP WAS NOT EXCEEDED. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
430 | 1990-12-29 | NE | other | UNKNOWN (FURNAS COUNTY) | K N ENERGY INC(KANSAS NEBRASKA GAS CO) | OVERHEAD CREEK CROSSING WAS HIT BY VEHICLE WHICH RAN OFF A GRAVEL ROAD. | 6000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
431 | 1990-12-18 | NM | maintenance | UNKNOWN (SAN JUAN COUNTY) | EL PASO NATURAL GAS CO | A 1/2" DIAMETER GLYCOL HOSE (FUEL LINE) TO THE DEHYDRATOR ON THE STANOLIND GAS COM. #1A GAS WELL BROKE AND IGNITED, SETTING FIRE TO THE DEHYDRATOR. THEGAS WELL WAS SHUT-IN AND THE FIRE WAS DYING OUT WHEN THE NAVAJO DAM VOLUNTEER FIRE DEPARTMENT ARRIVED AT THE SCENE. AS A PRECAUTIONARY MEASURE, THEY SPRAYED WATER ON AN ADJACENT HYDROCARBON LIQUID STORAGE TANK TO COOL IT OFF. THIS IS A NON-REPORTABLE INCIDENT, BUT WAS REPORTED AS A COURTESY TO THE DOT DUETO THE RESPONSE OF THE VOLUNTEER FIRE DEPARTMENT. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
432 | 1991-01-04 | AR | other | UNKNOWN (CHICOT COUNTY) | TEXAS GAS TRANSMISSION CORP | SINCE 1950, TEXAS GAS HAS OPERATED TWO 20" UNDERGROUND, NATURAL GAS PIPELINES CROSSING THE MISSISSIPPI RIVER AT THE LOCATION DESCRIBED ON THE ATTACHED FORM RSPA F7100.2. THESE LINES HAVE THE TEXAS GAS DESIGNATED NUMBERS OF 20" LINES 5 AND 6. ON JANUARY 4, 1991, AT APPROXIMATELY 5:55 AM., CST, AN UNDERWATER LEAK WAS DISCOVERED ON 20" LINE NO. 6. THE LINE WAS SHUT IN WITHIN 70 MINUTES OF DISCOVERY, AND A TELEPHONIC REPORT WAS MADE BEFORE 11:00 AM. BY TEXASGAS'S SENIOR ATTORNEY, NICK HETMAN. THE 20" NO. 5 LINE WHICH IS LOCATED APPROXIMATELY 150' NORTH OF THE FAILED LINE WAS SHUT IN WITHIN 24 HOURS AS A PRECAUTIONARY MEASURE. EXTREME FLOOD CONDITIONS AND SWIFT CURRENTS HAVE PROHIBITED DIVERS FROM INSPECTING THESE LINES; HOWEVER, SURVEY PARTIES (USING FATHOMETERS) HAVE DETERMINED SOME EXPOSURE OF THE NO. 5 LINE. NO APPARENT LEAKS HAVE BEEN DETECTED ON THE NO.5 LINE AT THIS TIME. REPLACEMENT PLANS FOR 20" LINE NOS. 5 AND 6 ARE UNDETERMINED AT THIS TIME. | 235000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
433 | 1991-01-18 | LA | other | UNKNOWN (WEST FELICIANA COUNTY) | TRANSCO GAS PIPELINE CORP | INCIDENT HAS BEEN VERIFIED TO BE THE 18" UNDERWATER PIPELINE CROSSING THE MISSISSIPPI RIVER. THE AFFECTED RIVER CROSSING WAS ISOLATED BY AUTOMATIC VALVEOPERATORS AT THE TIME OF THE INCIDENT. THE RIVER CROSSING IS ISOLATED & AUTOMATIC VALVE OPERATORS DEACTIVIATED. DUE TO THE RESENT LEVEL AND FLOW CONDITIONS OF THE RIVER, AN INVESTIGATION AT THIS TIME IS IMPOSSIBLE. AS SOON AS RIVER CONDITIONS PERMIT, AN INVESTIGATION OF THE CAUSE AND EVALUATION OF DAMAGE WILL BE CONDUCTED AND A SUPPLEMENTAL REPORT WILL BE FILED TO THE DEPARTMENT OF TRANSPORTATION. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
434 | 1991-01-06 | LA | other | UNKNOWN ( COUNTY) | ANR PIPELINE CO | 2" X 6" CONNECTION LOCATED IN 120' OF WATER IN GULF OF MEXICO. | 125000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
435 | 1991-01-26 | LA | other | UNKNOWN (ASSUMPTION COUNTY) | ACADIAN GAS PIPELINE SYSTEM |  | 105000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
436 | 1991-01-17 | TN | other | UNKNOWN (HAWKINS COUNTY) | EAST TENNESSEE NATURAL GAS CO | PIPELINE STRUCK BY OUTSIDE PARTY EXCAVATING SOIL FROM PIPELINE RIGHT-OF-WAY. NO PRIOR NOTIFICATION OF EXCAVATION WAS GIVEN BY OUTSIDE PARTY. PIPELINE IS MARKED WITH PERMANENT PIPELINE MARKERS IN AREA OF EXCAVATION. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
437 | 1991-01-18 | LA | other | UNKNOWN (TERREBONNE COUNTY) | UNITED GAS PIPELINE CO | TUG KAREN ELIZABETH, WITH FOUR EMPTY ARGES IN TOW, SRUCK AND RUPTURED 12" LINE CROSSING INTRACOASTAL CANAL IN TERREBONNE PARISH. | 500000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
438 | 1991-02-25 | OK | leaks and spills | UNKNOWN (CANADIAN COUNTY) | CONOCO INC |  | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
439 | 1991-02-10 | LA | leaks and spills | UNKNOWN ( COUNTY) | NATURAL GAS PIPELINE CO OF AMERICA |  | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
440 | 1991-02-05 | IA | maintenance | UNKNOWN (MARION COUNTY) | NATURAL GAS PIPELINE CO OF AMERICA |  | 53800 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
441 | 1991-01-22 | AR | maintenance | UNKNOWN (HOT SPRING COUNTY) | NATURAL GAS PIPELINE CO OF AMERICA |  | 71700 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
442 | 1991-02-15 | TX | other | UNKNOWN (BROOKS COUNTY) | VALERO INTERSTATE TRANSMISSION CO |  | 143000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
443 | 1991-02-17 | CA | leaks and spills | UNKNOWN (LOS ANGELES COUNTY) | SOUTHERN CALIFORNIA GAS CO | ON FEBRUARY 17, 1991, AT APPROXIMTELY 1:10 AM., WE DISCOVERED LEAK WHICH WASLATER DETERMINED TO BE CAUSED BY INTERNAL CORROSION. THE PIPELINE WAS SHUT-IN AT 1:25 AM. REPAIRS WERE MADE BY INSTALLING A 4" LEAK CLAMP. THE PIPELINE HAS NOT BEEN RETURNED TO SERVICE. NO CUSTOMERS WERE AFFECTED BY THE SHUT DOWN, NOR WERE THERE ANY FIRES OR INJURIES ASSOCIATED WITH THIS INCIDENT. ESTIMATED COSTS ASSOCIATED WITH THIS INCIDENT WERE $60,000. DOT NOTIFICATION 02/20/91, REFERENCE REPORT #60472. | 60000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
444 | 1991-02-15 | PA | maintenance | UNKNOWN (LYCOMING COUNTY) | TRANSCO GAS PIPELINE CORP | AT APPROXIMATELY 8:50 PM. EST ON FEBRUARY 15, 1991, TRANSCONTINENTAL GAS PIPELINE CORPORATIONS'S 12,600 HP SOLAR MARS TRUBINE EXPERIENCED A SLIGHT EXPLOSION, CAUGHT FIRE, AND BURNED. THE APPARENT CAUSE OF THE INCIDENT IS UNKNOWNAT THIS TIME. A TASK GROUP, CONSISTING OF PERSONNEL FROM TRANSCO, SOLAR, ANDA NEUTRAL OR OUTSIDE PARTY, HAS BEEN ESTABLISHED AND IS INVESTIGATING THE INCIDENT. UPON COMPLETION OF THE INVESTIGATION, A SUPPLEMENTAL REPORT WILL BEFILED WITH THE DEPARTMENT OF TRANSPORTATION. THE CAUSE OF THE INCIDENT WASTHE FAILURE OF A PORTION OF THE INLET GAS SCRUBBER INTERNALS WHICH RESULTED ONAPPROXIMATELY SIX POUNDS OF STEEL BEING CARRIED DOWN THE SUCTION LINE UNTILTHESE PIECES IMPACTED THE CENTRIFUGAL COMPRESSOR. THE TREMENDOUS FORCERESULTING FROM THE IMPACT LED TO TOTAL FAILURE OF THE COMPRESSOR BEARINGS ANDGAS SEALING SYSTEM AND THE RELEASE OF HIGH PRESSURE GAS (APPROXIMATELY 1,000PSIG) INTO THE COMPRESSOR BUILDING WHICH INITIATED THE FIRE. | 6000000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
445 | 1991-03-31 | TX | leaks and spills | UNKNOWN (SMITH COUNTY) | LONE STAR GAS CO | LINE BLEW OUT CREEK BOTTOM. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
446 | 1991-03-23 | IA | other | UNKNOWN (WRIGHT COUNTY) | NORTHERN NATURAL GAS CO (ENRON) | FROST HEAVE AND/OR FLOTATION CAUSED PIPE TO RAISE UP, RESULTING IN A LEAK ATA DRESSER COUPLED JOINT. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
447 | 1991-04-01 | OR | other | UNKNOWN (UNION COUNTY) | NORTHWEST PIPELINE CORP | A CABLE PLOWING TRACTOR, LAYING TELEPHONE CABLE STRUCK THE PIPELINE; 3" X 4"PUNCTURE. | 87600 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
448 | 1991-03-12 | MO | other | UNKNOWN (BUCHANAN COUNTY) | WILLIAMS NATURAL GAS CO | FARMER BURNING BRUSH AND GRASS NEAR VALVE CAUSED PACKING TO FAIL. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
449 | 1991-04-13 | KY | other | UNKNOWN (MARTIN COUNTY) | COLUMBIA GAS TRANSMISSION CORP | PASSENGER VEHICLE BROKE THROUGH BARRICADE AND HIT DRIP LINE RESULTING IN BELOW GROUND BREAK AT SHUT-OFF VALVE. 1/2" DRIP LINE BROKEN OFF BY PASSENGER VEHICLE ACCIDENT RESULTING IN IGNITION AND DESTRUCTION OF TWO MOTOR VEHICLES AND HOSPITALIZATION OF DRIVER. | 18400 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
450 | 1991-04-16 | OK | other | UNKNOWN (GRANT COUNTY) | WILLIAMS NATURAL GAS CO | A NATURAL GAS LEAK OCCURRED INSIDE A COMPRESSOR STATION BUILDING. THE GAS WAS IGNITED APPARENTLY BY AN ELECTRICAL SOURCE IN AN ADJACENT PART OF THE STRUCTURE. A COMPRESSOR VALVE CAP IS BELIEVED TO BE THE ORIGIN OF THE LEAK. | 400000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
451 | 1991-05-01 | TX | leaks and spills | UNKNOWN (UNKNOWN COUNTY) | BLUE DOLPHIN PIPELINE CO | WAS IN THE PROCESS OF PRESSURE TESTING THE PIPELINE WITH NATURAL GAS TO ESTABLISH AN NEW MAOP. LEAK OCCURRED AT APPROXIMATELY 500 PSI. PRESSURE WAS BLED TO 300 PSI AT WHICH TIME DIVERS INSTALLED A 1500 PSI WP BOLTED CLAMP. THE PIPELINE AND CLAMP WERE THEN PRESSURE TESTED TO 750 PSI WITH NATURAL GAS. NOOTHER LEAKS OCCURRED. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
452 | 1991-05-14 | NE | other | UNKNOWN (SCOTTS BLUFF COUNTY) | K N ENERGY INC(KANSAS NEBRASKA GAS CO) | THIS REPORT COVERS A LINE HIT THAT OCCURRED ON KN ENERGY, INC.'S (K N'S) 16-INCH STEEL, BURIED TRANSMISSION PIPELINE IN SCOTTS BLUFF COUNTY, NEBRASKA ON MAY 14, 1991. IGNITION DID NOT OCCUR AND THERE WERE NO INJURIES FATALITIES AS A RESULT OF THE LINE BEING HIT. SERVICE WAS TEMPORARILY INTERRUPTED TO APPROXIMATELY 100 CUSTOMERS IN THE COMMUNITY OF MINATARE, NEBRASKA. THE PIPELINE WAS HIT BY AN OUTSIDE PARTY OPERATING A "V" PLOW PULLED BY A LARGE TRACTOR.THE DAMAGED PORTION OF THE PIPELINE WAS IN A CLASS 1 LOCATION AND WAS MARKEDWITH PERMANENT LINE MARKERS. A PERMANENT REPAIR WAS COMPLETED BY USE OF A WELD SLEEVE. TELEPHONIC REPORT OF THE ABOVE INCIDENT WAS TRANSMITTED ON REPORT #71985 TO THE DEPARTMENT OF TRANSPORTATION AND TO THE NEBRASKA STATE FIRE MARSHAL'S OFFICE IN LINCOLN, NEBRASKA ON MAY 14, 1991. | 25000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
453 | 1991-05-07 | MI | other | UNKNOWN (OAKLAND COUNTY) | CONSUMERS POWER CO | EXPLOSION RESULTED WHEN GAS WAS VENTED FROM PIPING LOCATED AT THE CITY GATESTATION. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
454 | 1991-05-14 | AR | leaks and spills | UNKNOWN (MILLER COUNTY) | NATURAL GAS PIPELINE CO OF AMERICA | INTERNAL CORROSION SUSPECTED | 97000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
455 | 1991-06-09 | TX | leaks and spills | UNKNOWN (CRANE COUNTY) | VALERO TRANSMISSION CO | THE PIPELINE RUPTURED AT APPROXIMATELY 5 AM. ON JUNE 9, 1991. PROBABLE CAUSE IS EXTERNAL CORROSION PENDING VERIFICATION BY METALLURGICAL ANALYSIS. NO FIRE AND NO INJURIES. PIPELINE REPAIRED BY REPLACING WITH NEW PIPE. LINE BACKIN SERVICE ON JUNE 12,1991. | 325000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
456 | 1991-06-01 | AR | other | UNKNOWN (PULASKI COUNTY) | TEXAS EASTERN GAS PIPELINE CO | BULLDOZER MOVING FILL DIRT ON LEVEE, GOUGED A 5.5" X 1.5" X 5.75" PUNCTUREOF THE PIPELINE. NO FIRE OR FATALITIES OCCURRED. | 90000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
457 | 1991-06-11 | PA | other | UNKNOWN (WASHINGTON COUNTY) | PEOPLES NATURAL GAS CO |  | 51000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
458 | 1991-06-19 | KS | other | UNKNOWN (GRAHAM COUNTY) | K N ENERGY INC(KANSAS NEBRASKA GAS CO) |  | 3300 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
459 | 1991-07-17 | PA | leaks and spills | UNKNOWN (CLARION COUNTY) | CNG TRANSMISSION CORP |  | 60250 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
460 | 1991-04-10 | KS | other | UNKNOWN (SEDGWICK COUNTY) | KANSAS NATURAL INC | ELY 4:45 AM., THE LIQUIDS IN FRONT OF THE TPIG BEGAN TO ARRIVE AT THE FACILITY. THE LIQUIDS WERE SEPARATED FROM THE GAS IN A SEPARATOR AND THEN LEVEL CONTROLLED INTO TWO FRAC TANKS. DUE TO THE VOLATILITY OF THE LIQUIDS, HYDROCARBON VAPOR WAS GENERATED OUT OF THE FRAC TANKS. BECAUSE OF COOL AND CALM WEATHER CONDITIONS, THE VAPORS ACCUMULATED ALONG THE GROUND AROUND THE TANKS. ATAPPROXIMATELY 5:15 AM., THE VAPORS IGNITED AND A FLASH FIRE RESULTED. ONE OF THE INDIVIDUALS PRESENT WAS SEVERELY BURNED. THE APPARENT SOURCE OF IGNITION WAS THE ENGINE OF AN EMPLOYEE'S PICK-UP OPERATING NEAR THE TANKS. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
461 | 1991-08-06 | LA | leaks and spills | UNKNOWN (RED RIVER COUNTY) | UNITED GAS PIPELINE CO | INVESTIGATION INDICATES INNER DIAMETER FAILURE OF A LONGITUDINAL WELD SEAM ATTRIBUTED TO INTERNAL CORROSION. | 344174 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
462 | 1991-08-03 | LA | leaks and spills | UNKNOWN ( COUNTY) | ANR PIPELINE CO | SUSPECTED INTERNAL CORROSION; NOT VERIFIED SINCE GRIPPER CLAMP WAS INSTALLED. | 101800 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
463 | 1991-08-19 | OK | other | UNKNOWN (TULSA COUNTY) | TRANSOK INC | A BULLDOZER OPERATED BY BENNY CRAIG, SHERWWOD CONT\STRUCTION 4716 N. 193 E. AVE. TULSA, OKALHOMA 918-266-6861, WAS BUILDING A TEMPORARY BYPASS ROAD ALONGMINGO ROAD FOR THE OKLAHOMA DEPARTMENT OF TRANSPORTATION. THE BULLDOZER HITTHE PIPELINE RESULTING IN THE TEAR. | 16700 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
464 | 1991-08-02 | IN | other | UNKNOWN (PORTER COUNTY) | NORTHERN INDIANA PUBLIC SERVICE CO | CONTRACTOR WAS CLEARING THE AREA OF TREES AND BRUSH, USING A BULLDOZER, WHENHE PUNCTURED THE LINE THAT WAS CLEARLY MARKED. THE LEAKING GAS SOMEHOW IGNITED, CAUSING BURNES TO UPPER HALF OF THE BODY OF THE OPERATOR AND DESTROYING THE EQUIPMENT. | 400000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
465 | 1991-07-23 | MS | other | UNKNOWN (LOWNDES COUNTY) | TENNESSEE GAS PIPELINE CO | GAS ESCAPING FROM TWO IMPROPERLY SEATED VALVE CAP GASKETS IGNITED CAUSING BURNES TO FOUR WORKMEN IN THE VICINITY. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
466 | 1991-07-23 | KY | other | UNKNOWN ( COUNTY) | TENNESSEE GAS PIPELINE CO | AN EQUIPMENT OPERATOR DIGGING NEAR OUR LINE, GOUGED THE PIPELINE, CAUSING A LEAK AND SUBSEQUENT RUPTURE. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
467 | 1991-08-03 | PA | other | UNKNOWN (MONTGOMERY COUNTY) | TEXAS EASTERN GAS PIPELINE CO | WIND FROM STORM BLEW PART OF ROOF FROM A NEARBY WAREHOUSE INTO THE CONTROL LINE FOR A PRESSURE REGULATOR AT MEASURING STATION 517. THE PRESSURE REGULATOROPENED FULLY AND THE RELIEF VALVE WAS ACTIVATED AT 220 PSI AS DESIGNED. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
468 | 1991-05-10 | MT | other | UNKNOWN (FLATHEAD COUNTY) | MONTANA POWER CO | A LARGE LOG LOADER WAS PICKING UP LOGS STACKED IN THE AREA TRAVERSEE BY THE PIPELINE. IN AN EFFORT TO GET UNDER THE BOTTOM OF THE STACK, A LARGE BOTTOM TINE ON THE LOADER WAS DRIVEN BELOW THE SURFACE OF THE GROUND COVERING THE PIPELINE, PENATRATING THE PIPELINE. | 145757 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
469 | 1991-08-29 | OH | leaks and spills | UNKNOWN (RICHLAND COUNTY) | COLUMBIA GAS TRANSMISSION CORP | RUPTURE OF UNDERSLUNG PIPELINE DRIP LIFTED APPROXIMATELY 165' OF 20" PIPELINE OUT OF GROUND. INTERNAL CORROSION RESULTED IN A BRITTLE FRACTURE TYPE FAILURE. | 280000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
470 | 1991-09-21 | NC | other | UNKNOWN (WILSON COUNTY) | NORTH CAROLINA NATURAL GAS CORP | CONTRACTOR LAYING PARALLEL PIPELINE HIT EXISTING LINE TRACK HOE BUCKET. | 80000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
471 | 1991-09-24 | CA | other | UNKNOWN (LOS ANGELES COUNTY) | SOUTHERN CALIFORNIA GAS CO | FIRE. ON SEPTEMBER 24, 1991, AT APPROXIMATELY 6:30 PM, A FIRE OF UNKKNOWNORIGIN DESTROYED THE CONTENTS OF THE INSTRUMENTATION BUILDING AT THISFACILITY. GAS WAS CONTROLLED BY CLOSING THE VALVES ON PIPING LEADING INTO THEBUILDING. INVESTIGATION INTO THE CAUSE OF THE FIRE IS ON-GOING. NOCUSTOMERS WERE AFFECTED BY THE SHUTDOWN, NOR WERE THERE INJURIES ASSOCIATEDWITH THIS INCIDENT. ESTIMATED COSTS ASSOCIATED WITH THIS INCIDENT WERE$100,000. SUPPLEMENTAL REPORT 10/03/94 INDICATES THAT THE MOST LIKELY CAUSE OFTHE INCIDENT WAS AN ELECTRICAL SURGE RESULTING IN AN ARC THAT IGNITED GAS INTHE EQUIPMENT. ADDITIONAL INFORMATION INDICATED THAT THERE IS NOT CONCLUSIVEEVIDENCE AS TO THE CAUSE OF THE INCIDENT. MOST PROBABLE - ELECTRICAL SURGECAUSING FAILURE IN THE SYSTEM AND RESULTING IN AN ARC IGNITING GAS INSIDE THEEQUIPMENT. | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
472 | 1991-09-17 | LA | other | UNKNOWN (GULF OF MEXICO COUNTY) | CHEVRON USA INC | THE EXACT TIME OF INCIDENT IS UNKNOWN BECAUSE THE PIPELINE WAS NOT PRESSUREDUP DUE TO CONSTRUCTION ACTIVITIES AT MP 299 "B". | 300000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
473 | 1991-09-28 | LA | other | UNKNOWN (ASCENSION COUNTY) | MONTEREY PIPELINE CO | LINE WAS HIT BY A BACKHOE DIGGING IN THE AREA. | 75000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
474 | 1991-04-05 | TX | other | UNKNOWN (BASTROP COUNTY) | VALERO TRANSMISSION CO | VALVE (6") CASTING CRACKED FOR UNKNOWN REASON. THIS 6" VALVE WAS REMOVED AND THE 6" LINE WAS TIED INTO THE 12" LINE. | 7500 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
475 | 1991-03-27 | TX | other | UNKNOWN (NAVARRO COUNTY) | LONE STAR GAS CO | LINE WAS CUT INTO BY LAND OWNER USING BULL DOZER | 20000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
476 | 1991-02-26 | TX | maintenance | UNKNOWN (FORT BEND COUNTY) | UNITED TEXAS TRANSMISSION CO | UNITED TEXAS PERSONNEL FOUND DURING LEAK ANNUAL VALVE INSPECTION AND DISCOVERED A CRACK IN THE VALVE FLANGE. FOUND CRACK ON BOTTOM OF 8" FLANGE. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
477 | 1991-02-09 | TX | other | UNKNOWN (FANNIN COUNTY) | LONE STAR GAS CO | LINE WAS STRUCK AND PUNCTURED BY A DOZER BEING USED TO FILL IN AN OLD POND. | 5000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
478 | 1991-10-08 | CA | other | UNKNOWN (SANTA CLARA COUNTY) | PACIFIC GAS & ELECTRIC CO | CONTRACTOR STRUCK TRANSMISSION LINE WITH BULLDOZER CASUING SEVERAL DENTS ANDGOUGES; PRESSURE REDUED IN LINE TO SAFE PRESSURE. SECTION REPLACED | 60000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
479 | 1991-09-22 | TX | other | UNKNOWN ( COUNTY) | VALERO TRANSMISSION CO | THE PILELINE RUPTURED SEPTEMBER 22, 1991 FROM UNDETERMINED CAUSES AND WAS TAKEN OUT OF SERVICE IMMEDIATELY. THE RUPTURED SECTION WAS REPLACED AND PIPELINE WAS PLACED IN SERVICE ON OCTOBER 17, 1991. A METALLURGICAL ANALYSIS OF THE FAILED PIPE IS BEING CONDUCTED TO DETERMINE THE CAUSE OF THE FAILURE. EXPECTED COMPLETION DATE IS DECEMBER 15, 1991. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
480 | 1991-09-27 | LA | leaks and spills | UNKNOWN ( COUNTY) | ANR PIPELINE CO | LOCALIZED INTERNAL CORROSION, | 323000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
481 | 1991-10-18 | LA | leaks and spills | UNKNOWN ( COUNTY) | SOUTHERN NATURAL GAS CO |  | 120000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
482 | 1991-05-14 | TX | other | UNKNOWN (HENDERSON COUNTY) | TEXAS UTILITIES FUEL CO | TUFCO'S 16" PIPELINE WAS STRUCK AND PUNCTURED BY EQUIPMENT USED BY A THIRD PARTY CONTRACTOR INSTALLING A FIBER-OPTIC TELEPHONE CABLE. | 55000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
483 | 1991-06-07 | TX | other | UNKNOWN (HOPKINS COUNTY) | TEXAS UTILITIES FUEL CO | LIGHTNING STRIKE TO STEEL DUMP LINE ATTACHMENT TO 210 BBL. FIBERGLASS NATURAL GAS CONDENSATE STORAGE TANK. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
484 | 1991-06-12 | TX | leaks and spills | UNKNOWN (JEFFERSON COUNTY) | UNITED TEXAS TRANSMISSION CO | DUPONT EMPLOYEE DISCOVERED BUBBLES AROUND PIPELINE CASING VENT. UTTCO CREW EXCAVATED AND DISCOVERED LEAK COMING FROM INSIDE FILLED CASING. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
485 | 1991-07-09 | TX | other | UNKNOWN (BAYLOR COUNTY) | LONE STAR GAS CO | PIPE WAS HIT BY PLOW, KNOCKING A SMALL HOLE 1/2" DEEP. | 7000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
486 | 1991-08-19 | TX | other | UNKNOWN (KNOX COUNTY) | LONE STAR GAS CO | MR. BROWN'S EMPLOYEE WAS DEEP PLOWING WITH A MOLD BOARD BREAKING PLOW WHEN THE PLOW STRUCK THE LINE CAUSING A HOLE AND LOSS OF GAS. | 6800 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
487 | 1991-08-20 | TX | other | UNKNOWN (DONLEY COUNTY) | LONE STAR GAS CO | LINE WAS HIT BY PLOW. | 7600 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
488 | 1991-08-22 | TX | other | UNKNOWN (LEON COUNTY) | TEXAS UTILITIES FUEL CO | THIRD PARTY RIGHT-OF-WAY CLEARING CREW WERE WORKING ON TUFCO R.O.W. CONTRACTOR'S EQUIPMENT SHEARED A 2 INCH VALVE FROM A TWO INCH RISER THAT WAS CONNECTED TO THE 8" PIPELINE. | 5296 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
489 | 1991-09-16 | TX | other | UNKNOWN (PALO PINTO COUNTY) | LONE STAR GAS CO | DOZER WAS DIGGING A DRILLING SITE AND HIT THE LINE CAUSING HOLE IN THE PIPE. PIPELINE ROAD MARKINGS WERE 2998' FROM THE INCIDENT. | 22634 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
490 | 1991-04-05 | OK | other | UNKNOWN (GARVIN COUNTY) | LONE STAR GAS CO | LINE WAS HIT BY FRONT END LOADER. | 6827 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
491 | 1991-10-30 | OK | other | UNKNOWN (COMANCHE COUNTY) | TRANSOK INC | BULLDOZER OPERATOR RICKY NUNN CALLED IN TEAR AT 16:10 DURING CONVERSTATION HE STATED NO NOTIFICATION HAD BEEN GIVEN TO ANYU ONE-CALL SYSTEM. A BULLDOZEROPERATED BY RICKY NUNN'S DOZER SERVICE WAS BURYING TRASH FOR LAND OWNER (DALE COOBY). WHILE DIGGING TRASH PIT TRANSOK INC. PIPELINE WAS STRUCK RESULTINGIN 1/4" ROUND TEAR. | 12500 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
492 | 1991-10-24 | LA | other | UNKNOWN (ST JOHN THE BAPTIST COUNTY) | UNITED GAS PIPELINE CO | CONTRACTOR INSTALLING A NEW LINE, TO REPLACE INCIDENT INVOLVED FACILITY, CAUSED EARTH MOVEMENT WHICH RESULTED IN SEPARATION AT A COUPLING. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
493 | 1991-10-25 | KS | other | UNKNOWN (OSBORNE COUNTY) | WILLIAMS NATURAL GAS CO | FARMER TORE HOLE IN PIPELINE WITH DEEP GROUND RIPPER. | 5000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
494 | 1991-11-01 | CA | other | UNKNOWN (KERN COUNTY) | ARCO OIL & GAS CO - DIV OF ATLANTIC RICHFIELD | ON 11/1/91 AT APPROXIMATELY 10:15 A.M. A 1986 TOYOTA COROLLA WAS TRAVELLING EASTBOUND ON HIGHWAY 119 APPROXIMATELY 1.3 MILES EAST OF THE INTERSEDTION OF UTUPMAN ROAD AND HIGHWAY 119. THE VEHICLE VEERED OFF THE SOUTH SIDE OF THE HUGHWAY TRAVELLING APPROXIMATELY 525 FEET ACROSS UNDISTURBED LAND. THE VEHICLE CROSSED A PRIVATE ROAD EMBANKMENT AND CAME TO REST IN AN EXCAVATION. THE EXCAVATION WHICH WAS BARRICADED HAD BEEN DUG BY ARCO OIL AND GAS COMPANY TO MAKE REPAIRS TO A VALVE BOX. THE VEHICLE STRUCK AND DAMAGED A 2"X4" CONNECTIONON THE 1`0 INCH LINE CAUSING A RELEASE OF NATURAL GAS. NO PERSONAL INJURIESOCCURED. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
495 | 1991-11-05 | WV | leaks and spills | UNKNOWN (RANDOLPH COUNTY) | COLUMBIA GAS TRANSMISSION CORP | RELATED CORROSION ACROSS ADJACENT FULL ENCIRCLEMENT FITTING AND OTHER PIPE TOTALED APPROXIMATELY 32" IN LENGTH X MAXIMUM 9" WIDTH. REMAINING PIPE IN EXCELLENT CONDITION. | 34000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
496 | 1991-10-17 | AR | other | UNKNOWN (LAFAYETTE COUNTY) | LOUISIANA - NEVADA TRANSIT | ARKANSAS ACT 762 OF 1991 SPECIFIES THAT ANYONE DIGGING IN THE VICINITY OF GAS OR HAZARDOUS CHEMICALS IS REQUIRED TO GIVE NOTICE TO THE ARKANSAS ONE-CALL CENTER. NO NOTICE RECEIVED. I ATTEMPTED TO NOTIFY D.O.T. BEGINNING AT 4:45 P.M. ON THAT DATE AT 1-800-424-8802 BUT REACHED A RECORDING. I TRIED AGAIN ON THE FOLLOWING DAT AND WAS STILL UNSUCCESSFUL. TELEPHONIC NOTICE WAS GIVEN TO THE ARKANSAS PUBLIC SERVICE COMMISSION, PIPELINE SAFETY DEPARTMENT, ON OCTOBER 17, 1991. DOZER OPERATED BY TIMBER COMPANY LOGGING IN THE VICINITY OF LNT MAINLINE DUG INTO LINE CAUSING A TEAR APPTOXIMATELY 3" X 10". ELECTRIC LINES IN THE AREA MAY HAVE BEEN A FACTOR IN THE IGNITION WHICH BURNED THE DOZER. OPERATOR ESCAPED INJURY. | 66400 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
497 | 1991-11-12 | KS | other | UNKNOWN (KEARNY COUNTY) | COLORADO INTERSTATE GAS CO | COMBUSTION GASES FROM THE CYLINDER OF A GAS COMPRESSOR ENGINE ESCAPED THRU THE STARTING AIR INTAKE VALVE INTO THE STARTING AIR SYSTEM. AN EXPLOSION OCCURRED IN THE AIR PIPING IN THE COMPRESSOR & AUXILIARY BUILDINGS WHEN ACCUMULATED OIL FROM THE AIR IN THE COMPRESSOR & AUXILIARY BUILDINGS WHEN ACCUMULATED BLUBRICATING OIL FROM THE AIR COMPRESSORS IGNITED. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
498 | 1991-11-05 | LA | leaks and spills | UNKNOWN (CAMERON COUNTY) | TENNESSEE GAS PIPELINE CO | PIPELINE RUPTURED, CAUSING A FIRE AT CANAL CROSSING IN A RICE FIELD. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
499 | 1991-11-25 | NM | other | UNKNOWN (LEA COUNTY) | MAPLE GAS CORP | PIPELINE WAS ACQUIRED FROM TUCO, INC IN 1979 AND NO TEST RECORDS WERE TRANSFERRED AT THE TIME OF ACQUISITION.THIS IS THE PIPELINE WE BELIEVE SHOULD BE CLASSIFIED AS A GATHERING LINE. UNTIL A FINAL DETERMINATION IS MADE ON THE PROPER CLASSIFICATION OF THIS LINE,WE ARE CONTINUING INSPECTION, MAINTENANCE AND RECORDKEEPING FUNCTIONS AS THOUGH THE LINE WERE A TRANSMISSION LINE. THEREFORE WE ARE FILING THIS REPORT.AS I MENTIONED TO YOU, THE LEAK WAS DISCOVERED ON NOVEMBER 25, 1991 AND REPAIRED THE SAME DAY. AT THE TIME THE LEAK WAS DISCOVERED, IT WAS BELIEVED THE GAS LOSS WAS MINIMAL AND NOT OF A REPORTABLE QUANTITY. HOWEVER, WHEN MONTHLY VOLUMES WERE BALANCED, IT APPEARED THAT THE GAS LOSS WAS LARGER THAN ORIGINALLY THOUGHT AND WAS OF A REPORTABLE QUANTITY. | 300000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
500 | 1992-01-03 | PA | other | UNKNOWN (GREENE COUNTY) | COLUMBIA GAS TRANSMISSION CORP | SUBSTRATE COAL SEAM UNDER EFFECTED AREA WAS NOT MINED. SUBSIDENCE WAS NOT EXPECTED. ACTIVE MINING 1000 FEET AWAY. PIPELINE BROKE IN SCREW COUPLING DUETO LONGWALL MINING SUBSIDENCE. GAS MIGRATED 26 FEET TO HOUSE. EXPLOSION OCCURRED; HOUSE AND VEHICLE DESTROYED. IGNITION SOURCE UNKNOWN. | 105000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
501 | 1991-12-14 | OK | other | UNKNOWN (MCCLAIN COUNTY) | ONEOK EXPLORATION CO | LINE LOCATED AND GLAGGED IN 5 AREAS WHERE THE LINE WAS TO BE CROSSED. A PERMANENT CROSSING MARKER WAS WITHIN 60' OF THE POINT WHERE THE LINE WAS HIT. DOZER OPERATOR DEVIATED FROM PREDETERMINED ROUTE, WHICH WAS AGREED UPON BY CONTRACTOR AND ONEOK SERVICES, BY MAKING A LONG RADIUS TURN CHANGING DIRECTION FROM NORTH TO WEST. THE DOZER OPERATOR WAS PLOWING IN TELEPHONE CABLE AND HITTHE GAS LINE WHILE IN A TURN TO CHANGE DIRECTIONS BY 90 DEGREES. DOZER OPERATOR WAS TO TRAVEL PERPENDICULAR TO THE GAS LINE, MOVING NORTH TOWARD THE LINE AND TURNING 90 DEGREES TO TRAVEL WEST PARALLEL TO THE GAS LINE WITHOUT NEEDING TO CROSS OR BE "NEAR" THE GAS LINE. | 42200 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
502 | 1991-12-31 | VA | other | UNKNOWN (LOUDOUN COUNTY) | COLUMBIA GAS TRANSMISSION CORP | CONTRACTOR EMPLOYEE WAS HAMMERING HARD ON ROOF GAS VENT PIPE AND CAUSED A RELIEF DEVICE TO ACTIVATE. THE THRUST, FROM THE UNINTENDED RELEASE OF GAS, THREW THE EMPLOYEE OFF THE ROOF CAUSING INJURY. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
503 | 1992-01-19 | TX | other | UNKNOWN (RAINS COUNTY) | LONE STAR GAS CO | GAS CONTAINING HYDROGEN SULFIDE WAS ALLOWED TO ENTER TRANSMISSION SYSTEM. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
504 | 1992-01-20 | FL | maintenance | UNKNOWN (BRADFORD COUNTY) | FLORIDA GAS TRANSMISSION CO | THE FLANGE GASKET WHICH DEVELOPED THE LEAK WAS INSTALLED USING A FIBER GASKET AND A SEALER. THE SEALANT MATERIAL DAMAGED THE FIBER GASKET INSTALLATION RESULTING IN A LEAK. | 400000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
505 | 1991-12-07 | KS | other | UNKNOWN (SEWARD COUNTY) | CENTANA ENERGY CORP | ON DECEMBER 02/1991 JIM WHISENNAND, THE OWNER OF J&J OILFIELD SERVICE, PLACEDA ONE-CALL OPERATOR INFORMED MR. WHISENNAND THAT CENTANA ENERGY HAD FACILITIES IN THE AREA WHERE THE LINE RUPTURE OCCURRED ALONG WITH PANHANDLE EASTERN PIPELINE COMPANY (PEPL) AND SOUTHWESTERN BELL. ON DECEMBER 07, 1991 J&J OILFIELD SERVICE STARTED CONSTRUCTION IN THE AREA WHERE THE LINE RUPTURE OCCURRED. NO ONE AT CENTANA IS AWARE OF ANY ATTEMPT BY J&J OILFIELD SERVICE TO CONTACT CENTANA ENERGY CONCERNING FACILITIES IN THIS AREA. THEN AT 3:30 P.M. CENTANA'S 6" LINE WAS HIT AND RUPTURED CAUSING A LEAK AND SHORTLY THEREAFTER A FIR | 230000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
506 | 1992-01-09 | LA | other | UNKNOWN (VERMILION COUNTY) | NERCO OIL & GAS INC | TUG WAS PULLING ANCHORS TO DERRICK BARGE WHEN ANCHOR CABLE RUBBED HOLE IN PIPELINE. DRY GAS ESCAPED. NO POLLUTION. PLATFORM SUPPLYING GAS TO PIPELINE SHUTIN ON PSL. PIPELINE BLEW DOWN IN APPROXIMATELY 45 MINUTES. LINE INSTALLED IN 1971. NOT BURIED. REPAIRED WITH SLEEVE. | 65000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
507 | 1992-01-18 | LA | other | UNKNOWN (ST CHARLES COUNTY) | BRIDGELINE GAS DISTRIBUTION CO | A TEXACO 4" GAS PIPELINE RUPTURED IN A PIPE RACK AREA OF TEXACO'S PARADIS PLANT AROUND 5:00 O'CLOCK P.M. ON 1/18/92. BRIDGELINE'S LULING SYSTEM SUPPLY REGULATOR STATION IN LOCATED ADJACENT TO WHERE THIS TEXACO 4" PIPELINE RUPTURED. UPON RUPTURING, THE TEXACO 4" PIPELINE WHIPPED INTO A 1" FLANGED CONNECTION ON BRIDGELINE'S LULING SYSTEM PIPING UPSTREAM OF A REGULATOR STATION. THEIMPACT OF THE 4" PIPELINE ON BRIDGELINE'S 1" FLANGED CONNECTION CAUSED A 1" WELDNECK FLANGE TO SPLIT OPEN AND LEAK GAS. BECAUSE THE LOCATION OF THE LEAKON BRIDGELINE'S PIPING WAS UPSTREAM OF THE REGULATOR STATION, SEVERAL PLANT VALVES HAD TO BE CLOSED IN ORDER TO STOP THE GAS FROM LEAKING. BRIDGELINE DECIDED TO REPORT THE LEAKING 1" FLANGED CONNECTION AS AN INCIDENT WHEN IT WAS LEARNED THAT IT WOULD TAKE TIME TO CLOSE ALL OF THE TEXACO PLANT VALVES SUPPLYING GAS TO BRIDGELINE'S LEAKING PIPING. BRIDELINE FELT THAT THIS LEAK WAS SIGNIFICANT AT THE TIME OF THE INITIAL INVESTIGATION BECAUSE IT WAS UNKNOWN WHETHER THE RUPTURED TEXACO 4" LINE HAD CAUSED ANY OTHE DAMAGE TO BRIDGELINE PIPEING. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
508 | 1992-02-10 | HI | other | UNKNOWN (HONOLULU COUNTY) | GASCO INC | CONRACTOR EXCAVATING FOR NEARBY OIL LINE, PUNCTURED GAS LINE WITH TOOTH OF BACKHOE FRONT BUCKET. CONTRACTOR WAS TOLD GASCO WOULD COME OUT THE NEXT DAY. | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
509 | 1992-02-07 | TX | other | UNKNOWN (AUSTIN COUNTY) | UNITED TEXAS TRANSMISSION CO | ON FEBRUARY 4, 1992, ENTEX REPORTED A SERVICE INTERRUPTION ON UNITED TEXAS' SEALY 4" (INDEX 90-17). UNITED TEXAS PERSONNEL PATROLLED THE LINE BY AERIAL PATROL AND DETECTED A GAS LEAK IN THE BRAZOS RIVER. EXTENSIVE FLOODING OF THEBRAZOS RIVER WAS THE APPARENT CAUSE OF THE LEAK. ACTUAL DAMAGE TO THE PIPELINE COULD NOT BE DETERMINED. THE PIPELINE CROSSING WAS ABANDONED IN PLACE AND GAS WAS REROUTED THROUGH OTHER SOURCES TO RESTORE SERVICE TO ENTEX. | 30700 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
510 | 1992-01-22 | TX | other | UNKNOWN (MCLENNAN COUNTY) | LONE STAR GAS CO | IT IS BELIEVED THAT COOL WEATHER AND EXCESSIVE RAIN CAUSED PIPE TO BREAK. | 68117 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
511 | 1992-03-15 | TN | maintenance | UNKNOWN (DICKSON COUNTY) | TENNESSEE GAS PIPELINE CO | PIPELINE RUPTURED AT CROSSOVER PIPING, CAUSING A FIRE NEAR ROAD CROSSING ANDRUPTURING UPSTREAM AND DOWNSTREAM BLOW OFFS AND CROSSOVERS. | 4000000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
512 | 1992-03-10 | LA | other | UNKNOWN (MADISON COUNTY) | UNITED GAS PIPELINE CO | PIPELINE CREW INSTALLING WELDOVER SLEEVE OVER MECHANICAL COUPLING AT THE TIME OF THE INCIDENT. CONTRIBUTING FACTORS UNKNOWN AT THIS TIME. | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
513 | 1992-04-05 | TX | other | UNKNOWN (GALVESTON COUNTY) | UNION CARBIDE CORP | INCIDENT AND FIRE AT ADJACENT METER DAMAGED GASKETS AND GAUGE AT ABOVE GROUND VALVE RESULTING IN PRODUCT LEAKAGE. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
514 | 1992-04-10 | TX | other | UNKNOWN (COLORADO COUNTY) | INTRATEX GAS CO | MINOR GAS LEAKAGE AT TWO LOCATIONS ON 8" BLOWDOWN VALVES - STEM SEAL AND FLANGE SURFACE BETWEEN BONNET AND MAIN VALVE BODY. | 140500 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
515 | 1992-03-18 | NE | leaks and spills | UNKNOWN (OTOE COUNTY) | NATURAL GAS PIPELINE CO OF AMERICA | THE LEAKING SEGMENT OF PIPE WAS REMOVED AND REPLACED WIHT PRETESTED PIPE ANDRETURNED TO SERVICE ON APRIL 15. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
516 | 1992-04-20 | TX | other | UNKNOWN (HARRISON COUNTY) | CROSSTEX PIPELINE CO | AN ENGINE ON ONE OF THE BOOSTER COMPRESSORS CAUGHT FIRE. THE HEAT OF THE FIRE MELTED THE FUEL GAS REGULATORS CAUSING FUEL GAS TO FURTHER FUEL THE FIRE. DAMAGE WAS TOO EXTENSIVE TO DRAW ACCURATE CONCLUSIONS. | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
517 | 1992-04-05 | TX | other | UNKNOWN (GALVESTON COUNTY) | HOUSTON PIPELINE CO | THE COMBUSTION OF A LIQUID MATERIAL LOCATED IN A ROAD DITCH ADJACENT TO THE M | 102000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
518 | 1992-04-16 | LA | leaks and spills | UNKNOWN ( COUNTY) | STINGRAY PIPELINE CO |  | 53100 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
519 | 1992-04-23 | CO | other | UNKNOWN (LOGAN COUNTY) | K N ENERGY INC(KANSAS NEBRASKA GAS CO) | PRODUCER DISCONNECTED WELL LINE FROM METER RUN SO IT COULD RUN PIG AND ALCOHOL THROUGH LINE TO LOWER DEWPOINTS. PRODUCSER'S LINE WAS OPEN TO ATMOSPHERE AND POINTING TOWARD K N METER RUN. WHEN PIG EXITED LINE, IT SOME HOW IGNITEDGAS. THE RESULTING FIRE BURNED THROUGH GASKETS AND ALLOWED MAINLINE GAS TO CATCH ON FIRE. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
520 | 1992-04-05 | TX | other | UNKNOWN (GALVESTON COUNTY) | BLACK MARLIN PIPELINE CO | THE COMBUSTION OF A LIQUID MATERIAL LOCATED ON A ROAD DITCH ADJACENT TO THE METER STATION APPEARS TO HAVE ALLOWED NATURAL GAS LEAKAGE AT THE FLANGED JOINTS DUE TO EXCESSIVE HEATING. | 216000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
521 | 1992-04-14 | WV | leaks and spills | UNKNOWN (GILMER COUNTY) | COLUMBIA GAS TRANSMISSION CORP | INVESTIGATION REVEALED THAT A 62' SEGMENT OF OPERATOR'S LINE TM-7 WAS DAMAGED RESULTING FROM 1 43' RUPTURE ATTRIBUTED TO SELECTIVE SEAM CORROSION. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
522 | 1992-04-21 | LA | maintenance | UNKNOWN ( COUNTY) | TENNESSEE GAS PIPELINE CO | LEAK OCCURRED IN TEE FITTING | 125000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
523 | 1992-04-21 | MS | other | UNKNOWN (PANOLA COUNTY) | TENNESSEE GAS PIPELINE CO | CAUSE UNKNOWN UNDER INVESTIGATION. RUPTURE WITH NO FIRE ON 100-2 LINE IN WRINKLE BEND UPSTREAM OF HWY. 315 CASED CROSSING. | 98000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
524 | 1992-06-01 | KY | other | UNKNOWN (HANCOCK COUNTY) | WESTERN KENTUCKY GAS CO | UNDERGROUND GAS STORAGE WELLHEAD 3/4" LINE STRUCK BY A TRACTOR CAUSING A NIPPLE TO BREAK AND RELEASE GAS. THE GAS IGNITED CAUSING DRIVER TO SUSTAIN BURNS | 2000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
525 | 1992-06-24 | AL | other | UNKNOWN (LAWRENCE COUNTY) | DECATUR UTILITIES - DECATUR GAS DEPARTMENT | CONSTOCK COMMUNICATIONS, INC. A CONTRACTOR INSTALLING FIBER OPTICS CABLE FOR SOUTHCENTRAL BELL, HIT AND RUPTURED DECATUR UTILITIES' 10 INCH GAS MAIN AT APPROXIMATELY 17:55 JUNE 24, 1992. THE RUPTURE OCCURRED AT A STREAM CROSSING(FOXES CREEK ALONG U.S. HIGHWAY 20 IN THE HILLSBORO AREA. THE RUPTURE WAS DUE TO THE CROSSING, SINKING AND LOADING OF THE CONTRACTOR'S LARGE DOZIER (KOMATSU D85) ONTO THE 1- INCH STEEL GAS MAIN. THE DOZIER AND TWO BACKHOES (CATERPILLAR 416 AND CASE 580 E) WERE BURNED AFTER THE GAS IGNITED. THE OPERATOR OF THE DOZIER WAS ALSO BURNED. THE BACKHOES WERE APPARENTLY TRYING TO FREE THE DOZIER THAT WAS STUCK. BARLIER IN THE DAY (6.24.92, 10:00 A.M. -12:30 P.M.), KEM CARR MET WITH COMSTOCK PESONNEL (JERRY EDWARDS, MIKE EAVES, CONSTRUCTION CREW), SOUTH CENTRAL BELL (RONNY HICKOK, ANOTHER REPRESENTATIVE), HIGHWAYDEPARTMENT (MR. WHITE, ANOTHER MAINTENANCE MAN) CONCERNING THEIR INSTALLATION OF FIBER OPTICS CABLE AND CONFLICTS WITH OUR GAS MAIN. COMSTOCK HAD HIT OUR 10" GAS MAIN THE DAY BEFORE (6/23/92, 4:00 P.M.) CAUSING A RUPTURE AND GAS RELEASE. THEIR DOZIER HAD SUNK AND RUPTURED OUR GAS MAIN IN MUCH THE SAME MANNER AS ON THE 24TH. MR. CARR DESCRIBED THE DANGER IN THE CONSTRUCTION METHODS, THEIR LACK OF COOPERATION AND COMMUNICATION AND THEIR APPARENT LACK OF REGARD FOR OUR GAS FACILITIES. IT WAS AGREED BY THOSE IN THE MEETING INCLUDINGCOMSTOCK PERSONNEL THAT COMSTOCK WOULD STAY A MINIMUM OF 3 FEET AWAY FROM OUR GAS FACILITIES. IT WAS AGREED BY THOSE IN THE MEETING INCLUDING COSNTOCK PERSONNEL THAT COMSTOCK WOULD STAY A MINIMUM OF 3 FEET AWAY FROM OUR GAS MAIN THEY WERE TO NOTIFY DU IMMEDIATELY AND NOT PROCEED UNTIL WE HAD AGREED ON AN ACCEPTABLE INSTALLATION METHOD. IF CONDITIONS PREVENTED THEM FROM PLOWING THE CABLE IN AND MAINTAINING THE REQUIRED SEPARATIONS FROM OUR GAS MAIN, THEY WERE TO USE TRENCHING, BACKHOES OR OTHER METHODS TO KEEP THE DOZIER OFF THE GAS MAIN. | 200000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
526 | 1992-06-16 | LA | other | UNKNOWN ( COUNTY) | TENNESSEE GAS PIPELINE CO | LEAK AT INTERSECTION OF SIDE VALVE ASSEMBLY 525C-101.2. LEAK WAS NOT CONDSIDERED A HAZARD | 250000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
527 | 1992-06-17 | CA | other | UNKNOWN (LOS ANGELES COUNTY) | SOUTHERN CALIFORNIA GAS CO | CREW MEMBERS OVERPRESSURED A TWO-INCH RUBBER HOSE ASSEMBLY, CAUSING IT TO SEPARATE AND STRIKE THREE PEOPLE. HOSE RATING AND MAOP UNKNOWN. ONN JUNE 17,1992 AT APPROXIMATELY 6:30 A.M., GAS COMPANY EMPOYEES BEGAN BLOWING DOWN A SIX-FOOT SECTION OF LINE 765 THROUGH A TWO-INCH RUBBER HOSE ASSEMBLY TO A FREESTANDING FIRE CONTROL STACK LOCATED OUTSIDE THE EXCAVATION. THE HOSE ASSEMBLYSEPARATED AT THE FIRE CONTROL STACK END AFTER BEING OVERPRESSURRED. THE HOSE STRUCK THREE PEOPLE BEFORE BREAKING OFF AT THE INLET AND IT WAS APPROXIAMTELY FORTY SECONDS BEFORE IT WAS BROUGHT UNDER CONTROL BY CLOSURE OF THE INLET VALVE. TWO GAS COMPANY EMPLOYEES AND ONE CONTRACT INSPECTOR WEREINJURED. THE CONTRACT INSPECTOR'S INJURIES NECESSITATED INPATIENT HOSPITALIZATION. NO CUSTOMERS WERE AFFECTED NOR WERE THERE ANY FIRES ASSOCIATED WITH THIS INCIDENT. ESIMATED COSTS ASSOCIATED WITH INCIDENT WERE $300.00. DOT NOTIFICATION 06/18/92, REFERENCE REPORT #122500. | 300 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
528 | 1992-06-15 | NM | leaks and spills | UNKNOWN ( COUNTY) | EL PASO NATURAL GAS CO | WELD SEAM CORROSION AND THE DEVELOPMENT OF A NARROW OR CRACK-LIKE CORROSION PENETRATION IN THE EFW SEAM CAUSED THE PIPELINE TO RUPTURE. | 135708 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
529 | 1992-07-09 | LA | leaks and spills | UNKNOWN ((OFFSHORE) COUNTY) | ANR PIPELINE CO |  | 921400 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
530 | 1992-07-05 | IA | other | UNKNOWN (WARREN COUNTY) | NATURAL GAS PIPELINE CO OF AMERICA | FOLLOWING A PROCEDURE TO RESTORE SERVICE AT HIS BLOWNDOWN STATION, AN OPERATOR ACTIVATED THE VALVE CONTROL PANEL WHILE THE BLOWDOWN VALVES WERE BEING RESET. GAS VENTED THROUGH 4 OF THE 6 BLOWDOWN VALVES. | 90000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
531 | 1992-07-02 | LA | maintenance | UNKNOWN ( COUNTY) | TRANSCO GAS PIPELINE CORP | BUBBLES WERE OBSERVED BY TRANSCO PERSONNEL IN THE VICINITY OF TRANSCONTINENTAL GAS PIPE LINE CORPORATION'S PIPELINE WHILE FLYING OFFSHORE. DIVERS WERE DISPATCHED AND CONFIRMED THAT THE LEAK WAS A PINHOLE (3/16") IN THE 6 O'CLOCK POSITION IN A GIRTH WELD ON T.G.P.L.'S 16" PIPELINE IN VERMILION 67. THE PIPELINE WAS BLOWN DOWN AND THE REPAIR CLAMP WAS INSTALLED. | 53500 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
532 | 1992-07-13 | KS | leaks and spills | UNKNOWN (PAWNEE COUNTY) | NORTHERN NATURAL GAS CO (ENRON) |  | 107000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
533 | 1992-08-03 | WY | other | UNKNOWN (CAMPBELL COUNTY) | M I G C INC | STRESS ON LINE AT END OF CASING CAUSED RUPTURE. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
534 | 1990-12-23 | MS | other | UNKNOWN (MONROE COUNTY) | MISSISSIPPI VALLEY GAS | ONE LINE IN A DUAL 8" RIVER CROSSING BROKE IN A WELD AFTER BEING UNDERMINED BY FLOOD WATERS AND SUBJECTED TO FORCE OF RUSHING WATER, COLLECTED DEBRIS ANDWEIGHT OF PIPE IN THE RESULTING UNSUPPORTED SPAN. GAS SERVICES WAS LOST TO ABOUT 12,000 CUSTOMERS DOWNSTREAM. THE BROKEN CROSSING WAS TAKEN OUT OF SERVICE AND THE INTACT CROSSING INSPECTED. IT WAS ALSO UNDERMINED TO THE EXTENT THAT REPLACEMENT OF BOTH LINES RATHER THAN REPAIR OF INTACT LINE WAS DEEMED APPROPRIATE. TEMPORARY BY-PASSES WERE CONSTRUCTED TO ALLOW RESTORATION OF SERVICE AND A SINGLE 12" CROSSINGG WAS ULTIMATELY INSTALLED. THE LEAKING GAS CAUSED NO DAMAGE. THE COST OF THE LOST GAS AND THE GAS USED TO KEEP PRESSURE ON THE INTACT CROSSING UNTIL VALES ON BOTH HEADERS COULD BE CLOSED WAS $25,682. THE COST OF TEMPORARY BYPASSES AND RESTORATION OF SERVICE TO 12,000 CUSTOMERS WAS $284,710. THE COST OF THE NEW CROSSING AND OTHER IMPROVEMENTS WAS $226,301. ORDER 21002 STATES THAT ALL OF THE ABOVE COSTS ARE PROPERTY DAMAGE AND THAT THIS INCIDENT REPORT MUST BE MADE FOR THAT REASON EVEN THOUGH THE ESCAPING GAS WAS NOT THE CAUSE OF THE DAMAGE BUT WAS A RESULT OF THE CROSSING BYTHE WASHOUT ALSO NECESSITATED THE TEMPORARY BYPASSES, RESTORATION OF SERVICE TO CUSTOMERS AND REPLACEMENT OF CROSSING. IN USING THIS INCIDENT REPORT FOR STATISTICAL REPORTING, IT WOULD BE INCORRECT TO ATTRIBUTE ANY OF ANY OF THESE COSTS TO DAMAGE BY A GAS LEAK. | 536693 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
535 | 1992-08-02 | TX | maintenance | UNKNOWN (BRAZOS COUNTY) | FERGUSON-BURLESON COUNTY GAS GATHERING SYSTEM | JGM ARIEL THREE (3) STAGE NATURAL GAS COMPRESSOR PART OF A RURAL NATURAL GASGATHERING SYSTEM HAD A FAILURE RELEASING NATURAL GAS TO THE ATMOSPHERE AND INGNITED CAUSING THE COMPRESSOR TO BURN. THIS UNIT WAS STARTED ON 4-16-92. THE RESULTS OF THE METALURGICAL ANALYSIS MAY REVEAL MORE FACTS THAT WILL HELP DETERMINE THE CAUSE OF THE INCIDENT, REPORT NUMBER 130311.ON AUGUST 2, 1992 FERGUSON-BURLESON COUNTY GAS GATHERING SYSTEM, A SUBSIDIARY OF SOUTHWESTERN GAS PIPELINE, INC., EXPERIENCE A FIRE AT AN UNATTENDED FIELD GAS GATHERING COMPRESSOR SITE KNOWN AS THE STEEPHOLLOW #5, LOCATED ON BIRD POND RD APPROXIMATELY 3 MILES WEST OF HWY 30 AND 3.5 MILES SOUTH SOUTHEAST OFCOLLEGE STATION, TEXAS IN BRAZOS COUNTY. THE INCIDENT WAS DISCOVERED AT 9:30AM AND WAS REPORTED TO THE 24 HOUR EMERGENCY NUMBER AT 10:40 AM. THIS NOTIFICATION WAS MADE DUE TO THE AREA WHERE THE INCIDENT OCCURRED AND THE ESTIMATED DOLLAR AMOUNT OF DAMAGE. THE STEEPHPLLOW #5 COMPRESSOR SITE IS LOCATED IN A RURAL, CLASS 1 LOCATION APPROXIMATELY 2 MILES FROM A DWELLING INTENDED FOR HUMAN OCCUPANCY. THERE WERE NO PERSONNEL INJURED OR KILLED. THE FIRE WAS CONTAINED BY 10:30 AM AND THE REMAINING COMPRESSORS WERE BACK IN OPERATION BY 2:30 PM. THERE WAS NO LOSS OF GAS SERVICE SINCE THE SUBJECT GATHERING LINE SERVES ANOTHER PART OF THE OPERATORS GAS PROCESSING FACILITIES DOWNSTREAM OF THIS LOCATION. THE ESTIMATED PROPERTY DAMAGE IS $500,000.00. THIS IS A REPLACEMENT COST OF THE COMPRESSOR AND A $1,000.00 VALUE OF THE GAS LOST. THE COSTESTIMATE WAS DETERMINED THE DAY AFTER THE INCIDENT, THEREFORE, THIS INCIDENTWAS REPORTED TO THE NTSB EMERGENCY RESPONSE CENTER ON TUESDAY, AUHUST 4, 1992. MR. CHUCK KOVALL ASSIGNED THE RSPA INCIDENT REPORT NUMBER, 130311, AT THAT TIME. SHORTLY AFTER REPORTING THE INCIDENT TO THE NTSB IN WASHINGTON, MR. R.G. (BOB) HOLTER WITH THE RSPA IN HOUSTON CALLED AND I REPORTED THE CHAIN OF EVENTS AND SPECIFIC DETAILS TO HIM. MR. HOLTER INDICATED TO ME THAT SINCENO ONE WAS INJURED OR KILLED, THE GENERAL PUBLIC WAS NOT AFFECTED, THE FACILITIES ARE INTRASTATE AND ARE RURAL GATHERING, HE DID NOT BELIEVE HIS SUPERVISORS WOULD HAVE HIM INVESTIGATE. I INFORMED MR. HOLTER THAT THE INCIDENT HADBEEN REPORTED TO THE RAILROAD COMMISSION AT THE TIME OF THE INCIDENT AND MR.DANNY NICHOLS, ENGINEERING TECHNICIAN, FROM THE RRC'S HOUSTON OFFICE INVESTIGATED THE INCIDENT ON SITE. AFTER A THOROUGH INVESTIGATION OF THE EQUIPMENT,IT APPEARS THAT A VALVE COVER HAD BLOWN OFF, SHEARING THE BOLTS THAT HELD ITON THE SECOND STAGE CYLINDER RELEASING GAS TO THE ATMOSPHERE. THIS COULD HAVE BEEN THE SOURCE OF IGNITION, HOWEVER, THE ACTUAL SOURCE HAS NOT ACTUALLY BEEN DETERMINED. FERGUSON-BURLESON'S INSURANCE CARRIER REQUESTED THAT THE COMPRESSOR PACKAGE ASSEMBLER TAKE THE UNIT TO THEIR SHOP AND DISASSEMBLE IT TO TDETERMINE WHAT IF ANYTHING IS SALVAGEABLE, WHICH WILL HAVE A DIRECT AFFECT ON THE ACTUAL COST OF REPLACEMENT. THE SHEARED BOLTS HAVE BEEN SENT TO A METALURHIST'S FOR ANALYSIS, THE RESULTS OF WHICH HAVE NOT YET BEEN RECIEVED. SHOULD THE RESULTS OF THESE EXAMINATIONS CHANGE THE COST ESTIMATE SIGNIFICANTLY AND THE METALURGIST'S REPORT REVEAL SOMETHING NEW, A SUPPLEMENTAL REPORT WILL BE COMPLETED AND FORWARDED PROMPTLY. THE DAMAGED COMPRESSR UNIT IS BEING PREPARED FOR SHIPMENT TO THE PACKAGER FOR INSPECTION ON AUGUST 19, 1992, TO BESHIPPED AS SOON AS POSSIBLE. | 500000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
536 | 1992-07-21 | TX | other | UNKNOWN (WHEELER COUNTY) | PALO DURO PIPELINE CO | THE INCIDENT OCCURRED ON JULY 21 DURING SCHEDULED ROUTINE MAINTENANCE. A TWO(2) INCH VALVE ASSEMBLY USED TO BLOWDOWN A VERTICAL SEPARATOR BECAME DISCONNEDTED FROM THE THREADED NOZZLE OM THE SEPARATOR. THE FORCE OF THE BLOWDOEN GAS ROTATED THE VALVE ASSEMBLY COUNTER-CLOCKWISE, THEREBY LOOSENING THE THREADED CONNECTION. THE FORCE OF THE RELEASED GAS KNOCKED BOTH EMPLOYEES ON THE AREA TO THE GROUND. ONE EMPLOYEE REQUIRED INPATIENT HOSPITALIZATION. THE OTHER EMPLOYEE WAS TREATED FOR MINOR INJURIES AND RELEASED. SUPPL. REPORT4/7/1995 INDICATES THAT THE INCIDENT IS STILL UNDER INVESTIGATION AND ISCURRENTLY THE SUBJECT OF LITIGATION. (REQUESTED TO RECLASSIFY CAUSE OFINCIDENT). IF NATURAL'S COMPLETED INVESTIGATION INDICATES THATRECLASSIFICATION IS APPROPRIATE, NATURAL WILL FILE A SUPPL. REPORT (F.ROYFLEET 708-691-3786) | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
537 | 1992-07-28 | TX | other | UNKNOWN (BRAZOS COUNTY) | LONE STAR GAS CO OF TEXAS, INC |  | 5000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
538 | 1992-08-03 | LA | leaks and spills | UNKNOWN ( COUNTY) | NATURAL GAS PIPELINE CO OF AMERICA | INTERNAL CORROSION CAUSED LEAKS FROM TWO ISOLATED PITS 26 INCHES APART. THEPIPELINE HAD BEEN SHUT-IN. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
539 | 1992-08-19 | OH | other | UNKNOWN (FAIRFIELD COUNTY) | TEXAS EASTERN GAS PIPELINE CO | A FIBER OPTIC CABLE CONTRACTOR STRUCK TEXAS EASTERN'S 26" LINE 3. A FIRE BEGAN AND TWO CONTRACT CABLE EMPLOYEES DIED. THE FIRE LASTED 2 HOURS 35 MIUNTES. | 154000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
540 | 1992-08-27 | LA | other | UNKNOWN ( COUNTY) | TENNESSEE GAS PIPELINE CO | PLATFORM DESTROYED BY HURRICANE ANDREW | 1600000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
541 | 1992-08-24 | LA | maintenance | UNKNOWN ( COUNTY) | SOUTHERN NATURAL GAS CO | SEVERAL YEARS PRIOR TO THE INCIDENT UNDER CONSIDERATION, THE 12" EUGENEISLAND 261 SEA ROBIN PIPELINE WHICH TIES INTO THE 24" EUGENE ISLAND 330-206PIPELINE HAD A LEAK IN S SET OF FLANGES AT THE EUGENE ISLAND BLOCK 273 TIE-INLOCATION. SEA ROBIN INSTALLED A 12" 900# PLIDCO FLANGE REPAIR + SPLIT SLEEVETO REPAIR THE LEAKING FLANGES. THE PLIDCO FITTING RECENTLY DEVELOPED ANO-RING SEAL LEAK THAT WAS NOT DETECTABLE AT THE WATER SURFACE. THE WATERDEPTH IN THIS AREA IS APPROXIMATELY 180'. THE LEAK WAS DISCOVERED WHILEINSPECTING THE CONSTRUCTION OF OTHER FACILITIES IN THE IMMEDIATE VICINITY.THE LEAK WAS REPAIRED BY PUMPING THE SEAL AREA WITH A SEALING COMPOUND.SUPPLEMENTAL REPORT 12/15/94 INDICATES ITEM THAT LEAKED WAS A REPAIR COMPONENTTHE RATING OF WHICH WAS ESTABLISHED BY A PROTOTYPE TEST. REFERENCE 49 CFR192.143. LEAKING O-RING SEAL WAS THE CONSTRUCTION/MATERIAL DEFECT. SEE PART C | 120000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
542 | 1992-08-30 | TX | maintenance | UNKNOWN (ANDERSON COUNTY) | LONE STAR GAS CO | GIRTH WELD CRACKED WHERE A 30 DEGREE MITER CUT WAS MADE ON PIPE. | 5000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
543 | 1992-08-26 | LA | other | UNKNOWN (OFFSHORE COUNTY) | SOUTHERN NATURAL GAS CO | SHEAR JOINT (INSTALLED ON PIPELINE IN 1985) SEPARATION CAUSED BY A MUDSLIDE DURING HURRICANE ANDREW. | 1500000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
544 | 1992-08-25 | LA | other | UNKNOWN (OFFSHORE COUNTY) | TRUNKLINE GAS CO | DURING HURRICANE PLATFORM WAS SUBMERGED. UNKNOWN CONDITION. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
545 | 1992-08-27 | MS | other | UNKNOWN (ADAMS COUNTY) | MID - LOUISIANA GAS CO | HEAVY RAINFALL FROM HURRICANE ANDREW CAUSED RIVER TO RISE TO WITHIN 3' OF TOP BANK, EROSION OF BANK IN RIVERBEND ALLOWED TREES FLOATING DOWN RIVER TO STRIKE LINE, BREAKING 45 DEGREE ELBOW. | 31000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
546 | 1992-09-01 | TX | other | UNKNOWN (COLLIN COUNTY) | TEXAS UTILITIES FUEL CO | THIRD PARTY CONTRACTOR WAS TRENCHING FOR A NEW PIPELINE. CONTRACTOR WAS AWARE OF TUFCO'S PIPELINE AND HAD CEASED TRENCHING TO MOVE TO OPPOSITE SIDE OF TUFCO'S RIGHT-OF-WAY. IN ERROR, CONTRACTOR RESUMED DIGGING AT TURCO'S PIPELINE | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
547 | 1992-08-27 | LA | other | UNKNOWN ( COUNTY) | TRANSCO GAS PIPELINE CORP | AT APPROXIMATELY 9:35 A.M. ON AUGUST 27, 1992, HURRICANE ANDREW DESTROYED THE BLOCK 118E SHIP SHOAL PLATFORM OWNED BY ODECO. THE PLATFORM AND RISER WERECOMPLETELY OVERTURNED AND DESTROYED. TRANSCO HAD ONE 10" RISER ON THE PLATFORM. NO GAS WAS ONSERVED ON THE WATER SURFACE AT THIS LOACTION. THE PRODUCERWILL HAVE TO RECONSTRUCT THE PLATFORM AND THE TRANSCO PIPING AND FACILITIES WILL HAVE TO BE REPLACED AT THIS LOCATION, IN ADDITION TO OTHER UNDERWATER WORK THAT MUST OCCUR BEFORE THIS LOCATION WILL BE ABLE TO FLOW. | 750000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
548 | 1992-08-27 | LA | other | UNKNOWN ( COUNTY) | TRANSCO GAS PIPELINE CORP | ON AUGUST 27, 1992 THE EFM EQUIPMENT DATA INDICATED THE BLOCK 72A SHIP SHOALPLATFORM OWNED BY MOBIL GAVE WAY DUE TO HURRICANE ANDREW AT 9:35 A.M. TRANSCO HAD TWO 12" RISERS (ONE BELONGING TO NORTHERN NATURAL AND OPERATED BY TRANSCO), ONE 6" RISER, THREE 8" RISERS AND ONE 14" RISER. THE PLATFORM WAS NOTVISIBLE ON THE SURFACE OF THE WATER. ALL OF THE RISERS WERE DAMAGED AND PARTED FROM THE STRUCTURE. THE GAS ESCAPING FROM THE RISERS IGNITED AND WAS ON FIRE UNTIL 6:00 P.M. ON SEPTEMBER 1, 1992. COMPLETE RECONSTRUCTION OF PIPINGWILL HAVE TO BE ACCOMPLISHED BEFORE CERTAIN PRODUCERS CAN FLOW GAS. MAOP INFORMATION: 12" TO MOSQUITO BAY - 1168 PSIG; 12" TO MOBIL 72-J - 1168 PSIG; 8" LINES TO CHEVRON 108B, MOBIL 11-F AND MOBIL 87-B - 1250 PSIG; 6" TO ODECO 118-E - 1250 PSIG; ALL SHIP SHOAL PLATFORMS. | 4000000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
549 | 1992-09-05 | CA | leaks and spills | UNKNOWN (LOS ANGELES COUNTY) | STOCKER RESOURCES INC | STOCKER RESOURCES, INC. (STOCKER) WAS INFORMED IN SATURDAY, SEPTEMBER 5, 1992, BY CHEVRON PIPELINE CO. THAT A POSSIBLE LEAK EXISTED IN THE GRASSY MEDIAN DSTRIP OF SAN VICENTE BLVD. AT FOREST DRIVE. IT IS UNCLEAR WHETHER CHEVRON DISCOVERED THE LEAK DURING A LEAK SURVEY OR RECEIVED A COMPLAINT. STOCKER EMPLOYEE, JEFF WINKLER, WAS DISPATCHER TO THE SITE AND DISCOVERED DISCOLORED GRASS. BECAUSE THE AREA HISTORICALLY HAS SWAMP GAS, MR. WINKLER CONFIRMED THAT A PIPELINE LEAK EXISTED BY HAVING THE PIPELINE PRESSURED UP AND WITNESSED ADDISTIONAL EVIDENCE OF LEAK. PRODUCT WAS IMMEDIATELY SWITCHED INTO AN ADJACNETSTANDBY LINE. THE LEAK WAS ISOLATED AND DISCONTINUED WITHIN ON HOUR OF DISCOVERY. UPON EXCAVATION, IT WAS DISCOVERED THAT INTERNAL CORROSION, LOCALIZEDPITTING, HAD CAUSED THE LEAK. THE LEAK OCCURRED AT A LOW SPOT IN THE LINE, WHICH SIPPED SLIGHTLY TO AVOID A XITY SEWER LINE. LIQUID AND SOLIDS ACCUMULATING IN THIS SPOT CONTRIBUTED TO THE LEAK. ADHERING TO D.O.T. PROCEDURE, A 15' SECTION OF PIPELINE WAS REMOVED AND REPLACED. HYDROSTATIC PRESSURE TESTING WAS DONE BEFORE PUTTING THE LINE BACK IN SERVICE. TO PREVENT A RE-OCCURRENCE, OR ANY FURTHER CORROSION, IN ADDITION TO OUR NORMAL SCRAPPING AND PIGGINGOF THE PIPELINES, WE WILL INTRODUCE A CORROSION INHIBITING CHEMICAL TO COAT THE INTERNAL WALLS OF THE PIPELINES. ADDITIONALLY, WE WILL INCREASE THE FREQUENCY OF BALL OR POLY PIGGING OF LINES FROM SEMI-ANNUALLY TO MONTHLY. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
550 | 1992-09-19 | IA | other | UNKNOWN (ADAMS COUNTY) | CORNING MUNICIPAL UTILITIES | FLOOD WATER WASHED OUT THE PIPELINE RIVER CROSSING AND TRESS CAME DOWN THE RIVER AND HIT THE PIPE IN THE RIVER. THIS CAUSED TO BREAK IN AN ELBOW IN THE REVIER BANK. LINE WAS SHUT DOWN AND BREAK WAS CUT OUT AND A NEW 10 FT. SECTION WAS WELED IN. | 15000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
551 | 1992-09-23 | LA | other | UNKNOWN (CAMERON COUNTY) | TENNESSEE GAS PIPELINE CO | PLATFORM LEGS AND PIPELINES. ABOVE WATER PIPELINE RISERS ON CENTRAL GATHERING PLATFORM WERE VISIBLE ON A CLEAR DAY. | 3000000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
552 | 1992-10-01 | MO | other | UNKNOWN (CASS COUNTY) | WILLIAMS NATURAL GAS CO | CONTRACTOR WAS CLEANING CREEK BOTTOM WITH A HIGH LOADER. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
553 | 1992-10-14 | TX | other | UNKNOWN (WHARTON COUNTY) | GULF COAST NATURAL GAS CO | A HEAVY EQUIPMENT OPERATOR USING A 12-G MAINTAINER TO EXCAVATE AN EXITING DRAINAGE DITCH, STRUCK THE PIPELINE CUTTING A 3 X 2.5 INCH HOLE INTO THE PIPE. | 70000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
554 | 1992-10-05 | AL | other | UNKNOWN (DALLAS COUNTY) | TRANSCO GAS PIPELINE CORP | ON THE MORNING OF OCTOBER 5, 1992 AT 2:45 A.M., A PIPELINE RUPTURE AND FIRE OCCURRED ON MAIN LINE "A" AT MILE POST 867.56 IN DALLAS COUNTY, ALABAMA. THELINE SEGMENT WAS ISOLATED BY 4:14 A.M. AND ALLOWED TO BURN ITSELF OUT BY 7:45 A.M. THERE WERE NO REPORTED INJURIES AND DAMAGE WAS LIMITED TO APPROXIMATELY FOUR (4) ACRES OF TIMBER. THERE WAS NO INTERRUPTION OF SERVICE TO ANY OF TRANSCO'S CUSTOMERS. THE APPARENT CAUSE OF THE INCIDENT IS UNDER INVESTIGATION AT THIS TIME. AS SOON AS TRANSCO RECEIVES THE METALURGICAL RESULTS, A SUPPLEMENTAL REPORT INDICATING CAUSE WILL BE PROVIDED TO THE OFFICE OF PIPELINE SAFETY. | 1860900 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
555 | 1992-10-20 | TX | other | UNKNOWN ( COUNTY) | TRANSCO GAS PIPELINE CORP | VEHICLE STRUCK BUILDING AND METER SET. THE IMPACT CRACKED THE STRAINER WHICHPRODUCER HAD ABANDONED PRODUCTION FROM HIGH ISLAND 206 AND MADE NEW CONNECTIO IGNITED.N TO SAME TRANSCO UWTV ASSEMBLY FROM HIGH ISLAND 207. PRODUCER HAD COMPLETED DISASSEMBLING THE HIGH ISLAND 206 PLATFORM AND ON OCTOBER 20, 1992 WAS USING A SHRIMP BOAT TO PERFORM MMS REQUIRED BOTTOM GRID SEARCH FOR DEBRIS. WHILEPERFORMING THE GRID SEARCH,THE SHRIMP BOAT'S NET AND CHAIN SNAGGED THE PRODUCER'S VAVLE AND PIPELINE, PULLING IT OVER AND SEVERING TRANSCO'S UWTV ASSEMBLY AT THE WELD FOR 1 110 DEGREE ELL. DUE TO WEATHER AND SEA CONDITIONS, EQUIPMENT AND DIVERS WERE UNABLE TO ACCESS THE DAMAGE UNTIL EARLY ON OCTOBER 23, 1992. | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
556 | 1992-10-20 | TX | other | UNKNOWN ( COUNTY) | DELMAR OPERATING, INC | THE 10-INCH GEAR OPERATED BALL VALVE INSTALLED ON DELMAR'S TIE-IN ASSEMBLY WAS BURIED TO THE PROPER DEPTH AND WAS COVERED WITH LOOSE SAND WHICH HAD NATURALLY BACK FILLED INTO THE HOLE MADE DURING THE INSTALLATION OF THE ASSEMBLY.AS THE "CAPTAIN JIMMY" WAS LIFTING ITS NETS IN AN ATTEMPT TO RETRIEVE THE DEBRIS SNAGGED IN THE STARBOARD SIDE NET, THE NOW SLACK 3/8" TICKLE CHAIN ON THE PORT SIDE NET, DRAGGED UNDER THE LOOSE SAND AND HOOKED THE GEAR OPERATOR ON THE 10-INCH VALVE. THE TRAWLER, IN AN ATTEMPT TO FREE ITS PORT SIDE NET, CONTINUED RAISING THE NETS AND BEGAN TURNING IN A COUNTERCLOCKWISE DIRECTION. AS A RESULT OF THIS PROCEDURE, TRANSCO'S 6-INCH TIE-IN ASSEMBLY SEVERED AT THE110 DEGREE BEND AND THE 10-INCH PIPELINE WAS BENT BACK OVER ITSELF FORMING ALOOP OF APPROXIMATELY 10 FEET. THE 6-INCH BALL VALVE AT THE 12-INCH TRANSCO PIPELINE TIE-IN AND THE 8-INCH BALL VALVE AT THE ARCO TIE-IN TO THE ASSEMBLY HAVE BEEN CLOSED. | 302600 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
557 | 1992-10-20 | TX | maintenance | UNKNOWN ( COUNTY) | DELMAR OPERATING, INC |  | 202600 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
558 | 1992-10-07 | OK | leaks and spills | UNKNOWN (TEXAS COUNTY) | PANHANDLE EASTERN PIPELINE CO | STILL UNDER INVESTIGATION.THE TGPL SUBSEA TIE-IN VALVE ASSEMBLY AND THE DELMAR PIPELINE WERE REPAIRED AND ON NOVEMBER 6, 1992, THE PIPELINE FROM HIGH ISLAND 207 PLATFORM WAS IN THE PROCESS OF BEING PRESSURED UP BY BACK FLOWING FROM THE SUBSEA TIE-IN ASSEMBLY. APPROXIMATELY 35 MINUTES AFTER THE PIPELINE HAD REACHED OPERATING PRESSURE OF 1040 PSIG, AND AFTER A DIVING INSPECTOR REPORTED NO LEAKS ON VALVE BODIES OR FLANGES, THE PIPELINE RUPTURED, DISCHARGING NATURAL GAS INTO THE GULF OFMEXICO. THE DEPARTING PIPELINE SHUT-DOWN VALVE ON THE HIGH ISLAND 207 PLATFORM WAS CLOSED AT THE TIME OF THE INCIDENT. THE JACK-UP WORK BARGR WHICH WASPERFORMING THE WORK WAS THE GULF ISLAND II. ALL PERSONNEL ON BOARD THE BARGE WERE EVACUATED TO THE WORK VESSEL SEA OX WHICH WAS STANDING BY. THERE WERENO INJURIES OR POLLUTION ASSOCIATED WITH THIS INCIDENT. THE SUPPLY OF GAS USED TP PRESSURE UP THE PIPELINE FROM HIGH ISLAND 207 "A" PLATFORM WAS FORM ALATERAL LINE TIE-IN TO THE SUBSEA VALVE ASSEMBLY. THE CHECK VALVE WAS LOCKED OPEN ON THE HIGH ISLAND 207 LATERAL TIE-IN WHICH ALLOWED THE GAS TO BACK FLOW INTO THE PIPELINE. WHEN THE INCIDENT OCCURRED, TGPL NOTIFIED THE TWO PIPELINES WERE SHUT-IN. TWO HOURS AFTER THE INCIDENT, GAS CONTINUED TO BE DISCHARGED FROM THE RUPTURE WHICH INDICATED THAT THE GAS MUST BE COMING FROM A SOURCE OTHER THAN THE TWO PLATFORMS SUPPLYING GAS TO THEIR MAIN LINE TO SHUT-IN.APPROXIMATELY SIX HOURS LATER, THE GAS BEING DISCHARGED THROUGH THE RUPTURE HAD DECREASED TO A LEVEL WHICH ALLOWED A TGPL DIVER TO CLOSE THE VALVE ON THELATERAL LINE TIE-IN. UPON INSPECTION OF THE RUPTURED PIPELINE, IT WAS DETERMINED THAT THE FLANGED END OF THE HYDROCOUPLE END CONNECTOR MANAUFACTURED BYHYDRO TECH SYSTEMS, INC. HAD COME OFF OF THE PIPELINE. REPAIRS TO THE PIPELINE ARE IN PROGRESS AND WILL BE COMPLETED AS SOON AS PRACTICAL. | 130000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
559 | 1992-10-12 | MO | other | UNKNOWN (CALLAWAY COUNTY) | FULTON BOARD OF PUBLIC WORKS | LINE WAS MARKED AND LOCATOR HAD GONE TO OFFICE TO CHECK RECORDS FOR DEPTH.CONTRACTOR EXCAVATING FOR NEW STATE HIGHWAY HIT LINE. LINE WAS LOCATED AND MARKED. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
560 | 1992-11-10 | TX | other | UNKNOWN (WHARTON COUNTY) | TRANSCO GAS PIPELINE CORP | ON NOVEMBER 10, 1992 AN OUTSIDE COMPANY WAS PERFORMING SEISMIC WORK IN THE VICINITY OF TGPL'S 243" MCMULLEN LATERAL. IT APPEARED THAT WHILE PERFOMING THEIR WORK, THE SEISMOGRAP CREW HAD DRILLED A SHOT HOLE DIRECTLY OVER THE TGPL PIPELINE AND PLACED A 1/3 LB. CHARGE IN THE SHOT HOLE. THE DETONATION OF THECHARGE CAUSED A DENT WITH A CRACK IN THE BODY OF THE PIPE, THUS RESULTING INTHE LEAK. | 75000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
561 | 1992-11-17 | TX | other | UNKNOWN ( COUNTY) | TRANSCO GAS PIPELINE CORP | AS A RESULT OF THE LEAK INCIDENT, REPORTED BY TGPL, ON OCTOBER 20, 1992, (DOT CASE NO. 141753) PRODUCER INSTALLED A MECHANICAL CONNECTOR TO ONE END OF THEIR 1O" PIPELINE. ON NOVEMBER 6, 1992 PRODUCER'S MECHANICAL CONNECTOR FAILEDDURING REPRESSURING OF FACILITY. THE DAMAGE AND LEAK TO THE TGPL HYDRAULIC CONNECTOR WAS NOT DETECTED UNTIL THE FACILITY WAS REPRESSURED AGAIN ON NOVEMBER 17, 1992 AND RESULTED IN THIS REPORTABLE INCIDENT (CASE NO. 145215). | 60000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
562 | 1992-11-03 | IL | other | UNKNOWN (DU PAGE COUNTY) | NATURAL GAS PIPELINE CO OF AMERICA | VISUAL INSPECTION OF THE CARRIER PIPE FOUND THE EXTERNAL COATING TO BE IN GOOD CONDITION AND NO INTERNAL CORROSION. THE LEAK WAS NOT FOUND. NEW PIPE WAS INSTALLED. | 300000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
563 | 1992-11-03 | TX | other | UNKNOWN (SHIP SHOAL BLOCK 90 COUNTY) | TRUNKLINE GAS CO | FAILURE INITIATED IN DENT AT (PIPE POSITION) 12:00. BUT NOT ALL PIPE CAN BE ACCOUNTED FOR. | 1000000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
564 | 1992-11-10 | TX | other | UNKNOWN ( COUNTY) | LONE STAR GAS CO | PIPELINE HAD BEEN REMOVED FROM SERVICE TO INSTALL A REPLACEMENT SECTION. AFTER JOB COMPLETION, PIPELINE SEGMENT WAS PURGED, REPRESSURED AND RETURNED TO NORMAL SERVICE. APPROX. 20 MINUTES LATER A JOINT OF EXISTING PIPE SLIPPED FROM A DRESSER COUPLING AND ALLOWED SEPARATION OF PIPELINE JOINT CONNECTION. | 2350 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
565 | 1992-11-20 | TX | other | UNKNOWN (WEBB COUNTY) | VALERO TRANSMISSION CO | A METALLURIGICAL ANALYSIS IS BEING CONDUCTED TO DETERMINE THE CAUSE OF THIS FAILURE. | 47000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
566 | 1992-11-16 | TX | other | UNKNOWN (NUECES COUNTY) | VALERO TRANSMISSION CO | A FAILURE ANALYSIS IS BEING CONDUCTED TO VERIFY THE CAUSE OF THE RUPTURE. | 232000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
567 | 1992-11-24 | KS | other | UNKNOWN (SEDGWICK COUNTY) | WILLIAMS NATURAL GAS CO | PIPELINE WAS MARKED; HOWEVER, DUE TO HEAVY EXCAVATION FROM NEW PIPELINE CONSTRUCTION, OPERATOR ACCIDENTALLY HIT EXISTING LINE WHILE SHORING FOR NEW TRENCH | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
568 | 1992-11-22 | VA | other | UNKNOWN (LOUDOUN COUNTY) | CNG TRANSMISSION CORP | DURING COMMISSIONING OF COMPRESSOR STATION, THE ESD SYSTEM LOST PRESSURE. THE OPERATING SOFTWARE DID NOT ALLOW THE PRESSURE TO BE MADE UP AND THEREFORE A FULL ESD OCCURRED. ABLOCK VALVE DID NOT CLOSE AND HAD TO BE CLOSED MANUALLY. ALL CONDITIONS WERE CORRECTED PRIOR TO PLACING INTO SERVICE. | 54390 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
569 | 1992-10-08 | KS | leaks and spills | UNKNOWN (ELLSWORTH COUNTY) | NORTHERN NATURAL GAS CO (ENRON) |  | 183000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
570 | 1992-12-11 | TX | other | UNKNOWN (MCMULLEN COUNTY) | TRANSCO GAS PIPELINE CORP | WHILE PERFORMING PIGGING OPERATIONS ON DECEMBER 11, 1992, ON THE TGPL 20" SOUTH MCMULLEN LATERAL. LIQUIDS WERE BEING STORED IN FIVE FRAC TANKS SET UP ON TGPL PROPERTY AT STATION 04. ALL OF THE FRAC TANKS WERE FULL AND OVER NIGHT THE ATMOSPHERIC CONDITIONS CHANGED TO THERE WAS NO WIND. THE VAPORS FROM THEFRAC TANK VENTS SETTLED TO THE GROUND, AND APPARENTLY SPREAD TO A TRAVEL TRAILER (CONTRACTOR'S) PARKED NEARBY. AT APPROXIMATELY 7:15 A.M. ON DECEMBER 11. 1992, THE VAPORS WERE IGNITED BY A SOURCE FROM THE TRAILER AND RESULTED IN A "FLASH FIRE" TO THE TRAILER. AT THE TIME OF THE "FLASH FIRE" ONE CONTRACTOR EMPLOYEE WAS INSIDE THE TRAILER, AND TWO TGPL EMPLOYEES WERE WORKING ON THEAREA. ALL THREE MEN RECEIVED BURNS AND WERE TRANSPORTED BY HELICOPTER TO HOSPITAL IN SAN ANTONIO, TEXAS, WHERE ALL THREE WERE ADMITTED FOR TREATMENT. THE ONE CONTRACT WORKER WAS TREATED FOR SECOND AND THIRD DEGREE BURNS OVER APPROXIMATELY 25% OF HIS BODY INCLUDING THE BUTTOCKS AND THE BACKS OF HIS LEGS, WHILE THE OTHER RECEIVED SECOND AND THIRD DEGREE BURNS OVER APPROXIMATELY 18%OF HIS BODY INCLUDING HIS LOWER BACK, BUTTOCKS, EAR, WRIST AND KNEE. THEIR ANTICIPATED STAYS IN THE HOSPITAL ARE SIX AND EIGHT WEEKS, RESPECTIVELY. THERE WAS NO DAMAGE TO ANY OF TGPL'S FACILITIES. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
571 | 1992-11-20 | NY | other | UNKNOWN (NEW YORK COUNTY) | CONSOLIDATED EDISON CO OF NEW YORK | A CON EDISON CREW WAS PERFORMING A SCHEDULED REINFORCEMENT OF AN INSULATING CDURING SCHEDULED REINFORCEMENT OF TRANSMISSION MAIN, THE WELDER BURNED HOLE IOUPLING ON A 30-INCH TRANSMISSION MAIN WHEN THE WELDER UNINTENTIONALLY BURNEDN PIPE WALL CAUSING A LEAK. ---- A CON EDISON CREW WAS PERFORMING A SCHEDULE A HOLE IN THE PIPE WALL. A SEGMENT OF THE TRANSMISSION MAIN WAS ISOLATED ASD REINFORCEMENT OF AN INSULATING COUPLING ON A 30-INCH TRANSMISSION MAIN WHEN PART OF THE EMERGENCY PROCEDURE. THE WELDER UNINTENTIONALLY BURNED A HOLE IN THE PIPE WALL. A SEGMENT OF THE TRANSMISSION MAIN WAS ISOLATED AS PART OF THE EMERGENCY PROCEDURES. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
572 | 1992-12-05 | LA | other | UNKNOWN ( COUNTY) | UNITED GAS PIPELINE CO |  | 98000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
573 | 1992-12-11 | WY | other | UNKNOWN (PARK COUNTY) | WILLISTON BASIN INTERSTATE PIPELINE CO | EXPLOSION AND FIRE RESULTED FROM FAILURE OF HEAT EXCHANGE COIL WITHIN FIRED HEATER FOR THE DRY BED DEHYDRATION SYSTEM.7 | 150000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
574 | 1993-01-06 | ID | other | UNKNOWN (OWYHEE COUNTY) | NORTHWEST PIPELINE CORP | CONTRACT BACKHOE RUPTURED PIPE DURING BACKFILL OPERATION OF NEW LOOP IN SPITE OF PIPE DEPTHS MARKED ON THE IN-SERVICE 16 INCH LINE EVERY 100 FEET. COMPANY INSPECTOR WAS AT PADDING OPERATION ONE-HALF MILE AWAY. | 170000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
575 | 1992-12-29 | PA | leaks and spills | UNKNOWN (FAYETTE COUNTY) | COLUMBIA GAS TRANSMISSION CORP | RELATED CORROSION AREA TOTALED 16 SQUARE INCHES. REMAINING PIPE IN EXCELLENT CONDITION. INVESTIGATION REVEALED THAT A 57.5' SEGMENT OF OPERATOR'S LINE 1804 WAS DAMAGED RESULTING FROM A 41' RUPTURE ATTRIBUTED TO AN ISOLATED CORROSION DEFECT WHICH REDUCED THE PIPE WALL THICKNESS AND RESULTED IN A DUCTILE FRACTURE. THE CORRODED AREA APPEARS TO HAVE BEEN SHIELDED FROM CATHODIC PROTECTION BY A ROCK. | 165000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
576 | 1993-01-14 | AZ | other | UNKNOWN (PINAL COUNTY) | EL PASO NATURAL GAS CO | NUMBER OF OUR PIPELINES IN THAT STATE. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
577 | 1993-01-13 | AZ | other | UNKNOWN ( COUNTY) | EL PASO NATURAL GAS CO | THIS PIPELINE SEGMENT HAD BEEN BLOWNDOWN ON 1/10/93 AS A PRECAUTION. RECENTOF OUR PIPELINES IN THAT STATE. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
578 | 1993-01-08 | AZ | other | UNKNOWN ( COUNTY) | EL PASO NATURAL GAS CO | RECENT RAINS IN THE STATE OF ARIZONA HAVE FLOODED RIVERS, CAUSING DAMAGE TO A NUMBER OF OUR PIPELINES IN THAT STATE. FLOOD WATERS FROM THE SAN PEDRO RIVER WASHED AWAY SOME PEERS FOR A PIPELINE BRIDGE SUPPORTING OUR 6 5/8" LINE2071. THIS CAUSED THE PIPELINE TO FALL AND RUPTURE. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
579 | 1992-12-15 | MI | other | UNKNOWN (OSCEOLA COUNTY) | MICHIGAN CONSOLIDATED GAS CO (MICHCON) | MICHCON CONTRACTOR'S BACKHOE STRUCK 3" DIS. 3' UNKNOWN STUB ON SIDE OF PIPELINE THAT WAS NOT RECORDED BY PREVIOUS OWNER OF PIPELINE. STAKING LOCATION OFTHE PIPELINE WAS INACURATE | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
580 | 1992-11-20 | TX | maintenance | UNKNOWN (WARD COUNTY) | AMERICAN CENTRAL GAS CO INC | TESTS REVEAL THAT TGE 8" LINE PIPE INVOLVED FAILED DUE TO INTERNAL OVER-PRESSURIZATION. THE WALL THINNING IN THE ERW WELD SEAM FUSION LINE AT THE ORIGINOF THE BURST WAS THE RESULT OF SULFUR COMPOUNDS CORROSION. THE CORROSION HAD OCCURRED FROM THE I.D. PREFERENTIALLY IN THE FUSION LINE OF THE LONGITUDINAL ERW WELD SEAM. THE FINAL FRACTURE WAS LESS THAN 30% OF THE ORIGINAL WALL THICKNESS. ADDITIONALLY, THE FINAL FRACTURE AREA CONTAINED ERW WELD DEFECTS AT THE FUSION LINE. FLAT, PARTIALLY FUSED AREAS IN THE FUSION LINE ARE CALLED"PASTY" AND ARE THE RESULT OF A COLD WELD, LOW HEAT INPUT. THESE AREAS OFFER VERY LOW TO ALMOST NO STRENGTH AND LOWER THE STRENGTH OF THE PIPE WALL. | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
581 | 1993-01-21 | AZ | maintenance | UNKNOWN ( COUNTY) | EL PASO NATURAL GAS CO | OUR 30" CALIFORNIA LOOP LINE 1103 RUPTURED DUE TO A SEAM FAILURE. THERE WASA FIRE AND A 600' SEGMENT OF PIPE LINE WAS BLOWN OUT. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
582 | 1993-01-19 | AZ | other | UNKNOWN ( COUNTY) | EL PASO NATURAL GAS CO | OF OUR PIPELINES IN THAT STATE. FLOOD WATERS FROM THE GILA RIVER CAUSED OUR 26" CALIFORNIA LINE 1100 AND OUR 30" CALIFORNIA 1ST LOOP LINE 1103 TO RUPTURE. RELEASED GAS, EXPLODED AND IGNITED. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
583 | 1993-01-19 | AZ | other | UNKNOWN ( COUNTY) | EL PASO NATURAL GAS CO | OF OUR PIPELINES IN THAT STATE. FLOODS WATERS FROM THE GILA RIVER CAUSED OUR 8 5/8" MORENCI LINE 2006 TO RUPTURE. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
584 | 1993-01-19 | AZ | other | UNKNOWN ( COUNTY) | EL PASO NATURAL GAS CO | RAINS IN THE STATE OF ARIZONA HAVE FLOODED RIVERS, CAUSING DAMAGE TO A NUMBER OF OUR PIPELINES IN THAT STATE. FLOOD WATERS FROM THE GILA RIVER CAUSED OUR 6 5/8" MORENCI LOOP LINE 2007 TO RUPTURE. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
585 | 1993-01-07 | ID | other | UNKNOWN (BOUNDARY COUNTY) | PACIFIC GAS TRANSMISSION CO | MAINLINE RELIEF VALVE WITH A SET PRESSURE OF 930 PSIG OPENED PREMATURELY AT A LINE PRESSURE OF 781 PSIG. FATIGUE FAILURE OF A 1/4-INCH VALVE PREVENTED AUTOMATIC CLOSING OF THE RELIEF VALVE. DAMAGE TO FACILITIES WAS LESS THAN $1,000 AND CONSISTED ONLY OF A 1/4 INCH VALVE AND A PRESSURE SWITCH, BOTH OF WHICH FAILED IN FATIGUE, PROBABLY DUE TO VIBRATIONS CAUSED BY THE BLOWING GAS.THE AREA WAS NEVER UNSAFE AS THE FACILITY WAS DESIGNED FOR BLOWING GAS TO THE ATMOSPHERE, BUT BECAUSE IT IS A REMOTE LOCATION, IT WAS APPROXIMATELY 1 HOUR AND 15 MINUTES BEFORE THE GAS WAS SHUT OFF. THE INCIDENT OCCURRED AT A NEWFACILITY THAT HAS BEEN IN SERVICE ONLY FOUR MONTHS. | 85000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
586 | 1993-01-21 | VA | maintenance | UNKNOWN (CAMPBELL COUNTY) | TRANSCO GAS PIPELINE CORP |  | 54000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
587 | 1993-01-10 | OK | other | UNKNOWN (GARFIELD COUNTY) | ENOGEX INC (EX. MUSTANG FUEL CORP) | ON JANUARY 10, 1993, AT APPROXIMATELY 6:30 A.M., A LOW PRESSURE STORAGE TANKAT THE ENID POWER PLANT STATION FAILED. THE PRESSURE AT WHICH THE FAILURE OCCURRED IS STILL UNKNOWN. THERE WERE NO DEATHS OR INJURIES INVOLVED AND FIREDID NOT OCCUR AS A RESULT OF THIS FAILURE. THE LOCATION OF THE ENID POWER PLANT REGULATOR STATION IS GARFIELD COUNTY, OKLAHOMA, SECTION 19, TOWNSHIP 22 NORTH, RANGE 6 WEST. THE AREA IS PRIMARILY RURAL WITH A FEW INDUSTRAIL BUILDINGS IN THE AREA. DAMAGE TO SURROUNDING BUILDINGS WAS MAINLY BLOWN OUT WINDOWS, LOOSE LIGHT FIXTURES AND MINOR EXTERIOR DAMAGE, ALTHOUGH ONE BUILDING DIDRECEIVE MODERATE INTERIOR DAMAGE. OUR STATION PIPING AND COMPONENTS DID RECEIVE EXTENSIVE DAMAGE IN THE IMMEDIATE AREA WHERE THE STORAGE TANK WAS LOCATED. THE INLET SEPARATOR DUMP VALVE MALFUNCTIONED, CAUSING THE VALVE TO OPEN.IT APPEARS THAT LIQUIDS IN THE EXTERNAL FLOAT DISPLACEMENT CHAMBER BEGAN TO FREEZE AND EXPAND. THIS CAUSED THE DISPLACER TO RISE, SENDING SUPPLY GAS TO THE DUMP VALVE, WHICH THEN BEGAN TO OPEN. WITH THE DISPLACER FROZEN IN A RAISED POSITION, THE DUMP VALVE REMAINED PARTIALLY OR FULLY OPEN, DUMPING WHAT LIQUID WAS IN THE SEPARATOR INTO THE STORAGE TANK AND THEN ALLOWED HIGH PRESSURE GAS TO FILL THE STORAGE TANK, INCREASING ITS INTERNAL PRESSUREEE. THE RELIEF VALVE WAS OPEN AND RELIEVING CONTINOUSLY. AS THE RESULT OF THE LOW AMBIENTAIR TEMPERATURES OF 25 DEGRESS F, HYDRATES FORMED WHICH PLUGGED OFF THE RELIEF VALVE, CAUSING PRESSURE IN THE TANK TO INCREASE UNTIL THE TANK RUPTURED. THE RELIEF VALVE WAS SET AT 35 PSIG AND THE OPERATING PRESSURE OF THE STORAGETANK WAS 30 PSIG. ALTHOUGH THE RELIEF VALVE WAS SET 5 PSIG ABOVE THE STORAGE TANK'S OPERATING PRESSURE, WE DO NOT FEEL THIS CONTRIBUTED TO THE RUPTURE.OWEVER, THIS FINDING DID RAISE A CONCERN ON OUR PART OF THE QUALITY OF WORK BEING DONE BY THE CONTRACTOR PERFORMING RELIEF VALVE TESTING. WE ARE IN THE PROCESS OF REVIEWING ALL OUR RELIEF VALVE SETTINGS TO ENSURE THAT THEY ARE NOT SET ABOVE MAXIMUM ALLOWABLE OPERATING PRESSURES. | 80000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
588 | 1993-01-15 | WY | other | UNKNOWN (CAMPBELL COUNTY) | M I G C INC | ON JANUARY 15, 1993 A FIRE OCCURRED IN A MIGC, INC. COMPRESSOR STATION. DAMAGES OCCURRED TO THE WHITE ENGINE WHICH DRIVES ONE COMPRESSOR. TELEPHONIC MOTICE TO 1-800-424-8802 WAS MADE ON JANUARY 1118, 1993. TELEPHONIC NOTICE TO1-777-7427, STATE OF WYOMING WAS MADE ON JANUARY 18, 1993. MR. JOHN JACQUOT RESPONDED TO THE CALL. THE TIME LAPSE BETWEEN JANUARY 15, DATE OF THE INCIDENT AND JANUARY 18, THE DATE OF REPORTING WAS NECESSARY DUE TO THE DIFFICULTY OF DETERMINING THE AMOUNT OF DAMAGE. | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
589 | 1993-01-20 | KY | leaks and spills | UNKNOWN (PIKE COUNTY) | ASHLAND EXPLORATION CO | INVESTIGATORS OF THE SURROUNDING AREA DISCOVERED A LEAK ON AN UNKNOWN SECTION OF ABANDONED PIPELINE OWNED BY AEI. THIS LEAK WAS A POSSIBLE SOURCE OF THEEXPLOSION ALTHOUGH THE ACTUAL SOURCE WAS NEVER CONCLUSIVELY CONFIRMED. INJURED PARTY RELEASED FROM HOSPITAL AND BACK TO WORK WITH NO APPARENT PERMANENT INJURY. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
590 | 1993-01-23 | TX | leaks and spills | UNKNOWN ( COUNTY) | UNOCAL NORTH AMERICAN OIL & GAS DIV | LEAK WAS FOUND IN 6 -5/8" RISER ABOVE THE WATER LEVEL. THE SPLASHTRON COATING WORE OFF IN THE AREA OF THE LEAK ALLOWING CORROSION TO OCCUR. THE SUBJECTPIPE WAS REPLACED AND THE SYSTEM WAS PRESSURE TESTED AND PLACED BACK ON PRODUCTION 1/29/93.7 | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
591 | 1993-01-13 | LA | other | UNKNOWN ( COUNTY) | UNITED GAS PIPELINE CO | METULURGICAL REPORT & FURTHER INVESTIGATION IN PROGRESS. | 52000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
592 | 1993-01-24 | MA | other | UNKNOWN (ESSEX COUNTY) | TENNESSEE GAS PIPELINE CO | PIPELINE BEGAN TO LEAK WHEN THE SOIL OVERBURDEN CAUSED EXCESSIVE PRESSURE ONTHE PIPELINE IN AN AREA OF SOFT, UNSTABLE SOIL. (LARGE VOLUMES OF FILL WEREPLACED ON TOP OF PIPE IN A WET/BOGGY AREA). | 58000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
593 | 1993-01-12 | TX | leaks and spills | UNKNOWN (ORANGE COUNTY) | TRISTAR GAS COMPANY | ON JANUARY 12, 1993 AT APPROXIMATELY 10:00P.M., THE REGULATOR AT THE GAS SUPPLY SOURCE ON TRISTAR GAS COMPANY'S PIPELINE MALFUNCTION. THIS ALLOWED THE PRESSURE ON TRISTAR'S LINE TO REACH 310 PSIG. THE REGULATOR AT THE DELIVERY POINT TO TRINITY INDUSTRIES FACILITY DIDN'T REACT QUICKLY ENOUGH TO PREVENT TRINITY'S SYSTEM FROM BEING EXPOSED TO THIS PRESSURE. TRINITY HAS NO OVERPRESSURE PROTECTION ON THEIR SYSTEM. THIS AMOUNT OF PRESSURE DAMAGED A PORTION OFTHEIR SYTEM. ON JANUARY 15, 1993 A LEAK WAS DISCOVERED ON TRISTAR'S PIPELINE. DUE TO THE CORROSION EXISTING ON THIS PIPELINE, IT IS SUSPECTED THAT THE HIGH PRESSURE CAUSED THE LEAK. | 5000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
594 | 1992-12-28 | LA | leaks and spills | UNKNOWN ( COUNTY) | ANR PIPELINE CO |  | 52000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
595 | 1993-02-10 | TX | maintenance | UNKNOWN (REFUGIO COUNTY) | UNITED GAS PIPELINE CO | THE MATERIAL DEFECT WAS A "HARDSPOT" ON THE PIPE DUE TO THE MANUFACTURE'S PROCESS. THE "HARDSPOT" WAS PREVIOUSLY INDENTIFIED AND REINFORCED WITH A SLEEVE. THE REINFORCING SLEEVE CONTAINED THE DEFECT. | 55000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
596 | 1993-02-27 | CA | other | UNKNOWN (SAN BERNARDINO COUNTY) | SOUTHERN CALIFORNIA GAS CO | ON FEBRUARY 27, 1993, AT 8:20 A.M., WE REALIZED A DROP IN PRESSURE ON LINE 2000. OUR INVESTIGATION REVEALED THAT A LANDSLIDE, ATTRIBUTE TO RECENT RAINS,STRESSED THE LINE TO THE POINT OF FAILURE. PERMANENT REPAIRS WERE COMPLETEDBY RELOCATING 2033' AROUND THE LANDSLIDE AREA. SERVICE WAS INTERRUPTED AT 2:17 P.M. TO SIX CUSTOMERS AND RESTORES WERE COMPLETED AT 10:45 P.M. THERE WERE NO FIRES OR INJURIES ASSOCIATED WITH THIS INCIDENT. GAS LOSS ASSOCIATED WITH THIS INCIDENT WAS 9,801.94 MCF. ESTIMATED COSTS ASSOCIATED WITH THIS INCIDENT WERE $500,000. | 500000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
597 | 1993-03-04 | KS | other | UNKNOWN (RUSH COUNTY) | K N ENERGY INC(KANSAS NEBRASKA GAS CO) | FOR EXAMINATION UNTIL WINTER SNOW MELT DECREASES. A TEMPORARY BYPASS LINE HAS BEEN INSTALLED ON AN EXISTING COUNTY ROAD BRIDGE NEARBY. THE PIPELINE SECTION CANNOT BE REMOVED UNTIL THE HEAVY STREAM FLOW RECEDES. THIS AREA HAS RECEIVED CONSIDERABLE AMOUNTS OF SNOW THIS WINTER AND THE SPRING MELTING AND DRAINAGE WILL CONTINUE FOR SOME TIME BEFORE A PERMANENT REPAIR CAN BE MADE. SERVICE WAS TEMPORARILY INTERRUPTED TO 4 RURAL CUSTOMERS. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
598 | 1993-03-01 | OH | other | UNKNOWN (HOLMES COUNTY) | COLUMBIA GAS TRANSMISSION CORP | PRIVATE PROPERTY OWNER'S BULLDOZER BROKE MAINLINE FEED TO TOWN OF MILLERSBURG, OHIO. GAS SERVICE WAS INTERRUPTED TO APPROXIMATELY 1,330 COLUMBIA GAS OF OHIO DISTRIBUTION CUSTOMERS FOR 24-HOUR PERIOD. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
599 | 1993-03-07 | NE | other | UNKNOWN (FRANKLIN COUNTY) | K N ENERGY INC(KANSAS NEBRASKA GAS CO) | PIPELINE RUPTURED UNDER FLOWING STREAM. RUPTURED PORTION CAN NOT BE REMOVEDFOR EXAMINATION UNTIL WINTER SNOW MELT DECREASES. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
600 | 1993-02-24 | CA | other | UNKNOWN (LOS ANGELES COUNTY) | SOUTHERN CALIFORNIA GAS CO | ON FEBRUARY 24, 1993, AT 9:00 A.M., WE RECEIVED A REPORT THAT LINE 85 HAD RUPTURED AND WAS ON FIRE. OUR INVESTIGATION REVEALED THAT A LANDSLIDE, ATTRIBUTED TO RECENT RAINS, STRESS THE LINE TO THE POINT OF FAILURE AND THE ESCAPINGGAS WAS THEN IGNITED BY OVERHEAD ELECTRICAL FACILITIES. PERMANENT REPAIRS WERE MADE BY CAPPING BOTH ENDS OF THE DAMAGED SECTION. A RELOCATION OF 2100' AROUND THE LANDSIDE AREA IS PLANNED. SERVICE WAS INTERRUPTED AT 10:30 A.M. TO NINETY CUSTOMERS LOCATED AT THE PARADISE RANCH MOBILE HOME PARK AND RESTORES WERE COMPLETED AT 7:30 P.M. THERE WERE NO INJURIES ASSOCIATED WITH THIS INCIDENT. ESTIMATED COSTS ASSOCIATED WITH THIS INCIDENT WERE $552,628. DOT NOTIFICATION 02/24/93, REFERENCE REPORT# 159480. | 552628 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
601 | 1993-02-20 | TX | maintenance | UNKNOWN ( COUNTY) | TRANSCO GAS PIPELINE CORP | AT APPROXIMATELY 10:00 A.M. ON FEBRUARY 20, 1993 ENRON PERSONNEL REPORTED TOTGPL'S GAS CONTROL THAT BUBBLES WERE SIGHTED IN THE VICINITY OF TGPL'S PIPELINE IN MATAGORDA ISLAND BLOCK 681. LATE AFTERNOON IN FEBRUARY 20, 1993, TRANSCO PERSONNEL WERE ABLE TO CONFIRM THAT THE LEAK WAS FROM A TGPL PIPELINE. DIVERS WERE DISPATCHED TO THE LEAK LOCATION DURING THE MORNING OF FEBRUARY 21,1993 AND FOUND THAT THE LEAK WAS COMING FROM THE VENT PLUG ON THE 12' TAP VALVE IN BLOCK 681. WHILE IN THE PROCESS OF CLOSING TO TAP VALVE SO THAT THE MINOR REPAIR COULD BE MADE, THE 1/2" VENT PLUG BEGAN TO LEAK MORE SEVERELY. ATAPPROXIMATELY 3:00 P.M. ON FEBRUARY 21, 1993 THE DECISION WAS MADE TO SHUT-IN AND BLOW DOWN THE 20" PIPELINE FROM MATAGORDA ISLAND BLOCK 669 AND MAKE THENECESSARY REPAIR. | 56000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
602 | 1993-03-18 | TX | maintenance | UNKNOWN (BRAZOS COUNTY) | BRAZOS PIPELINE SYSTEM | AAA 1/2 INCH HEAVY DUTY PIPE NIPPLE RATED AT 6,125 PSI CRACKED IN THE THREADS CAUSING THE RELEASE OF GAS WHICH IGNITED CAUSING THE RELEASE OF GAS WHICH IGNITED CAUSING THE 1969 WAUKESHA GAS COMPRESSOR TO CATCH ON FIRE. THIS IS A MANUFACTURED COMPONENT. | 300000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
603 | 1993-03-23 | NY | other | UNKNOWN (NEW YORK COUNTY) | CONSOLIDATED EDISON CO OF NEW YORK | A CRACK DEVELOPED ON A SEGMENT OF THE NEW YORK FACILITIES. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
604 | 1993-05-02 | CO | maintenance | UNKNOWN (MONTEZUMA COUNTY) | NORTHWEST PIPELINE CORP | PIPE WAS SUBJECTED TO LINEALOG SURVEY IN 1972 AND NO CORROSION WAS IDENTIFIED IN THIS AREA AT THAT TIME. VISUAL EXAMINATION OF THE DAMAGED PIPE FOUND THE INTERNAL AND EXTERNAL CONDITION TO BE GOOD. THEE CAUSE OF THE FAILURE IS STILL BEING INVESTIGATED. | 365500 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
605 | 1993-04-27 | NE | other | UNKNOWN (ANTELOPE COUNTY) | K N ENERGY INC(KANSAS NEBRASKA GAS CO) | A 2-INCH STEEL, BURIED TRANSMISSION PIPELINE WAS HIT BY A THIRD PARTY CONTRACEXPLOSION DEMOLISHED STRUCTURE. (SUSPECTED OF BEING FUELED BY NATURAL GAS) LETOR IN ANTELOPE COUNTY, NEBRASKA ON APRIL 27, 1993. IGNITION DID NOT OCCUR AAK WAS DETECTED ON SERVICE LINE IN FRONT OF STRUCTURE WITHING 24" OF UNDERPINND THERE WERE NO INJURIES OR FATALITIES RESULTING FROM THE INCIDENT. SERVICENING WITH CAUSE OF LEAK STILL UNDER INVESTIGATION. END OF PIPE, WHERE THREADE WAS TEMPORARILY INTERRUPTED TO 219 CUSTOMERS IN ORCHARD, NE AND 15 RURUL CUSD FOR ATTACHMENT OF SCREW ELL, HAD APPARENT STRESS FRACTURE (AT THREADS CAUSITOMERS. THE PIPELINE DIG-IN WAS CAUSED BY A CONTRACTOR DIGGING HOLES FOR ANNG LEAKAGE. CURRENTLY SUSPECTED CAUSE OF LEAK WAS GROUND SHIFT AND STRUCTUREELECTRIC POLE RELOCATION PROJECT. THE 2-INCH LINE WAS PREVIOUSLY LOCATED ANDSHIFTING DUE TO EXPLOSION. MARKED WITH PIN FLAGS BY A K N EMPLOYEE AND A LINE MARKER WAS LOCATED NEARBY. TELEPHONIC REPORT OF THE INCIDENT WAS MADE ON REPORT NO.170068 TP PETTY OFFICER EVANSON AT THE DEPARTMENT OF TRANSPORTATION ON APRIL 27, 1993. THE CALL WAS MADE OAFTER COMPANY OFFICIALS DETERMINED THAT NOTIFICATION WAS DESIREDEVEN THOUGH THE INCIDENT DID NOT CAUSE OVER $50,000 IN DAMAGE, INCLUDING GASLOSS. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
606 | 1993-05-10 | OK | other | UNKNOWN (HUGHES COUNTY) | TRANSOK INC | ON MAY 10, 1993 AT 15:30 AN OPERATOR AT TRANSOK'S GREASY CREEK PROCESSING PLANT NOTIFIED THE GAS CONTROL CENTER THAT ALL COMPRESSORS HAD SHUTDOWN DUE TO LOW SUCTION PRESSURE. AT THIS SAME TIME GAS CONTROL WAS NOTICING A PRESSURE LOSS ON THE LINE FEEDING THIS PLANT ( A 24" STEEL PIPELINE DESIGNATED AS LINE#15). GAS CONTROL IMMEDIATELY NOTIFIED THE SOUTHEAST DISTRICT SUPERINTENDENT T.J. BOGLE AND NORTHEAST MONITOR PRESSURE AT THESE SITES ON LINE #115 TO ATTEMPT TO IDENTIFY THE SECTION WITH THE POSSIBLE LEAK. UPON ARRIVAL AT THE NORTH CANADIAN VALVE TWO SOUTHEAST DISTRICT EMPLOYEES, MIKE WINTERS AND RICKY SPRKS, NOTED A PLUME OF WATER RISING FROM THE NORTH CANADIAN RIVER IN THE AREAOF THE PIPELINE RIGHT-OF-WAY. AT 16:10 MIKE WINTERS REPORTED BY RADIO TO GAS CONTROL THAT THEY HAD FOUND THE LEAK AND THAT THEY HAAD CLOSED VALVES # 15-21 AND 15-23 TO COMPLETEE THE ISOLATION OF THIS SECTION OF LINE. THE LEAK APPEARS TO BE APPROX. 50 FEET SOUTH OF THE NORTH BANK OF THE NORTH CANADIAN RIVER. THE ESTIMATED DEPTH OF THE WATER OVER THE LOCATION WHERE THE LEAK OCCURRED IS APPROX. 20 FEET. CONDITIONS ON THE RIVER AT WETUMKA ACCORDING TO THE RIVER FORECAST CENTER ON 5/10/93 AT 15:30 WERE 18.1 FEET AND FLOOD STAGE IS 25.1 FEET. THE AREAA OF THE LEAK IS A CLASS 1 LOCATION WITH THE CLOSEST OCCUPIED RESIDENCE APPROX. 1/4 MILE AWAY. ON 5/11/93 THE TRANSOK ENGINEERING AND CONSTRUCTION DEPARTMENTS BEGAN SURVEYING THE CROSSING FOR REPAIRING OR REPLACING. THE OPTION OF REBORING THE RIVER AND INSTALLING NEW PIPE IS THE OPTION PRESENTLY BEING EXAMINED. | 600000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
607 | 1993-04-16 | TX | leaks and spills | UNKNOWN (LIMESTONE COUNTY) | TEXAS UTILITIES FUEL CO | TOP COATING AT LEAK SITE WAS DISBONDED. | 78876 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
608 | 1993-05-06 | TX | maintenance | UNKNOWN (GAINES COUNTY) | AMAERICAN GAS STORAGE CORP |  | 3000000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
609 | 1993-05-28 | AK | other | UNKNOWN (SUSITNA BOROUGH COUNTY) | ENSTAR NATURAL GAS CO |  | 3500000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
610 | 1993-05-12 | KS | other | UNKNOWN (SEDGWICK COUNTY) | WILLIAMS NATURAL GAS CO | TURBULENT FLOODWATERS IN THE ARKANSAS RIVER CAUSED THE 16" LINE TO SEPARATE. THE LINE WAS CAPPED ON EACH SIDE OF THE RIVER. THE REPAIRS TO THE LINE WILL BE MADE AFTER THE WATER RECEDES. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
611 | 1993-05-12 | LA | other | UNKNOWN ( COUNTY) | SEA ROBIN PIPELINE CO | TWO SMALL PINHOLE LEAKS WERE DISCOVERED AT THE 6 O'CLOCK POSITION ON THE PIPE. INSPECTION BY DIVERS REVEALED NO EVIDENCE OF COATING DAMAGE OR EXTERNAL DETERIORATION OF THE PIPE. AN ULTRASONIC THICKNESS GAUGE WAS EMPLOYED TO CHECK THE PIPE WALL THICKNESS AROUND THE CIRCUMFERENCE OF THE PIPE AT THE POINT OF THE LEAKS AND WITHIN SEVERAL FEET EITHERSIDE OF THE LEAK LOCATION. NO METAL LOSS OR EVIDENCE OF DECREASED WALL THICKNESS WAS FOUND AS MIGHT BE EXPECTEDIF THE LEAKS WERE ATTRIBUTABLE TO INTERNAL CORROSION. THE LEAKS WERE NOT INTHE WELD SEAM OF THE PIPE. THE INVESTIGATION PRODUCED NO OTHER EVIDENCE THAT WOULD ALLOW DETERMINATION OF THE CAUSE OF THE LEAKS. A PERMANENT REPAIR WAS MADE BY INSTALLING AN ANSI 900# SERIES MECHANICAL CLAMP. | 206000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
612 | 1993-05-12 | NC | other | UNKNOWN (BURKE COUNTY) | PIEDMONT NATURAL GAS CO INC | CONTRACTOR INSTALLING NEW PIPELINE PARALLEL TO EXISTING LINE FOR PIEDMONT DAMAGED EXISTING LINE DURING EXCAVATION. CONTRACTOR WAS OBLIGATED TO LOCATE EXISTING LINE BY EXPOSING IT WAS NEEDED. THE INTERVAL IN THE AREA OF DAMAGE WAS TOO LARGE. AS A RESULT OF THE DAMAGE, SERVICE WAS INTERRUPTED TO 3,368 CUSTOMERS. | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
613 | 1993-05-19 | LA | leaks and spills | UNKNOWN ( COUNTY) | COLUMBIA GULF TRANSMISSION CO | SCENARIO: LEAK DISCOVERED BY SEA ROBIN HELICOPTER PILOT 5/19/93. DIVING CONTRACTOR MOBILZED MIDNIGHT 5/20/93. LEAK CONFIRMED TO BE COLUMIA PIPELINE 9:00 PM 5/22/93. PINHOLE LEAK REPAIR COMPLETED WITH HYDROTECH SUB-SEA REPAIR CLAMP 7:00 PM 5/25/93.ISOLATED CORROSION CELL SINGLE PIT STATUS WAS DETERMINED FROM RESULTS OFEXTENSIVE ULTRASONIC INSPECTION OF THE AFFECTED AREA. A THIRTY DAYBATERIOLOGICAL COUNT LABORATORY ANALYSIS IS UNDERWAY TO DETERMINE WHETHERTHE CAUSE WAS FROM CHEMICAL ATTACK OR BACTERIOLOGICAL ATTACK.APPROPRIATE INHIBITOR PROGRAM WILL BE INITIATED. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
614 | 1993-05-01 | NY | other | UNKNOWN (ALBANY COUNTY) | SELKIRK COGEN PARTNERS | BECHTEL CORPORATION OF NEVADA EXPOSED AND DAMAGED A 3 FOOT LONG SECTION OF THE PIPELINE DURING EXCAVATION ACTIVITIES ON THE PHASE II SITE. DATE OF NOTIFICATION : 05/03/93. TIME OF NOTIFICATION : 8:00 AM. RESPONSE: UPON NOTIFICATION THAT DAMAGE TO THE PIPELINE HAD OCCURRED, THE SELKIRK COGEN PROJECT OPERATOR MADE ARRANGEMENTS TO ENTER THE EXCAVATION FOR A CLOSER EVALUATION OF THE DAMAGE. THE EXCAVATION WAS ENTERED AND THE DAMAGE WAS INSPECTED BY THE OPERATOR AND BECHTEL CONSTRUCTION AT APPROXIMATELY 13:00 SEVERAL DENTS AND GOUGES OF THE OUTSIDE SURFACE OF THE PIPE WAS FOUND. THE DAMAGES AREAS WERE MEASURED AND THE PHOTOS WERE TAKEN. THE PIPE WAS FOUND TO CONTAIN SEVERAL DENTS,THE LARGEST OF WHICH WAS APPROXIMATELY 5/8 INCH DEEP. THE DAMAGE WAS WITHIN3 FEET OF PIPELINE WELD NUMBER W4. FOLLOWING THE INSPECTION, THE DECISION WAS MADE TO IMMEDIATELY DEPRESSURIZE THE LINE TO ALLOW REPAIR OF THE DAMAGE. THE MAIN ISOLATION VALVE WAS CLOSED AT 16:43. THE PIPELINE WAS ALLOWED TO DEPRESSURIZE BY CONSUMPTION OF THE GAS IN THE PACKAGE BOILERS ON THE COGEN SITEELIMINATING THE NEED TO VENT THE GAS TO ATMOSPHERE. THE GAS LINE PRESSURE HAD BLEED DOWN AND THE COGEN ISOLATION VALVE WAS CLOSED AT 20:15. SKIBACK PIPELINE CO. WAS MOBILIZED AND ARRIVED ON SITE ON 05/05/93 AND PROCEEDED WITH THE REPAIRS WHICH CONSISTED OF REPLACING THE DAMAGED PORTION OF THE PIPE. WELDNUMBER W4 WAS REMOVED WITH THE DAMAGED PIPE AND A PRETESTED SECTION OF REPLACEMENT PIPE WAS INSTALLED WITH WELDS LABELED W4A AND W4B. FOLLOWING THE REPAIR, THE PIPE COATING WAS CLOSELY INSPECTED AND REPAIRED AS REQUIRED. THE PIPE EXPOSED DURING THE DURING THE REPAIR WAS FOUND TO SHOW NO EVIDENCE OF CORROSION AND THE INTERIOR SURFACE OF THE PIPE WAS ALSO CLEAN. THE NEW YORK STATEPUBLIC SERVICE COMMISION WAS NOTIFIED OF THE INCIDENT AND SR. GAS & PETROLEUM INSPECTOR JOHN HENRY MCCAULEY WAS ON SITE TO INSPECT ALL OF THE REPAIRS MADE TO THE PIPELINE AND TO OBSERVE THE BACKFILLING OF THE PIPE AFTER THE REPAIRS WERE COMPLETED. FOLLOWING THE REPAIRS, THE LINE WAS PIGGED AND REFILLED WITH NATURAL GAS. NATURAL GAS SERVICE WAS RESTORED TO THE COGEN PROJECT ON 05/07/93 AT 15:12. | 40000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
615 | 1993-04-28 | KS | other | UNKNOWN (JOHNSON COUNTY) | WILLIAMS NATURAL GAS CO | UNAUTHORIZED ENTRY OF WNG FACILITIES IN WHICH THE CONTROLLERS ON REGULATORS WERE ADJUSTED RESULTING IN AN OVERPRESSURE SITUATION. THE MAOP OF THE TWO PIPELINES WERE EXCEEDED. THE FBI WAS BROUGHT IN TO INVESTIGATE. TWO 26" PIPELINES WERE OVERPRESSURED FOR APPROXIMATELY 2 HOURS WHEN UNAUTHORIZED ENTRY WASMADE AT WNG'S SOUTH GLAVIN METERING STATION. AN OVERPRESSURE CONDITION WAS CREATED WHEN THE CONTROLLERS ON SEVERAL REGULATORS WERE ADJUSTED ALLOWING THEPIPELINES TO PRESSURE UP TO 435 PSIG. THE FBI AND LOCAL LAW ENFORCEMENT WERE SUBSEQUENTLY NOTIFIED. THE LINES WERE FREQUENTLY PATROLLED WITH FIU'S DURING THE DAYS ENSUING THE INCIDENT. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
616 | 1993-06-07 | LA | other | UNKNOWN (CONCORDIA COUNTY) | MID - LOUISIANA GAS CO | PART 3 - STRONG RIVER CURRENT SCOURED CHANNEL BELOW THE PIPE NEAR THE EDGE OF ALEAK OCCURRED IN MISS. RIVER. STRONG CURRENT HAS PREVENTED COMPLETION OF INVOF A SANDBAR CAUSING PIPE TO BECOME SUSPENDED OVER THE BOTTOM. THE FORCE OF THEESTIGATION AND REPAIR. LINE IS SHUT-IN AND SERVICE BEING MAINTAINED BY ADDITCURRENT CAUSED THE SUSPENDED PIPE SWING AND EVENTUALLY BREAK INTO A HEAT AFFECTEIONAL LINES ACROSS THE RIVER SUPPLEMENTAL REPORT TO BE FILED.D ZONE OF A GIRTH WELD. PART 4 - HEAT AFFECTED ZONE ADJACENT TO GIRTH WELD.PART B.1 - CHANNEL BOTTOM SCOUR IN MISSISSIPPI RIVER. | 150000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
617 | 1993-06-15 | MI | other | UNKNOWN (ST CLAIR COUNTY) | MICHIGAN CONSOLIDATED GAS CO (MICHCON) | INGNITION OF GAS VENTING FROM WELL RIG LUBRICATOR BOTTLE DURING ROUTINE WELLWORK TO RETRIEVE A PACKER. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
618 | 1993-06-06 | LA | other | UNKNOWN ( COUNTY) | NATURAL GAS PIPELINE CO OF AMERICA | THE PIPELINE WAS APPARENTLY STRUCK BY A JACK-UP RIG BEING TOWED TO A DRILLING SITE. REPAIRS ARE IN PROGRESS. | 500000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
619 | 1993-05-31 | TX | other | UNKNOWN (GAINES COUNTY) | AMAERICAN GAS STORAGE CORP | 1/2" XH PIPE NIPPLE (SCH 40) BROKE OFF AT THREADS. IF METALURGICAL REPORT DIFFERS FROM INITIAL FINDINGS, A SUPPLEMENTAL REPORT WILL BE SUBMITTED. | 400000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
620 | 1993-06-03 | AL | maintenance | UNKNOWN (CHILTON COUNTY) | TRANSCO GAS PIPELINE CORP | AT APPROXIMATELY 10:30 PM CST ON JUNE 3, 1993, A FIRE OCCURRED AT COMPRESSORSTATION 100 LOCATED NEAR BILLINGSLEY, ALABAMA. THE FIRE OCCURRED ON STEAM TURBINE UNIT #2. TWO EMPLOYEES SUFFERED MINOR INJURIES AND WERE TAKEN TO A LOCAL HOSPITAL. ONE EMPLOYEE WAS TREATED AND RELEASED, THE OTHER EMPLOYEE SUSTAINED SECOND DEGREE BURNS TO HIS LEFT AND AND SMOKE INHALATION AND WAS KEPT IN THE HOSPITAL TWO NIGHTS FOR OBSERVATION AND THEN WAS RELEASED. COMPRESSOR IUNIT #2 HAS EXTENSIVE DAMAGE AND THE COMPRESSOR HUILDING AND ADJACENT COMPRESSOR UNITS ALSO HAVE SOME DAMAGE. THE CAUSE OF THE INCIDENT IS UNKNOWN AT THIS TIME. A TASK GROUP HAS BEEN ESTABLISHED AND IS INVESTIGATING THE INCIDENT. UPON COMPLETION OF THE INVESTIGATION, A SUPPLEMENTAL REPORT WILL BE FILED WITH THE DEPARTMENT OF TRANSPORTATION. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
621 | 1993-06-19 | CA | other | UNKNOWN (RIVERSIDE COUNTY) | SOUTHERN CALIFORNIA GAS CO | ON JUNE 19,1993 , AT APPROXIMATELY 11:34 AM, CASH EQUIPMENT RENTALS DAMAGED LINE 2000 WITH A TOOTH ON THE FRONT BUCKET OF A CATIPILAR MODEL 988 LOADER WHILE EXCAVATING. A 6"X3" HOLE WAS GOUGED IN THE LINE AT ABOUT THE ONE O'CLOCK POSITION. ALL OFF - LINE TAPS, EXCEPT ONE, WERE SECURED. ALL SERVICES WERE RESTORED BY THE NEXT DAY. PERMANENT REPARIS WERE COMPLETED BY INSTALLING A FIELD FABRICATED BAND OVER THE DAMAGED AREA. THERE WERE NO FIRES OR INJURIES ASSOCIATED WITH THIS INCIDENT. GAS LOSS CALCULATION WAS 16,480 MCF. ESTIMATED COSTS ASSOCIATED WITH THIS INCIDENT WERE $62,500. UNDERGROUND SERVICE ALERT WAS NOT NOTIFIED. | 62500 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
622 | 1993-06-15 | TX | other | UNKNOWN (BRAZOS COUNTY) | TEXAS UTILITIES FUEL CO | OPERATOR WAS LOADING FILL DIRT WITH A JOHN DEERE 544E FRONT END LOADER ON TUFCO R.O.W. KNOCKED HOLE IN 24" LINE NORTH OF BVO 113 ABOUT 200 YDS.PIPELINE COLORS & TUFCO SINGS. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
623 | 1993-06-24 | LA | leaks and spills | UNKNOWN (OUACHITA COUNTY) | TENNESSEE GAS PIPELINE CO | LINE 100-2, DOWNSTREAM OF COMPRESSOR STATION RUPTURED, CAUSING A FIRE. | 300000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
624 | 1993-07-30 | LA | maintenance | UNKNOWN ( COUNTY) | TRANSCO GAS PIPELINE CORP | THE CHECK VALVE DID NOT CLOSE COMPLETELY WHEN MECHANICAL SLIP JOINT DISENGAGED, ALLOWING THE RELEASE OF GAS PRESSURE. | 350000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
625 | 1993-07-15 | WA | other | UNKNOWN (SPOKANE COUNTY) | PACIFIC GAS TRANSMISSION CO | WHILE REPAIRING A TIE-IN WELD ON NEW 34-INCH STATION PIPING, AN EXPLOSIVEMIXTURE OF GAS BUILT UP INSIDE THE PIPE FROM A LEAKING VALVE RESULTING IN AFLASH FIRE. THE WELDER REPAIRING THE WELD WAS BURNED OVER THE LOWER HALF OFHIS BODY AS THE HOT GASES CAME OUT A 2-INCH VENT INSTALLED AS AN AIR SOURCE | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
626 | 1993-07-13 | TX | other | UNKNOWN (MATAGORDA COUNTY) | TRANSCO GAS PIPELINE CORP | AT APPROXIMATELY 8:40 PM CST ON JULY 13,1993 A SMALL EXPLOSION AND FLASH FIRE OCCURRED ON THE NUMBER 1 SLUG CATCHER AT COMPRESSOR STATION 24 LOCATED IN MARKHAM, TEXAS. TWO EMPLOYEES SUFFERED INJURIES. ONE EMPLOYEE WAS TREATED AND RELEASED WITH MINOR BRUISES, THE OTHER EMPLOYEE SUSTAINED SECOND DEGREE BURNSTO HANDS, ARMS, AND FACE. NO DAMAGE TO COMPANY FACILITIES OCCURRED OTHER THAN VEHICLES LOCATED NEAR THE SITE. THE SLUG CATCHER WAS ISOLATED AND BLOWN DOWN. A FOAM PLUG WITH PLYWOOD SHIELD WAS INSTALLED TO ISOLATE THE WELDING AREA.WELDING BEGAN TO INSTALL A FLANGE UNTIL A GLOW WAS NOTICED AT THE BOTTOM OF THE FOAM PLUG HAD CAUGHT FIRE AND IGNITED SLUDGE VAPOR FROM THE SLUG CATCHER. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
627 | 1993-07-15 | LA | other | UNKNOWN (LAFOURCHE COUNTY) | TENNESSEE GAS PIPELINE CO |  | 55000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
628 | 1993-07-24 | NM | leaks and spills | UNKNOWN (HIDALGO COUNTY) | EL PASO NATURAL GAS CO | PART 3. ON 7/24 AT 7:30 PM (MDT) A LEAK WAS REPORTED ON OUR PIPLINE. AN 18" RUPTURE WAS DISCOVERED AND THE PIPELINE SEGMENT WAS ISOLATED BY 10:40 PM. THEPIPELINE WAS REPAIRED AND ETURNED TO SERVICE BY 3:38PM ON 7/25. AT THE TIME OF THE RUPTURE THIS INCIDENT DID NOT MEET THE COST CRITERIA FOR A TELEPHONIC REPORT TO DOT. SUSEQUENT REVIEW OF METERING CHARTS FOR THE PIPELINE INDICATEDTHAT THE PIPELINE HAD BEEN LEAKING SINCE 6:00 PM ON 7/21; HOWEVER OUR FIRST DISCOVERY OF A LEAK DID NOT OCCUR UNTIL 7/24. THE GAS LOST FROM 7/21 UNTIL THELEAK WAS ISOLATED 7/24 (77 HRS) RESULTED IN A TOTAL PROPERY DAMAGE OVER $50,000 AND CONSEQUENTLY THIS INCIDENT WAS TELEHONICALLY REPORTED OT DOT ON 7/26.SUPPLEMENTAL REPORT ON 3.13.95 INDICATES ADDITIONAL INFORMATION IN PART A -FAILURE WAS DUE TO STRESS CORROSION CRACKING. | 108000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
629 | 1993-07-30 | MO | other | UNKNOWN (HOWARD COUNTY) | PANHANDLE EASTERN PIPELINE CO | FLOODING ON THE MISSOURI RIVER CAUSED A LEVEE TO BREAK ON THE EAST SIDE OF THE RIVER NEAR PEPL'S FOUR PIPELINES. THE WATER VELOCITY WASHED COVER OFF THE PIPELINE RESULTING IN LINES FLOATING TO THE WATER SURFACE AS WELL AS UNDERMINING VALVE AND PIPING SUPPORT STRUCTURES. PRESSURE WAS REDUCED IN SOME OF THE PIPING AND SOME SEGMENTS WERE REMOVED FROM SERVICE AND BLOWN DOWN WHILE THE PIPING IS BEING STABILIZED AND INSPECTED. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
630 | 1993-08-01 | NM | other | UNKNOWN (RIO ARRIBA COUNTY) | GAS CO OF NEW MEXICO | LINE BREAK AT RIVER CROSSINGLINE BREAK AT RIVER CROSSING. THEORIZED THAT RIVER BOTTOM LOWERED. THE EROSION OF TH BOTTOM EXPOSED PIPELINE THAT BROKE DUE TO WATER AND MATERIAL FORCES. | 225000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
631 | 1993-08-04 | TX | maintenance | UNKNOWN (GUADALUPE COUNTY) | INTRATEX GAS CO | PROBABLE CAUSE OF FAILURE WAS A HARD SPOT ON THE BODY OF THE PIPE 29" FROM THE DSAW SEAM AT THE 7:00 O'CLOCK POSITION. | 614334 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
632 | 1993-08-14 | NY | leaks and spills | UNKNOWN (BROOME COUNTY) | COLUMBIA GAS TRANSMISSION CORP | A CORROSION INDUCED DUCTILE PIPELINE RUPTURE OCCURRED DUE TO AN APPARENT SHIELDING OF CATHODIC PROTECTION CURRENT. GAS IGNITED AND THE SUBSEQUENT FIRE DESTROYED A NEARBY DWELLING. | 277000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
633 | 1993-08-24 | LA | other | UNKNOWN (EAST CARROLL COUNTY) | COLUMBIA GULF TRANSMISSION CO | ON AUGUST 24, 1993, BETWEEN 10:30 AND 10:45 AM, COLUMBIA GULF PIPELINE 200 RUPTURED IN A CROSSING OF THE MISSISSIPPI RIVER NEAR LAKE PROVIDENCE, LOUISIANA. GAS ESCAPING FROM THE RUPTURE IGNITED NEAR THE WEST BANK OF THE RIVER. VALVES UPSTREAM AND DOWNSTREAM OF THE RIVER CROSSING WERE CLOSED AND FIRE BURNEDOUT AT 12:15 PM. THE PIPELINE PRESSURE AT THE TIME OF THE RUPTURE WAS 750 PSIG. GAS FLOW IN LINE 200 WAS DIVERTED TO ADJACENT PIPELINES. MISSISSIPPI RIVERTRAFFIC WAS STOPPED BY MEMPHIS COAST GUARD FOR 3 HOURS. AT THE TIME OF THISINCIDENT, THE MISSISSIPPI RIVER WAS AT FLOOD STAGE AND HAS REMAINED AT OR NEAR FLOOD STAGE SINCE THE TIME. FOR THIS REASON, IT HAS NOT BEEN POSSIBLE TO CONDUCT A COMPLETE INVESTIGATION OF THIS INCIDENT TO DETERMINE A POSSIBLE CAUSE. UNDERWATER ELECTRONIC SCANNING DEVICES HAVE BEEN USED TO LOCATE THE RUPTURED PIPELINE. THE CROSSING CONSISTS OF TWO 24 INCH PIPELINES. SCAN DATA SHOWSTHAT THE RUPTURE OCCURRED IN THE NORTH LINE. APPROXIMATELY 1500 FEET OF PIPEIN THREE SECTIONS ARE OUT OF THE DITCH AND LYING ACROSS THE SOUTH LINE. INVESTIGATION OF THE INCIDENT IS CONTINUING, AS RIVER CONDITIONS PERMIT, EFFORTS WILL BE MADE TO RECOVER THE PIPE IN ORDER TO DETERMINE A POSSIBLE CAUSE OF THEFAILURE. AT SUCH TIME AS A PROBABLE CAUSE IS DETERMINED, A SUPPLEMENTAL REPORT WILL BE SUBMITTED. SUPPLEMENTAL 2/29/94 - FURTHER INVESTIGATION OF THISINCIDENT HAS REVEALED THAT THE RUPTURED PIPELINE IS ON THE RIVER BOTTOM AT ADEPTH OF APPROX. 80 FEET. THE ESTIMATED COST TO LIFT THE DAMAGED LINE ISAPPROX. $1,500,000. FOR THIS REASON, COLUMBIA GULF HAS OBTAINED PERMISSIONFROM THE U.S. ARMY CORP OF ENGINEERS TO ABANDON THE LINE IN PLACE. BECAUS WEHAVE BEEN UNABLE TO RECOVER THE DAMAGED PIPELINE, WE ARE UNABLE TO DETERMINETHE CAUSE OF THE FAILURE. COLUMBIA CAN ONLY SPECULATE REGARDING THE ACTUALCAUSE OF THE FAILURE. COLUMBIA PLANS TO REPLACE THE FAILED SECTION WITH ANEW 30" PIPELINE BORED SIGNIFICANTLY BELOW THE RIVER BOTTOM. THE SUPPLEMENTALREPORT WILL CLOSE OUTR FILE ON THIS INCIDENT. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
634 | 1993-08-21 | TX | leaks and spills | UNKNOWN (MCLENNAN COUNTY) | TEXAS UTILITIES FUEL CO | PART 3 NARRATIVE - THE RUPTURE WAS WEST OF TRADINGHOUSE POWER PLANT; AND ABOUT TWO HUNDRED YARDS OUT IN LAKE TRADINGHOUSE. | 952000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
635 | 1993-07-27 | TX | other | UNKNOWN (GALVESTON COUNTY) | AMOCO GAS CO | PLEASE REFERNCE INVESTIGATION CONDUCTED BY DAVID BORN OF YOUR HOUSTON OFFICE. ON THE MORINGING OF JULY 27, 1993 AMOCO GAS COMPANY REMOVED THE CHOCLATE BAYOU TRANSMISSION LINE FROM SERVICE. LATER THAT MORNING, WE REMOVED FROM SERVICE A LOOP LINE BY COLD CUTTING IT AT OUR TEXAS CITY TERMINAL AND REMOVING A FLANGED TEE JOINING THE LINES APPROXIMATELY 2000 FEET SOUTH OF THE TEXAS CITY TERMINAL AND REPLACING IT WITH A FLANGED SPOOL PIECE. A WELD NECK FLANGE WAS WELDED TO THE LINE THAT WOULD BE PUT BACK IN SERVICE AND BLIND FLANGE BOLTED TO THE WELD NECK FLANGE. AT APPROXIMATELY 4:00 M, WE BEGAN PRESSURING THE LINE THROUGH THE BYPASS ON A MAIN LINE BLOCK VALVE 6 MILES AWAY. AT APPROXIMATELY 4:55 PM, THERE WAS AN EXPLOSION AND FIRE. THE LINE PRESSURE WAS APPROXIMATELY 270 PSIG WHEN THE EXPLOSION OCCURRED. A REVIEW OF THE DEBRIS INDICATES THERE WAS AN EXPLOSION INSIDE THE PIPELINE BEING PRESSURED. THE CAUSE OF THE EXPLOSION HAS NOT BEEN DETERMINED AND IS UNDER INVESTIGATION. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
636 | 1993-08-01 | TX | other | UNKNOWN (GREGG COUNTY) | UNITED GAS PIPELINE CO | PART 3 NARRATIVE - THE CAUSE OF THE FAILURE IS UNDER METALLURGICAL INVESTIGATION. A SUPPLEMENTAL REPORT WILL BE SUBMITTED AS SOON AS POSSIBLE. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
637 | 1993-09-09 | LA | maintenance | UNKNOWN (JEFFERSON DAVIS COUNTY) | TENNESSEE GAS PIPELINE CO | PART 3 NARRATIVE - DURING REMOVAL OF WALKER RICE FARM SALES METER, 2 INCH SIDE VALVE 507F - 131 FAILED, CAUSING GAS TO LEAK. IN PULLING VALVE STEM, INCORRECT BOLTS WERE REMOVED CAUSING VALVE TO DISASSEMBLE. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
638 | 1993-09-12 | KS | maintenance | UNKNOWN (OTTAWA COUNTY) | NORTHERN NATURAL GAS CO (ENRON) | HARD SPOT IN PIPE WALL | 260000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
639 | 1993-09-18 | WV | leaks and spills | UNKNOWN (POCAHONTAS COUNTY) | COLUMBIA GAS TRANSMISSION CORP | AN INTERNAL CORROSION INHIBITOR PROGRAM IS SCHEDULED TO BEGIN AT THE BEGINNING OF THE 1993 STORAGE WITHDRAWAL SEASON.INTERNAL CORROSION CAUSED RUPTURE OF STORAGE LINE DRIP, RESULTING IN IGNITION AND THE BURNING OF APPROXIMATELY 5 ACRES OF TREES. | 105000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
640 | 1993-09-18 | WV | leaks and spills | UNKNOWN (COCO KANAWHA COUNTY) | COLUMBIA GAS TRANSMISSION CORP | PART 3 NARRATIVE - BARE PIPE IS LOCATED ON A 65% GRADE ROCK HILLSIDE WITH 1 FOOT OF UNCONSOLIDATED ROCK COVER. THIS RESULTED IN INEFECTIVE CATHODIC PROTECTION AT THE POINT OF FAILURE. | 91000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
641 | 1993-09-23 | AZ | other | UNKNOWN (MARICOPA COUNTY) | BLACK MOUNTAIN GAS CO | BLUE STAKE WAS NOT COMPLETE. CONTRACTOR DUG AFTER DIGGING POTHOLE CONTRACTORASSUMED BLUE STAKE WAS WRONG. BACKHOE HIT LINE. | 5000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
642 | 1993-08-09 | TX | other | UNKNOWN (GALVESTON COUNTY) | VALERO TRANSMISSION CO | THE PIPELINE RUPTURED AT THIS LOCATION. AT THIS TIME, THE CAUSE OF THE RUPTURE IS NOT KNOWN THE RUPTURED PIPE IS BEING ANALYZED BY A METALLURGIST. WHEN THE RESULTS ARE AVAILABLE A COPY WILL BE SENT TO THE TRRC. | 48000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
643 | 1993-08-25 | TX | other | UNKNOWN (KLEBERG COUNTY) | VALERO TRANSMISSION CO | OUR PIPELINE WAS HIT AND PUNCTURED BY A MESQUITE EARTH MOVER WHILE KING RANCH PERSONNEL WERE DIGGING A DRAINAGE DITCH ACROSS THE ROW. VALERO PERSONNEL HAD LOCATED, FLAGGED AND STAKED THE LINE AND HAD MADE DAILY CHECKS UNTIL THE PIPELINE WAS EXPOSED. THE LINE WAS HIT ABOUT 30 FEET FROM WHERE IT WAS EXPOSED AND 10 FEET FROM ONE OF OUR STAKES. | 45000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
644 | 1993-09-04 | CT | other | UNKNOWN ( COUNTY) | IROQUOIS GAS TRANSMISSION SYSTEM | ON SEPTEMBER 4, 1993, AT APPROXIMATELY 17:30 HOURS A SURVEY CREW UNDER CONTRACT TO IROQUOIS TO PERFORM A MARINE HYDROGRAPHIC AND GEOPHYSICAL SURVEY OF OUR OFFSHORE PIPELINE DISCOVERED AN ACOUSTIC DISTURBANCE IN THE WATER COLUMN. UPON FURTHER INVESTIGATION SMALL BUBBLES WERE FOUND RISING TO THE SURFACE OF THE WATER. USING AN UNDERWATER CAMERA MOUNTED ON A REMOTE OPERATED VEHICLE (ROV) IT WAS DETERMINED THAT THE BUBBLES WERE ORIGINATING FROM THE SEA FLOOR IMMEDIATELY ABOVE A BURIED SUBSEA TEE AND VALVE ASSEMBLY IN APPROXIMATELY 70 FEET OF WATER. THIS ASSEMBLY HAD BEEN INSTALLED DURING ORIGINAL CONSTRUCTION OF THE MAINLINE IN 1991 TO CONNECT A FUTURE CUSTOMER. THE MAGNITUDE OF THE LEAKWAS MINIMAL AND IT WAS NOT CONSIDERED TO PRESENT A SAFETY HAZARD TO THE PUBLIC. THE ACTUAL DATE AND TIME THAT THE LEAK ORIGINATED IS UNKNOWN. THE OPERATING PRESSURE OF THE MAINLINE AT POINT AND TIME OF DISCOVERY WAS APPROXIMATELY 800 PSIG. A WORK BOAT AND DIVING CREW WERE MOBILIZED ON SEPTEMBER 26, 1993, AND BEGAN EFFORTS TO UNCOVER THE VALVE ASSEMBLY THE NEXT DAY. AFTER THE ASSEMBLY WAS UNCOVERED IT WAS DETERMINED THAT THE SOURCE OF THE LEAKAGE WAS A GREASE FITTING ON THE DOWNSTREAM SEAT OF A 16" BALL VALVE. THE CAP ON THE GREASE FITTING WAS MISSING THE BALL CHECKS IN THE FITTING WERE ALLOWING A SMALL AMOUNT OF GAS TO ESCAPE. IT IS BELIEVED THAT THE CAP WAS NEVER REPLACED AFTER VALVE WAS SERVICED FOLLOWING FINAL HYDROSTATIC TEST IN 1991. THE LEAK WAS REPAIRED BY REPLACING THE CAP ON THE GREASE FITTING. REPAIR ACTIVITIES WERE COMPLETED AND THE ASSEMBLY BACKFILLED ON OCTOBER 6, 1993. THIS LEAK IS BEING REPORTEDBECAUSE THE COST OF MOBILIZING AND OPERATING THE MARINE VESSEL TO SUPPORT THE REPAIR CREW OF SUBSEA WORK IS EXPECTED TO EXCEED $50,000. THERE WAS NO PROPERTY DAMAGE AND THE COST OF GAS LOST WAS MINIMAL. TELEPHONIC NOTICE WAS GIVENTO THE NRC ON SEPTEMBER 10, 1993, BECAUSE IT WASN'T UNTIL THEN THAT IT WAS DETERMINED THAT THE COST OF INVESTIGATION AND REPAIR COULD EXCEED $50,000. | 91000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
645 | 1993-10-04 | LA | leaks and spills | UNKNOWN ( COUNTY) | COLUMBIA GULF TRANSMISSION CO |  | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
646 | 1993-09-27 | LA | other | UNKNOWN ( COUNTY) | COLUMBIA GULF TRANSMISSION CO |  | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
647 | 1993-10-22 | TN | other | UNKNOWN (PUTNAM COUNTY) | TENNESSEE GAS PIPELINE CO | CONSTRUCTION CREW PERFORMING CONSTRUCTION OF 10' OFFSET LINE STRUCK 4 INCH LATERAL LINE WITH BACKHOE. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
648 | 1993-10-07 | WV | leaks and spills | UNKNOWN (DODDRIDGE COUNTY) | COLUMBIA GAS TRANSMISSION CORP | A 62 FT. SECTION OF PIPELINE SUSTAINED A RUPTURE AS THE RESULT OF SELECTIVE SEAM CORROSION. | 91000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
649 | 1993-10-15 | LA | other | UNKNOWN (CAMERON COUNTY) | COLUMBIA GULF TRANSMISSION CO | PIPE APPEARS TO HAVE BEEN SNAGGED BY OUTSIDE FORCE, EITHER A BARGE OR A TUG, AND PULLED OFF DITCH LINE APPROXIMATELY 12' CAUSING A BUCKLE AND CRACK IN THE PIPE ALONG A FIELD GIRTH WELD RESULTING IN A LEAK. | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
650 | 1993-10-12 | KS | other | UNKNOWN (MEADE COUNTY) | NATURAL GAS PIPELINE CO OF AMERICA | PART 3 NARRATIVE - VENTED 24" NIGHT CAP EXITTED PIPE DUE TO A PRESSURE DIFFERENTIAL OF UNKNOWN SIZE. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
651 | 1993-10-12 | MO | other | UNKNOWN (BUTLER COUNTY) | MISSISSIPPI RIVER TRANSMISSION CORP | DRESSER COUPLING FAILED WHILE REPAIRING A LEAK. PIPE PULLED FROM THE COUPLING. UNEVEN TERRAIN PLUS NORMAL AND AXIAL FORCES CONTRIBUTED TO THE FAILURE.PART 2 OTHER- DRESSER COUPLING. | 192000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
652 | 1993-08-05 | CO | other | UNKNOWN ( COUNTY) | ROCKY MOUNTAIN NATURAL GAS CO INC |  | 930000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
653 | 1993-10-02 | LA | maintenance | UNKNOWN ( COUNTY) | NATURAL GAS PIPELINE CO OF AMERICA | LEAKING FLANGE CONNECTION ON 24" BALLFLANGE CONNECTOR. | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
654 | 1993-10-05 | LA | other | UNKNOWN ( COUNTY) | TENNESSEE GAS PIPELINE CO | LEAK DISCOVERED AFTER BUBBLES, OIL SHEEN DETECTED AT SURFACE. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
655 | 1993-11-16 | MS | other | UNKNOWN (ADAMS COUNTY) | MID - LOUISIANA GAS CO | PART 3 NARRATIVE - HEAVY RAINFALL RUNOFF WASHED OUT SUPPORTING SOIL AROUND 1OR MORE DRESSER COULINGS IN A NORMALLY DRY CREEK BOTTOM RESULTING IN PIPE MOVEMENT AND PULLOUT FROM AN EXPOSED MECHANICAL COUPLING. | 46000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
656 | 1993-10-26 | FL | other | UNKNOWN (DADE COUNTY) | FLORIDA GAS TRANSMISSION CO | PART 3 NARRATIVE - PIPELINE HIT BY CONTRACTOR WITH AN AUGER WHILE INSTALLINGOCCUPANT UTILIZED PROPANE CYLINDERS INSIDE HOUSE FOR SPACE/WATER HEATING PARTGUARD RAIL POSTS ALONG ROADWAY.2 APPARENT CAUSE- D LEAKING PROPANE CYLINDER. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
657 | 1993-10-21 | OK | other | UNKNOWN (LATIMER COUNTY) | ARKLA ENERGY RESOURCES | MECHANICAL FAILURE OF BEARING (IN BLOWER) IGNITED OIL (LUB) STARTING A FIRE IN THE CRANKCASE WHICH RESULTED IN AN EXPLOSION INJURING 2 COMPANY EMPLOYEES. | 40000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
658 | 1993-11-04 | WV | leaks and spills | UNKNOWN (JACKSON COUNTY) | COLUMBIA GAS TRANSMISSION CORP | PART 3 - INTERNAL CORROSION CAUSED RUPTURE OF A PIPELINE DRIP RESERVOIR; THERESULTING FIRE DESTROYED ONE HOUSE TRAILER, DAMAGED OTHER DWELLINGS, AND DESTROYED MULTIPLE VEHICLES. PART A CORROSION #2 OF DRIP RESERVOIR. | 250000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
659 | 1993-11-16 | TX | maintenance | UNKNOWN ( COUNTY) | TRANSCO GAS PIPELINE CORP | CAUSE IS UNKNOWN AT THIS TIME. A COMPLETE EXAMINATION WILL BE PERFORMED TODETERMINE THE REASON FOR THE FAILURE. A SUPPLEMENTAL REPORT WILL BE FILEDUPON COMPLETION OF THE INVESTIGATION. PART 3 NARRATIVE- 20" 900 # ENDCONNECTOR GAVE WAY CAUING THE RUPTURE AND FIRE. THE REASON FOR THE INCIDENTIS UNKNOWN AT THIS TIME. SUPPLEMENTAL REPORT 8/22/94 INDICATES THAT A 20" ENDCONNECTOR FAILED, CAUSING THE PIPELINE TO RUPTURE AND FIRE. INSPECTION OF THECONNECTOR AND 20" PIPE INDICATES THAT THE CONNECTOR DID NOT ADEQUATELY ENGAGE,ALLOWING SLIPPAGE AT THE POINTS OF CONNECTION. | 1500000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
660 | 1993-10-28 | TX | other | UNKNOWN (TARRANT COUNTY) | CORNERSTONE NATURAL GAS CO |  | 52000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
661 | 1993-11-15 | TX | other | UNKNOWN (WHARTON COUNTY) | TRANSCO GAS PIPELINE CORP | RUPTURE OCCURRED IN BODY OF 30" LINE PIPE OUTSIDE OF THE FILLET WELD OF A WELD SADDLE USED TO REINFORCE A 6" BRANCH CONNECTION. MCI"S INVESTIGATIVE REPORT ON THE RUPTURE CONCLUDED THAT THERE WAS NO METALLURGICAL CAUSE OF THE FAILURE. THE SUSPECTED CAUSE OF TH FAILURE IS EXCESSIVE STRESSES DUE TO MOVEMENT OF THE 30" PIPELINE BY SOIL SUBSIDENCE. | 229000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
662 | 1993-11-17 | TX | other | UNKNOWN ( COUNTY) | ANR PIPELINE CO | PIPELINE WAS STRUCK BY LEGS OF JACKUP RIG THAT WAS DRAGGED OVER THE 36" LINE. | 2500000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
663 | 1993-12-20 | NE | other | UNKNOWN (GOSPER COUNTY) | K N ENERGY INC(KANSAS NEBRASKA GAS CO) | THERE WAS A PIPELINE MARKER WITHIN 100 FT. OF BREAK. THE INCIENT OCCURRED WHEN THE BUCKET OF A FRONTEND LOADER ACCIDENTLY HOOKED THE LINE AS A FARMER CLEARED SNOW FROM AN AREA IN PREPARATION TO GRINDING HAY. THE TOP OF GROUND LINETRAVERSES THE FARMERS LAND, WITH THE EXACT LOCATION WELL MARKED WITH PERMANENT PIPELINE MARKERS. THE LOCATION HAS BEEN WELL KNOWN BY THE FARMER FOR MANY YEARS. THE PRIME FACTOR IN THIS INCIDENT WAS THE SNOW COVER. THE ACTUAL BREAKOCCURRED APPROXIMATELY 100 FEET FROM THE POINT WHERE CONTACT WAS MADE BY THEPIECE OF MACHINERY. NO ONE WAS IN THE AREA OF THE BREAK, THERE WAS NO FIRE AND THERE WERE NO INJURIES. REPAIRS WERE MADE TO THE PIELINE AND THE LINE WAS PLACEDF BACK INTO SERVICE AT APPROXIMATELY 12:00, NOON. GAS SERVICE WAS RESTORED TO ALL CUSTOMERS WITHOUT FURTHER INCIDENT. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
664 | 1993-12-20 | WI | leaks and spills | UNKNOWN (ASHLAND COUNTY) | NORTHERN NATURAL GAS CO (ENRON) |  | 750000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
665 | 1993-11-23 | IN | other | UNKNOWN (HENRY COUNTY) | ANR PIPELINE CO | PIPELINE WAS STRUCK BY A TRENCHING MACHINE USED TOLAY DRAINAGE TILE. | 58000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
666 | 1994-01-15 | LA | other | UNKNOWN ( COUNTY) | TENNESSEE GAS PIPELINE CO | LEAK DISCOVERED AFTER BUBBLES, OIL SHEEN DETECTED AT SURFACE. PARTT 2 D- UNDER INVESTIGATION POSSIBLE PINHOLE LEAK. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
667 | 1993-12-22 | OK | maintenance | UNKNOWN (LOGAN COUNTY) | WILLIAMS NATURAL GAS CO | AN ACETYLENE GIRTH WELD FAILED COMPLETELY. THE BASE METAL REMAINED INTACT THE FRACTURE WAS ENTIRELY IN THE WELD METAL AND OCCURRED SYMMETRICALLY BETWEEN THE ADJACENT JOINTS . | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
668 | 1993-12-16 | PA | other | UNKNOWN (TIOGA COUNTY) | CNG TRANSMISSION CORP | SUPPLY LINE TO ESD POWER OPERATOR ON 8" BLOWOFF FROZE OFF FROM MOISTURE IN LINERESULTING IN VALVE OPENING AND DSICHARGING GAS TO ATMOSPHERE.GAS WAS BEING DISCHARGED THROUGH BLOWOFF DESIGNED TO DISCHARGE GAS SAFELY. | 155000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
669 | 1993-12-27 | KS | other | UNKNOWN ( COUNTY) | NORTHERN NATURAL GAS CO (ENRON) | APPARENTLY A FOREIGN OBJECT DAMAGED THE DRIVER TURBINE. VIBRATION RESULTED, CAUSING TURBINE DESTRUCTION AND A FIRE. | 750000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
670 | 1994-01-14 | MS | leaks and spills | UNKNOWN ( COUNTY) | SOUTHERN NATURAL GAS CO | STRESS CORROSION CRACKING IN THE BODY OF THE PIPE IN CONJUNCTION WITH CORROSION FATIGUE PROPAGATED INTO A FAILURE AND PIPELINE RUPTURE WITH NATURAL GAS IGNITION. PART A - CORROSION PRELIMINARY BATTELLE INVESTIGATION INDICATES LOW PH STRESS CORROSION CRACKING IN ASSOCIATION WITH CORROSION FATIGUE AT INTITALPOINT OF FAILURE. | 1187500 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
671 | 1993-12-02 | KS | other | UNKNOWN (BARTON COUNTY) | K N ENERGY INC(KANSAS NEBRASKA GAS CO) | A 1" DISCHARGE LINE ON AN INLINE DRIP BROKE OFF AS AN APPARENT FREEZE BROKE LOOSE. THE FIELDMAN WAS STRUCK ON THE HEAD BY THE PIECE OF 1" PIPE CAUSING ANINJURY THAT REQUIRED SEVERAL DAYS INT HE HOSPITAL. THERE WAS NO FIRE OR FURTHER DAMAGE. THE FIELDMAN OPENED THE VALVE ON THE DRIP TOO MUCH TO CLEAR AN APPARENT FREEZE. THIS WAS ROUTINE OPERATION TO CLEAR LIQUID FROM THE DRIP. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
672 | 1993-11-22 | CA | other | UNKNOWN (SANTA CLARA COUNTY) | PACIFIC GAS & ELECTRIC CO | A 20" LINE WAS CUT & CAPPED DOWNSTREAM OF A DRESS COUPLING. A 7' SECTION OF PIPE & THE WELDED CAP WAS BLOWN OUT OF THE DRESSER COUPLING WHEN THE LINE WASPRESSURIZED TO 190 PSIG. A COMPANY EMPLOYEE WAS INJURED. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
673 | 1993-11-24 | MS | other | UNKNOWN (OKTIBBEHA COUNTY) | TEXAS EASTERN GAS PIPELINE CO | EMPLOYEE D.L. BURROUGHS WAS APPARENTLY STRUCK BY A PIPELINE VALVE HANDWHEEL WHILE THE PIPELINE CREW WAS LAUNCHING A CLEANING PIG. TEXAS EASTERN BELIEVES THAT THE GAS DRIVEN MOTOR OPERATOR FOR THE VALVE ENGAGED AND THE UNSECURED HANDWHEEL STRUCK THE EMPLOYEE. ALTHOUGH PERSONNEL WERE IN THE IMMEDIATE VICINITY OF THE ACCIDENT, THERE WERE NO KNOWN EYE WITNESSES. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
674 | 1994-02-12 | LA | leaks and spills | UNKNOWN ( COUNTY) | TENNESSEE GAS PIPELINE CO | PART 3 - DURING PIGGING OPERATIONS, LEAK DISCOVERED BY HELICOPTER CREW (BUBBLES AT SURFACE). | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
675 | 1994-02-22 | ID | leaks and spills | UNKNOWN (ELMORE COUNTY) | NORTHWEST PIPELINE CORP | THE INCIDENT OCCURRED AT 1645 HOURS ON FEBRUARY 22, 1994 AT MILEPOST 0.1717 ON NORTHWEST'S RENO 16 INCH LINE. THE SITE IS IN A 21 MILE VALVE SECTION THATCONSISTS OF CULTIVATED LAND AND DESERT. THE LINE IS NOT LOOPED IN THIS SECTION AND NORTHWEST INTERRUPTED SERVICE AT THE FLYING H FARMS DELIVERY POINT WHERE INTERMOUNTAIN GAS, A LOCAL DISTRIBUTION COMPANY, SERVES A RESIDENTIAL AREAOF MOUNTAIN HOME AIR FORCE BASE, WHICH HAS A POPULATION OF APPROXIMATELY 1000 PEOPLE. THE INCIDENT APPEARS TO HAVE BEEN THE RESULT OF THE PIPE COATING (COAL TAR ENAMEL WITH FELT OUTER WRAP) BEING DISBONDED AND SHIELDING THE PIPE FROM CATHODIC PROTECTION IN A THREE FOOT SECTION. IN THE FAILURE INITIATION AREA, EXTERNAL CORROSION HAD REDUCED THE PIPE WALL THICKNESS TO THE POINT OF COMPROMISING THE PIPE STRENGTH. THE ERW PIPE SEAM WAS NOT AFFECTED AND THE PIPEAND COATING ADJACENT TO THE CORRODED AREA WAS IN GOOD CONDITION. APPROXIMATELY 60 FEET OF PIPE WAS REPLACED. THERE WERE NO INJURIES OR FIRE ASSOCIATED WITH THE RUPTURE AND THE LINE WAS RESTORED TO SERVICE BY 0750 HOURS ON FEBRUARY23, 1994. FULL SERVICE WAS RESUMED AT THE FLYING H FARMS DELIVERY POINT BY 1030 HOURS THE SAME DAY. PART3 - DISBONDED PIPE COATING SHIELDED THE PIPE FROMCATHODIC PROTECTION. | 170200 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
676 | 1994-01-19 | MD | other | UNKNOWN (PRINCE GEORGES COUNTY) | WASHINGTON GAS LIGHT CO | ON THE EVENING OF JANUARY 18, 1994, THE TEMPERATURE DROPPED TO SINGLE DIGITSOF NINE DEGREES AT 6:00 P.M. AND CONTINUED TO DROP TO A LOW OF FOUR BELOW ZERO BY 6:00 A.M. ON THE MORNING OF JANUARY 19, 1994. THIS EXTREME WEATHER CONDITION CREATED AND EXCESS DEMAND AND REDUCED PRESSURES ON THE FAR END OF WASHINGTON GAS TRANSMISSION SYSTEM. WHEN PRESSURES ON BOWIE'S DISTRIBUTION REGULATOR SYSTEM REACHED A LOW OPERATING LEVEL ON THE MORNING OF JANUARY 19, 1994, SELECTED SECTIONS WERE SHUT OFF (APPROXIMATELY 1,700 METERS) IN ORDER TO PREVENT THE PRESSURE LOSS TO ANOTHER 10,000 METERS THAT COULD HAVE POSSIBLY BEEN AFFECTED. THIS WAS DONE AT THE EXTREME END OF THE TRANSMISSION SYSTEM AND SERVICE WAS RESTORED TO ALL OUTAGES AT THE FIRST SIGN OF A PRESSURE INCREASE ON THE TRANSMISSION SYSTEM. ADDITIONALLY, 577 METERS WERE VALVED OFF IN WALDORF, MARYLAND, SOME 15 MILES SOUTH OF BOWIE. AT THE TIME OF TELEPHONIC REPORTING, THE CAUSE FOR THIS PRESSURE PROBLEM WAS UNKNOWN. FURTHER INVESTIGATION UNCOVERED A FROZEN DISTRIBUTION REGULATOR THAT WAS RELATED TO WEATHER CONDITIONS AND NOT THE BOWIE PRESSURE PROBLEM. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
677 | 1994-01-13 | CA | other | UNKNOWN (SAN JOAQUIN COUNTY) | UNION ISLAND PIPELINE CO | THE PUMP SEAL ON THE ODORANT INJECTION SYSTEM PUMP FAILED CAUSING THE RELEASETHE PHILADELPHIA FIRE DEPATMENT HAS INVESTIGATED THIS INCIDENT WHICH WAS INIT OF APPROXIMATELY ONE QUART OF CAPTAN 50 ODORANT. THE MERCAPTAN ODORANT TRAVEIALLY BELIEVED TO BE A HOUSE FIRE FROM AN INTERNAL SOURCE ON JANUARY 25, 1994LED DOWNWIND APPROXIMATELY 1.3 MILES TO THE DELTA ISLAND ELEMENTARY SCHOOL. T. THE RESULTS OF THE PHILDELPHIA FIRE DEPARTMENT INVESTIGATION, OF WHICH THEHE SCHOOL STAFF DETECTED THE ODDORANT INSIDE ONE OF THE SCHOOL BUILDINGS, ANDSPECIFIC HAVE NOT BEEN RELEASED TO THE PHILADELPHIA GAS WORKS, INDICATES THAT SUSPECTING A GAS LEAK, EVACUATED THEIR FIRST THROUGH FOURTH GRADES TO A NEAR THE CAUSE OF THE FIRE WAS DUE TO THE MIGRATION OF NATURAL GS INTO THE BASEMEBY BUILDING. ONE TEACHER REPORTED SHORTNESS OF BREATH AND WAS SENT BY AMBULANNT OF 2452 S. PHILIP STREET WHICH WS IGNITED BY THE HEATER IN THAT BASEMENT.CE TO A HOSPITAL. SHE WAS EVALUATED AND RELEASED THAT DAY. THE SCHOOL CHILDRETHE PHILADELPHIA GAS WORKS DISPUTES THESE FINDINGS AT THIS TIME. INITIAL INVEN RETURNED TO THIER CLASSROOMS WITHIN TWO HOURS.STIGATION PON ARIVAL FOUND NO INDICATION OF GAS MIGRATION INTO THE RESIDENCES AT 2450, 2452, 2454. AT NO TIME WERE READINGS LEL FOUND INSIDE DURING THE INVESTIGATION AND REPAIR OF THE 6" GAS MAIN. THE RESULTS OF THE INVESTIGATION WERE GIVEN BY PHONE TO THE PHILADELPHIA GAS WORKS ON JANUARY 2, 1994 AT 1330 HOURS TELEPHONIC NOTICE WAS MADE TO THE NATIONAL RESPONSE CENTER, SERIAL #219022 ON JANUARY 27, 1994. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
678 | 1994-01-25 | AL | maintenance | UNKNOWN (MOBILE COUNTY) | MOBILE GAS SERVICE CORP | A LEAK OCCURRED WHEN AN END CAP BLEW OFF THE END OF AN 18" STEEL PIPE AT RANGELINE ROAD AND HAMILTON BOULEVARD. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
679 | 1993-12-27 | TX | other | UNKNOWN (PARMER COUNTY) | WESTAR TRANSMISSION CO | LINE CUT BY FARMER WHILE DEEP PLOWING. | 45430 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
680 | 1994-01-02 | TX | leaks and spills | UNKNOWN (COTTLE COUNTY) | LONE STAR GAS CO | A CORROSION LEAK ON 4" DRESSER COUPLING CAUSED THE LEAK. THE LEAK WAS ADJACENT TO STATE HWY. 83. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
681 | 1994-01-24 | TX | leaks and spills | UNKNOWN (GALVESTON AREA COUNTY) | BLUE DOLPHIN PIPELINE CO | PINHOLE GAS LEAK CAUSED BY APPARENT LOCALIZED INTERNAL CORROSION. LEAK WAS REPAIRED BY INSTALLATION OF 1500 PSIG WP BOLTED PIPELINE CLAMP. PART A - 250 #ZINC ANODES WERE INSTALLED ON 1/4 MILE SPACING DURING THE INITIAL CONSTRUCTION IN 1965. IMPRESSED CURRENT IS SUPPLIED TO BOTH THE OFFSHORE AND ONSHORE ENDS OF THE PIPELINE. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
682 | 1994-01-20 | LA | other | UNKNOWN (ACADIA COUNTY) | COLUMBIA GULF TRANSMISSION CO | IN PREPARATION FOR A PIGGING OPERATION ON LINE 200, COLUMBIA EMPLOYEES WERE PUMPING A CLEANING SOLUTION INTO THE PIPELINE. UNANTICIPATED ACTUATION OF A LIQUID RELIEF VALVE LOCATED ON THE PORTABLE TRIPLEX PUMPING UNIT RESULTED IN THE RELEASE AND IGNITION OF NATURAL GAS. A 5,460 GALLON TANKER, TRACTOR AND PORTABLE TRIPLEX PUMPING UNIT WERE LOCATED ADJACENT TO THE LINE 200 BLOW DOWN STACK, THE BLOW DOWN STACK AND PUMP WERE CONNECTED BY A TWO-INCH 5000 PSIG ARMORED HOSE. PRELIMINARY INVESTIGATION CONCLUDES THAT THE PORTABLE PUMPING UNIT'S LIQUID OVERPRESSURE RELIEF VALVE ACTUATED, RESULTING IN AN INITIAL RELEASEOF CLEANING SOLUTION AND SUBSEQUENT RELEASE OF NATURAL GAS. THE GAS IGNITED,RESULTING IN THE DESTRUCTION OF THE TANKER, TRACTOR AND PORTABLE PUMPING UNIT AND INJURY OF THREE EMPLOYEES. TWO INJURED EMPLOYEES SUFFERED FIRST DEGREE BURNS TO THE FACE AND THE THIRD SUFFERED FIRST AND SECOND DEGREE BURNS TO THEHANDS. ALL INJURED EMPLOYEES RETURNED TO WORK IMMEDIATELY AFTER EMERGENCY TREATMENT. THE IGNITION SOURCE IS SPECULATIVE AND REMAINS UNKNOWN. THE GAS BURNED FOR 1 HOUR AND 10 MINUTES UNTIL IT COULD BE SHUT OFF. THE SUBJECT PIPELINEWAS RETURNED TO SERVICE 45 MINUTES AFTER EXTINGUISHING THE FIRE. THERE WAS NODAMAGE TO THE UNDERGROUND STRUCTURE. SUBSEQUENT ACTION INCLUDED REPLACEMENT OF THE ABOVE GROUND CROSSOVER PIPING AS A PRECAUTIONARY MEASURE. | 331000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
683 | 1994-02-01 | MD | other | UNKNOWN (MONTGOMERY COUNTY) | TRANSCO GAS PIPELINE CORP | PART 3- THIRD PARTY CONTRACTOR'S BACKHOE PUNCTURED THE PIPELINE WHILE PERFORMING WORK ADJACENT TO THE R.O.W. | 70000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
684 | 1994-02-20 | LA | leaks and spills | UNKNOWN ( COUNTY) | TRANSCO GAS PIPELINE CORP |  | 60000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
685 | 1994-03-08 | LA | maintenance | UNKNOWN (TERREBONNE COUNTY) | TRANSCO GAS PIPELINE CORP | LACK OF FUSION IN LONGITUDINAL SEAM | 120000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
686 | 1994-03-05 | LA | leaks and spills | UNKNOWN ( COUNTY) | TENNESSEE GAS PIPELINE CO |  | 65000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
687 | 1994-01-21 | MS | maintenance | UNKNOWN (WINSTON COUNTY) | SOUTHERN NATURAL GAS CO | GIRTH WELD FAILURE: X-RAYS MADE AFTER INCIDENT REVEALED SEVERAL "BURNS THROUGH" AND THE LACK OF WELD MATERIAL PENETRATION OVER 50% OF THE JOINT CIRCUMFERENCE. THE X-RAYS SHOWED THAT THE REMAINDER OF THE GIRTH WELD WAS SATISFACTORY. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
688 | 1994-01-26 | TX | other | UNKNOWN (COLLINGSWORTH COUNTY) | LONE STAR GAS CO |  | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
689 | 1994-03-18 | LA | leaks and spills | UNKNOWN ( COUNTY) | TENNESSEE GAS PIPELINE CO | INTERNAL CORROSION LEAK DISCOVERED BY CONOCO PERSONNEL LARGER REPAIR CLAMP INSTALLED ENCOMPASS EARLIER LEAKS (2-12-94) ULTRASONICS REVEALED NO FURTHER LOCALIZED PITTING. | 125000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
690 | 1994-02-27 | MI | other | UNKNOWN (MECOSTA COUNTY) | ANR PIPELINE CO | THE PIPE RUPTURE WAS CAUSED BY A CRACK AT THE TOE OF A WELD JOINTING A WELDOLET TO THE BODY OF THE PIPE. | 1500000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
691 | 1994-03-15 | MI | other | UNKNOWN ( COUNTY) | ANR PIPELINE CO |  | 57000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
692 | 1994-03-30 | LA | other | UNKNOWN ( COUNTY) | TENNESSEE GAS PIPELINE CO |  | 10000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
693 | 1994-03-17 | LA | maintenance | UNKNOWN ( COUNTY) | TENNESSEE GAS PIPELINE CO | LEAK DISCOVERED BY CONOCO. GAS BOIL REPORTED IN EC48. SLIGHT BROKEN SHEEN ONWATER. | 20000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
694 | 1994-04-07 | TX | other | UNKNOWN (VICTORIA COUNTY) | GULF COAST NATURAL GAS CO | CAUSE OF RUPTURE IS CURRENTLY UNKNOWN, TEST ARE BEING CONDUCTED ON FAILEDSECTION OF 14" PIPE REMOVED AFTER INCIDENT TO DETERMINE CAUSE. | 66278 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
695 | 1994-03-22 | MS | other | UNKNOWN (TUNICA COUNTY) | TEXAS GAS TRANSMISSION CORP | ON MARCH 22, 1994, AT APPROXIMATELY 4:25 P.M. CST, A PROPETY OWNER NOTIFIEDTEXAS GAS OF AN APPARENT RUPTURE ON HIS LAND IN A RURAL AREA NEAR THE TOWN OFTUNICA, MISSISSIPPI. DISTRICT PERSONNEL WERE DISPATCHED IMMEDIATELY TO THERUPTURE SITE AS WELL AS TO BLOCK VALVE LOCATIONS UPSTREAM AND DOWNSTREAM OFTHE RUPTURE SITE. THE LINE WAS THEN ISOLATED AND BLOWN DOWN WITH NO RESULTINGFIRE OR PERSONAL INJURY. A METALLURGICAL REVIEW IS CONTINUING AT THIS TIME;HOWEVER, THE PRELIMINARY INVESTIGATION INDICATES THE FAILURE ORIGINATED IN ADENT CONTAINING A GOUGE. GROUND COVER AT THE POINT OF FAILURE WASAPPROXIMATELY FOUR FEET (4'). ALTHOUGH THE FAILURE OCCURRED ON AGRICULTURALLAND, THERE WAS NO EVIDENCE OF RECENT TILLING OR EXCAVATING ACTIVITIES IN THEAREA OF THE FAILURE. THE AGE OF THE DENT AND GOUGE HAVE NOT BEEN DETERMINED.IT IS POSSIBLE THEY MAY HAVE OCCURRED DURING ORIGINAL CONSTRUCTION (1946).REPLACEMENT OF THE FAILED SECTION IS CURRENTLY UNDERWAY; HOWEVER, EXCESSIVERAINFALL HAS PREVENTED COMPLETION. IT IS ANTICIPATED THE 18" NO.2 LINE WILL BERETURNED TO SERVICE IN THE NEAR FUTURE. | 125500 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
696 | 1994-03-19 | LA | leaks and spills | UNKNOWN ( COUNTY) | NATURAL GAS PIPELINE CO OF AMERICA |  | 150000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
697 | 1994-03-23 | NJ | other | UNKNOWN (MIDDLESEX COUNTY) | TEXAS EASTERN GAS PIPELINE CO | THE CAUSE OF THE INCIDENT IS UNDER INVESTIGATION BY THE NTSB.PIPELINE MARKERIS PRESENT ON ROAD AND NEAR PLANT GATE ENTRANCE TO THE ASPHALT PLANT WHERE THEINCIDENT OCCURRED. CASING VENT MARKERS ARE ALSO PRESENT NEAR WHERE THEPIPELINE EXITS THE ASPHALT PLANT.THE COMPANY IS UNABLE TO ESTIMATE AT THISTIME THE EXTENT OF THIRD PARTY PROPERTY DAMAGES ASSOCIATED WITH THIS INCIDENT.SUPPLEMENTAL REPORT 5/2/1995 INDICATES THAT NTSB DETERMINED THAT THE PROBABLECAUSE OF THE INCIDENT WAS MECHANICAL DAMAGE TO THE EXTERIOR SURFACE OF THEPIPELINE. AN ATTACHMENT INDICATES THAT THIRD PARTY PROPERTY DAMAGES ASSOCIATEDWITH THIS INCIDENT ARE INCOMPLETE AND UNSUBSTANTIATED. THE NTSB ESTIMATEDPROPERTY DAMAGES OF $25 MILLION. THERE IS A LETTER ATTACHED TO REPORT THATEXPLAINS IN DETAIL THE DIFFICULTIES IN ESTIMATING THE THIRD PARTY PROPERTYDAMAGE. SUPPLEMENTAL REPORT 5/2/1995 INDICATES A CHANGE IN PROPERTY DAMAGEFROM 1,750,000 TO 25,000,000. THIRD PARTY PROPERTY DAMAGES ASSOCIATED WITHTHIS INCIDENT ARE INCOMPLETE AND UNSUBSTANTIATED. THE NTSB ESTIMATED PROPERTYDAMAGES OF 25 MILLION. NTSB DETERMINED THAT THE PROBABLE CAUSE OF THEINCIDENT WAS MECHANICAL DAMAGE TO THE EXTERIOR SURFACE OF THE PIPELINE. | 25000000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
698 | 1994-04-17 | LA | other | UNKNOWN (CONCORDIA COUNTY) | MID - LOUISIANA GAS CO | STRONG RIVER CURRENT CAUSED SCOURING TO OCCUR WHICH EXPOSED THE PIPE NEAR THEEDGE OF A SAND BAR CAUSING A SECTION TO BECOME SUSPENDED ABOVE THE CHANNELBOTTOM. THE FORCE APPLIED BY THE CURRENT CAUSED THE PIPE TO SWING OR VIBRATEAND EVENTUALLY BREAK AT GIRTH WELD. | 165000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
699 | 1994-04-17 | LA | other | UNKNOWN (WEST FELICIANA COUNTY) | TRANSCO GAS PIPELINE CORP | RUPTURED OCCURRED IN A 30" MISSISSIPPI RIVER CROSSING WHILE THE RIVER WAS ABOVE FLOOD STAGE. BECAUSE OF THE RIVER CURRENTS AND THE LOCATION OF RUPTURE, THE PRIMARY CAUSE OF THE INCIDENT CANNOT BE DETERMINED. TRANSCO WILL NOT ATTEMPT ANY REPAIR OF THE 30" CROSSING. THE 30" CROSSING WILL BE ABANDONED IN PLACE AND REPLACED WITH A NEW DIRECTIONAL DRILLED CROSSING, THE COST OF WHICH IS INCLUDED IN THE ESTIMATED COST OF DAMAGE/LOSS/REPAIR. | 5000000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
700 | 1994-04-26 | OR | maintenance | UNKNOWN ( COUNTY) | PACIFIC GAS TRANSMISSION CO | A SMALL CRACK DEVELOPED IN A FIELD WELD BETWEEN TWO DIFFERENT SPECIFICATIONSOF PIPE INSTALLED IN 1992 WHICH RESULTED IN A MINOR GAS LEAK. INCIDENT IS REPORTABLE ONLY BECAUSE COST OF REPAIRS, INCLUDING COST OF GAS BLOWN TO ATMOSPHERE, EXCEEDED $50,000. CAUSE OF FAILURE IS UNDER INVESTIGATION. | 150000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
701 | 1994-03-17 | LA | leaks and spills | UNKNOWN (STINGRAY COUNTY) | TRUNKLINE GAS CO |  | 95000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
702 | 1994-03-23 | LA | leaks and spills | UNKNOWN ( COUNTY) | TENNESSEE GAS PIPELINE CO | 1/4" PIN HOLE DISCOVERED AT BOTTOM OF 26" O.D. PIPELINE DRIP. | 75000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
703 | 1994-05-02 | TX | other | UNKNOWN (GALVESTON COUNTY) | FLORIDA GAS TRANSMISSION CO | PIPELINE DAMAGED BY BOAT TRAFFIC IN A SHALLOW, INLAND NAVIGABLE WATERWAY. THE PIPELINE RUPTURE RESULTED FROM DAMAGE CAUSED BY BOAT TRAFFIC IN A SHALLOW,INLAND WATERWAY. | 520000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
704 | 1994-05-06 | LA | other | UNKNOWN (ACADIA COUNTY) | TRANSCO GAS PIPELINE CORP | OIL TRANSPORT BARGE BEING PUSHED BY TUG BOAT RAN INTO THE 12" PIPELINE ON THE EAST SIDE OF THE BAYOU. (BAYOU DE CANNES). PART B- PERMANENT PIPELINE CROSSING MARKERS. | 888205 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
705 | 1994-05-27 | LA | leaks and spills | UNKNOWN ( COUNTY) | TENNESSEE GAS PIPELINE CO | LEAK DISCOVERED BY HELICOPTER CREW (BUBBLES AT SURFACE). | 52000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
706 | 1994-05-25 | LA | leaks and spills | UNKNOWN ( COUNTY) | COLUMBIA GULF TRANSMISSION CO | TWO SMALL INTERNAL CORROSION PIN HOLE LEAKS (18'APART) WERE REPAIRED WITH DASPIT CLAMPS. PART 1 B). X=1885229.89 Y=105490.26 | 150000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
707 | 1994-04-18 | IA | leaks and spills | UNKNOWN (GUTHRIE COUNTY) | NORTHERN NATURAL GAS CO (ENRON) | SHORT COATED REPLACEMENT SECTION IN A BARE, DRESSER COUPLED LINE. | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
708 | 1994-04-14 | KS | other | UNKNOWN (FORD COUNTY) | NATURAL GAS PIPELINE CO OF AMERICA | UNDER INVESTIGATION. PIPE SECTION HAS BEEN ISOLATED BUT NOT YET REMOVED FROMITS CASING. | 138600 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
709 | 1994-04-12 | LA | leaks and spills | UNKNOWN ( COUNTY) | NATURAL GAS PIPELINE CO OF AMERICA | PIPE SEGMENT ABANDONED. NO FLOW IN THE AFFECTED SEGMENT. | 400000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
710 | 1994-04-20 | LA | other | UNKNOWN ( COUNTY) | TENNESSEE GAS PIPELINE CO | WORK BOAT DROPPED ANCHOR. LEAK DISCOVERED BY TEXACO PERSONNEL. WORK BOAT ANCHOR SNAGGED T.G.P. 12" PIPELINE IN SOUTH PASS BLK 54. | 400000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
711 | 1994-06-19 | LA | leaks and spills | UNKNOWN ( COUNTY) | CHEVRON PIPELINE CO |  | 69000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
712 | 1994-06-23 | LA | other | UNKNOWN ( COUNTY) | TENNESSEE GAS PIPELINE CO | PIPELINE RUPTURED ON 20 IN. 526A-100 LINE IN MOUTH OF GRAND BAYOU, LOUISIANA.APPROXIMATELY 200 FEET OF PIPELINE HAD BECOME EXPOSED DUE TO THE WASHOUT & ERROSION. | 650000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
713 | 1994-06-22 | OK | leaks and spills | UNKNOWN (HUGHES COUNTY) | TRANSOK INC | ON JUNE 22, 1994 AT 17:55 TRANSOK'S GREASY CREEK PROCESSING PLANT RECEIVED SEVERAL CALLS FROM PRIVATE CITIZENS ABOUT A LOUD NOISE IN THE STORAGE FIELD. AT THE SAME TIME TELEMETRY WAS SHOWING A RAPID PRESSURE DROP. MILTON JOHNSON (OPERATOR) NOTIFIED RICK RAMSEY (FIELD OPERATOR) AND GAS CONTROL CENTER OF THELEAK IN THE SOUTH END OF THE STORAGE FIELD. RICK RAMSEY PROCEEDED TO THE LEAK AREA FOUND THE LEAK TO BE ON THE 12" LATERAL AND ISOLATED THE WELLS ATTACHED TO THIS LINE AND MAINLINE VALVE. SITUATION WAS UNDER CONTROL AT 18:33. THE LEAK OCCURRED IN HUGHES COUNTY SW 1/4 OF SE 1/4 SECTION 36 TOWNSHIP 8N RANGE 11E. GAS LOSS WAS FIGURED AT 20,271MCF. THE AREA OF THE LEAK IS IN A CLASS 1 LOCATION WITH THE CLOSEST OCCUPIED RESIDENCE APPROX. 400 FEET AWAY. | 63500 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
714 | 1994-06-30 | VA | leaks and spills | UNKNOWN (CULPEPER COUNTY) | TRANSCO GAS PIPELINE CORP |  | 250000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
715 | 1994-07-21 | LA | leaks and spills | UNKNOWN ( COUNTY) | CHEVRON PIPELINE CO |  | 75000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
716 | 1994-08-10 | LA | leaks and spills | UNKNOWN ( COUNTY) | NATURAL GAS PIPELINE CO OF AMERICA | PENDING INVESTIGATION. THE AFFECTED PIPE SECTION IS ISOLATED. REPAIRS ANDFURTHER INVESTIGATION ARE NOT COMPLETE. SUPPLEMENTAL REPORT 3/21/95 INDICATESTHAT XRAY CONFIRMED INTERNAL CORROSION. LOCALIZED INTERNAL PITTING SHOWN BYXRAY. INSTALLED LEAK CLAMP. | 226012 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
717 | 1994-08-10 | LA | leaks and spills | UNKNOWN (TERREBONNE COUNTY) | TRANSCO GAS PIPELINE CORP | FAILURE INITIATED IN THE LONG SEAM AS A RESULT OF INTERNAL PITTING CORROSIONON BOTH SIDES AND IN THE LONG SEAM. | 500000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
718 | 1994-08-21 | LA | other | UNKNOWN ( COUNTY) | COLUMBIA GULF TRANSMISSION CO | SPECULATION INDICATES THAT A 20' SEGMENT OF 6" PIPE AND VALVE HAD BEEN SEVERED BY A SURFACE VESSEL FISHING NET OR ANCHOR IN ROUGH SEAS. | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
719 | 1994-08-16 | LA | leaks and spills | UNKNOWN ( COUNTY) | COLUMBIA GULF TRANSMISSION CO | ONE SMALL INTERNAL CORROSION PIN HOLE LEAK WAS REPAIRED WITH A LEAK CLAMP. AT 7:40 AM, AUGUST 14, 1994, A BUBBLE LEAK WAS REPORTED BY A HELICOPTER TRANSPORT SERVICE DISPATCHER. WITHIN HOURS, SEVERAL PIPELINES WERE SHUT-IN. FURTHERINVESTIGATION AND EVALUATION RESULTED IN A DETERMINATION THAT THE LEAK WAS ON A COLUUMBIA GULF PIPELINE. AN ESTIMATED REPAIR COST EXCEEDING $50,000 WAS THE INCIDENT REPORT TRIGGER MECHANISM RESULTING IN THE AUGUST 16, 1994 NATIONAL RESPONSE CENTER TELEPHONE REPORT. ONE SMALL INTERNAL CORROSION PIN HOLE LEAK WAS REPAIRED WITH A PIPELINE CLAMP ON AUGUST 27, 1994. MINERAL MANAGEMENT SERVICE WAS DULY NOTIFIED AND THERE WERE NO ENVIRONMENTAL UPSETS. THE PIPELINEIS BACK IN SERVICE. | 150000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
720 | 1994-08-05 | TX | other | UNKNOWN ( COUNTY) | TRUNKLINE GAS CO | LEAKING FLANGE DISCOVERED ON 6" BALL VALVE ON 12" FUTURES TAP OF TGC 300-1 (30") LINE. FUTURES WAS BLOWN DOWN, 6" VALVE REMOVED AND NEW 6" BLIND FLANGE W/BLEEDER VALVE INSTALLED. | 59000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
721 | 1994-08-20 | NM | other | UNKNOWN (VALENCIA COUNTY) | TRANSWESTERN PIPELINE CO | DIFFERENTIAL SETTLING OF PIPELINE AND ABOVE GROUND APPURTENCES CAUSED UNDUE STRESS OF BELOW GROUND BRANCH CONNECTION LEADING TO FAILURE OF THE WELDED BRAN | 2200000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
722 | 1994-05-30 | IA | leaks and spills | UNKNOWN (WRIGHT COUNTY) | NORTHERN NATURAL GAS CO (ENRON) | HOT SPOT PROTECTED WITH ANODES | 70000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
723 | 1994-08-01 | TX | leaks and spills | UNKNOWN (CLAY COUNTY) | SAGINAW PIPELINE COMPANY, L.C. | SUSPECTED LEAK REPORTED BY AERIAL FLYOVER | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
724 | 1994-08-12 | TX | leaks and spills | UNKNOWN (CLAY COUNTY) | SAGINAW PIPELINE COMPANY, L.C. | AERIAL FLYOVER REPORTED SUSPECTED LEAK. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
725 | 1994-09-25 | NM | maintenance | UNKNOWN (BERNALILLO COUNTY) | GAS CO OF NEW MEXICO | CONSTRUCTION EMPLOYEES MAKING TAP ON PIPELINE, VAPORS FROM THE PIPELINE FILLELINE WAS BEING RETIRED. ON 09/25/94 FOUTZ 7 BURSUM (CONTRACTOR WORKING FOR GCD THE BELLHOLE. WHEN WELDERS STARTED WELDING, THE VAPORS IGNITED IN FLASH FIRNM) WAS RETIRING A 16" TRANSMISSION MAIN AT COORS BY-PASS & 7 BAR LOOP ROAD.AT APPROXIMATELY 0900 HRS. MR. LEROY MARTINEZ OF FOUTZ & BURSUM WAS HOLDING A STEEL PLATE, TO BE WELDED, OVER THE END OF THE 16" LINE. LEAKING GAS IGNITED CAUSING A FLASH FIRE THAT BURNED MR. MARTINEZ. HE WAS HOSPITALIZED FOR 2ND.DEGREE BURNS HE SUSTAINED. THE LEAKING GAS WAS TRACED BACK TO A 2" PIPE THATWAS CONNECTED TO THE 16" MAIN FROM A 10" MAIN. THE GAS CAME FROM A 2" PIN-OFF TEE THAT WAS IN THE CLOSED POSITION BUT DID NOT GIVE A POSITIVE SHUT-OFF. THIS 2" LINE HAS SINCE BEEN RETIRED. | 647 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
726 | 1994-08-29 | TX | other | UNKNOWN (CHAMBERS COUNTY) | MID CON TEXAS PIPELINE CORP | A BARGE SET A STABILIZING LEG ON THE PIPELINE. | 66500 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
727 | 1994-09-07 | NY | leaks and spills | UNKNOWN (ERIE COUNTY) | NATIONAL FUEL GAS DISTRIBUTION CORP | ON 09/07/1994, AT 4:36 P.M., LINE C-46 RUPTURED AND IGNITED. LINE IS STORAGELINE FOR COLDEN STORAGE. STORAGE WAS ON INJECTION AT 897 PSIG. NATIONAL FUELNOTIFIED AT 4:40 P.M. RESPONDED, SHUTTING VALVE TZ56,CLOSING LINE DOWN. FIREOUT AT 5:18 P.M. ALL SECTIONS OF LINE INVOLVED ARE TO BE SHIPPED TO BATTELLELABS FOR ANALYSIS. DAMAGE TO 3.5 ACRES OF FOREST. NO INJURIES TO PERSONS.LINE RUPTURED, IGNITED. SUPPLEMENTAL REPORT 1/10/95 INDICATES CHANGES TOPROPERTY DAMAGE: TOTAL OF $111,135.00, WITH GAS LOST AMOUNT = $44,460, PROPERTYDAMAGE = $10,066 AND REPLACEMENT COST $56,429. ALSO NARRATIVE CHANGES INCLUDE:LINE INSTALLED 1953. BARE, 16", GR. B SEAMLESS .375 WALL PIPE. LAID ON SHALEAT THIS SITE. CORROSION HAD REDUCED THE WALL AT THE RUPTURE SITE AND FAILUREAND FIRE OCCURRED. | 111135 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
728 | 1994-09-03 | IL | leaks and spills | UNKNOWN (MORGAN COUNTY) | PANHANDLE EASTERN PIPELINE CO | FAILURE OCCURRED DUE TO LOCALIZED INTERNAL CORROSION. AN INVESTIGATION IS CURRENTLY UNDERWAY. | 47300 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
729 | 1994-08-26 | TX | other | UNKNOWN (THROCKMORTON COUNTY) | LONE STAR GAS CO | LONE STAR CREW WAS BACKFILLING A PIPELINE. THE TRACK OF A CATAPILLAR HIT THIS PIPELINE AND PUNCHED A HOLE IN IT. GAS IGNITED BURNING THE OPERATOR AND CATAPILLAR. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
730 | 1994-09-04 | LA | leaks and spills | UNKNOWN ( COUNTY) | TENNESSEE GAS PIPELINE CO | DURING PIGGING OPERATIONS, LEAK DISCOVERED BY SONAT CREW (BUBBLES AT SURFACE) | 200000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
731 | 1994-08-27 | MN | maintenance | UNKNOWN ( COUNTY) | NORTHERN NATURAL GAS CO (ENRON) | LONGITUDINAL SEAM FAILURE | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
732 | 1994-09-22 | IL | other | UNKNOWN (WAYNE COUNTY) | TRUNKLINE GAS CO | MALFUNCTION OF COMPRESSOR STATION EMERGENCY SHUT DOWN SYSTEM OPENNED BLOW-OFFS WITHOUT ISOLATING THE STATION YARD PIPING. | 123000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
733 | 1994-10-23 | WV | leaks and spills | UNKNOWN (RANDOLPH COUNTY) | COLUMBIA GAS TRANSMISSION CORP | THE RUPTURE OCCURRED AT A CORRODED AREA ON THE PIPE WHERE CATHODIC PROTECTIONCURRENT APPEARS TO HAVE BEEN SHIELDED BY A LARGE ROCK. THE FRACTURE MECHANISM EVALUATION IS NOT YET AVAILABLE FROM COLUMBIA'S METALLURGICAL CONSULTANT. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
734 | 1994-09-07 | TX | leaks and spills | UNKNOWN (MATAGORDA COUNTY) | VALERO TRANSMISSION CO | FIELD PERSONNAL HAD BEEN OUT 3 DAYS PRIOR TO 09/07/94. THERE WAS NO LEAK AT THAT TIME. WHEN THEY WERE OUT AGAIN ON 09/07/94, A PINHOLE LEAK, PROBABLY DUETO EXTERNAL CORROSION, WAS FOUND ON THE 3" RISER OFF THE 16" PORTION OF LINE#27. THE LEAK WAS REPAIRED ON 09/11/94. | 40000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
735 | 1994-10-20 | TX | other | UNKNOWN (HARRIS COUNTY) | VALERO TRANSMISSION CO | AT APPROXIMATELY 10:45 A.M. ON OCTOBER 20, 1994, VALERO'S PEARLAND FIELD OPERATIONS OFFICE BECAME AWARE VIA RADIO AND TV NEWSCASTS OF AN INCIDENTS INVOLVING A POSSIBLE RUPTURE OF A COLONIAL PIPELINE IN THE VICINITY OF THE SAN JACINTO RIVER. BECOAUSE VALERO'S 12" SINCO NATURAL GAS PIPELINE CROSSES THE SAN JACINTO RIVER IN CLOSE PROXIMITY TO THE COLONIAL PIPELINE, VALERO IMMEDIATELY BEGAN MONITORING THE GAS PRESSURE ON ITS 12" SINCO LINE TO PROVIDE AN IMMEDIATE INDICATION OF FAILURE. IN ADDITION, VALERO'S GAUGERS WERE DISPATCHED TO MLBV'S ON EACH SIDE OF THE RIVER AND PLACED ON STANDBY NOTICE TO CLOSE THE VALVES AND ISOLATE THE RIVER CROSSING IN CASE OF THE LINE FAILURE. AT 3:45 P.M., ASUBSTANTIAL DROP IN PRESSURE ON THE 12"SINCO PIPELINE WAS NOTED BY VALERO'SGAS CONTROL. VALERO'S GAUGERS WERE INSTRUCTED TO CLOSE THE MLBV'S AND ISOLATETHE PIPELINE SECITON THAT CROSSES THE SAN JACINTO RIVER. VALERO'S GAUGER SHUT THE ARCO LYONDELL MLBV INSIDE THE ARCO LYONDELL FACILITY ON SHELDON ROAD,LOCATED ON THE WEST SIDE OF THE SAN JACINTO RIVER, AT 4:30 PM. WHILE INSIDE THE LYONDELL FACILITY, THE GAUGER ALSO SHUT IN THE ARCO CHEMICAL MLBV AT 4:45P.M. VALERO'S GAUGER SHUT IN THE CROSBY EAST MLBV, LOCATED ON THE EAST SIDE OF THE SAN JACINTO RIVER AT 4:45 P.M. AS AN ADITIONAL PRECAUTION, VALERO'S GAUGER SHUT-IN THE NORTH SHIP CHANNEL MLBV AT 4:15 P.M. AT APPROXIMATELY 5:00 P.M., VALERO PERSONNEL NOTIFIED THE TRRC EMERGENCY NOITICATION HOTLINE OF THE 12" SINCO RUPTURE. AT APPROXIMATELY 6:00 P.M. DEAN SCOATT WITH THE TRRC CALLEDAND DISCUSSED THE INCIDENT WITH VALERO'S ENVIRRONMENTAL AND REGULATORY PERSONNEL AND ADVISED THAT THE TRRC WOULD NOTIFY VALERO IF FURTHER INFORMATION ORACTION WAS REQUIRED. AT 6:30 P.M., VALERO'S FIELD MANAGEMENT PERSONNEL INSPECTED THE 12" SINCO RUPTURE SITE WITH LYONDELL PETRO CHEMICAL AND ARCO CHEMICALPERSONNEL; HOWEVER, DUE TO THE FLOOD WATER DEPTH, NO PHYSICAL ON-SITE CONFIRMATION OF THE 12" SINCO RUPTURE WAS POSSIBLE UNTIL THE FLOOD WATERS RECEDE. AT APPROXIMATELY 7:00 P.M., MARY MCDANIEL WITH TRRC CALLED AND DISCUSSED THE INCIDENT WITH VALERO'S ENVIRONMENTAL AND REGULATORY PERSONNEL AND ADVISED THATTHE TRRC WOULD NOTIFY VALERO IF FURTHER INFORMATION OR ACTION WAS REQUIRED.AT APPROXIMATELY 10:00 P.M. JAMIE HERNANDEZ WITH THE TRRC CALLED AND DISCUSSED THE INCIDENT WITH VALERO'S PEARLAND FIELD OPERATIONS PERSONNEL. VALERO PLANS TO LEAVE THE RIVER SECTION ISOLATED AND OUT OF SERVICE UNTIL THE FLOOD WATERS RECEDE AND REPAIRS CAN BE MADE. SUPPLEMENTAL REPORT 11/22/94 INDICATES THATVALERO IS CURRENTLY REPLACING THE DAMAGED RIVER CROSSING IN ACCORDANCE WITHPLANS SUBMITTED TO THE TRRC. TELEPHONE CONVERSATION WITH MR. SOMMER INDICATESTHAT THIS WAS COMPLETED 12/94. | 800000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
736 | 1994-10-17 | NV | maintenance | UNKNOWN (WASHOE COUNTY) | PAIUTE PIPELINE CO | FAILURE OCCURRED AT THREADED CONNECTION ON VENT STACK. INCIDENT OCCURRED WHILE BLOWING-DOWN A TEMPORARY BY-PASS PIPE. VENT STACK FAILED AT THREADED CONNECTION. VENT PIPE HIT EMPLOYEE IN LEFT ARM AND LEG. EMPLOYEE REQUIRED OVER-NIGHT STAY IN HOSPITAL. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
737 | 1994-10-10 | AR | other | UNKNOWN (HEMPSTEAD COUNTY) | ARKLA ENERGY RESOURCES | CONTRACTOR LAYING PHONE CABLE HIT NGT'S LINE AM-46,14" OD. PIPELINE ROW WAS CLEARLY MARKED. TELEPHONE COMPANY'S CONTRACTOR WAS OFF OF THEIR ASSIGNED ROW.COVER ON PIPELINE WAS OVER 36", A METER STATION WAS CLEARLY VISIBLE A POINT WERE CONTRACTOR DEVIATED FROM THEIR ASSIGNED ROW. | 25000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
738 | 1994-11-16 | MO | other | UNKNOWN (CASS COUNTY) | WILLIAMS NATURAL GAS CO | DOZER HIT PIPELINE WHILE WORKING IN AREA. | 17000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
739 | 1994-10-27 | LA | other | UNKNOWN ( COUNTY) | COLUMBIA GULF TRANSMISSION CO | NO REMARKS. SUPPLEMENTAL REPORT 1/31/95 INDICATES CHANGE IN PART 3 -MARRATIVE DESCRIPTION. TEXAS EASTERN TRANSMISSION CORPORATION'S 16" GRIPPERINTERCONNECTION FAILED RESULTING IN DAMAMGE TO COLUMBIA'S 6" PIPELINE AT THETIE-IN POINT. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
740 | 1994-11-21 | MS | other | UNKNOWN (PERRY COUNTY) | FLORIDA GAS TRANSMISSION CO | PIPELINE HIT BY BULLDOZER BLADE WHILE CONSTRUCTING EROSION TERRACES OVER PIPELINE RIGHT OF WAY. | 75000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
741 | 1994-07-21 | WV | leaks and spills | UNKNOWN (KANAWHA COUNTY) | CABOT OIL & GAS CORP | THE PIPELINE WAS SUBMERGED IN A CREEK CROSSING AND OVER THE YEARS DEBRISHITTING THE PIPE HAD DAMAGED THE COATING CAUSING LOCALIZED CORROSION. ON JULY21, 1994 WHILE TESTING TO ESTABLISH A NEW MAOP ON PIPELINE #A-30, A SECTION OFPIPE THAT RUNS THROUGH KELLY'S CREEK RUPTURED. THE SEQUENCE OF EVENTS THATLED UP TO THIS INCIDENTS ARE AS FOLLOWS: PRIOR TO TESTING THIS SEGMENT OFPIPELINE, APPROXIMATELY 4026 FEET IN LENGTH, OF WHICH 1700 FEET IS CLASS III,SEVEN TEEN DIG-OUTS WERE PERFORMED IN ORDER TO ESTABLISH THE WALL THICKNESS OFTHE PIPE. IN ADDITION, SEVEN COUPONS WERE CUT OUT FROM THESE DIG-OUTLOCATIONS AN D WERE SENT TO A LAB TO BE METALLURGICALLY TESTED. ON THE DAY OFTHE TEST, THE PIPELINE WAS PURGED OF NATURAL GAS WITH NITROGEN AND THENON-EXISTENCE OF NATURAL GAS WAS VERIFIED WITH A COMBUSTIBLE GAS INDICATOR. A500 PSI MAOP WAS TO BE ESTABLISHED WITH A TEST PRESSURE OF 750 PSI. IN ORDERTO OBTAIN THE 750 PSI TEST PRESSURE, THE DIFFERENCE BETWEEN THE TEST PRESSUREAND THE ESTABLISHED MAOP OF 220 PSI WAS DIVIDED INTO FOURTHS GIVING 175 PSITEST PRESSURE SEGMENTS. THE FIRST STAGE OF THE TEST WAS TO PRESSURIZE THELINE TO THE ESTABLISHED MAOP OF 220 PSI. THIS PRESSURE WAS MAINTAINED FORAPPROXIMATELY 15 MINUTES WHILE THIS SECTION OF PIPELINE, APPROXIMATELY 4026FEET, WAS BEING WALKED. THE SECOND STAGE OF THE TEST WAS TO PRESSURIZE THELINE TO 395 PSI AND MAINTAIN THIS PRESSURE WHILE THE LINE WAS BEING WALKED.THE THIRD STAGE REQUIRED PRESSURIZING THE PIPELINE TO 570 PSI. THIS TESTPRESSURE WAS ALSO MAINTAINED FOR APPROXIMATELY 15 MINUTES WHILE THE LINE WASBEING WALKED. THE FOURTH, AND FINAL STAGE OF THE TEST, REQUIRED THAT THEPIPELINE BE PRESSURIZED TO 750 PSI. UPON ACHIEVING A TEST PRESSURE OFAPPROXIMATLEY 700 PSI, THE PIPELINE RUPTURED IN A CREEK CROSSING. AS ARESULT OF THIS RUPTURE, TWO INDIVIDUALS, WHICH ARE NON-EMPLOYEES, WERETRANSPORTED TO THE HOSPITAL, ONE OF WHICH WAS TREATED FOR HIGH HEART RATE ANDTHEN RELEASED APPROXIMATELY 3 HOURS LATER. THE SECOND INDIVIDUAL SUSTAINED ACONCUSSION AND WAS HOSPITALIZED FOR TWO DAYS. ALSO, AS A RESULT OF THISRUPTURE, 5 HOUSE TRAILERS, APPROXIMATELY 6 AUTOMOBILES AND 2 CAMPERS RECEIVEDDAMAGE. ONE OF THE HOUSE TRAILERS RECEIVED EXTENSIVE DAMAGE WHILE THE OTHERFOUR RECEIVED DAMAGE RANGING FROM BROKEN WINDOWS TO DENTED OUTER SHELLS. THEDAMAGE TO THE AUTOMOBILES AND CAMPERS RANGED FROM BROKEN WINDSHIELDS TODENTED HOODS. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
742 | 1994-11-29 | TX | other | UNKNOWN (DALLAS COUNTY) | LONE STAR GAS CO OF TEXAS, INC | CONTRACTOR INSTALLING NATURAL GAS DISTRIBUTION MAIN HIT PIPELINE WITH A TRENCHING MACHINE. | 43000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
743 | 1994-12-04 | LA | maintenance | UNKNOWN (TANGIPAHOA COUNTY) | FLORIDA GAS TRANSMISSION CO |  | 52000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
744 | 1994-11-11 | TX | other | UNKNOWN (CASS COUNTY) | NATURAL GAS PIPELINE CO OF AMERICA | NATURAL GAS WAS BLOWING FROM THE VENT OF A CASED CROSSING. THE CARRIER PIPEWAS REMOVED AND REPLACED WITH PRETESTED PIPE. BECAUSE HYDROTESTING FAILED TOID ENTIFY THE SOURCE OR CAUSE OF THE LEAK, THE CARRIER PIPE WAS RETIRED. | 110941 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
745 | 1994-12-02 | LA | other | UNKNOWN ( COUNTY) | TENNESSEE GAS PIPELINE CO | JACK-UP RIG, IN APPARENT EMERGENCY LOWERED A LEG AND SET DOWN ON 16IN. TGP PIPELINE, CAUSING RUPTURE AND SUBSEQUENT FIRE. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
746 | 1994-11-20 | TX | other | UNKNOWN ( COUNTY) | TRANSCO GAS PIPELINE CORP | A TUG TOWING A SEMI-SUBMERSIBLE RIG IN THE GALVESTON 237 AREA, EXPECTING BADWEATHER, SAT THE RIG ON THE BOTTOM. THE RIG SAT DOWN ON THE 12" PIPELINE DRIVING IT 6 FEET INTO THE MUD AND SEVERING THE LINE. | 390000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
747 | 1994-11-15 | TX | other | UNKNOWN (ANDERSON COUNTY) | LONE STAR GAS CO OF TEXAS, INC | DAMAGE BY ROAD GRADER. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
748 | 1994-12-20 | CO | other | UNKNOWN (ADAMS COUNTY) | COLORADO INTERSTATE GAS CO | CIG'S PIPELINE NUMBER 2B-20" RUPTURED AT 3:08 AM ON 12/20/94; THE RUPTUREEXTENDED FOR APPROXIMATELY 36 FEET ALONG THE PIPE. ESCAPING NATURAL GASIGNITED AND, IN ADDITION TO THE FORCE OF THE RUPTURE, SERIOUSLY DAMAGED CIG'SGRIMM AND FIRST CREEK METER STATIONS WHICH ARE LOCATED ADJACENT TO THEPIPELINE ROW. SERVICE WAS RESTORED TO THE CUSTOMERS SERVED BY THE METERSTATIONS AND THE 2B PIPELINE WAS RETURNED TO SERVICE AT 5 PM ON 12/21/1994.SUBSEQUENT INVESTIGATION DETERMINED THAT THE FRACTURE ORIGINATED ON THEOUSTIDE SURFACE OF THE PIPE BODY AT THE TOE OF THE REINFORCEMENT FOR A 4"BRANCH CONNECTION. AT THIS LOCATION, THERE WAS EVIDENCE OF A SHALLOW,PREEXISTING CRACK ALONG THE OUTSIDE SURFACE OF THE PIPE. THE CAUSE OF THEFAILURE HAS BEEN DETERMINED TO BE SLOW CRACK GROWTH. THE POSSIBLE CAUSE OF THESLOW CRACK GROWTH IS FATIGUE, HOWEVER, THE EXACT NATURE OF THIS GROWTH ISSTILL UNDER DETERMINATION. ADDITIONAL INFORMATION FOR CLASSIFICATION OF PART 2- APPARENT CAUSE - FATIGUE. | 467000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
749 | 1994-12-16 | TX | other | UNKNOWN ( COUNTY) | TRANSCO GAS PIPELINE CORP | THE RUPTURE ON THE 12" PIPELINE WHICH OCCURRED ON DECEMBER 16, 1994 AT M.P.22.786 WAS CAUSED BY THE SAME OUTSIDE PARTY DAMAGE THAT CAUSED THE RUPTURE OFTHE 12" PIPELINE AT M.P.22.75 WHICH WAS REPORTED TO THE NATIONAL RESPONSECENTER ON NOVEMBER 20, 1994 (REPORT NO. 270374). THE OUTSIDE PARTY DAMAGE WASCAUSED BY A TUG TOWING A SEMI-SUBMERSIBLE RIG IN THE GALVESTON 237 ARA,EXPECTING BAD WEATHER, SAT THE RIG ON THE BOTTOM. THE RIG SAT DOWN ON THE 12"PIPELINE WITH TWO PADS HITTING THE LINE AT TWO SEPARATE LOCATIONS. BECAUSE OFTHE DISTANCE BETWEEN THE TWO DAMAGED AREAS, THE DAMAGE AT M.P. 22.786 WAS NOTDETECTED DURING THE INITIAL INVESTIGATION AND REPAIR OF THE ORIGINAL RUPTUREINCIDENT (N OVEMBER 20, 1994). | 250000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
750 | 1994-12-15 | AK | leaks and spills | UNKNOWN ( COUNTY) | ENSTAR NATURAL GAS CO | 10 FOOT SECTION OF PIPE CUT OUT AND REPLACED FOR PERMANENT REPAIR. COATINGDAMAGED DURING CONSTRUCTION. LOCALIZED CORROSION CAUSED PITTING TO OCCUR. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
751 | 1994-12-20 | OK | leaks and spills | UNKNOWN (NOBLE COUNTY) | WILLIAMS NATURAL GAS CO | FAILED JOINT BLEW OUT - SENDING PIPE SPECIMEN FOR ANALYSIS. FURTHERCLASSIFICATION OF PART 2 - APPARENT CAUSE - STATES THAT THIS FAILURE IS UNDERINVESTIGATION. SUPPLEMENTAL REPORT 3/27/1995 INDICATES THAT FURTHERINVESTIGATION CHANGED CAUSE TO CORROSION (INTERNAL). SUPPL - PART A - ALSO IDOF PIPE BARE, OD IS INEFFECTIVELY COATED - COUPLED SECTION. | 80000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
752 | 1995-01-01 | AL | other | UNKNOWN ( COUNTY) | EXXON CO USA | ON DECEMBER 28, 1994, BUBBLES WERE OBSERVED PERCOLATING NEAR THE PIPELINESWHICH TRAVERSE BETWEEN EXXON'S "A" PLATFORM IN MOBILE BLOCK 62 AND THE SSTILOCATED IN THE SAME BLOCK. DUE TO SEA CONDITIONS AND THE SIZE OF THE BUBBLES,THE BUBBLES WERE UNABLE TO BE OBSERVED FROM THE AIR. ALTHOUGH THERE WAS NOPOLLUTION, CHANGE IN OPERATING CONDITIONS OR PIPELINE PRESSURE, PRECAUTIONARYMEASURES WERE TAKEN TO ASCERTAIN THE SOURCE OF THE BUBBLES. AFTER NOTIFYINGTHE ALABAMA PUBLIC SERVICE COMMISSION, ALABAMA OIL AND GAS BOARD, MOBILE MSOOF THE USCG, AND CORPS OF ENGINEERS OF EXXON'S PLANS TO ASCERTAIN THE SOURCEOF THE BUBBLES, WORK BEGAN TO UNCOVER THE PIPELINES ON DECEMBER 30 1994. ONJANUARY 1, 1995 AFTER UNCOVERING THE PIPELINES, DIVERS DISCOVERED A SMALL LEAKAROUND THE BALL VALVE ON THE "3" FUEL GAS PIPELINE. IT IS BELIEVED THAT THEPACKING AND THE SEALANT BECAME EXPOSED TO PRESSURE WHEN THE HALL VALVE WASNOT FULLY OPENED. AFTER DIVERS ENSURED THAT THE VALVE WAS FULLY OPENED,PACKING WAS INJECTED AND THE PACKING AROUND THE STEM OF THE BALL VALVE WASTIGHTENED. REPAIR WORK WAS COMPLETED ON JANUARY 4, 1995. UPON COMPLETION OFOTHER UNRELATED MAINTENANCE WORK ON OTHER PIPELINES, THE 3" FUEL GAS PIPELINEWAS COVERED ON JANUARY 12, 1995. | 210000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
753 | 1995-01-19 | LA | leaks and spills | UNKNOWN ( COUNTY) | ARAN ENERGY CORPORATION | EXTERNAL CORROSION OVER TIME. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
754 | 1994-12-12 | LA | other | UNKNOWN ( COUNTY) | HALL-HOUSTON OIL COMPANY | NO ONE WITNESSED INCIDENT. REPORT INDICATED ANCHOR DRAGGED ACROSS PIPELINE SEGMENT. PART B - TYPE OF MARKING- AS-BUILT WAS SUBMITTED TO NOAA FOR MAPPING & PIPELINE BURIED ACCORDING TO DOT/DOI REGULATIONS. | 417975 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
755 | 1995-01-08 | TX | other | UNKNOWN ( COUNTY) | DALEN RESOURCES OIL & GAS CO. | PIPE APPEARED TO DEVELOP SPLIT 1/2" X 1/16" ON TOP SIDE. SUSPECT POSSIBLE DEFECTIVE PIPE. LEAK REPAIRED WITH CLAMP | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
756 | 1995-01-09 | AL | other | UNKNOWN ( COUNTY) | EXXON CO USA | ON JANUARY 9, 1995 WHILE PERFORMING MAINTENANCE WORK ON THE 10" PRODUCED GASPIPELINE FROM MOBILE BLOCK 62 "A" TO MOBILE BLOCK 62 SSTI, DIVERS DISCOVEREDBUBBLES PERCOLATING FROM THE SEALANT INJECTION PORT ON THE BALL VALVE. THEREWAS NO POLLUTION AS A RESULT OF THE RELEASE OF BUBBLES. NOTIFICATION WAS MADETO THE ALABAMA PUBLIC SERVICE COMMISSION (APSC) AND THE ALABAMA OIL AND GASBOARD (AO GB) ON JANUARY 9, 1995. AFTER DETERMINING THE EXTENT OF THE REPAIRWORK, THE NATIONAL RESPONSE CENTER (NRC) WAS CONTACTED ON JANUARY 10, 1995.ALL FACILITIES IN THE FIELD WERE SHUT IN AND THE PRODUCED GAS PIPELINESYSTEM WAS DEPRESSURIZED BEFORE PROCEEDING WITH REPAIRING THE INJECTION PORT.THE PIPELINE WAS REPAIRED BY INJECTING SEALANT AND PLUGGING THE INJECTIONPORT. THIS WORK WAS COMPLETED ON JANUARY 10, 1995. UPON COMPLETION OF OTHERUNRELATED MAINTENANCE WORK ON OTHER PIPELINES, THE 10" PRODUCED GAS PIPELINEWAS COVERED ON JANUARY 12,1995. | 110000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
757 | 1995-01-24 | LA | maintenance | UNKNOWN ( COUNTY) | TRANSCO GAS PIPELINE CORP | THE HYDROCOUPLE END CONNECTOR SLIPPED OFF THE END OF THE 12" PIPELINE DURINGAN ABNORMAL PRESSURE CONDITION. THEIS ABNORMAL PRESSURE CONDITION DID NOT EXCEED THE MAOP OF THE PIPELINE. | 255000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
758 | 1995-01-31 | FL | other | UNKNOWN (ALACHUA COUNTY) | FLORIDA GAS TRANSMISSION CO |  | 29000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
759 | 1995-02-01 | TX | leaks and spills | UNKNOWN ( COUNTY) | ENRON OIL & GAS CO | CORROSIVE SPOT ON DEPARTING LINE (LOCALIZED ) DEVELOPED SMALL HOLE. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
760 | 1995-02-07 | WV | other | UNKNOWN (LOGAN COUNTY) | COLUMBIA GAS TRANSMISSION CORP | THIRD PARTY CONTRACTOR DOZER PUNCTURED COLUMBIA'S PIPELINE WHILE CLEARINGINTERSECTING RIGHT-OF-WAY FOR ANOTHER OPERATOR'S NEW PIPELINE CONSTRUCTIONPROJECT. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
761 | 1995-02-23 | PA | maintenance | UNKNOWN (CLINTON COUNTY) | CNG TRANSMISSION CORP | SPECULATION PENDING FINAL ANALYSIS | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
762 | 1995-02-25 | MI | maintenance | UNKNOWN (MANISTEE COUNTY) | BASIN PIPELINE CORP | ADDITIONAL INFORMATION IS BEING COLLECTED TO ALLOW DETERMINATION OF THE CAUSE OF THE FAILURE. GASKET FAILED IN INSULATING FLANGE AT PIG RECEIVER WHILE PUMPING METHANOL INTO LINE TO REMOVE HYDRATE PLUG. GASKET FURNISHED BY NATIONALOILWELL IN FLANGE INSULATION KIT REPORTEDLY PACKAGED BY FLANGE PROTECTION, INC. W/GASKET REPORTEDLY MANUFACTURED BY GARLOCK. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
763 | 1995-03-19 | LA | other | UNKNOWN (ST HELENA COUNTY) | TRANSCO GAS PIPELINE CORP | SIZE, SHAPE, AND SEVERITY OF THE GOUGE (44") INDICATES IT WAS CAUSED BY ALARGE PIECE OF EXCAVATION EQUIPMENT (PROBABLY) A BACKHOE. FAILURE INITIATED INA GOUGE OF UNKNOWN ORIGIN. | 619000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
764 | 1995-03-14 | LA | leaks and spills | UNKNOWN (CAMERON COUNTY) | MOBIL EXPLORATION & PRODUCING US INC | EXTERIOR SURFACE OF PIPE WAS FREE AND CLEAR OF ANY SIGNS OF EXTERNAL CORROSION. PIPE-TO-SOIL READING AT THIS LOCATION WAS -1.053 VDC. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
765 | 1995-03-06 | WA | other | UNKNOWN (COWLITZ COUNTY) | NORTHWEST PIPELINE CORP |  | 719000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
766 | 1995-04-12 | CA | other | UNKNOWN (LOS ANGELES COUNTY) | CHEVRON PIPELINE CO | THE INCIDENT OCCURRED AT 1340 PST ON MARCH 6, 1995 IN A REMOTE AREA AT MILEPOST 1272. 7 NEAR CASTLE ROCK WASHINGTON. THE FAILURE OCCURRED ON NORTHWEST PIPELINE CORPORATION'S 26 INCH IGNACIO, COLORADO TO SUMAS, WASHINGTON MAINLINE.IN THE ACCIDENT AREA THE LINE IS PARALLELED BY NORTHWEST'S 30 INCH LOOPLINE AND A 14 INCH PRODUCTS LINE OWNED BY OLYMPIC PIPELINE COMPANY. NORTHWEST'S 26INCH PIPE RUPTURED OR BUILDING DAMAGE. NEITHER OF THE ADJACENT LINES WERE DAMAGED REPAIRS WERE COMPLETE BY REPLACEMENT OF 201 FEET OF 26 INCH PIPE AND THE LINE WAS PURGED ON SATURDAY MARCH, 11, 1995. THE LINE WAS NOT RETURNED TO FULL SERVICE UNTIL MARCH 15, 1995 PENDING GEOTECHNICAL ASSESSMENTS OF THE SLIDE AREA AND EXCAVATION OF THE 26 AND 30 INCH LINES TO RELIEVE STRESSES. NATURAL GAS SERVICE WAS INTERRUPTED TO TWO INDUSTRIAL USERS FOR 3 HOURS AT ONE LOCATION AND 5 HOURS AT THE OTHER. GEOTECHNICAL ENGINEERING ASSESEMENT OF THE SITE AREA CONCLUDES THAT THE PIPELINES WERE IMPACTED BY A RECENT LANDSLIDE THAT EXTENDS APPROXIMATELY 1000 FEET UPSLOPE FROM THE PIPELINES. PRELIM8INARY REPORTS OF LABORATORY ANALYSIS OF SELECTED SAMPLES OF THE FAILED PIPE INDICATE THE FAILURE WAS DUE TO RADICAL MOVEMENT OF THE BURIED LINE INDUCING A BUCKLE. THE BUCKLING AND THE STRESS ASSOCIATED WITH THE MOVEMENT CAUSED THE PIPE TO RUPTURE AT THE BUCKLE. APPROXIMATELY 495 FEET OF 26 INCH LINE AND 268 FEET OF 30 INCH LINE WAS EXCAVATED AND LEFT FREE TO ENABLE FREE MOVEMENT OF THE LANDSLIDE. SUBSEQUENT INSPECTIONS OF THE TWO LINES CONFIRMED THAT THEIR SERVICEABILITY IS NOT IMPAIRED. THE SITE IS SECURED AND THE PIPELINES ARE OBSERVED DAILY. SURFACE DISPLACEMENT MEASUREMENTS ARE BEING TAKEN THREE TIMES PER WEEK AT THIS TIME. PLANS FOR LONG TERM REMEDIATION OF THE SITE WILL BE DEPENDENT ON CONTINUED EVALUATION OF THE CHARACTER AND EXTENT OF THE LANDSLIDE.CONTRACTOR WAS REMOVING PIPELINES IN AREA OF CHEV. DRY GAS LINE; CONTR. HADSTOCKPILED SOIL OVER THE GAS LINE. CONTRACTOR, WHILE REMOVING DIRT, FORGOTWHERE ORIGINAL GRADE WAS; THEY EXCAVATED TOO DEEPLY & PUNCTURED ACTIVE LINE. | 5000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
767 | 1995-03-24 | IA | maintenance | UNKNOWN ( COUNTY) | NORTHERN NATURAL GAS CO (ENRON) | SUPPLEMENTAL REPORT WILL FOLLOW WHEN FAILURE CAUSE IS KNOWN.FAILURE THROUGH A 4" BRANCH CONNECTION ON 26" PIPE. EXACT CAUSE OF FAILURE NOT KNOWN YET. | 75000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
768 | 1995-03-27 | NC | other | UNKNOWN (MECKLENBURG COUNTY) | PIEDMONT NATURAL GAS CO INC |  | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
769 | 1995-04-19 | CA | other | UNKNOWN (VENTURA COUNTY) | SOUTHERN CALIFORNIA GAS CO | ON APRIL 19, 1995, AT APPROXIMATELY 5:05 P.M., A LARGE MUD SLIDE IN BIG VCANYON CAUSED THE SOUTHERN CALIFORNIA GAS COMPANY'S 116" TRANSMISSION LINE1003 TO RUPTURE IN THE BOTTOM OF THE CANYON. COMPANY PERSONNEL WEREIMMEDIATELY DISPATCHED TO IDENTIFY THE LOCATION AND ISOLATE THE BREAK. VALVESMLV 1003-27. 83-0 AND MLV 1003-23.85 WERE CLOSED AND GAS BROUGHT UNDER CONTROLAT 6:39 P.M. THE INCIDENT RESULTED IN TEMPORARY LOSS OF GAS SERVICE TO 3RESIDENTAL CUSTOMERS THERE WERE NO INJURIES, EVACUATIONS OR STREET CLOSURES.THE AREA OF RUPT URE IS COVERED WITH LANDSLIDE MATERIAL AND CANNOT BE VISUALLYINSPECTED AT THIS TIME. FIELD OBSERVATIONS INDICATE THAT ONE OR MORE WELDLOCATIONS BROKE DUE TO THE EARTH MOVEMENT. THE AREA IS CURRENTLY BEINGEVALUATED TO DETERMINE A SAFE ALIGNMENT FOR RELOCATION OF THE PIPELINE. WE AREIN THE PROCESS OF DETERMINING HOW LONG THE PIPELINE CAN BE OUT OF SERVICE ANDIF INSTALLATION OF A TEMPORARY BYPASS IS REQUIRED UNTIL PERMANENT REPAIRS CANBE MADE. THE AMOUNT OF DAMAGE TO COMPANY FACILITIES IS CURRENTLY ESTIMATED AT$150,000. PER MESSAGE FR. G. LAFEVERS 5/26, RUPTURE LENGTH IS APPROX. 5 FT.THE PIPE HAS BROKEN AT WELD AND SEPARATION IS APPROX. 5FT. RUPTURED SECTION ISSTILL BURIED UNDER LAND SLIDE MATERIAL. | 150000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
770 | 1995-04-17 | OK | other | UNKNOWN (OKLAHOMA COUNTY) | WILLIAMS NATURAL GAS CO | A GAS DETECTOR SENSOR MALFUNCTIONED AND ACTIVATED THE EMERGENCY SHUT DOWN SYSTEM. OUR SCADA SYSTEM INDICATED THAT THE INTAKE VALVE DID NOT CLOSE COMPLETELY. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
771 | 1995-04-08 | KS | leaks and spills | UNKNOWN (COWLEY COUNTY) | WILLIAMS NATURAL GAS CO | HOT SPOT SURVEY - COUPLED LINE | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
772 | 1995-03-31 | ID | maintenance | UNKNOWN (ELMORE COUNTY) | NORTHWEST PIPELINE CORP | THREE QUARTER INCH SPLIT LONGITUDINAL SEAM. SPLIT CLOSED WHEN PRESSURE WASREDUCED DELAYING LEAK IDENTIFICATION AND REPORTING. REPAIRS WERE MADE BYREPLACING 73 FEET OF PIPE DURING STOPPLE BYPASS OPERATION TO MAINTAINCONTINUITY OF SERVICE. SPLIT IN LONG SEAM (3/4 INCH) ERW PIPE IDENTIFIED BYDEAD VEGETATION DURING LEAK SURVEY. INITIALLY DETERMINED TO BE NON-REPORTABLE,STOPPLE/BYPASS REPAIRS ESCALATED COSTS ABOVE REPORTING THRESHOLD. | 303000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
773 | 1995-04-25 | LA | maintenance | UNKNOWN ( COUNTY) | TRANSCO GAS PIPELINE CORP | THE CLAMP ON THE MID RISER CONNECTOR ASSEMBLY ON THE 16" RISER FAILED. | 250000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
774 | 1995-04-19 | MS | maintenance | UNKNOWN (JEFFERSON DAVIS COUNTY) | SOUTHERN NATURAL GAS CO | TURBINE UNIT WAS PRESSURE TESTED BY THE MANUFACTURER PURSUANT TO INDUSTRYDESIGN SPECIFICATION APPLICABLE AT THE TIME OF MANUFACTURING.SOLAR T1001S-15SATURN TURBINE NATURAL GAS COMPRESSOR ENGINE RATED @1080 HORSEPOWER. A FIREOCCURED IN A TURBINE COMPRESSOR UNIT. CAUSE OF THE FIRE IS PRESENTLY UNKNOWN,BUT INVESTIGATION IS CONTINUING. THERE WAS NO EXPLOSION. | 750000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
775 | 1995-05-19 | TN | other | UNKNOWN (WASHINGTON COUNTY) | EAST TENNESSEE NATURAL GAS CO | THUNDER STORM WITH HEAVY LIGHTNING MOVED THROUGH THE AREA JUST BEFORE FIRE WAS REPORTED. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
776 | 1995-06-02 | CA | other | UNKNOWN (CONTRA COSTA COUNTY) | PACIFIC GAS & ELECTRIC CO | VANDAL ENTERED REGULATION FACILITY BY SCALING FENCE. OPERATED 14 VALVES THATWERE LOCKED IN POSITION BY CHAINS. RELIEF VALVE OPENED DUE TO OVERPRESSURE ASA RESULT OF VALVE CHANGES. GAS RELEASED THROUGH RELIEF VALVE WAS IGNITED BY VANDAL, RESULTING IN INJURY. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
777 | 1995-06-27 | WV | leaks and spills | UNKNOWN (KANAWHA COUNTY) | COLUMBIA GAS TRANSMISSION CORP | LOCAL SUPERVISOR RESPONDED TO VERIFY A LEAK CALLED IN BY NEARBY RESIDENT. PIPE RUPTURED WHILE SUPERVISOR WAS RETURNING TO OFFICE. EMERGENCY ACTION INCLUDED ISOLATING AREA AND EVACUATING THREE RESIDENTS. ISOLATION COMPLETED BY 1900HOURS. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
778 | 1995-06-25 | MN | other | UNKNOWN (MILLE LACS COUNTY) | VIKING GAS TRANSMISSION CO | WELDER'S HELPER RECEIVED FLASH BURN WHEN GRINDING WELD BEVEL ON 24" PIPE. ONSUNDAY, JUNE 25, 1995 APPROXIMATELY 12:45 P.M., EARL STEINBRENNER (CONTRACTWELDERS HELPER) WAS GRINDING A BEVEL ON A 24" NATURAL GAS PIPELINE. THE BEVEL WAS ON THE OPEN END OF THE DOWNSTREAM PIPE THAT JUST HAD A NITE-CAP REMOVED. THE WELDER WAS ASKED IF THEY WANTED THE AIR MOVERS TURNED ON, AND DECIDED TO TEST THE INSIDE OF PIPE WITH A COMBUSTIBLE GAS DETECTOR AND STATED IT WAS O.K. (O % LEL). THE WELDERS'S HELPER PROCEEDED WITH THE BEVEL PREPARATION AND HAD BEEN GRINDING ON THE 24" PIPE END FOR APPROXIMATELY 10 MINUTES PRIPR TO THE INCIDENT. THE WELDER'S HELPER WAS GOING TO TOUCH UP A SPOT ON THE BEVEL WHEN THE FLASH OCCURRED. THE FLASH WAS INSTANTANEOUS AND SELF-EXTINGUISHED IMMEDIATELY. HE WAS WEARING A FACE SHIELD AND SAFETY GLASSES. THE WELDER'S HELPERRECEIVED MINOR BURNS TO THE FACE AND NECK AREA WHICH REQUIRED MEDICAL ATTENTION. THE VICTIM WAS TAKEN TO HENNEPIN COUNTY MEDICAL CENTER FOR A REQUIRED 24HOUR OBSERVATION PERIOD, THAN RELEASED ON THE MORNING OF JUNE 26TH WITH NO SERIOUS INJURIES. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
779 | 1995-04-25 | CA | other | UNKNOWN (MONTEREY COUNTY) | PACIFIC GAS & ELECTRIC CO | THE THIRD-PARTY WAS WORKING AND STRUCK THE LINE AT A LOCATION 3,000 FEET AWAY FROM WHERE THEY SAID THE WERE GOING TO BE WORKING. A FARMER PLOWING A FIELDSOUTH OF GREENFIELD STRUCK A GAS TRANSMISSION MAIN WITH A RIPPER. SERVICE WASDISRUPTED TO APPROXIMATELY 2,455 CUSTOMERS. NO INJURIES OR FATALITIES OCCURRE | 270000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
780 | 1995-06-02 | TX | other | UNKNOWN (TRAVIS COUNTY) | LONE STAR GAS CO | LINE P DAMAGED FROM FLOOD WATERS OF THE COLORADO RIVER CAUSING RUPTURE AT BOTH ENDS OF THE RIVER CROSSING. | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
781 | 1995-06-16 | CO | other | UNKNOWN (MORGAN COUNTY) | YOUNG GAS STORAGE COMPANY., LTD. | GAS ESCAPED FROM THE BODY CAVITY VENT OF A 16", ANSI CLASS 900 BALL VALVE ASTHE VALVE WAS BEING OPENED DURING ROUTINE MAINTENANCE. THE GAS IGNITED AND BURNED AN EMPLOYEE WHO WAS ATTEMPTING TO STOP THE FLOW OF GAS BY CLOSING THE 16" VALVE. INVESTIGATION DETERMINED THAT THE 1" THREADED PLUG ASSOCIATED WITH THE VENT, WHICH IS LOCATED NEAR THE BOTTOM OF THE VALVE BODY, HAD NOT BEEN REPLACED IN THE VENT OPENING AFTER THE VALVE WAS DRAINED SUBSEQUENT TO THE ORIGINAL, POST-CONSTRUCTION HYDROSTATIC TEST, AND THAT THIS VALVE DESIGN PERMITS LINE PRESSURE TO BE IN THE BODY CAVITY AT ALL TIMES EXCEPT WHEN THE 16" VALVEIS FULLY CLOSED. FACTORS CONTRIBUTING TO THE ACCIDENT INCLUDE THE FAILURE TOREPLACE THE VENT PLUG AFTER HYDROSTATIC TESTING, AND THE EMPLOYEE'S DECISIONTO REENTER THE AREA IN AN ATTEMPT TO STOP THE FLOW OF ESCAPING GAS. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
782 | 1995-07-01 | IL | leaks and spills | UNKNOWN (JOHNSON COUNTY) | TRUNKLINE GAS CO | ISOLATED CORRODED AREA WAS SMALL ENOUGH SO AS NOT TO BE READILY IDENTIFIABLEWITH CLOSE INTERVAL CATHODIC PROTECTION SURVEY EQUIPMENT AND TECHNIQUES AVAILABLE TODAY. NO OTHER CORROSION OBSERVED. PIPELINE CAME TO REST ON A ROCK LEDGE WHICH DAMAGED THE COATING. FAILURE ORIGINATED AT 6:00 POSITION. BRITTLE PIPE IS SUSPECTED. | 1750000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
783 | 1995-06-28 | ID | maintenance | UNKNOWN (BEAR LAKE COUNTY) | NORTHWEST PIPELINE CORP | LABORATORY ANALYSIS IDENTIFIED THE ORIGIN OF THE FAILURE AS A LONGITUDINAL GOUGE, .150" DEEP AND ONE FOOT IN LENGTH LOCATED IN THE 5:00 POSITION OF THE PIPE. THE LONG SEAM WAS LOCATED IN THE 6:00 POSITION. THE GOUGE WAS THE RESULT OF MECHANICAL DAMAGE MADE DURING THE ORIGINAL 1956 CONSTRUCTION. THEINCIDENT OCCURRED AT 12:55 A.M. MDT ON JUNE 28, 1995 IN A REMOTE WETLAND AREANEAR DINGLE, IDAHO, WHICH IS LOCATED IN THE SOUTHWESTERN PART OF THE STATE.THE 22 INCH PIPELINE RUPTURE IGNITED AND DAMAGED 350 FEET OF PIPE. THERE WERENO INJURIES AND PROPERTY DAMAGE WAS LIMITED TO BRUSH AND A SMALL GROVE OFTREES. THE 18 MILE LINE SEGMENT WAS ISOLATED WITHIN 55 MINUTES AND THE FIREWAS EXTINGUISHED WITHIN 95 MINUTES. NATURAL GAS SERVICE WAS INTERRUPTED TOINTERMOUNTAIN GAS COMPANY, THE LOCAL NATURAL GAS DISTRIBUTION COMPANY SERVINGTHE CITY OF MONTPELIER, IDAHO, AND THE SURROUNDING AREA. APPROXIMATELY 1000INTERMOUNTAIN CUSTOMERS WERE AFFECTED BY THE SERVICE INTERRUPTION. SERVICEWAS RESTORED TO INTERMOUNTAIN WITHIN 22 HOURS USING A TEMPORARY BYPASS.APPROXIMATELY 415 FEET OF 22 INCH PIPE WAS REPLACED AND THE 22 INCH MAINLINEWAS RETURNED TO FULL SERVICE ON JULY 2, 1995. LABORATORY ANALYSIS OF THEFAILED PIPE SPECIMENS IDENTIFIED THE ORIGIN OF THE FAILURE AS A LONGITUDINALGOUGE .150" DEEP, AND ONE FOOT IN LENGTH. THE GOUGE, LOCATED IN THE 5 O'CLOCKPOSITION, WAS THE RESULT OF OUTSIDE FORCE MECHANICAL DAMAGE MADE DURING THEORIGINAL 1956 CONSTRUCTION OF THE LINE. | 700000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
784 | 1995-06-27 | LA | leaks and spills | UNKNOWN ( COUNTY) | TENNESSEE GAS PIPELINE CO | UNKNOWN FACTORS - SUSPECTED INTERNAL CORROSION | 226000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
785 | 1995-05-30 | TX | other | UNKNOWN (HIDALGO COUNTY) | TECO GAS GATHERING COMPANY | ON MAY 30, 1995, AT APPROXIMATELY 2200 HOURS, TECO PIPELINE COMPANY RECEIVEDAN EMERGENCY CALL FROM TEXAS ONE CALL CONCERNING A FIRE NEAR OUR PIPELINE. TECO PERSONNEL IMMEDIATELY RESPONDED AND UPON ARRIVAL DISCOVERED A FIRE AT OUR METER STATION NEAR HARGIL, TEXAS. APPARENT CAUSE OF THE ACCIDENT WAS LIGHTNING HITTING A FIBERGLASS TANK IN THE STATION YARD. THE TANK IGNITED ALSO CAUSING A 2" DUMP LINE AND A 1/2" NIPPLE OFF OF THE SEPARATOR TO BREAK AND IGNITE. ALL INLET POINTS TO THE PIPELINE SYSTEM WERE IMMEDIATELY SHUT IN AND THEFIRE WAS BROUGHT UNDER CONTROL. THE FIRE WAS COMPLETELY OUT BY 0010 HOURS ON 31 MAY, 1995, TWO (2) HOURS AND TEN (10) MINUTES AFTER THE LIGHTNING HAD STRUCK. REPAIR WORK AT THE STATION BEGAN IMMEDIATELY. ALL VALVES, CONTROLS, AND METERS THAT WERE AFFECTED BY THE HEAT WERE EITHER REPLACED OR REPAIRED. | 139250 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
786 | 1995-07-01 | OH | other | UNKNOWN (MUSKINGUM COUNTY) | NATIONAL GAS & OIL CORP | ON JULY 1, 1995, A FIRE OCCURED AT AN UNATTENDED NATIONAL GAS & OIL CORPORATION STORAGE COMPRESSOR STATION DAMAGING A METAL BUILDING AND ENGINE/COMPRESSOR. A ONE INCH PIPE FITTING LOCATED ON THE COMPRESSOR FAILED RELEASING GAS INTO THE BUILDING THAT WAS IGNITED BY THE ENGINE. THE EMERGENCY SHUTDOWN DEVICE(ESD) WAS ACTIVATED AND THE GAS FIRE WAS EXTINGUUISHED IN APPROXIMATELY 10 MINUTES. NO PERSONAL INJURIES WERE SUSTAINED AND DAMAGE TO THE FACILITY WAS ESTIMATED AT APPROXIMATELY $285,000. NO COMPANY EMPLOYEES WERE CONSIDERED A CONTRIBUTING FACTOR TO THE INCIDENT AND THEREFORE WERE NOT ALCOHOL OR DRUG TESTED FOLLOWING THE INCIDENT.THE CAUSE OF THE INCIDENT WAS THE FAILURE OF A ONE INCH PIPE NIPPLE LOCATED ON THE INTERSTAGE MANIFOLD OF THE COMPRESSOR. THE PIPE NIPPLE CONNECTED A RELIEF VALVE TO THE INTERSTAGE MANIFOLD BETWEEN THE FIRST STAGE AND SECOND STATE COMPRESSOR CYLINDERS. THE PHYSICAL APPEARANCE OF THE FITTING INDICATES THAT THE FAILURE RESULTED FROM METAL FATIGUE. | 285000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
787 | 1995-07-22 | OK | other | UNKNOWN (WOODS COUNTY) | ONG TRANSMISSION CO | LIGHTNING STRUCK GAS PURCHASE METER SETTING RESULTING IN A FIRE WHICH DESTROYED VARIOUS PIECES OF PRODUCTION EQUIPMENT. | 65000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
788 | 1995-07-31 | MS | other | UNKNOWN (ALCORN COUNTY) | COLUMBIA GULF TRANSMISSION CO | THE PRECISE MECHANISM AND ROOT CAUSE OF THIS FAILURE REMAINS UNDETERMINED. APPARENTLY, NUMBER 5 TURBINE AND COMPRESSOR LUBE OIL SYSTEM SHUT DOWN DUE TO ANUNDETERMINED FAULT. SUBSEQUENTLY, THE SEAL OIL DRAINED THROUGH THE COMPRESSOR SEALS, WHICH CAUSED THE SEAL OIL LEVEL TO DROP AND GAS TO MIGRATE FROM THECOMPRESSOR CASE TO THE OIL SUMP RESERVOIR. THE MIGRATING GAS ATOMIZED THE SUMP OIL, AND A MIXTURE OF OIL MIST/VAPOR AND NATURAL GAS WAS RELEASED INTO THECOMPRESSOR BUILDING. AN EXPLOSION AND FIRE RESULTED. THE IGNITION SOURCE IS UNKNOWN. NUMBER 5 UNIT AUTOMATICALLY SHUT DOWN. WHEN AN EMPLOYEE RESPONDED,IGNITION AND EXPLOSION OCCURRED WHEN HE OPENED THE COMPRESSOR BUILDING DOOR.THIS RESULTED IN 1ST, 2ND AND 3RD DEGREE BURNS AND HOSPITALIZATION OF THEEMPLOYEE. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
789 | 1995-07-22 | LA | maintenance | UNKNOWN (VERMILION BLOCK 96 COUNTY) | COLUMBIA GULF TRANSMISSION CO | LEAK OCCURRED AT FILLET WELD ON THE 6" LEG OF 6" X 36 EXTRUDED STRONGBACK ENCIRCLEMENT SADDLE AT UNDERSEA HOT TAP TIE IN CONNECTION. PIN HOLE LEAK AT 12:00 POSITION ON FILLET WELD. EXACT LEAK MECHANISM HAS NOT BEEN DETERMINED. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
790 | 1995-07-07 | KS | other | UNKNOWN (LYON COUNTY) | PANHANDLE EASTERN PIPELINE CO | FIVE SCC CRACKS, LINEARLY ALIGNED, LINKED TOGETHER TO FORM A FLAW APPROXIMATELY FOUR (4) INCHES LONG RESULTING IN THE RUPTURE. | 220000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
791 | 1995-08-12 | TX | other | UNKNOWN (LIBERTY COUNTY) | PRAXAIR, INC | DAMAGE CAUSES BY FIRE FROM OUTSIDE SOURCE AS A RESULT OF CAR ACCIDENT. A CARIS ENGULFED IN FLAMES AND BLACK SMOKE AFTER A GAS LINE EXPLODED EARLY SATURDAY ALONG FM 563 SOUTH OF LIBERTY. THREE PEOPLE WERE INJURED IN THE EXPLOSION.OFFICIALS ALSO EVACUATED FOUR OTHER HOMES DURING THE FIRE, WHICH OCCURRED AFTER A DRIVER RAN OFF THE ROAD AND STRUCK A VALVE. TWO WOMEN BURNED IN THE EXPLOSION WERE REPORTED IN CRITICAL CONDITION SATURDAY NIGHT. | 25000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
792 | 1995-09-13 | WV | other | UNKNOWN (LOGAN COUNTY) | COLUMBIA GAS TRANSMISSION CORP | PRELIMINARY INVESTIGATION INDICATES THE PIPELINE WAS DAMAGED BY A COAL STRIPPING OPERATOR'S DOZER TRACK TURNING AROUND IN WET, SOUPY DRAINAGE DITCH LOCATION ON THE PIPELINE RIGHT-OF-WAY. CRACK PROPOGATION IN THE RESULTING DENT/GOUGE AREA CAUSED THE RUPTURE. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
793 | 1995-08-15 | TX | leaks and spills | UNKNOWN (GREGG COUNTY) | TRIDENT NGL PLANT | CORROSION COUPONS AT PLANT INLET SHOWED NO SIGNIFICANT CORROSION. | 10000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
794 | 1995-08-24 | TX | other | UNKNOWN ( COUNTY) | CHEVRON PIPELINE CO | TWO CHEVRON U.S.A. PRODUCTION CO., INC. OPERATORS WERE IN THE PROCESS OF OPENING A PIG LAUNCHER ON A 16" PIPELINE OWNED BY CHANDELEUR PIPLINE COMPANY, A WHOLLY OWNED SUBSIDIARY OF CHEVRON PIPE LINE COMPANY. THE PIG LAUNCHER WAS LOCATED ON CHEVRON U.S.A. PRODUCTION CO., INC.'S MAIN PASS BLOCK 41 "B" PLATFORM. THE OPERATORS HAD BEEN REQUESTED TO BLEED DOWN THE PRESSURE ON THE SEGMENTOF CHANDELEUR PIPE LINE COMPANY'S 16" PIPELINE EXTENDING FROM "B" TO "L" PLATFORMS. FOR REASONS CURRENTLY UNKNOWN, THE OPERATORS BEGAN OPENING THE LAUNCCHER CLOSURE BEFORE BLEEDING PRESSURE OFF THE LAUNCHER. AS ONE OF THE OPERATORS WAS IN THE PROCESS OF LOOSENING THE BOLTS WHICH SECURED THE CLAMP ON THE LAUNCHER CLOSURE, THE HIGH PRESSURE GAS (1020 PSI) CONTAINED IN THE LAUNCHER ESCAPED CAUSING FATAL INJURIES TO BOTH OPERATORS AND CAUSED DAMAGE TO THE CLOSURE ASSEMBLY. THERE WERE NO EYEWITNESSES TO THE INCIDENT. CHEVRON U.S.A. PRODUCTION CO., INC. IS CURRENTLY CONDUCTING AN INVESTIGATION INTO THE INCIDENT. ASUPPLEMENTAL REPORT WILL BE SUBMITTED WHEN THE INVESTIGATION HAS BEEN COMPLETED. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
795 | 1995-09-25 | KY | other | UNKNOWN (FLOYD COUNTY) | COLUMBIA GAS TRANSMISSION CORP | COAL OPERATOR'S DOZER GOUGED 2 FOOT HOLE IN PIPELINE WHILE WORKING HAUL ROADFOR STRIPPING OPERATIONS. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
796 | 1995-09-01 | LA | other | UNKNOWN ( COUNTY) | TRUNKLINE GAS CO | DAMAGE CAUSE UNKNOWN - CRACK IN 1/2" NPT NIPPLE EXTRA HEAVY. NIPPLE AND VALVEWAS BLEEDER ASSEMBLY ON HYDROTECH REPAIR CLAMP. CAUSE OF INCIDENT IS UNKNOWN.DUE TO UNDERWATER LOCATION AND NO VISIBLE POLLUTANT, VERIFICATION OF LEAK ONLINE 1004-B-1100 WAS NOT CONFIRMED UNTIL 8:00 A.M. ON 09/08/95. REPAIRSCOMPLETED AT 7:25 A.M. ON 09/14/95. DUE TO UNDERWATER LOCATION AND NO VISIBLEPOLLUTANT, VERIFICATION OF LEAK IN LINE 1004-B-1100 WAS NOT CONFIRMED UNTIL9/8/1995. REPAIRS COMPLETED AT 7:25AM ON 9/14/1995. | 150000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
797 | 1995-09-29 | PA | other | UNKNOWN (YORK COUNTY) | COLUMBIA GAS TRANSMISSION CORP | EXCAVATION CONTRACTOR OPERATING A RIPPER ON A BULLDOZER IN EARTH MOVING OPERATION STRUCK LINE., ONE 200' +/- NORTH, ONE 229' +/- SOUTH. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
798 | 1995-09-27 | TX | leaks and spills | UNKNOWN (HARRIS COUNTY) | EASTEX GAS TRANSMISSION CO | 6" GAS LINE WAS BEING UTILIZED AS A FLOWLINE FROM PRODUCING WELL (OIL-SALTWATER) SAMPLES OF SALTWATER FROM LINE INDICATED REASON FOR CORROSION. | 3500 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
799 | 1995-10-04 | LA | other | UNKNOWN ( COUNTY) | SOUTHERN NATURAL GAS CO | SHEAR JOINT (INSTALLED ON PIPELINE IN 1993) SEPARATION CAUSED BY MUDSLIDE DURING HURRICANE OPAL. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
800 | 1995-10-06 | TX | other | UNKNOWN ( COUNTY) | ANR PIPELINE CO | PIPELINE WAS STRUCK BY 1" CABLE THAT WAS DRAGGED OVER OUR 12" LATERAL LINE. | 150000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
801 | 1995-10-03 | LA | other | UNKNOWN ( COUNTY) | TEXAS EASTERN GAS PIPELINE CO | TEXAS EASTERN SUBSEA TAP VALVE ASSEMBLY MUST BE REPLACED. BOAT ANCHORS PULLEDA 6" PIPELINE, OWNED BY UNITED MERIDIAN CORPORATION, AWAY FROM ITSCONNECTION TO TEXAS EASTERN DURING HURRICANE OPAL, RESULTING IN THE LOSS OFGAS IN THE TEXAS EASTERN PIPELINE. (BOAT OWNER HAS NOT BEEN IDENTIFIED). | 980000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
802 | 1995-10-23 | LA | other | UNKNOWN ( COUNTY) | VASTAR RESOURCES, INC. | AFTER UNSUCCESSFUL ATTEMPT TO PRESSURE UP LINE, LEAK WAS NARROWED DOWN BY BOATBY LOCATING BUBBLES. SUBSEQUENTLY, A SIDE SCAN SONAR AND MAGNETOMETER SURVEYWERE CONDUCTED- BREAK IS AT X=2,771, 360 AND Y=192,090.LINE PARTED DUE TO AMUD SLIDE IN THE VICINITY OF THE LINE. SUSPECT HURRICANE OPAL TRIGGERED THEMUD SLIDE THE LINE WAS NOT IN SERVICE AT THE TIME OF THE INCIDENT BECAUSEOTHE R REPAIRS WERE NECESSARY IN ANOTHER PORTION OF THE LINE. LINE PART WASDISCOVERED WHEN GAS WAS FLOWED INTO THE LINE BUT UNABLE TO PRESSURE UP> 90PSIG. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
803 | 1995-10-14 | TX | other | UNKNOWN (PECOS COUNTY) | INTRATEX GAS CO | IN THE PROCESS OF RETURNING THE 30" SUCTION VALVE TO SERVICE, THE TECHNICIANHOOKED UP THE ELECTRICAL CONNECTION TO THE VALVE ACTUATOR AND PROCEEDED TO OPEN THE VALVE, BUT THEN THE ELECTRICAL CONNECTION FAILED, CAUSING THE PILOT GAS VALVE TO VENT A SMALL QUANTITY OF GAS WHICH MAY HAVE IGNITED BY ELECTRICALARCING. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
804 | 1995-10-28 | TX | other | UNKNOWN (BROOKS COUNTY) | VALERO TRANSMISSION CO | THE CENTER BOLT THAT RETAINS THE VALVE CHAIR LOOSENED AND PERMITTED GAS TO ESCAPE AND IGNITE. THE ESD SYSTEM ACTIVATED AND EXTINGUISHED THE FIRE. | 45000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
805 | 1995-10-21 | TX | maintenance | UNKNOWN (JEFFERSON COUNTY) | HOUSTON PIPELINE CO | SMALL CRACK IN CIRCUMFERENTIAL WELD. | 5000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
806 | 1995-10-25 | TX | other | UNKNOWN (CHAMBERS COUNTY) | TEJAS GAS PIPELINE COMPANY | A CONTRACTOR WAS EMPLOYED BY THE OPERATOR TO MOW THE PIPELINE RIGHT-OF-WAY. THE MOWER STRUCK AN EXPOSED SEGMENT OF PIPELINE IN THE BOTTOM OF A ROAD DRAINAGE DITCH. PIPE WAS NOT VISIBLE DUE TO PRESENCE OF VEGETATION BEING MOWED. | 24000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
807 | 1995-04-18 | TX | maintenance | UNKNOWN (REEVES COUNTY) | WEST TEXAS GAS INC | PIPE JOINT WOULD PROBABLY NOT HAVE FAILED IF DELHI RELIEF VALVES HAD PROPERLYOPERATED.ANALYSIS REVEALED INTERNAL STRESS LINES IN LINE WITH THE STEP WISEFLOW ON THE PIPE JOINT. EXCESS PRESSURE ON PIPELINE DUE TO FAILURE OF RELIEFVALVES ON DELHI PIPELINE. | 10000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
808 | 1995-12-06 | AL | other | UNKNOWN (JACKSON COUNTY) | MARSHALL COUNTY GAS DISTRICT | OKADEE 4" GATE VALVE LEAKING THROUGH SLIGHTLY (<1PSI). ATTEMPTING TO CHANGE OUT A 4" AXIAL FLOW WITH AN IMPACT WRENCH. LOW OVERCAST, LOW BAROMETRIC PRESSURE, LOW WIND, TYPE OF DAY. EMPLOYEES WERE ATTEMPTING TO IMPACT REMOVE THE LAS BOLT WHEN IGNITION OCCURRED. FOUR MEN WERE PRESENT AT THE SITE (INTERMEDIATE RUN AT NORANDAL REGULATOR STATION). PRESENT WERE MARSHALL COUNTY GAS DISTRICT EMPLOYEES: DAVID BROWN, CARL RICE, LEONARD KIRKLAND, AND PAUL BOWDEN. THREE WERE SLIGHTLY BURNED ON HANDS AND FACE AREA BUT NONE OF WHICH RECEIVED TREATMENT. HOWEVER, PAUL BOWDEN, 37 YEAR OLD WHITE MALE, RECEIVED SLIGHT FIRST DEGREE BURNS TO UPPER FACIAL AREA AND BOTH HANDS REQUIRING IN-PATIENT HOSPITALIZATION AND WAS RELEASED THE NEXT DAY (12-7-95). ALL FOUR EMPLOYEES RECEIVED DRUG TESTS WITHIN 32 HOURS. AT THIS TIME, THE LAB HAS THE SAMPLES AND THE RESULTS SHOULD BE RETURNED TO THE MRO NEXT WEEK. INCIDENT WAS REPORTED TO DOT AT 3:00 P.M., 12-6-95, BY RICHARD T. LAWSON, MANAGER. REPORT #3163240. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
809 | 1995-11-23 | LA | other | UNKNOWN ( COUNTY) | TEXAS EASTERN GAS PIPELINE CO | OCCURRED IN OUTER CONTINENTAL SHELF, OFFSHORE LOUISIANA. A SHRIMPING NET PULLED A PRODUCER'S 6" LATERAL LOOSE FROM TEXAS EASTERN'S 30" LINE 41-A-7 TAP ASSEMBLY CAUSING A LOSS OF NATURAL GAS IN LINE 41-A-7. | 250000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
810 | 1995-12-13 | TN | other | UNKNOWN (RUTHERFORD COUNTY) | UNITED CITIES GAS CO | SECTION OF PIPE DAMAGED WAS NOT MARKED. SECTION THAT WAS DAMAGED WAS STUBOUT LEFT FROM LAST RELOCATION TO SERVE FARM TAP. WAS NOT MARKED BY LOCATOR. HE WAS NOT AWARE OF THIS SECTION. TRACK-HOE HIT 4" STEEL LINE CAUSING LINE CUT. | 25000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
811 | 1995-12-09 | MA | other | UNKNOWN (BRISTOL COUNTY) | ALGONQUIN GAS TRANSMISSION CO | GENERAL AREA OF INCIDENT WAS ON-GOING SHOPPING CENTER DEVELOPMENT. AT TIME OFINCIDENT OPERATOR WAS GRADING ADJACENT TO ROW UNDER CONTRACTOR DIRECTION. EQUIPMENT OPERATOR DECIDED ON HIS OWN TO EXTEND WORK INTO ROW. AGREED UPON NOTIFICATION WAS NOT GIVEN TO ALGONQUIN FOR APPROVAL OF GRADING AND DISPATCH OF STAND-BY PERSONNEL. PIPELINE STRUCK AND RUPTURED BY DOZER EQUIPPED WITH RIPPERDURING UNAUTHORIZED GRADING OPERATION. | 320000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
812 | 1996-01-06 | PA | leaks and spills | UNKNOWN (MONROE COUNTY) | COLUMBIA GAS TRANSMISSION CORP | THERE ARE INDICATIONS THAT CATHODIC PROTECTION CURRENT SHIELDING FROM SHALE ROCK RESULTED IN LOCALIZED PITTING AND PIPE WALL LOSS TO A POINT WHERE A COMBINATION OF DUCTILE AND BRITTLE FRACTURES OCCURRED RESULTING IN A RUPTURE OF THE PIPE. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
813 | 1995-12-21 | CO | maintenance | UNKNOWN (ELBERT COUNTY) | COLORADO INTERSTATE GAS CO | MATERIAL DEFECT IN PIPE DUE TO FAULTY MANUFACTURING PROCESS. CIG'S PIPELINE NO. 2B-20" RUPTURED AT 12:45PM ON 12/21/95 IN RURAL EASTERN COLORADO. THE RUPTURE EXTENDED FOR APPROXIMATELY 133 FEET ALONG THE PIPE; ESCAPING NATURAL GASDID NOT IGNITE. THERE WERE NO INJURIES TO EMPLOYEES OR THE MEMBERS OF THE PUBLIC, AND NO SIGNIFICANT PROPERTY DAMAGE OCCURRED. ALSO, THERE WAS NO INTERRUPTION OF SERVICE TO ANY CUSTOMERS. EXAMINATION OF THE FAILURE SITE, AND PRELIMINARY METALLURGICAL ANALYSIS OF PIECES OF THE FAILED PIPE, DETERMINED THAT THEFRACTURE ORIGINATED IN THE BODY OF THE PIPE AT A LAMINATION IN THE PIPE WALL. A SUPPLEMENTARY REPORT WILL BE SUBMITTED IF THE FINAL METALLURGICAL ANALYSIS INDICATES A DIFFERENT CAUSE OF FAILURE. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
814 | 1995-12-10 | LA | other | UNKNOWN ( COUNTY) | SOUTHERN NATURAL GAS CO | MUDSLIDE AT TIE-IN OF MAIN PASS BLOCK 72 PIPELINE IN MAIN PASS BLOCK 151 SEPARATED "BREAKWAY" JOINT. TAP COORDINATES ARE 2911.6, 8,852.6. | 280000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
815 | 1996-01-07 | TX | maintenance | UNKNOWN (PANOLA COUNTY) | KOCH GATEWAY PIPELINE COMPANY | THE CAUSE OF THE RUPTURE HAS NOT YET BEEN CONFIRMED. THE PIPE IS TO BE ANALYZED BY METTALLURIGICAL CONSULTANTS INC. SINCE THE RUPTURE OCCURRED IN THE LONGITUDINAL SEAM OF THE PIPE, A MATERIAL DEFECT IS SUSPECTED. A SUPPLEMENTAL REPORT WILL BE FILED. | 138035 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
816 | 1995-12-22 | TX | other | UNKNOWN (BRAZORIA COUNTY) | ARCO PIPE LINE CO | WEATHER CONDITIONS INCLUDING MUD AND WATER, QUESTIONABLE INTERGITY OF EXISTING UNDERGROUND PIPING (CONDUCTING TEST) LOCATION OF BARRICADE FENCE, DRESSER TD-4 H DOZER | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
817 | 1996-01-12 | OK | other | UNKNOWN (OKLAHOMA COUNTY) | ENOGEX INC (EX. MUSTANG FUEL CORP) |  | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
818 | 1996-01-14 | IL | leaks and spills | UNKNOWN (FAYETTE COUNTY) | NATURAL GAS PIPELINE CO OF AMERICA | UNDER INVESTIGATION. WILL BE FILING SUPPLEMENTAL. SUPPLEMENTAL RECEIVED 4/22/96 INDICATES CHANGE IN CAUSE FROM OTHER TO CORROSION. PIPE WAS USED UNDER CONDITIONS WHERE GAS WAS WET. THIS PROMOTED INTERNAL CORROSION OF THE LONGITUDINAL SEAM. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
819 | 1996-01-10 | LA | other | UNKNOWN (JEFFERSON COUNTY) | SOUTHERN NATURAL GAS CO | PIPELINE RUPTURED AND GAS IGNITED. CAUSE UNKNOWN AT THIS TIME. SUPPLEMENTALREPORT FILED 6/10/1996 UPDATES CAUSE TO DAMAGE BY OUTSIDE FORCES, ANDINCREASES PROPERTY DAMAGE TO $372,000, PER ERIC E. THOMAS. COMMENTS STATETHAT ALTHOUGH THE CAUSE OF THE RUPTURE IS NOT KNOWN TO A HIGH DEGREE OFCERTAINTY, SCARRING INDICATES THE LIKELIHOOD THAT THE PIPE WAS STRUCK BY ANEXTERNAL SOURCE AT SOME TIME IN THE PAST, PRODUCING A STRESS RISER THATULTIMATELY RESULTED IN FAILURE. | 372000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
820 | 1996-01-12 | MS | other | UNKNOWN (WASHINGTON COUNTY) | TEXAS GAS TRANSMISSION CORP | ON JANUARY 12, 1996, AT APPROXIMATELY 8:26 P.M. A RELIEF VALVE LOCATED APPROXIMATELY 10 MILES SOUTH OF GREENVILLE, MISSISSIPPI, OPENED ON TEXAS GAS 26-INCH, NO.1 LINE. THE RELIEF VALVE IS INSTALLED TO PROVIDE OVERPRESSURE PROTECTION ON TWO SECTIONS OF THE 26-INCH LINE THAT HAVE AN MAOP OF 674 PSIG. THESE TWO SECTION ARE LOCATED FROM MILE 110.35 TO 111.74 AND MILO 113.52 TO 113.90 ON TEXAS GAS MAINLINE SYSTEM. PIPE MATERIAL SPECIFICATIONS IN THESE SECTIONS ARE A.O. SMITH, 26" O.D. X 0.282" W.T. GRADE X-52. THE RELIEF VALVE IS LOCATEDIN A RURAL AREA AT MILE 104.3 AND HAS A SET PRESSURE OF 741 PSIG (10% ABOVE MAOP). CALCULATED CAPACITY OF THE WKM RELIEF VALVE IS 35.7 MMCF/H. THE FOLLOWING IS A SUMMARY OF EVENTS THAT RESULTED IN ACTIVATION OF THE RELIEF VALVE. 4:00 PM-TEXAS GAS PERSONNEL AT CLARKSDALE COMPRESSOR STATION (MILE 171) REPORTED TO GAS CONTROL IN OWENSBORO, KENTUCKY THAT THE STATION'S GENERAL ELECTRIC TURBINE HAD SHUT DOWN. 5:00 PM SINCE THEY WERE UNABLE TO RESTART THE TURBINE AS ANTICIPATED, PERSONNEL AT CLARKSDALE STATION NOTIFIED GAS CONTROL OF THAT FACT AND INFORMED GAS CONTROL THAT ADDITIONAL PERSONNEL WERE ENROUTE TO ASSIST. GAS CONTROL RELAYED THIS INFORMATION TO PERSONNEL AT GREENVILLE AND LAKE CORMORANT STATIONS AND ADVISED TO ADJUST OPERATING CONDITITONS ACCORDINGLY. 5:47 PM GAS CONTROL RECEIVED A HIGH PRESSURE ALARM OF 675 PSIG INDICATING THAT THE 674 PSIG MAOP ON TWO SECTIONS OF THE 26-INCH, NO.1 LINE HAD BEEN EXCEEDED. 8:05 PM. ALTHOUGH ENCOUNTERING UNEXPECTED PROBLEMS, CLARKSDALE PERSONNEL CONTINUED IN THEIR EFFORTS TO RESTART THE GENERAL ELECTRIC TURBINE WHILE ADDITIONAL CLARKSDALE PERSONNEL WERE WORKING TO BRING A PRATT & WHITNEY TURBINE ON LINE. 8:26 PM GAS CONTROL RECEIVED AN ALARM INDICATING THAT THE RELIEF VALVE AT MILE 104.3 HAD OPENED. A TEXAS GAS EMPLOYEE WAS SENT TO THE RELIEF VALVE SITE. 9:20 PM CLARKSDALE PERSONNEL REPORTED TO GAS CONTROL THAT THE PRATT & WHITNEY TURBINE HAD BEEN SUCCESSFULLY STARTED. 9:55 PM GAS CONTROL NOTIFIED BY THE FIELD THAT THE RELIEF VALVE AT MILE 104.3 WAS CLOSED. 1O:45 PM GAS CONTROL RECEIVED SYSTEM NOTIFICATION THAT PRESSURE ON THE 26-INCH, NO.1 LINE HAD FALLEN BELOW THE MAOP OF 674 PSIG. THIS EVENT RESULTED IN A CALCULATED GAS LOSSOF 43.3 MMCF AT AN ESTIMATED COST OF $104,000. | 104000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
821 | 1995-12-26 | IN | maintenance | UNKNOWN (ST JOSEPH COUNTY) | TRUNKLINE GAS CO | DURING THE REMOVAL OF THE FAILED WELD, THE PIPE SEPARATED VERTICALLY BY SEVERAL INCHES NECESSITATING ADDITIONAL EXCAVATION FOR LINE UP SO AS TO MINIMIZE FUTURE RESIDUAL STRESS. GIRTH WELD FRACTURED FROM 9:00 TO 3:00 POSITION. PIPELINE APPEARED TO BE UNDER HIGH RESIDUAL STRESS AT WHAT MAY HAVE BEEN A ROAD CROSSING (CASED, NOT SHORTED) TIE-IN DURING ORIGINAL CONSTRUCTION. | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
822 | 1996-01-13 | MS | other | UNKNOWN (HANCOCK COUNTY) | KOCH GATEWAY PIPELINE COMPANY | PIPELINE WAS FOUND TO BE KINKED WITH A LARGE BOAT ANCHOR BENEATH THE PIPELINE. DAMAGE APPEARS TO HAVE BEEN CAUSED BY THE PIPELINE BEING HOOKED AND LIFTEDBY A LARGE BOAT ANCHOR. THE ANCHOR WAS ABANDONED AND IN CLOSE CONTACT WITH PIPELINE. THE PIPELINE WAS INDENTED BY ANCHOR RESULTING IN A LEAK. | 125000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
823 | 1996-01-18 | LA | other | UNKNOWN ( COUNTY) | TENNESSEE GAS PIPELINE CO | EVIDENCE INDICATES UNKNOWN OUTSIDE PARTY DAMAGED PIPE SEVERAL YEARS PRIOR TOTHE RUPTURE. SHELL PLATFORM AT E.I. - 18 CALLED GAS CONTROL AT 2:50 PM TO REPORT PRESSURE DROP FROM 1100 T0 200 PSI - ALSO LARGE BALL OF FIRE 2-5 MILES NEOF PLATFORM. D524 BEGAN CHECKING PRESSURES, ETC. AT 3:15 AM VERIFIED THAT SHELL E.I. 18 HAD BEEN SHUT IN AND 5194-102 MLV CLOSED, ADDITIONAL PRODUCERS WILL HAVE TO BE SHUT IN - UNMANNED PLATFORMS AND WELLS. NO LIQUIDS SUSPECTED INLINE. INVOLVED-PIPE HAD SCRAPES AND GOUGES COVERED BY BARNACLES. | 200000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
824 | 1996-01-19 | LA | other | UNKNOWN (CAMERON COUNTY) | ANR PIPELINE CO | THE ACCIDENTAL OVERTEMPERATURE OF LUBE OIL AND FUEL VALVE COMPONENTS BY THE BACKFLOW OF 900 DEGREE F. EXHAUST GASES DUE TO A FRACTURED 6TH STAGE BLEED AIRVALVE OUTLET FLANGE. EXHAUST GAS ESCAPING FROM THE 6TH STAGE BLEED AIR VALVEOUTLET DUCT IMPINGED ON A FUEL GAS VALVE. THE HOT TURBINE EXHAUST MELTED THESEALS ON THE FUEL VALVE RESULTING IN A RELEASE OF GAS AND IGNITION. THETURBINE EXHAUST, WHICH WAS THE SOURCE OF IGNITION, WAS AT A TEMPERATURE ABOVETHE AUTO IGNITION OF NATURAL GAS. | 420000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
825 | 1996-01-26 | TX | other | UNKNOWN (ROBERTS COUNTY) | NORTHERN NATURAL GAS CO (ENRON) | WELDER ASSISTING DURING TACK WELDING OF 24" END CAP. WELDING ARC CAUSED ANDIGNITION. WELDER WAS HIT BY MOVING END CAP. CAUSE LISTED AS IGNITION. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
826 | 1996-01-23 | NY | other | UNKNOWN (NEW YORK COUNTY) | CONSOLIDATED EDISON CO OF NEW YORK | STEEL BEAM FOUND IN CONTACT WITH TOP BRACE USED FOR REINFORCEMENT OF A COMPRESSION COUPLING. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
827 | 1996-02-18 | OH | other | UNKNOWN (LAWRENCE COUNTY) | COLUMBIA GAS TRANSMISSION CORP | FAILURE SITE EVALUATION DETERMINED THAT A BRITTLE FRACTURE OCCURRED AT A WRINKLE BEND. THE RELEASE OF GAS IGNITED RESULTING IN MINIMAL COLLATERAL DAMAGE. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
828 | 1996-02-04 | AR | other | UNKNOWN ( COUNTY) | NORAM GAS TRANSMISSION | POWER LINE BREAK AT A ROAD CROSSING (HWY 50) DROPING ON TO NORAM VENT PIPE CAUSING AN ELECTRICAL CONNECTION WHICH ARCED FROM THE BURIED CASING ONTO THE CARRIER PIPE. THE ARCING BURNED THROUGH THE PIPE WALL CAUSING A LEAK WHICH IGNITED. THE FLAMES WERE RISING OUT OF OUR VENT PIPE ON ONE SIDE CAUSING THE HWYTO BE CLOSED AND THE LINE TO BE SHUTIN. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
829 | 1995-10-05 | LA | other | UNKNOWN ( COUNTY) | ARAN ENERGY CORPORATION | GAS LINE WAS SEVERED DURING AN APPARENT MUD SLIDE CAUSED BY HURRICANE OPAL. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
830 | 1996-02-06 | LA | other | UNKNOWN ( COUNTY) | SOUTHERN NATURAL GAS CO | 4 POINT DIVE BOAT WAS WORKING TO REPAIR AN ADJACENT P/L. WHILE SETTING ANCHORS, ONE OF THE ANCHOR CABLES SNAGGED VALVE IN MAIN PASS 77 LINE AND PULLED P/L APART AT A LOAD LIMITING CONNECTOR NEAR VALVE. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
831 | 1996-02-08 | PA | other | UNKNOWN (ALLEGHENY COUNTY) | THREE RIVERS PIPELINE | INCIDENT OCCURED APPROX 6 YEARS AFTER 3RD PARTY DAMAGE. DENT REDUCED WALL THICKNESS TO 0.200". IN ADDITION, POSSIBLE SETTLING STRESSES ASSOCIATED WIT IMPROPER SUPPORT AND THERMAL EXPANSION MAY HAVE CONTRIBUTED. | 31400 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
832 | 1996-02-22 | OH | other | UNKNOWN (TUSCARAWAS COUNTY) | EAST OHIO GAS CO | A BLOCKAGE OCCURRED IN TRANSMISSION PIPELINE (TPL) #5 DUE TO THE FREEZE-UP OF LIQUIDS WHICH HAD ACCUMLATED IN THE LINE. AS A RESULT OF THE BLOCKAGE, THE UPSTREAM SECTION OF THIS PIPELINE OVER-PRESSURIZED, AND A RUPTURE OCCURRED ATPIPE STATION 3107+31. | 200000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
833 | 1996-02-26 | LA | maintenance | UNKNOWN ( COUNTY) | COLUMBIA GULF TRANSMISSION CO | A MICARTA RING WAS REPLACED WITH A STAINLESS STEEL RING AND THE PIPELINE WASRETURNED TO SERVICE. A LEAK WAS DISCOVERED AT A SWIVEL FLANGE CONNECTING THESUB-SEA PIPELINE TO THE OFFSHORE PLATFORM | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
834 | 1996-02-26 | MO | other | UNKNOWN (JACKSON COUNTY) | MISSOURI GAS ENERGY | AN 18" CLAY TILE STORM SEWER HAD BEEN INSTALLED ACROSS THE TOP OF THE 26" GAS LINE AT THE POINT OF RUPTURE. INSTALLATION DATE OF THE STORM SEWER UNKNOWN. | 60000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
835 | 1996-02-28 | AL | other | UNKNOWN (CLEBURNE COUNTY) | SOUTHERN NATURAL GAS CO | VANDALS CUT LOCKED CHAINS OFF OF THE OPERATORS FOR THE 20" TALLAPOOSA GATE BLOCK VALVE AND THE TWO 6" BLOWOFF VALVES LOCATED ON EITHER SIDE OF THE BLOCK VALVE. THE VANDAL'S DID NOT ALTER THE POSITION OF THE 20" VALVE, WHICH WAS OPEN, BUT DID OPEN THE 6" BLOWOFF VALVES WHICH WERE PREVIOUSLY IN THE CLOSED POSITION. PRIOR TO OPENING THE 6" VALVES, SMALL THREADED VENT PLUGS LOCATED BETWEEN THE BLOWOFF CAP CLOSURE FITTINGS AND THE VALVES WERE REMOVED. THIS ALLOWED NATURAL GAS TO ESCAPE TO THE ATMOSPHERE THROUGH THE SMALL VENTS AT A PRESSURE OF 450 PSIG AFTER THE BLOWOFF VALVES WERE OPENED. THE VANDALS POURED GASOLINE ON THE GROUND FROM THE BLOWOFFS TO THE EDGE OF A COUNTY ROAD CREATING A TRAIL TO ACT AS A "FUSE" FOR A DISTANCE OF ABOUT 60 FEET. THE GASOLINE TRAIL WAS IGNITED; CAUSING A SMALL GRASS FIRE UP TO THE BLOWOFFS. IT APPEARED THAT THE VANDAL'S INTENT WAS TO CREATE A NATURAL GAS EMERGENCY, BUT THE NATURAL GAS,BEING LIGHTER THAN AIR, NEVER IGNITED. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
836 | 1996-03-19 | LA | maintenance | UNKNOWN ( COUNTY) | ANR PIPELINE CO | ONE-INCH WIDE CRACK IN A GIRTH WELD RUNNING FROM THE 12'OCLOCK POSITION TOTHE 8 O'CLOCK POSITION. THE APPARENT CAUSE WILL NOT BE DETERMINED UNTIL AFTERTHE 30 DAY DEADLINE FOR REPORTING - A SUPPLEMENTAL REPORT WILL FOLLOW.SUPPLEMENTAL REPORT RECEIVED 2/21/96 INDICATES CHANGE IN CAUSE FROM OTHER TOCONSTRUCTION/MATERIAL DEFECT (C). | 75000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
837 | 1996-04-13 | OK | other | UNKNOWN (CLEVELAND COUNTY) | ONG TRANSMISSION CO | HIGH SPEED VEHICLE ACCIDENT RESULTED IN ONE VEHICLE STRIKING METER AND REGULATOR SETTING. HIGH SPEED VEHICLE ACCIDENT RESULTED IN FOUR FATALITIES. ONE OFTHE VEHICLES HIT THE METER SETTING CAUSING GAS LEAK AND FIRE. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
838 | 1996-04-29 | FL | other | UNKNOWN (POLK COUNTY) | FLORIDA GAS TRANSMISSION CO | PIPELINE HIT BY THIRD PARTY WITH BACKHOE. | 69000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
839 | 1996-05-06 | FL | other | UNKNOWN (DADE COUNTY) | FLORIDA GAS TRANSMISSION CO | PIPELINE HIT BY THIRD PARTY WITH POST HOLE AUGER. | 116000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
840 | 1996-05-03 | MA | other | UNKNOWN (ESSEX COUNTY) | TENNESSEE GAS PIPELINE CO | A THIRD PARTY CONTRACTOR, NOT WORKING FOR TENNESSEE GAS, ACCIDENTALLY DUG INTO THE LINE WHILE WORKING IN A GRAVEL YARD. VENT MARKING AT RAILROAD CROSSING, APPROXIMATELY 432FT. UPSTREAM AND MARKING APPROXIMATELY 350FT. DOWNSTREAM. | 80000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
841 | 1996-05-10 | LA | maintenance | UNKNOWN (CAMERON PARISH COUNTY) | NATURAL GAS PIPELINE CO OF AMERICA | A PIN HOLE LEAK IN GIRTH WELD CAUSED GAS AND CONDENSATE TO ESCAPE. PRESSUREESSEL SLEEVE AND STRUCTURAL CLAMP SYSTEM INSTALLED. | 171388 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
842 | 1996-05-09 | WV | other | UNKNOWN (HARRISON COUNTY) | CNG TRANSMISSION CORP | HEAVY & CONSECUTIVE RAINS CAUSED GROUND TO SLIP WHICH RESULTED IN PIPELINE DEVELOPING A "WRINKLE BEND" RESULTING IN A LEAK. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
843 | 1996-05-25 | NY | other | UNKNOWN (SARATOGA COUNTY) | NIAGARA MOHAWK POWER CORP | PIPELINE WAS DAMAGED UNKNOWN YEARS AGO PREVIOUS TO INCIDENT AND NOT REPORTEDTO NIAGARA MOHAWK. FINAL VERIFICATION THAT DAMAGE CAUSED ULTIMATELY LED TO PIE FAILURE BEING PERFORMED BY BATTELLE MEMORIAL INSTITUTE. PRELIMINARY INVESTIGATION INDICATES DAMAGE BY A THIRD PARTY SEVERAL YEARS AGO CAUSED PIPE TO FAIL AT PRESSURE APPROACHING MAOP. BATTELLE INSTITUTE VERIFYING CAUSE OF FAILURE. | 60000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
844 | 1996-06-05 | AL | leaks and spills | UNKNOWN (CLEBURNE COUNTY) | SOUTHERN NATURAL GAS CO | PRELIMINARY METALLURGICAL EXAMINATION INDICATES THAT STRESS CORROSION CRACKING IS MOST LIKELY OF THE LOW PH VARIETY. COATING AT THIS PARTICULAR POINT ON THE PIPELINE WAS POOR. HOWEVER, COATING ON ADJACENT PORTIONS OF THE PIPELINE WAS REPORTED TO BE GOOD. ALTHOUGH METALLURGICAL TESTING IS NOT YET COMPLETE, PRELIMINARY INDICATION IS THAT STRESS CORROSION CRACKING CONTRIBUTED TO THE INCIDENT. CORROSION IN A DENT OF THE PIPE RESULTED IN AN APPROXIMATE 1-1/2"LONG CRACK THROUGH WHICH GAS LEAKED. SUPPLEMENTAL REPORT SUBMITTED 11/27/96INDICATES STRESS CORROSION CRACKING CONTRIBUTED TO THE INCIDENT. CORROSION INA DENT OF THE PIPE RESULTED IN AN APPROXIMATE 1 1/2 INCH LONG CRACK THROUGHWHICH GAS LEAKED. VISIBLE EXTERNAL CRACKS - COATING AT THIS PARTICULAR JOINTON THE PIPELINE WAS POOR. HOWEVER COATING ON THE ADJACENT PORTIONS OF THEPIPELINE WAS REPORTED TO BE GOOD. FINAL METTALURGICAL ANALYSIS INDICATES THATTHE STRESS CORROSION CRACKING IS OF THE HIGH PH VARIETY. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
845 | 1996-05-20 | TX | other | UNKNOWN (SUTTON COUNTY) | VALERO TRANSMISSION CO | FORENSIC ENGINEERING AND METALLURGICAL EXPERTS ARE CURRENTLY REVIEWING THEINCIDENT TO DETERMINE THE CAUSE OF THE NATURAL GAS RELEASE AND FIRE. ASUPPLEMENTAL REPORT WILL BE FILED UPON COMPLETION OF THE INVESTIGATION. ASUPPLEMENTAL REPORT RECEIVED 1/24/97 INDICATES THAT THE INVESTIGATION INTO THECAUSE OF THE FIRE THAT OCCURRED AT THE SONORA COMPRESSOR STATION ON MAY 20,1996 IS STILL OPEN AND IT APPEARS THAT WE WILL NEVER BE ABLE TO CONCLUSIVELYDETERMINE THE SEQUENCE OF EVENTS THAT CAUSED THE FIRE. A TEAM COMPOSED OF (1)A FORENSIC ENGINEERING CONSULTANT, BEARD ENGINEERING; (2) METALLURGICALEXPERTS, BRYANT/LEE ASSOCIATES AND METALLURGICAL CONSULTANTS; AND (3) COMPANYPERSONNEL HEADED BY JOHN SOMMER CONDUCTED AN EXHAUSTIVE INVESTIGATION OF THEFIRE AND CONCLUDED THAT THE MOST PROBABLE CAUSE OF THE INCIDENT WAS THEMECHANICAL FAILURE OF AN 1/2" TUBING CONNECTION ON THE UNIT 612 VALVE OPERATORPOWER GAS SUPPLY MANIFOLD. FORENSIC AND METALLURGICAL TESTS OF ALL OTHERMECHANICALLY FAILED EQUIPMENT REVEALED THAT THE FAILURES WERE CAUSED BY THEINTENSE HEAT OF THE FIRE AND WERE NOT THE CAUSE OF THE INCIDENT. PROPERTYDAMAGE FOR THIS INCIDENT ROSE FROM $3,250,000 TO $4,000,000. | 4000000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
846 | 1996-06-13 | MT | other | UNKNOWN (ROOSEVELT COUNTY) | WILLISTON BASIN INTERSTATE PIPELINE CO | ON JUNE 13, 1996, WILLISTON BASIN EMPLOYEES WERE COMPLETING A 3800 FOOT RELOCATION ON WILLISTON BASIN'S SACO TO MORGAN CREEK EIGHT INCH PIPELINE TO ACCOUMMODATE FUTURE HIGHWAY RECONSTRUCTION. THE RELOCATION PROJECT WAS NEARLY COMPLETE EXCEPT FOR THE TIE-INS TO THE EXISTING LINE AT EACH END. AT 7:00 AM AN EIGHT INCH VALVE (VALVE #14) WAS CLOSED ON THE NORTH END AND AT 9:30 AM TWO MAINLINE EIGHT INCH VALVES WERE SHUT TO ALLOW TIE-IN AT THE SOUTH END. THE VALVES WERE GREASED TO STOP ANY LEAKAGE AND THE LINE WAS BLOWN DOWN. THE NORTH TIE-IN WAS TO BE LOCATED WITHIN THIRTY FEET OF A VALVE BOX WHICH HOUSED VALVE #14. LINE PRESSURE WAS APPROXIMATELY 548 PSIG UPSTREAM OF VALVE #14 AT THE TIME OF THE INCIDENT. THE VALVE BOX ALSO CONTAINED A THREE INCH PIPELINE TAKEOFFWHICH SUPPLIES GAS TO THE TOWN OF POPLAR, MONTANA, APPROXIMATELY SIXTEEN MILES NORTHEAST. TIE-IN WORK PROCEEDED WITH A CREW AT EACH END OF THE RELOCATION. THE CREW ON THE NORTH SIDE OF THE RIVER PROCEEDED WITH THE TIE-IN BY MAKINGTWO CIRCUMFERENTIAL CUTS APPROXIMATELY 4-5 INCVHES APART. THE WELDER THEN PROCEEDED DOWN THE PIPELINE APPROXIMATELY 15-18 FEET AND MADE ANOTHER CUT. THE WELDER THEN RETURNED TO THE ORIGINAL CUTS AND WITH A HAND TORCH STARTED CUTTING THE SMALL SEGMENT INTO THREE PIECES. THE TWO SEGMENTS ON TOP OF THE PIPE WERE KNOCKED OUT FIRST. AT APPROXIMATELY 10:15 AM WHEN THE BOTTOM SEGMENT WAS KNOCKED OUT THE TWO OPEN ENDS OF THE PIPELINE SLAMMED TOGETHER. THE CREW IMMEDIATELY REALIZED THAT SOMETHING HAD PARTED UPSTREAM AND THERE WAS A LOUD ROARFROM GAS BEING RELEASED ON THE OTHER SIDE OF THE VALVE BOX. THE CREW EVACUATED THE AREA IMMEDIATELY. THE GAS IGNITED WITHIN SECONDS OF THE RELEASE CONSUMING THE VALVE BOX AND ASSOCIATED PIPELINE EQUIPMENT THAT WAS PARKED ADJACENT TO THE WORK AREA. CREWS IMMEDIATELY RESPONDED BY SHUTTING THE EIGHT INCH PIPELINE IN UPSTREAM AT THE NEXT VALVE APPROXIMATELY SIX MILES AWAY AT VALVE NUMBER 13 AT THE WOLFPOINT TAKEOFF. ANOTHER CREW ALSO SHUTIN THE THREE INCH PIPELINE THAT RUNS TO POPLAR MONTANA AT THE CLOSEST MAINLINE VALVE APPROXIMATELY TWO MILES AWAY. AT 10:35 AM THE PIPELINE WAS SHUTIN AND WAS BLOWING DOWN. AT 10:45 AM LAW ENFORCEMENT OFFICALS ARRIVED AND STARTED CONTROLLING TRAFFIC SINCE THIS LOCATION IS APPROXIMATELY 200 FEET FROM MONTANA HIGHWAY 13. THE LOCAL FIRE DEPARTMENT ARRIVED AT 10:45 AM AND WERE INSTRUCTED TO STANDBY UNTIL THE PIPELINE HAD BLOWN DOWN. AT 11:00 AM THE FIRE DEPARTMENT PUT OUT SOME GRASS FIRES AND AT 11:15 AM THE FIRE DEPARTMENT EXTINGUISHED THE FIRES ASSSOCIATED WITH PIPELINE EQUIPMENT AND THE VALVE BOX. AT APPROXIMATELY 11:50 AM COMPANY PERSONAL BEGAN SURVYING THE AREA AND DISCOVERED A CRATER ABOUT FIFTEEN FEET INDIAMETER AND SIX FEET DEEP WITH A SHORT STYLE 38 DRESSER COUPLING PARTED FROM THE PIPELINE AT THE BOTTOM OF THE CRATER. THE LOCATION WHERE THE COUPLING PARTED WAS APPROXIMATELY THIRTEEN FEET UPSTREAM FROM THE VALVE BOX THAT HOUSEDTHE POPLAR TAKEOFF AND VALVE #14.THE NORTH CREW CONSISTED OF SEVEN COMPANY EMPLOYEES. ONLY ONE MINOR PERSONAL INJURY WAS REPORTED AS A RESULT OF THIS INCIDENT WHICH CONSISTED OF A JAMMED FINGER RECEIVED WHILE AN EMPLOYEE WAS EVACUATING THE SCENE. AT 5:10 PM TEMPORARY REPAIRS WERE MADE, WELDS WERE X-RAYED AND PURGING BEGAN. THE LINE WAS PRESSURED TO 120 PSIG AND HELD THERE UNTIL A LEAK SURVEY WAS COMPLETED ON APPROXIMATELY 800 FEET OF PIPELINE UPSTREAM OF THE LOCATION OF THE INCIDENT. NO PROBLEMS WERE FOUND AND AT THIS POINT ALL VALVES WERE OPENED AND THE PIPELINE WAS RETURNED TO NORMAL SERVICE. THE ONLY INTERRUPTION OF SERVICE WAS ASSOCIATED WITH FARMTAP CUSTOMERS ALONG THE RIGHT-OF-WAY. DAMAGES WERE SIGNIFICANT DUE TO THE GAS IGNITING, PROBABLY DUE TO STATICELECTRICITY OF FLYING DEBRIS CREATING A SPARK, AND THE CLOSE PROXIMITY OF PARKED COMPANY EQUIPMENT. DAMAGES AMOUNTED TO $184,000 WITH THE MAJORITY OF EXPENSES ASSOCIATED WITH FIRE DAMAGE TO TWO WELDING TRUCKS, A BACKHOE/LOADER, A TRUCK MOUNTED CRANE, AND A PICKUP. | 184000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
847 | 1996-05-21 | TX | other | UNKNOWN (HARDIN COUNTY) | TRUNKLINE GAS CO | #4025-B4 SUCTION EMERGENCY SHUT DOWN SYSTEM BLOWDOWN VALVE OPENED DUE TO A DEVICE FAILURE. | 86100 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
848 | 1996-06-19 | KY | maintenance | UNKNOWN ( COUNTY) | TENNESSEE GAS PIPELINE CO | COMPRESSOR ROD BROKE, DAMAGING THE PACKING, RESULTING IN THE RELEASE OF GAS INTO THE COMPRESSOR BUILDING. | 412500 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
849 | 1996-06-25 | LA | leaks and spills | UNKNOWN (UNION COUNTY) | NORAM GAS TRANSMISSION | FAILURE BEGAN FROM PIT ON BOTTOM OF PIE AND PROPAGATED VERTICALLY AROUND THECIRCUMFERENCE OF PIPE. | 22000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
850 | 1996-06-16 | OK | leaks and spills | UNKNOWN (HARPER COUNTY) | WILLIAMS NATURAL GAS CO | PIPE SEGMENT FAILURE ANALYST TO BE COMPLETED BY 07/30/96. GENERAL CORRISION OF WELD SEAM- FAILURE ANALYST NOT COMPLETED AS OF THIS DATE. | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
851 | 1996-06-24 | LA | other | UNKNOWN ( COUNTY) | TENNESSEE GAS PIPELINE CO | THE PIPELINE CROSSES BURRWOOD BAYOU. THIS BAYOU HAS ENLARGED FROM 100'WIDE AND 15' DEEP TO OVER 1100' WIDE AND 30' DEEP. THE LINE WAS SUSPENDED IN THE BAYOU AND THEN FAILED. | 110000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
852 | 1996-06-28 | KS | leaks and spills | UNKNOWN (RENO COUNTY) | PANHANDLE EASTERN PIPELINE CO | UNDER INVESTIGATION | 430000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
853 | 1996-07-07 | LA | leaks and spills | UNKNOWN ( COUNTY) | TENNESSEE GAS PIPELINE CO | BUBBLES WERE DISCOVERED BY THE PRODUCER 100 YARDS OFF PLATFORM. LEAK WAS A PIN HOLE AT THE 6 O'CLOCK POSITION CAUSED BY INTERNAL CORROSION. LEAK WAS AT 6O'CLOCK POSITION - PIN HOLE LEAK. | 80000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
854 | 1996-08-12 | LA | other | UNKNOWN ( COUNTY) | TRUNKLINE GAS CO | ANCHOR FROM DIVE BOAT RUPTURED 12" LINE 319B-1500. | 830000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
855 | 1996-08-28 | LA | other | UNKNOWN (PLAQUEMINES COUNTY) | KOCH GATEWAY PIPELINE CO | 16" VENICE JCT-CHALMETTE LINE RUPTURED ON LAKE PETIT, LAT 29DEG43.4', LONG 89DEG47.6, SEC 28, T-15-S, R-14-E, PLAQUEMINES PARISH, LA. INSPECTION OF FAILED PIPE REVEALED MECHANICAL DAMAGE AT MULTIPLE POINTS IN CENTER OF NAVIGATIONAL CHANNEL. LIKELY CAUSED FROM CONTACT WITH MARINE TRAFFIC AT SOME PREVIOUS TIM | 264014 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
856 | 1996-08-29 | TX | other | UNKNOWN (WHARTON COUNTY) | TRUNKLINE GAS CO | 8/29/96 10:15 A.M. - NOTIFIED OF CROSSING LOCATION AND SCHEDULED TO MEET ON SITE 9/30/96 TO LOCATE AND MARK FACILITIES. TRANS TEXAS STRUCK 20" LINE 100-1WITH TRENCHER WHILE CROSSING TRUNKLINE FACILITIES. | 65000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
857 | 1996-09-03 | LA | leaks and spills | UNKNOWN ( COUNTY) | TRUNKLINE GAS CO | PIPE BODY 1/4" HOLE AT 6 O'CLOCK. CATHODIC P/S .982V - BATCH TREAT WITH BIOCIDE ON AN AS NEEDED BASIS. LEAK ON 12" LINE 1000 - 4B - 1100. | 250000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
858 | 1996-08-29 | MT | other | UNKNOWN (CARBON COUNTY) | MONTANA POWER CO | THIRD PARTY DOZER WITH RIPPER TOOTH SNAGGED MONTANA POWER COMPANY 4" RED LODGE NATURAL GAS TRANSMISSION PIPELINE. LINE PARTED AT GIRTH WELD. NO INJURIES.NO DAMAGE AT SITE. MONTANA POWER HAD TO RELIGHT TOWN OF RED LODGE. 1500 CUSTOMERS. STATUTE REQUIRES THEY CONTACT 1-CALL. | 93000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
859 | 1996-09-10 | NM | leaks and spills | UNKNOWN (CHAVES COUNTY) | EL PASO NATURAL GAS CO | A SEGMENT OF OUR LINE NO. 1300 RUPTURED, BLOWING OUT 26 FEET OF PIPE, MOST OF IT IN A SINGLE SEGMENT WHICH LANDED 100 FEET FROM THE PIPELINE. | 240000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
860 | 1996-09-17 | WI | other | UNKNOWN (LACROSSE COUNTY) | NORTHERN NATURAL GAS CO (ENRON) | CONTRACTOR BUILDING A LOGGING ROAD DID NOT CALL ONE-CALL AND TORE A HOLE IN THE PIPE WITH A DOZER BLADE. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
861 | 1996-09-04 | TX | maintenance | UNKNOWN (HENDERSON COUNTY) | LONE STAR GAS CO | FAILURE APPEARS TO HAVE OCCURED AT A MECHANICAL COUPLING AND INCLUDED FAILUREOF ALL OR MOST OF THE 439 FT. SEGMENT. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
862 | 1996-09-28 | CA | other | UNKNOWN (COLUSA COUNTY) | PACIFIC GAS & ELECTRIC CO | THE PIPELINE PRESSURE WAS SLOWLY BEING RAISED FROM 575 PSIG TO ACCOMMODATE AFUTURE SHUTDOWN. THE PIPELINE RUPTURED WHEN THE PRESSURE REACHED 760 PSIG. THE NORMAL OPERATING PRESSURE FOR THIS LINE RANGES FROM 550 TO 800 PSIG. THE RUPTURED LINE DID HAVE EXTERNAL THIRD PARTY DAMAGE. THE ACTUAL FAILURE CAUSE AND SOURCE OF EXTERNAL DAMAGE IS CURRENTLY UNDER INVESTIGATION. | 500000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
863 | 1996-10-12 | TX | other | UNKNOWN (REEVES COUNTY) | DELHI GAS PIPELINE CORP | 49 USC SECTION 60123(D) | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
864 | 1996-10-04 | MN | other | UNKNOWN (CARVER COUNTY) | NORTHERN NATURAL GAS CO (ENRON) | CONTRACTOR HIT PIPELINE WITH A TILING MACHINE. DID NOT CALL "ONE-CALL". | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
865 | 1996-10-02 | TX | other | UNKNOWN (HARRISON COUNTY) | TEXAS GAS GATHERING INC | PIGGING THE 16 INCH LINE (TEXAS GAS GATHERING). FLOWING CONDENSATE AND PIG WASTES INTO 3 FRAC TANKS AND 2 STOCK TANKS FROM SLUDGE CATCHER, AT BULLARD JUNCTION COMPRESSOR STATION-TGG. FILLED UP ALL FRAC TANKS AND STOCK TANKS WITH FLUID, FROM SLUDGE CATCHER. SHUT SLUDGE CATHCHER IN. (NO FLOW TO TANKS). BEFORE BRINGING IN HAUL TRUCKS, LET GAS VAPOR AROUND TANKS DISSIPATE. (APPROX 45 MINUTES TO 1 HOUR). C&S TRUCK (HAUL TRUCK) PULLED UP TO FRAC TANKS, TO HAUL OUT OF MIDDLE FRAC TANK. TRUCK WAS 90% LOADED. A BLUE FLAME COULD BE SEEN LOW TO THE GROUND COMING AROUND REAR OF FRAC TANK. THE FLAME COULD BE SEEN GOING UP EXHAUST STACK ON MACK TRUCK. THE FLAME THEN PROCEEDED TO COME UP FROM UNDERTHE TRUCK AND THEN FLASH BURN, THE DRAFT INTO WOODS. (LASTED APPROX 2 SECONDS). AN EMPLOYEE WAS CAUGHT UP IN THE FLASH BURN, RECEIVED 2ND DEGREE BURNS TO15% OF HIS BODY. CAUSE OF ACCIDENT: 1. WEATHER CONDITIONS (VERY HUMID, AND NO WIND). 2. ONLY IGNITION SOURCE LOCATED WAS THE EXHAUST MANIFOLD ON THE MACKTRUCK. 3. STATIC ELECTRICITY. | 2000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
866 | 1996-10-06 | LA | other | UNKNOWN ( COUNTY) | VASTAR RESOURCES, INC | SHEAR JOINT (INSTALLED AUG. 1996) SEPARATION CAUSED BY MUDSLIDE DURING HURRICANE JOSEPHINE. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
867 | 1996-10-06 | LA | other | UNKNOWN ( COUNTY) | VASTAR RESOURCES, INC | DIVERS INSPECTED BREAK ON 10/21/96 & CONFIRMED THAT LINE PARTED @ THE DESIGNED WEAK LINK (BREAK-AWAY JOINT). MUD SLIDES LEFT APPROX 100' AND SEPARATION. ONE END OF THE LINE WAS BURIED DEEPER & WAS NOT LOCATED BECAUSE OF THE ONSET OF BAD WEATHER. THE BREAK-AWAY JOINT WILL BE REPLACED & A REPLACEMENT SECTIONOF PIPE WILL BE FABRICATED. PART 3 - LINE PARTED @ A BREAK-AWAY JOINT INSTALLED IN THE LINE. BELIEVED TO HAVE BEEN CAUSED BY A MUD SLIDE TRIGGERED BY TROPICAL STORM JOSEPHINE. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
868 | 1996-10-04 | TX | leaks and spills | UNKNOWN ( COUNTY) | KOCH GATEWAY PIPELINE CO | DAMAGED PIPE SENT TO METALLURGIST CONSULTANT TO DETERMINE CAUSE OF RUPTURE. RESULTS NOT RECEIVED. ADDITIONAL INFORMATION IS BEING OBTAINED TO HELP US ASSESS THE CAUSE AND FACTORS CONTRIBUTING TO THE INCIDENT, AND UPON RECEIVING, WE WILL PROVIDE A NARRATIVE DESCRIPTION OF THE RESULTS. | 500000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
869 | 1996-10-13 | WI | other | UNKNOWN (JACKSON COUNTY) | NORTHERN NATURAL GAS CO (ENRON) |  | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
870 | 1996-10-20 | GA | other | UNKNOWN (SUMTER COUNTY) | SOUTH GEORGIA NATURAL GAS CO | A VEHICLE WHOSE DRIVER LOST CONTROL, LEFT THE HIGHWAY AND PASSED THROUGH EXISTING BARRICADES, PENETRATING AMERICUS #1 METER STATION'S CHAIN LINK FENCE. THE VEHICLE STRUCK THE RTU MOUNTING POST, BREAKING OFF INSTRUMENTATION LINES, IGNITING THE ESCAPING GAS. THE NEARBY REGULATOR WAS EVENTUALLY DAMAGED BY THEFIRE CAUSING A REGULATOR FAILURE AND ACTIVATION OF THE OVERPRESSURE RELIEF VALVE RESULTING IN AN ADDITIONAL IGNITION SOURCE. THE METER STATION, CONSUMED IN FIRE, WAS EXTENSIVELY DAMAGED. THE DRIVER OF THE VEHICLE ESCAPED UNHARMED.MILE POST: 16.891 ON LINE #6 - AMERICUS #1 METER STATION. ESTIMATED PRESSURE: INLET 950 PSIG - DELIVER 150 PSIG. PART B -DAMAGE BY OUTSIDE FORCES 2(B): P/L MARKERS, SIGNS ON FACILITY FENCE, BARRICADES. ADDITIONAL INFO: INCIDENT RESULTED FROM VEHICULAR ACCIDENT. PRIOR NOTIFICATION PROCEDURE WAS NOT APPLICABLE. | 125000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
871 | 1996-10-18 | LA | leaks and spills | UNKNOWN ( COUNTY) | TRUNKLINE GAS CO |  | 67400 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
872 | 1996-10-26 | TX | other | UNKNOWN (SOUTH ADDITION COUNTY) | ANR PIPELINE CO | THE CAUSE OF THE LEAK HAS NOT YET BEEN DETERMINED. WE ARE PRESENTLY EVALUATING VARIOUS REPAIR OPTIONS. A SUPPLEMENTAL REPORT WILL FOLLOW UPON RESOLUTION OFTHESE UNKNOWN ISSUES. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
873 | 1996-10-23 | LA | other | UNKNOWN ( COUNTY) | TENNESSEE GAS PIPELINE CO | DREDGER NOTIFIED OPERATOR ON 10/18/96 FOR DREDGING ON 10/19/96 AND 10/20/96.THEY DID NOT NOTIFY OPERATOR THAT THEY HAD MOVED BACK TO AREA ON 10/23/96. NARRATIVE DESC: SPUD ON DREDGER HIT LINE 526A-300 (12"). GAS CAUGHT FIRE, DREDGE WAS BURNING. | 225000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
874 | 1996-11-01 | MT | other | UNKNOWN (MISSOULA COUNTY) | MONTANA POWER CO | REPORT OF TRANSMISSION PIPELINE INCIDENT WHICH OCCURRED ON THE MONTANA POWERCOMPANY NATURAL GAS TRANSMISSION SYSTEM NEAR MISSOULA, MONTANA ON NOVEMBER 1, 1996. THE INCIDENT WAS SUBJECT TO TELEPHONIC REPORTS MADE TO JOEL TIERNEY OF THE MONTANA PUBLIC SERVICE COMMISSION AND TO THE NATIONAL RESPONSE CENTER (UNDER INCIDENT #366368) ON NOVEMBER 1, 1996. THIRD PARTY CONTRACTOR EXCAVATING FOR NEW PARKING LOT, PUNCTURED MPC 8" BONNER-STONE NATURAL GAS TAPLINE WITHA FRONT END LOADER. NO FIRE, EXPLOSION, OR INJURIES. VALVE, TYPE: V4-8" FIG 34449 1/2 ROCKWELL. MT CODE ANNOTATED: TITLE 69 CHAPTER 4 PART 5 "EXCAVATIONSNEAR UNDERGROUND FACILITIES". | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
875 | 1996-11-16 | OK | leaks and spills | UNKNOWN (BEAVER COUNTY) | NATURAL GAS PIPELINE CO OF AMERICA | PIPELINE RUPTURE OF NO.2 - 26" MAINLINE DUE TO EXTERNAL CORROSION. | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
876 | 1996-11-29 | WI | other | UNKNOWN (JUNEAU COUNTY) | NORTHERN NATURAL GAS CO (ENRON) | LINE HIT BY A BACKHOE ENLARGING A DRAIN DITCH. | 53750 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
877 | 1996-11-11 | AZ | other | UNKNOWN (MARICOPA COUNTY) | EL PASO NATURAL GAS CO | THE BUCKEYE RURAL FIRE DEPT. RESPONDED TO A FIRE AT THE RAINBOW VALLEY METERSTATION. THE FIRE CONTINUED TO BURN UNTIL VALVE SECTION VA 72 AND VA 73 ON LINE NO. 1103 WAS SHUT IN. INVESTIGATION REVEALED THAT THE INCIDENT WAS A RESULT OF VANDALISM. THE COUNTY SHERIFF'S DEPT. IS INVESTIGATING THE INCIDENT. SINCE VANDALISM WAS INVOLVED, EL PASO REPORTED THE INCIDENT TO THE FBI; HOWEVER, BECAUSE THE SHERIFF'S DEPT. IS ALREADY INVESTIGATING THE INCIDENT THEY DECLINED TO PROCEED WITH ANY FURTHER INVESTIGATION. VANDALISM REPORTED TO THE FBI. | 60000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
878 | 1996-11-17 | LA | other | UNKNOWN ( COUNTY) | VASTAR RESOURCES, INC. | AN APPARENT RELEASE FROM THE PIPELINE WAS DETECTED DUE TO WATER TURBULENCE SPOTTED DURING A HELICOPTER FLY-OVER OF THE LINE. THERE WERE NO INJURIES OR FATALITIES ASSOCIATED WITH THE SUNDAY, NOVEMBER 17, 1996 APPARENT RELEASE, AND TEH CAUSE HAS NOT YET BEEN DETERMINED. DIVERS BEGAN THE PROCESS OF ATTEMPTINGTO LOCATE THE PIPELINE IN THE VICINITY OF THE APPARENT RELEASE ON MONDAY, NOVEMBER 18, 1996 TO DETERMINE ITS CAUSE. IN ATTEMPTING TO DO SO, THE FATALITY OF A DIVER OCCURRED ON THURSDAY NOVEMBER 28, 1996. WHILE NOT RESULTING FROM THE PIPELINE LEAK OR REPAIR, AND NOT BELIEVED TO FALL WITHIN THE REPORTING REQUIREMENTS OF 49 CFR SECTION 191.5 OR 191.15, THIS FATALITY IS BEING REPORTED TO ENSURE COMPLETION OF DOT RECORDS. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
879 | 1996-11-11 | LA | other | UNKNOWN ( COUNTY) | ANR PIPELINE CO | ANCHOR HIT PIPELINE, GOUGE IN DENT WAS LEAKING AT 3 O'CLOCK POSITION, WHICHRESULTED IN THE LEAK. REPLACE D WITH 22'-4" OF 10" PIPE, 0.348 W.T. OCCURRED11/11/96, 1900 HOURS EST. | 135000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
880 | 1996-11-19 | LA | maintenance | UNKNOWN ( COUNTY) | TENNESSEE GAS PIPELINE CO | CLAMP ON VALVE OPERATOR LEAKING AND POSSIBLE CRACK IN BODY OF THE VALVE. BUBBLES DISCOVERED AT OR NEAR 523M-2901 SUBSEA ASSEMBLY. DIVE BOAT ON SITE 11/20/96 AND ABLE TO LOCATE AREA ONLY. CHEVRON, JACK DUPRE INITIALLY NOTICED BUBBLES. TGP - ALLEN ASHLEY 3:00PM 11/21/96 LOOKED LIKE TGP. REPORTED 11/25/96 WAITED BECAUSE OF NOT BEING SURE IF LEAK WOULD BE GREATER THAN $50,000. | 80000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
881 | 1996-11-24 | AL | other | UNKNOWN (CALHOUN COUNTY) | SOUTHERN NATURAL GAS CO | A LEAK OCCURRED IN THE PIPE THREADS OF 1" PIPE AT ITS CONNECTION TO A 1" THREADED COUPLING. NEARBY RESIDENTS REPORTED THE LEAK TO THE LOCAL FIRE DEPARTMENT, WHICH PROMPLTY EVACUATED THE AREA. THE CAUSE OF THE LEAK IS UNKNOWN AT THIS TIME. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
882 | 1996-11-28 | MN | maintenance | UNKNOWN (OLMSTED COUNTY) | NORTHERN NATURAL GAS CO (ENRON) | PIPE SUBMITTED FOR METALLURGICAL ANALYSIS TO DETERMINE CAUSE OF FAILURE. | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
883 | 1996-02-10 | MI | other | UNKNOWN (LENAWEE COUNTY) | ANR PIPELINE CO | THE FAILURE WAS THE RESULT OF EXTERNAL DAMAGE TO THE PIPELINE THAT MOSTPROBABLY OCCURRED FOUR MONTHS EARLIER DURING OUR OWN MAINTENANCE ACTIVITIESTHAT WE CONDUCTED IN THIS AREA. | 450000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
884 | 1996-12-07 | CA | other | UNKNOWN (FRESNO COUNTY) | PACIFIC GAS & ELECTRIC CO | PART B- WOODEN LATHES WITH YELLOW RIBBON. A TRACK-WHEELED CATERPILLAR WITH A6' RIPPER DUG INTO TRANSMISSION LINE 300A AT APPROX MILE POST 374.5, HARRISRANCH, RURAL AREA NEAR COALINGA. EXCAVATOR WAS WORKING FOR HARRIS RANCH. | 78000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
885 | 1996-07-22 | CA | other | UNKNOWN (COLUSA COUNTY) | PACIFIC GAS & ELECTRIC CO | OPERATOR OF TRACTOR/RIPPER RIPPED INTO TRANSMISSION LINE CAUSING TRACTOR TO BE BLOWN INTO AIR. OPERATOR WAS INJURED AND TAKEN TO HOSPITAL. OPERATOR RELEASED FROM HOSPITAL 7/23/96. | 64000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
886 | 1996-12-03 | TX | other | UNKNOWN (DUVAL COUNTY) | VALERO TRANSMISSION CO | GAS COMPRESSOR UNIT 98 HAD A VALVE COVER BLOW OFF CAUSING A FIRE. THE FIRE BLEW ACROSS UNIT 94 CAUSING THE COVER ON THE COMPRESSOR CRANKCASE TO BLOW OFF.UNITS 98, 94 AND 188 HAD FIRE DAMAGE. THE COMPRESSOR BUILDING WAS HEAVILY DAMAGED. MATERIALS INVOLVED: COMPRESSOR UNITS & COMPRESSOR BUILDING | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
887 | 1996-12-23 | AL | other | UNKNOWN (MOBILE COUNTY) | KOCH GATEWAY | CONTRACTOR WAS CAUTIONED TO NOTIFY KOCH PRIOR TO WORKING ON ROW, HOWEVER THEY DID BEGIN WORKING PRIOR TO NOTIFYING KOCH. CONTRACTOR WORKING OVER KOCH'S ROW WITHOUT PRIOR APPROVAL FROM KOCH. ALSO, CONTRACTOR HAD REMOVED SIGN PRIOR TO DIGGING. | 81425 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
888 | 1996-12-10 | KS | leaks and spills | UNKNOWN (LEAVENWORTH COUNTY) | WILLIAMS NATURAL GAS CO | FAILURE ANALYSIS TO BE COMPLETED IN 4 TO 6 WEEKS; 20' "T" DRIP FAILED ON LINE "EJ" | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
889 | 1997-01-10 | OK | other | UNKNOWN (BRYAN COUNTY) | TRANSOK INC | PILOT REGULATOR ON RELIEF VALVE FAILED CAUSING RELIEF VALVE TO OPEN. | 58064 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
890 | 1996-10-30 | MI | other | UNKNOWN (ST. CLAIR COUNTY) | GREAT LAKES GAS TRANSMISSION CO | THERE WAS NO ADVERSE IMPACT ON PERSONS OR PROPERTY FROM THE VENTED GAS. IN ADDITION, IT WAS NOT ANTICIPATED IMMEDIATELY FOLLOWING THE EVENT THAT THE COSTOF CLEANUP WOULD EXCEED $50,000. HOWEVER, SINCE THE NUMBER OF CLAIMS MADE TOGREAT LAKES FOR CLEANUP OF THE LIQUID HAS ESCALATED, ESTIMATED EXPENDITURES BY GREAT LAKES TO REMOVE THE LIQUID FROM THE AREA ARE NOW IN THE RANGE OF $135,000. (IT IS LIKELY THAT ACTUAL DAMAGES TO PROPERTY, LOSS IN VALUE FROM THE INCIDENT, ARE LESS THAN $50,000, THOUGH THE CLEAN-UP AND INSPECTION COSTS AREHIGHER.) THIS REVISION IN ESTIMATED EXPENDITURES, THEREFORE, HAS PROMPTED GREAT LAKES TO FILE THE INCIDENT REPORT MENTIONED ABOVE, IN THE EVENT THE REPORTMIGHT OTHERWISE BE REQUIRED. SEE ORIGINAL REPORT FOR DETAILS OF EVENTS. | 135000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
891 | 1996-12-27 | OK | other | UNKNOWN (TULSA COUNTY) | OKLAHOMA NATURAL GAS CO | CONSTRUCTION WAS NOT SUPPOSE TO BEGIN UNTIL 12/31/96. ONE-CALL WAS NOTIFIED AT 9:00 12/29/96 AND LINE WAS HIT AT 11:50 ON 12/29/96. LANDOWNER MADE A ONE-CALL REQUEST FOR WORK BEGINNING 12/31/96. CONTRACTOR STARTED WORK EARLY AND HIT THE LINE WHILE BURYING BRUSH. SUPPLEMENTAL REPORT RECEIVED 3/4/97 CHANGESONE CALL NOTIFICATION TO 9:00 ON 12/27/1996 AND LINE WAS HIT AT 11:50 ON12/27/1996. | 80798 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
892 | 1997-01-02 | AL | other | UNKNOWN (MOBILE COUNTY) | TRANSCO GAS PIPELINE CORP | THE SIZE AND SHAPE OF THE GAUGE (12") INDICATES IT WAS CAUSED BY A LARGE PIECE OF EXCAVATION EQUIPMENT (PROBABLY) A BACKHOE. LEAK INITIATED IN GAUGE OFUNKNOWN ORIGIN. | 75515 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
893 | 1997-01-07 | GA | maintenance | UNKNOWN (CARROLL COUNTY) | SOUTHERN NATURAL GAS CO | SEAL IN COUPLING APPEARS TO HAVE FAILED RESULTING IN A LEAK WHICH, AFTER A SHORT PERIOD OF TIME, BLEW ENOUGH SOIL AWAY TO DECREASE OVERBURDEN ALLOWING PIPE TOPULL OUT OF COUPLING. IT IS BELIEVED THAT A SEAL FAILED IN A MECHANICALCOUPLING RESULTING IN A LEAK WHICH, OVER A SHORT PERIOD OF TIME, REMOVED THESOIL COVER OVER THE PIPE. THIS DECREASED THE OVERBURDEN LOAD THAT KEPT IN PIPEAND COUPLING INTACT, ALLOWING THE PIPE TO BLOW OUT OF THE COUPLING, RELEASINGNATURAL GAS. THERE WAS NO GAS IGNITION. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
894 | 1996-07-22 | MO | leaks and spills | UNKNOWN (CASS COUNTY) | PANHANDLE EASTERN PIPELINE CO | GENERAL EXTERNAL CORROSION IN AN AREA OF DISBONDED COATING. INCIDENT LOCATION: 1/2 MI EAST & 1/2 MI SOUTH OF KANSAS-MISSOURI LINE & HIGHWAY 2. | 180000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
895 | 1997-01-26 | CA | other | UNKNOWN (SANTA CRUZ COUNTY) | PACIFIC GAS & ELECTRIC CO | HEAVY RAINFALL CAUSED LARGE MUDSLIDE THAT CAUSED LINE RUPTURED. | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
896 | 1997-01-20 | WV | other | UNKNOWN (KANAWHA COUNTY) | CNG TRANSMISSION CORP | BATTLE RIDGE CONSTRUCTION COMP CALLED THE MORNING OF 1/20/97 AND REPORTED THEY SMELLED GAS NEAR THEIR CONSTRUCTION AREA. CNGT PERSONNEL INVESTIGATED AND FOUND LEAK BLOWING ON TL-272. ISOLATED SECTION, EVACUATED GAS, FOUND SPLIT INPIPE APP. 2"LX1/4W. FAILURE WAS CAUSED BY LARGE SPOIL PILE ON LINE BY CONTRACTOR. COMP PRODUCTION: $45,950.00 - GATHERING: $3200.00. | 83200 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
897 | 1997-01-19 | PA | other | UNKNOWN (GREENE COUNTY) | CNG TRANSMISSION CORP | A COMBINATION OF CONDENSATION AND EXTREMELY COLD TEMPERATURES CAUSED THE AXELSON R/V TO FAIL @ A PRESSURE BELOW THE SET POINT OF 1008 PSIG. R/V COULD NOTRE-SEAT DUE TO A ROLLED O-RING. APPARENT CAUSE: WEATHER CONDITIONS. RELIEFVALVE, TYPE H-L, SN#8632. | 62475 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
898 | 1997-02-09 | WA | other | UNKNOWN (COWLITZ COUNTY) | NORTHWEST PIPELINE CORP | AXIAL SOIL LOADING ON THE PIPE CREATED LOADING IN EXCESS OF THE GIRTH WELD STRENGTH, PULLING THE PIPELINE APART WITH A CLEAN BREAK AT THE GIRTH WELD WHICH RESULTED IN RAPID GAS LOSS AND IGNITION. | 195000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
899 | 1997-02-08 | WA | other | UNKNOWN (WHATCOM COUNTY) | NORTHWEST PIPELINE CORP | LAND MOVEMENT FROM SIDE SLOPE PLACED LATERAL LOAD ON PIPELINE WHICH EXCEEDEDTHE YIELD STRENGTH, CAUSING THE PIPELINE TO RUPTURE. THE LINE RUPTURE OCCURRED ON 2/8/97, AT 11:20PM, MST. THE TELEPHONIC NOTICE WAS MADE AT 1:05 AM, MST02/09/97. | 375000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
900 | 1997-02-08 | LA | other | UNKNOWN (ST. MARY COUNTY) | BRIDGELINE GAS DISTRIBUTION CO | ATHENA SPUD BARGE SPUDDED DOWN NEAR THE 20" PIPELINE. INCLEMENT WEATHER MOVEDTHE SPUD BARGE INTO THE PIPELINE CAUSING THE RUPTURE. THE LEAK OCCURRED IN THE ATCHAFALAYA BAY IN ST. MARY PARISH, LA AT APPROX 5:30 A.M. FROM A 20" NATURAL GAS PIPELINE. THE LEAK WAS THE RESULT OF DAMAGE INCURRED FROM A "JACK-UP"TYPE BARGE DURING INCLEMENT WEATHER AS SHOWN ON THE ATTACHED REPORT FROM RSPA F7100.2. ESTIMATES OF REPAIRS ARE $200,000. THERE WERE NO INJURIES, FATALITIES, OR POLLUTION, AND AT NO TIME WAS THERE A THREAT TO THE COMMUNITY OR THEENVIRONMENT. MILE POST/VALVE STATION: 600' SW OF RABBIT ISLAND "D" PLATFORM. | 200000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
901 | 1997-03-04 | TX | other | UNKNOWN (CROCKETT COUNTY) | OASIS PIPELINE CO | OZONA COMPRESSOR STATION BLOW DOWN VALVE OPENED INADVERTANTLY CAUSING A LOSSOF GAS WITHIN THE COMPRESSOR SITE. OTHER: CONTRO FUNCTION - GAS RELEASE | 85140 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
902 | 1997-02-22 | NE | other | UNKNOWN (NANCE COUNTY) | K N INTERSTATE GAS TRANSMISSION CO | PIPELINE SEPARATED AT GIRTH WELD IN LOUP RIVER X-ING. UNABLE TO DETERMINEEXACT CAUSE BECAUSE OF LOCATION OF FAILED SEGMENT IN LOUP RIVER. RIVERCROSSING FAILED AT OR NEAR GIRTH WELD. POSSIBLY DUE TO ICE FLOW IN RIVER. | 240000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
903 | 1997-03-20 | MT | other | UNKNOWN (RICHLAND COUNTY) | WILLISTON BASIN INTERSTATE PIPELINE CO | GIRTH WELD FAILED ON BURIED 12-INCH PIPELINE DUE TO SETTLING AND FROST HEAVE. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
904 | 1997-03-19 | SD | other | UNKNOWN (LAWRENCE COUNTY) | WILLISTON BASIN INTERSTATE PIPELINE CO | A D-7 CRAWLER-TRACTOR WAS BEING USED FOR RECLAMATION WORK NEAR OUR 8-INCHPIPELINE WHEN IT RIPPER TOOTH HOOKED AND PUNCTURED THE TOP OF THE PIPE. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
905 | 1997-03-13 | IL | maintenance | UNKNOWN (COLES COUNTY) | CENTRAL ILLINOIS PUBLIC SERVICE | THE WHITE/SUPERIOR NATURAL GAS ENGINE/COMPRESSOR (UNIT #3) WAS OVERHAULED BYCOOPER ENERGY SERVICES, CURRENT OEM, IN 1996. THE OVERHAUL WORK WAS COMPLETED12/14/96. THE UNIT #3 HAD OPERATED 612 HOURS FROM START-UP UNTIL THE MARCH 13,1997 INCIDENT. PRELIMINARY INVESTIGATION REVEALED THAT THE BALANCE NUT ON THE#3 COMPRESSOR CYLINDER ASSEMBLY ON UNIT #3 WAS NOT TIGHT AGAINST THE ASSEMBLYCROSSHEAD. THE POSITION OF THE BALANCE NUT ALLOWED THE NUT TO BREAK THE WIPERPACKING GLAND OUT OF ITS PROPER POSITION. THE CONTINUED BEATING, OF THEBALANCE NUT ON THE WIPER PACKING GLAND WEB, EVENTUALLY BROKE THE JOINT WHERETHE #3 COMPRESSOR CYLINDER ASSEMBLY DISTANCE PIECE BOLTED TO THE COMPRESSORFRAME. MOVEMENT OF THE #3 COMPRESSOR CYLINDER ASSEMBLY AWAY FROM THECOMPRESSOR FRAME, OPENED THE SUCTION AND DISCHARGE FLANGE CONNECTIONS TO THECOMPRESSOR CYLINDER. THE LOOSE FLANGE CONNECTIONS ALLOWED GAS TO ESCAPE INTOTHE COMPRESSOR BUILDING. PRELIMINARY INVESTIGATION REVEALED NO FAILURE ORINTERNAL DAMAGE TO THE #3 COMPRESSOR CYLINDER. | 750000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
906 | 1997-03-21 | TX | other | UNKNOWN (EL PASO COUNTY) | EL PASO NATURAL GAS CO | AT APRROX. 8:20 AM ON 3/21/97 ELPASO'S 8-5/8 ELECTRIC CO LOOP LINE NO 2058RUPTRUED. THE SITE OF THE RUPTURE IS ON A CONSTUCTION SITE ON PROPERTY AT THENORTHWEST CORNER OF RESLER DR. AND REDD RD. IN EL PASO. FOUR PEOPLE WEREHOSPITLALIZED AND 2 WERE TREATED ON SITE. THE GAS DID NOT IGNITE AND THEREWERE NO FIRES DUE TO THE RUPTURE. THE PIPELINE SEGMENT WAS SHUT IN BY 9:00 AM.IT WAS FIRST BELEIVED THAT THE RUPTURE WAS DUE TO THE PIPELINE BEING HIT BYHEAVY CONSTRUCTION EQUIP. HOWEVER SUBSEQUENT INVESTIGATION REVEALED THATTHERUPTURES WAS STREES RELATED AND THAT THE PIPELINE RUPTUREDDUE TO THE WEIGHT OFA D-9 BULLDOZER PARKED ON TOP OF THE PIPELINE. THE PIPELINE WAS PROPERLYMARKED. THE PIPELINE WAS REPAIRED BY REPLACING 78.4 FEET OF PIPELINE AND WASBACK IN SERVICE BY 5:30 PM OF THE SAME DAY. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
907 | 1997-03-21 | LA | maintenance | UNKNOWN ( COUNTY) | ANR PIPELINE CO | LEAKING 1/2" HYDRAULIC SEALANT FITTING (PLUG) ON SUBSEA HYDROTECH HOT TAPASSEMBLY. | 90000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
908 | 1997-04-12 | GA | maintenance | UNKNOWN (CARROLL COUNTY) | SOUTHERN NATURAL GAS CO | IT IS BELIEVED THAT A SEAL FAILED IN A MECHANICAL COUPLING RESULTING IN APRESSURE RELEASE AND SUBSEQUENT PIPELINE RUPTURE AT THE COUPLING JOINT. THEREWAS NO GAS IGNITION. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
909 | 1997-04-08 | AL | other | UNKNOWN ( COUNTY) | SOUTHERN NATURAL GAS CO | EMPLOYEE REMOVED A 2" BULL PLUG NOT REALIZING THAT GAS PRESSURE WAS STILLPRESENT IN A SHORT PUP OF PIPE BEHIOND THE PLUG. THE PLUG BLEW OUT STRIKINGEMPLOYEE IN THE FACE. EMPLOYEE WAS HOSPITALIZED OVERNIGHT AFTER SUGICALREPAIR OF LACERATED TONGUE. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
910 | 1997-04-03 | TX | other | UNKNOWN ( COUNTY) | ANR PIPELINE CO | 20" SUBSEA TAP WAS PULLED APART BY THE ANCHOR OF THE SHIP. | 700000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
911 | 1997-04-07 | MI | other | UNKNOWN (CHIPPEWA COUNTY) | GREAT LAKES GAS TRANSMISSION CO | ON OR ABOUT APRIL 7 1997, GREAT LAKE S GAS TRANSMISSION COMPANY RECIEVED INFO.THAT A LARGE SCTION OF HILLSIDE HAD SUBSIDED IN THE AREA OF ITS SOO LATERAL 103/4 INCH MAINLINE AND 12 3/4 INCH LOOPLINE IN CHIPPEWA COUNTY, MICHIGAN ANDTHAT THE PIPELINES WERE PARTIALLY EXPOSED. GREAT LAKES IMMEDIATELY SENTPERSONNEL TO THE SITE TO INVESTIGATE AND FOUND THAT AN APPROXIMATELY 970 FEETOF MAIN AND LOOP LINE MOVED BETWEEN 45 AND 50 FEET LATERALLY AND 25 TO 30 FEETVERTICALLY. THE OPERATING PRESSURE OF BOTH LINES WAS SUBSEQUENTLY LOWERED FROMAPPROXIMATELY 800 PSIG TO 600 PSIG AT THE LOCATION AND PERSONNEL WEREDISPATCHED TO MAN BLOCK VALVES ON EITHER SIDE OF THE LANDSIDE AREA IN THEEVENT THAT THE LINES RUPTURED. AFFECTED CUSTOMERS WERE NOTIFIED OF THESITUATION ON APRIL 8, 1997. GREAT LAKES ALSO NOTIFIED THE DEPARTMENT OFTRANSPORTATION OFFICE LOCAL AUTHORITIES AND THE NATIONAL RESPONSE CENTER(NRC).NRC NOTIFICATION (CONFORMATION NO. 383039) WAS MADE T EDT O TUESDAY APRIL 8 ,1997. GRAT LAKES ALSO COMMISIONED A GEOTECHNICAL SURVEY TO ASSESS SOILSTABILITY AND ASSIST IN LOCATING PERMANENT REPLACEMENT PIPELINES. UPONINITITLA INVESTIGATION IT APPEARED THAT THE LANDSIDE WAS THE RESULT OFLATERALLY UNSTABLE SOILS DUE TO HIGH MOISTURE CONTENT AND A POSSIBLE LOSS OFLATERAL SUPPORT DUE TO EROSION SIDE CUTTING OF THE RIVER CHANNEL AT THE BASEOF THE SLOPE. THE PRELIMANARY INVESTIGATION ALSO REVEALED THAT THE AREA HADNOT YET STABILIZED AND FURTHER SHIFTS MIGFHT OCCUR. EFFORTS BEGAN TO STABILIZETHE SITE BY DIRECTING EXCESS AWAY FROM THE LANDSLIDE AREA. GREAT LAKES SOOLATERAL MAINLINE AND LOOPLINE PROVIDE THE SOLE TRANSPORTATION SOURCE FORNATURAL GSA TO THE COMMUNITIES OF RUDYARD AND SAULT STE. MARIE, MICHIGAN, ANDSAULT STE. MARIE ONTARIO, CANADA. THIS NECESSITATED GREAT LAKES TO BEGINEMERGENCY EFFORTS TO MAINTAIN TRANSPORTATION THROUGH THIS AREA OF ITS PIPELINESYSTEM. TO MAINTAIN SERVICE, GREAT LAKES INSTALLED IN A TEMPORARILY STABILIZEDAREA AN ABOVE-GROUND, 12 3/4 INCH DIAMETER EMERGENCY BYPASS LINE APPROX. 834FEET IN LENGHT THAT WOULD ALLOW FOR THE ISOLATION AND REMOVAL FROM SERVICE OFTHE IMPACTED MAINLINE AND LOOPLINE. ON SUNDAY APRIL 13,1997 TH EEXISTING 123/4 INCH LOOPLINE WAS REMOVED FROM SERVICE AND THE NEW 12 3/4 INCH TEMPORARYBYPASS LINE WHICH WAS PRESSURE TESTED THE PREVIOUS DSAY WAS PLACED INTOSERVICE AT 75% OF NORMAL OPERATING PRESSURE THE EXISTING 10 3/4 INCH MAINLINEWAS THEN SHUT IN AND BLOWN DOWN. FOLLOWING COMPLETION OF THE TEMPORARY BYPASS,GREAT LAKES BEGAN CONSTRUCTION OF A PERMANENT REROUTE AROUND TO THE SOUTHEASTOF THE LANDSLIDE AREA. THE TOTAL LENGHT OFHTE PERMANENT BYPASS IS APPROX. 1235FEET FOR BOTH THE 10 3/4 INCH MAINLINE AND THE 12 3/4 INCH LOOP. THE PERMANENT10 3/4 INCH MAINLINE BYPASS PRESSURE WAS COMPLETED ON SUNDAY, APRIL 20, 1997,AND WAS THEN TIED-IN AND PLACED INTO SERVICE ON TUESDAY, APRIL 22, 1997.AFTER THE MAINLINE WAS PLACED INTO SERVICE, THE TEMPORARY 12 3/4 INCH BYPASSWAS REMOVED FROM SERVICE AND THE PIPE SECTION BLOWN DOWN. THE PERMANENT 123/4 INCH LOOPLINE BYPASS PRESSURE TEST WAS COMPLETED ON MONDAY APRIL 21,1997, AND WAS THEN TIED IN AND PLACED INTO SERVICE ON WED., APRIL 23, 1997.FOLLOWING COMPLETION OG THE PERMANENT BYPASS CONSTRUCTION, THE TEMPORARY 123/4 INCH BYPASS AND THE IMPACTED PORTIONS OF THE MAINLINE AND LOOPLINE WERECUT INTO SECTIONS AND REMOVED FROM THE SITE. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
912 | 1997-03-26 | TX | leaks and spills | UNKNOWN (STARR COUNTY) | VALERO TRANSMISSION CO |  | 250000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
913 | 1997-04-20 | MO | leaks and spills | UNKNOWN (BOONE COUNTY) | PANHANDLE EASTERN PIPELINE CO | UNDER INVESTIGATION. | 500000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
914 | 1997-04-18 | MS | maintenance | UNKNOWN (CALHOUN COUNTY) | COLUMBIA GULF TRANSMISSION CO | THE VALVE PLUG FROM SUCTION SIDE CLEARANCE POCKET CAME OFF FROM VALVE STEMCAUSING COMPRESSOR HEAD STRIPPED OFF FROM COMPRESSOR. CONSTRUCTION DEFECT:CAUSE OTHER: PROBLEM WITH ORIGINAL EQUIPMENT. | 60000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
915 | 1997-04-14 | TX | leaks and spills | UNKNOWN (STARR COUNTY) | VALERO TRANSMISSION CO | LINE FAILURE DUE TO STRESS CORROSION CRACKING. | 125000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
916 | 1997-05-03 | GA | maintenance | UNKNOWN (CARROLL COUNTY) | SOUTHERN NATURAL GAS CO | A PIPE CONNECTION IN A MECHANICAL COUPLING FAILED, RESULTING IN A PRESSURERELEASE AND SUBSEQUENT PIPELINE RUPTURE AT THE COUPLING JOINT. THE GAS IGNITEDAND BURNED SURROUNDING VEGETATION. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
917 | 1997-05-14 | WY | maintenance | UNKNOWN (ALBANY COUNTY) | COLORADO INTERSTATE GAS CO | C.1. LKEAK WAS AT A SMALL 1/4 LONG CRACK IN THE LONGITUDINAL WELD. C.3.C. TESTDURATION IS UNKNOWN. LEAK WAS DISCOVERED BY A GAS DETECTION INSTRUMENT DURINGA ROUTINE LEAK SURVEY. ALTHOUGH ONLY 44 FEET OF PIPE WAS REPLACED, THE REPAIRCOSTS EXCEEDED $50,000 DUE TO THE ADDITIONAL TIME, PERSONNEL. AND EQUIPMENTNECESSITATED BY THE HIGH WATER TABLE AT THE REPAIR SITE. | 51000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
918 | 1997-05-05 | TX | leaks and spills | UNKNOWN (RUSK COUNTY) | TEJAS GAS PIPELINE CO | INTERNAL CORROSION PIT ON ERW SEAM, AND THE SEAM WAS NOT IN THE NEUTRAL ZONEAT A FIELD BEND. (SEAM WAS AT 5:30) SEAM INSTALLED AT THE 5:30 POSITION ANDWAS IN A LOW SPOT (LIQUID TRAP). | 48523 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
919 | 1997-05-27 | TX | leaks and spills | UNKNOWN (HARRISON COUNTY) | TALCO ASPHALT OIL CO |  | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
920 | 1997-05-13 | TX | other | UNKNOWN (RUSK COUNTY) | LONE STAR PIPELINE CO (TRANSMISSION DIVISION) | LINE WAS STRUCK BY MOTOR GRADER OPERATED BY RUSK COUNTY, TX. PERSONNEL | 110000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
921 | 1997-05-05 | NY | other | UNKNOWN (ELLISBURG COUNTY) | NIAGARA MOHAWK POWER CORP |  | 60000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
922 | 1997-05-20 | TX | leaks and spills | UNKNOWN (HARRIS COUNTY) | TPC SERVICES, INC. | AT 10:30 AM MAY 20 1997 A CALL WAS RECIEVED AT TPC'S OPERATIONS CENTER STATINGTHAT BUBBLES WERE REPORTED IN MATAGORDA ISLAND BLOCK 485 APPROX. ONE HALF MILETO THE NORTH TO TPC'S MI 485 MAINFOLD PLAT FORM. A TECHNICIAN WAS SENT OUT BYHELICOPTER TO OVERFKY THE AREA WHERE THE BUBBLES WERE SPOTTED AND TO GETACCUATRE COORDINATES ON THE LEAK. AT 11:30 THE TECHNICIAN REPORTED THAT THEBUBBLES WERE A[PPROX. ONE HALF MILE NORHT OF OUR 485 MAINFOLD PLATFORM ANDTHAT THERE WAS NO VISIBLE SHEEN. BECAUSE WE HAVE TWO 20" NATURAL GAS PIPELINES THAT PASS VERY CLOSE TO THE BUBBLE SITE, THE VICTORIA OFFICE BEGAN TO LINEUP A DIVE BOAT AND DIVERS T GO OUT AND INVESTIGATE THE LEAK SORCE.NOTIFICATION CALLS WERE MADE TO NRC TEXAS RAILROAFD COMMISIOIN , TEXAS GENERALLAND OFFICE, AND THE U.S. COAST GUARD IN PORT LAVACA. THE DIVERS AND DIVE BOATWERE SET UP TO LEAVE PORT O'CONNER TEXAS AT 3:00 PM MAY 20 1997. BY 4:00 PMDIVERS ARRIVED AT THE LEAK SITE AND BEGAN PREPARATIONS TO DIVE ON THE LEAK.THE LEAK WAS LOCATED AT 6:45 PM, LEAK SITE COORDINATES WERE TAKEN AND IT WASDETERMINED THAT THE LEAK WAS ON ONE OF TWO 20" PIPELINES. ONCE THE SITECOORDINATES WERE CALLED IN THE LEAK SITE WAS PLOTTED AND IT WAS DETERMINEDTHAT THE LEAK WAS PROBABLY COMING FROM THE 20" EL GODO PIPELINE AND TO BLOWTHE PIPELLINE DOWN. THIS WAS SCHEDULED TO OCCUR AT 6:00 AM JUNE 21 1997. INADDITION , AMERICAN OILFIELD DIVERS, WAS CONTACTED TO DETERMINE THEAVAILABILITY OF A 20" REPAIR CLAMP, A FOUR POINT DIVE BOAT , AND A DIVE TEAM.AOD RESPONDED THAT THEY WOULD HAVE A DIVE BOAT , DIVERS, AND ALL THENECCESSARY EQUIPMENT READY TO DEPART PORT O'CONNER AT 3:00 AM ON MAY 22 1997.ON WED. MORNING THEY CALLED BACK TO CHANGE THE TIME TO 12:00 AM MAY 22 1997AND CHANGE THE DEPARTURE LOCATION TO THE GRASSO DOCKS AT FREEPORT TEXAS. ATAROUND 8:00 AM WED. MORNING THE TEXAS GENERAL LAND OFFICE CALLED FOR AN UPDATEAND THE COAST GUARD WAS UPDATED ON THE SITUATION, A COURTESY CALL WAS ALSOPLACED TO THE TNRCC TO REPORT THE VENTING OF THE GAS AT OYSTER LAKE DURINGTHE BLOW OF THE EL GORDO PIPELINE/ THE LEAK SITE WAS OVERFLOWN AND NO SHEENCOULD BE DETECTED ON THE WATER. BY 10:15 AM MAY 22, 1997 TH EDIVE BOAT ADCREW WERE ON THE LAKE SITE. THE BUBBLES HAD DIMINSHED GREATLY HOWEVER, ASMALL SHEEN HAD FORMED. COORDINATES OF THE LEAK SITE WERE CALLED IN AND WEREX2907009.71 AND Y217878.13. THESE COORDINATES CONFIRMED THAT THE LEAK WAS ONTHE EL GORDO PIPELINE. THE DIVERS SPENT MOST OF THE DAY TRYING TO REMOVE THECONCRETE OFF THE PIPE. BY 6:37 AM MAY 23, 1997 SUFFICENT CONCRETE AND MASTICHAD BEEN REMOVED AT THE LEAK LOCATION ON THE PIPE TO INSTALL THE REPAIR CLAMP.AFTER THE REPAIR CLAMP WAS INSTALLED THE PIPELINE WAS REPRESSURED UP ANDADIVER WAS SENT DOWN TO CHECK THE REPAIR CLAMP FOR LEAKS. NO GAS BUBBLES WEREDETECTED COMING FROM THE REPAIR CLAMP, SO THE DIVER APPLIED A PROTECTIVECOATINGOF SYNTHOGLASS TO ALL EXPOSED AREWWAS OF PIPE. AT 9:00 AM MAY 24, 1997THE DIVE BOAT DEPARTED THE JOB SITE. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
923 | 1997-05-01 | NM | other | UNKNOWN (SANTA FE COUNTY) | PUBLIC SERVICE COMPANY OF NEW MEXICO - GAS SVCS | MCC, CONTRACTOR INSTALLING A WATER LINE HAD PHONED FOR LINE SPOTS TO NEWMEXICO ONE CALL SYSTEM(#97043007440022). LINE SPOTS WERE COMPLETED BY PNMGAS SERVICES USING ROOSTER TAILS AND PAINT AT 8:50 AM ON 5-1-97. AT 11:30AM MCC KNOCKED A 2' PURGING TEE OFF THE 12" SANTA FE TRANSMISSION LINE.THIS DAMAGE OCCURED BECAUSE MCC DIDNT USE CAUTION AND MAINTAIN 18"CLEARENCE FROM THE TRANSMISSION LINE WHILE EXCAVATING. THREE MCC CREWMEMBERS WERE TAKEN TO THE HOSPITAL FOR MINOR INJURIES BUT WERE NOTADMITTED. THE BLOWING LINE WAS CONTROLLED AT 12:45 PM. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
924 | 1994-08-14 | WV | other | UNKNOWN (KANAWHA COUNTY) | AJAX PIPELINE CO | GAS IGNITED WHEN IGNITED LINE WAS BEING PUMPED. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
925 | 1996-08-26 | TX | leaks and spills | UNKNOWN (HEMPHILL COUNTY) | NORAM GAS TRANSMISSION, A NORAM ENERGY COMPANY | FAILURE OCCURRED IN PITTED AREA LOCATED ON BOTTON QUADRANT INSIDE PIPE. | 66000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
926 | 1996-12-14 | AR | other | UNKNOWN (LAWERENCE COUNTY) | MISSISSIPPI RIVER TRANSMISSION CORP | P | 56664 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
927 | 1997-05-20 | ME | other | UNKNOWN (YORK COUNTY) | GRANITE STATE GAS TRANSMISSION INC | TRAVELED HEAVY TRACK EQUIPMENT ACROSS PIPELINE ROW THRU YEAR ROUNDWETLANDAREA. MACHINE SANK IN SOFT SOIL COMING INTO CONTACT WITH PIPE.PIPELINE WAS TAKEN OUT OF SERVICE AND DAMAGED SECTION REPLACED. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
928 | 1997-05-23 | LA | leaks and spills | UNKNOWN ( COUNTY) | TRUNKLINE GAS CO | NO DATA | 125000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
929 | 1997-06-17 | TX | leaks and spills | UNKNOWN (HARRISON COUNTY) | NORAM GAS TRANSMISSION, A NORAM ENERGY COMPANY | THERE WERE 2 LEAKS WITHIN 3' AREA ON BOTTOM SIDE OF PIPE. ONE ABOUT THE SIZEOF 1 1/2" & THE OTHER MAYBE 1/8". IN NORROW CREEK 2' WIDER & 1' DEEP. PIPELINEWAS FOUND TO BE PARTIALLY EXPOSED IN CREEK, COATING FOUND TO BE DETERIORATED. | 158500 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
930 | 1997-06-08 | LA | leaks and spills | UNKNOWN (LOUISIANA COUNTY) | ANR PIPELINE CO | PIPELINE WAS CONCRETE COATED WITH SOMATIC WRAP. INTERNAL CORROSION - PIN HOLELEAK AT 7 OCLOCK POSITION. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
931 | 1997-06-02 | MS | other | UNKNOWN (ST LOUIS COUNTY) | TENNESSEE GAS PIPELINE CO | BOLT FAILURE ON COMPRESSOR VALVE CAP ALLOWED GAS TO BE RELEASED RESULTING INTHE FIRE AND EXPLOSION IN BUILDING A AT STATION 530. | 3500000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
932 | 1997-07-19 | LA | other | UNKNOWN ( COUNTY) | SOUTHERN NATURAL GAS CO | STORM FORCES FROM HURRICANE DANNY NDAMAGED THE PLATFORM SUPPORT FOR THE METERRUNS AT MILEPOST 10.762 ON THE 6" ELOI BY PIPELINE SUCH THAT METER PIPING WASSEVERED CAUSING A RELEASE OF GAS. THERE WAS NO IGNITION. | 75000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
933 | 1997-07-24 | TX | other | UNKNOWN ( COUNTY) | WESTAR TRANSMISSION CO |  | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
934 | 1997-07-14 | OH | other | UNKNOWN (BUTLER COUNTY) | CINCINNATI GAS & ELECTRIC CO | STILL UNDER INVESTIGATION AND WILL BE PROVIDED BY A SUPPLEMENTAL REPORT. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
935 | 1997-07-29 | IL | other | UNKNOWN (MADISON COUNTY) | ILLINOIS POWER CO | ON JULY 29, 1997 AT APPROX. 1450 HRS A THIRD PARTY DUG INTO THE 10" MAIN ATHIGHLAND AND CUT IN THE PIPE APPROX. 6" BY 3'. THE APPROPRIATE PERSONNEL WERENOTIFIED AND BEGAN TO RESTORE TO NORMAL CONDITIONS. BECAUSE GAS WAS VENTING TOATMOSPHERE, GAS SUPPLY DISPATCHERS TOOK APPROPRIATE ACTION TO REDUCE PRESSUREON THE DAMAGED LINE.AT 1710 HRS. THE BULLDOZER WAS STILL IN THE LINE ANDCATHODIC PROTECTION PERSONNEL HAD BEEN REQESTED TO SHUT OFF RECTIFIERSTATIONS. AT 1800 HRS. THE LINE WAS SHUT DOWN TO 105 PSI. AT 1910 HRS.PERSONNEL WERE CALLED TO BRING IN THE CNG TRAILOR AS A BACKUP FOR ST. JACOB.TH NUMBER OF CUSTOMERS THAT WOULD BE AFFECTED HAQD AN OUTAGE OCCURRED WASAPPROX. 500 IN ST. JACOB AND 384 IN HIGHLAND. DECISION WAS MADE TO MAKE ATEMPORARY REPAIR USING A DRESSER SLEEVE RATED FOR 500 PSI. AT 2310 HRS. THEAREA BEGAN LOWERING THE LINE TO 60 PSI. ON JULY 30 1997, APPROX. 0130 HRS.TEMPORARY REPAIRS WERE COMPLETED. FOR OPERATIONS THE VALVE AT HIGHLAND WASCLOSED AND PETERS#2 WAS PUT ON BYPASS. ALL THE GAS SERVING THE AREA WAS COMINGFROM HOFFMAN, THROUGH THE HILLSBORO TRANSFER STATION DOWN THROUGH FRANKLIN ST.IN SUMMARY TEMPORARY REPAR WAS COMPLETED WITHOUT INJURY OR NO CUSTOMER OUTAGE.PERMANENT REPAIR WAS COMPLETED AND THE LINE RETURNED TO NORMAL OPERATION ONAUGUST 8. | 151000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
936 | 1997-08-09 | LA | leaks and spills | UNKNOWN ( COUNTY) | NATURAL GAS PIPELINE CO OF AMERICA |  | 51232 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
937 | 1997-07-21 | IN | other | UNKNOWN (MARION COUNTY) | CITIZENS GAS & COKE UTILITY |  | 1000000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
938 | 1997-08-21 | LA | leaks and spills | UNKNOWN ( COUNTY) | NATURAL GAS PIPELINE CO OF AMERICA |  | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
939 | 1997-08-21 | TX | maintenance | UNKNOWN (MOORE COUNTY) | MIDGARD ENERGY COMPANY |  | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
940 | 1997-08-11 | IL | leaks and spills | UNKNOWN (GRUNDY COUNTY) | NATURAL GAS PIPELINE CO OF AMERICA |  | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
941 | 1997-07-01 | IL | other | UNKNOWN (CLINTON COUNTY) | MISSISSIPPI RIVER TRANSMISSION CORP | WATER LINE CONTRACTOR TRENCHING TO INSTALL WATER LINE. THE TRENCHER WASCUTTING 60" DEEP DITCH, PIPELINE DEPTH WAS 3' - 3". | 55000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
942 | 1997-08-12 | LA | leaks and spills | UNKNOWN (OFFSHORE LA, FEDERAL WAT COUNTY) | ANR PIPELINE CO | INTERNAL CORROSION - 3 PINHOLE LEAKS WITHIN A 23 INCH SECTION OF THE PIPE. | 130000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
943 | 1997-08-04 | TX | other | UNKNOWN (LIBERTY COUNTY) | GULF COAST NATURAL GAS CO | HAD AN EXPLOSION IN FRAC TANKS AT MOSS BLUFF ON THE 16" LINE, SYSTEM 903 NEARHANKAMER, AT 11:30 AM ON 8/04/97. TEMPORARY PIG TRAPS WERE INSTALLED ON BOTHENDS AND PIG WAS BEING PUSHED FROM THE NORTH END TO THE SOUTH. LIQUIDS WERECAUGHT IN FOUR FRAC TANKS. | 335000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
944 | 1997-09-09 | LA | other | UNKNOWN ( COUNTY) | SOUTHERN NATURAL GAS CO | A FIRE OF UNKNOWN ORIGIN OCCURRED IN PRODUCER'S EQUIPMENT ON THE MAIN PASSBLOCK 59 PLATFORM ALSO OWNED BY PRODUCER. THE FIRE SPREAD TO PRODUCER'S METERSTATION, WHICH WAS OPERATED BY SOUTHERN, DAMAGING METER PIPING, ELECTRONICMEASUREMENT EQUIPMENT, AND RELATED DEVICES AND MATERIAL. THE PLATFORM ESDSYSTEM ACTIVATED SHUTTING DOWN GAS FLOW BUT WHETHER A GAS RELEASE OCCURREDCANNOT BE DETERMINED. | 75000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
945 | 1997-09-16 | LA | leaks and spills | UNKNOWN (LAFAYETTE PARISH COUNTY) | LOUISIANA INTRASTATE GAS CO, L.L.C. | UNKNOWN AT THIS TIME. ADDITIONAL INFORMATION WILL BE CONTAINED IN SUPPLEMENTALREPORT. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
946 | 1997-09-14 | CO | other | UNKNOWN (LOGAN COUNTY) | K N INTERSTATE GAS TRANSMISSION CO | GAS IGNITED WHILE PURGING 24" SUCTION HEADER AT KN STERLING COMPRESSORSTATION. FIRE IGNITED LUMBER, PLASTIC AND CARDBOARD AND BURNED GRASS INSIDEAND OUTSIDE OF STATION FENCE. FIRE DEPARTMENT WAS CALLED. SUPPLY VALVE WASIMMEDIATELY CLOSED, EXTINGUISHING FIRE. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
947 | 1997-10-06 | TX | other | UNKNOWN (SHERMAN COUNTY) | MIDGARD ENERGY COMPANY | A TRUCK HAULING FEED WAS HIT BY A PICK-UP, CAUSING THE TRUCK TO RUN OFFHIGHWAY 15 AND RUN OVER OUR REGULATOR/METER STATION. ABOVE GROUND EQUIPMENTWAS DAMAGED WHEN HIT BY TRUCK. | 1228 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
948 | 1997-09-19 | MI | leaks and spills | UNKNOWN (OSCEOLA COUNTY) | MICHIGAN GAS STORAGE CO | CREVICE IN LONG SEAM LOCATED ON BOTTOM ALLOWED CORROSION PRODUCTS TOACCUMULATE CAUSING PITTING AND FOR PITS TO LINK UP. | 23000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
949 | 1997-10-27 | VA | other | UNKNOWN (GREENE COUNTY) | COLUMBIA GAS TRANSMISSION CORP | CONTRACTOR'S D6 BULLDOZER SLID INTO A DITCH PUNCTURING EXPOSED PIPE RESULTINGIN A FIRE. ACCORDING TO THE EQUIPMENT OPERATOR, THE CAUSE WAS LIKELY ACOMBINATION OF BOTH WET AND SLIPPERY SOIL CONDITIONS AND OPERATION TOO CLOSETO THE DITCH. | 300000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
950 | 1997-10-28 | TX | leaks and spills | UNKNOWN (ARANSAS COUNTY) | CCNG GAS GATHERING, L.P. | PROGRESSIVE ISOLATE CONE-SHAPED PIT PERFORATION IN PIPE WALL OF APPROXIMATELYPROGRESSIVE ISOLATED CONE-SHAPED PIT PERFORATION IN PIPE WALL OF APPROXIMATELYFORT-FIVE YEARS OF MONITORED PIPELINE QUALITY GAS SERVICE. | 44000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
951 | 1997-10-24 | MN | other | UNKNOWN (ITASCA COUNTY) | GREAT LAKES GAS TRANSMISSION CO | THE LEAK WAS DISCOVERED DURING A ROUTINE SURVEY. INVESTIGATION REVEALED ACRACKED GIRTH WELD THAT WAS LEAKING. THE CRACK WAS CIRCUMFERENTIALLYORIENTATED AT APPROXIMATELY THE 6:00 POSITION AND WAS MEASURED TO BE 4.25INCHES LONG, RESULTING IN PIPE REPLACEMENT. PART D - BRIEF DESCRIPTION: ASMENTIONED IN PART 3, ABOVE, THE CRACK IN THE WELD EITHER WAS NOT PRESENT ORWAS NOT DETECTED DURING THE ORIGINAL CONSTRUCTION IN 1968 EVEN THOUGH ALLPRODUCTION WELDS WERE NONDESTRUCTIVELY TESTED AT THAT TIME. GREAT LAKES ISINVESTIGATING THE FAILURE AND HAS RETAINED THE SERVICES OF A CONSULTANT TOEXAMINE THE DEFECTIVE WELD REMOVED FROM SERVICE IN AN ATTEMPT TO DETERMINE THECAUSE OF THE DEFECT (CIRCUMFERENTIAL CRACK). IT SHOULD BE NOTED THAT THEPIPELINE SECTION WAS SHUT IN AND THEN BLOWN DOWN PRIOR TO REMOVAL OF A SEGMENTOF PIPE CONTAINING THE LEAKING WELD. A REPLACEMENT PIPE SEGMENT WAS THENINSTALLED AND PLACED INTO SERVICE. THE NRC WAS CONTACTED AT APPROXIMATELY1710 HOURS ON OCTOBER 24, 1997, (NRC CASE NO, 408825) | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
952 | 1997-10-22 | LA | leaks and spills | UNKNOWN ( COUNTY) | SOUTHERN NATURAL GAS CO | PART A - PIPING WAS ABOVE THE WATERLINE OFFSHORE. PART 3 - TWO VERY SMALL"PINHOLE LEAKS WERE DISCOVERED IN 3" PIPING ON OFFSHORE PLATFORM. NOSIGNIFICANT EVENT WAS LINKED TO THE LEAKS. ESTIMATED COST OF REPAIR IS THEREASON FOR CLASSIFYING AS AN INCIDENT. | 200000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
953 | 1997-10-23 | TX | leaks and spills | UNKNOWN (GREGG COUNTY) | TEXAS EASTERN GAS PIPELINE CO | PIPELINE RUPTURE FROM APPARENT INTERNAL CORROSION. | 150000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
954 | 1997-10-18 | MN | other | UNKNOWN (FREEBORN COUNTY) | NORTHERN NATURAL GAS CO. | FARMER WAS CHISEL PLOWING THE FIELD WHEN THE PLOW STRUCK THE PIPELINE. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
955 | 1997-11-05 | TX | leaks and spills | UNKNOWN (BRAZORIA COUNTY) | HOUSTON PIPELINE CO | INTERNAL CORROSION. | 20000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
956 | 1997-11-12 | AR | other | UNKNOWN (UNION COUNTY) | NORAM GAS TRANSMISSION, A NORAM ENERGY COMPANY | PIPE PULLED OUT OF COUPLING BECAUSE OF WASHOUT AREA. | 63000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
957 | 1997-12-17 | LA | leaks and spills | UNKNOWN (BLOCK 286/287 COUNTY) | COLUMBIA GULF TRANSMISSION CO | PIN HOLE LEAK AT 9 O'CLOCK POSITION. POSSIBLE CAUSE: INTERNAL CORROSION ORMATERIAL DEFECT. A CLAMP WAS INSTALLED TO STOP LEAK. X=1,885,229.89Y=105,490.26. SMALL PINHOLE LEAK AT 9:00 POSITION. | 80000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
958 | 1997-12-02 | LA | other | UNKNOWN (OFFSHORE COUNTY) | COLUMBIA GULF TRANSMISSION CO | A TRAWLING NET PULLED A 1/2" POWER GAS NIPPLE OFF FROM THE 18" VALVE. THEREMAINDER OF THE 1/2" NIPPLE WAS REMOVED AND A PIPE PLUG WAS INSTALLED. ATRAWLING NET PULLED A 1/2" POWER GAS NIPPLE OFF THE PIPELINE VALVE. THEREMAINDER OF THE 1/2" PIPE NIPPLE WAS REMOVED AND A 1/2" PIPE PLUG WASINSTALLED. | 200000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
959 | 1997-12-07 | TX | leaks and spills | UNKNOWN ( COUNTY) | ANR PIPELINE CO | PIN HOLE LEAK AT 6:30 POSITION CONSISTENT WITH INTERNAL CORROSION. | 170000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
960 | 1997-12-28 | LA | other | UNKNOWN (ST. MARY PARISH COUNTY) | MARATHON ASHLAND PIPE LINE LLC | ON DECEMBER 28, 1998 AT APPROXIMATELY 8:35 A.M., A SPHERE ARRIVED AT THEGARDEN CITY FACILITY AND BECAME STUCK IN THE 30" RADIAL FLOW TEE UPSTREAM OFTHE PIG TRAP (I.E., RECEIVER). IT IS BELIEVED THAT ONE OR TWO PREVIOUSSPHERES WERE ALREADY SETTING IN THE TEE. THE DOWNSTREAM DELIVERY PRESSURE TOEXXON DROPPED RAPIDLY AND DELIVERIES TO EXXON AND THE PIPELINE DISCHARGEFACILITY (PDF) WERE STOPPED. THE SPHERES WERE BELIEVED TO BE STUCK DUE TOHYDRATE FORMATION AT THE DOWNSTREAM END OF THE RADIAL FLOW TEE. SINCE THEREWAS NO METHANOL READILY AVAILABLE AND NO PLACE TO INJECT METHANOL NEAR THERADIAL FLOW TEE, THE OPERATOR DECIDED TO USE DIFFERENTIAL PRESSURE TO TRY TOFREE THE STUCK SPHERES. A VALVE ON THE UPSTREAM SIDE OF THE RECEIVER WASCLOSED AND THE PRESSURE ON THE RECEIVER WAS REDUCED TO CREATE A DIFFERENTIALPRESSURE TO MOVE THE SPHERE. WHEN THE VALVE WAS OPENED, ONE OR TWO SPHERESDISLODGED, MOVED RAPIDLY INTO THE RECEIVER AND CREATED A PRESSURE SURGE ON THESCRAPER TRAP PIPING AND APPURTENANCES. A 3/4" X 1/2" SWAGE FITTING, WHICH WASLOCATED BETWEEN THE TOP OF THE RECEIVER LEVEL INDICATOR AND THE 1/2"PLUGGED BLOWDOWN VALVE, FAILED AT THE TOP OF THE 3/4" THREADS ALLOWING A SMALLAMOUNT OF CONDENSATE TO BE BLOWN INTO THE AIR AS A MIST THAT MOVED IN ANORTHERNLY DIRECTION AND COATED SOME PIPING, GRAVEL AND CANE STUBBLE. AS THEPIPING WAS BEING SHUT IN AND SECURED, IT WAS NOTICED THAT THE MOTOR- OPERATEDVALVE ACTUATOR ON ONE OF THE TWO 30" BLOCK VALVE TO THE RECEIVER WASHYDROSTATICALLY TESTED FOR ONE HOUR PRIOR TO RETURNING TO SERVICE. ANEMERGENCY RESPONSE CONTRACTOR WAS CALLED OUT TO CLEAN UP THE CONDENSATERESIDUE USING ABSORBANT PADS.ADDITIONAL OPERATIONAL CORRECTIVE ACTIONS TAKENINCLUDE: INSTALLATION OF METHANOL INJECTION PORTS NEAR BOTH THE UPSTREAM ANDDOWNSTREAM ENDS OF THE RADIAL FLOW TEE; A GUIDELINE FOR HANDLING SITUATIONSWHERE SPHERES BECOME STUCK IN RADIAL FLOW TEES AS PREPARED, IMPLEMENTED ANDREVIEWED WITH STATION OPERATIONS PERSONNEL; AND, ACCURACY OF THE WATERMONITORING INSTUMENTS WAS CHECKED AND VERIFIED. PRESSURE SAFETY SWITCHESWILL BE INSTALLED TO PROHIBIT THE VALVE FROM ACTUATING WHEN A SPECIFIEDPRESSURE DIFFERENTIAL IS EXCEEDED. ALSO, A SAFETY REVIEW TRAINING SESSION ISPLANNED WITH OPERATIONS PERSONNEL CONCERNING POTENTIAL ENERGY HAZARDSASSOCIATED WITH A HIGH PRESSURE GAS FACILITY. | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
961 | 1997-10-21 | KS | other | UNKNOWN (WABAUNSEE COUNTY) | K N INTERSTATE GAS TRANSMISSION CO | USING GEL PIG TO REMOVE CONTAMINATION FROM PIPELINE. OPENED DOWNSTREAMBLOWDOWNS TO PROVIDE PRESSURE DIFFERENTIAL TO MOVE PIG TRAIN. PRODUCT FROMEARLIER PIG RUN WAS INSIDE OF PIPE AND ESCAPED AS A MIST APPROX. 1.5 HOURSAFTER BLOWDOWNS WERE OPENED. CLOSED BLOWDOWN APPROX. 7 MINUTES AFTER MISTINGBEGAN. MIST AFFECTED ORCHARD, STOCK POND, CATFISH POND, PUBLIC ROAD ANDDWELLING. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
962 | 1997-11-15 | SC | maintenance | UNKNOWN (YORK COUNTY) | SOUTH CAROLINA PIPELINE CORP | DURING THE CALENDAR YEARS OF 1995 AND 1996,SOUTH CAROLINA PIPELINE CORPORATION(SCPC) INSTALLED EIGHTY FIVE (85) MILES OF 16' NATURAL GAS TRANSMISSION MAINWITH A DESIGNED M.A.O.P. OF 1200 PSIG IN PARALLEL WITH AN EXISTING 12"REDUCING TO 10" LINE A SYSTEM FOR INCREASED SAFETY AND TO ALLOW SCPC TOACCOMMODATE ADDITIONAL CONTRACT VOLUMES OF GAS FROM ONE OF TWO INTERSTATESUPPLIERS, TRANSCONTENTIAL PIPE LINE COMPANY. THE LINE A SYSTEM WAS INSTALLEDIN 1957 AND 1958 AND SCPC HAD CONCERNS ABOUT THE 12" PORTION OF THIS LINE ANDDECIDED TO INTELLIGENTLY SURVEY (SMART PIG) APPROXIMATELY TWENTY - FIVE MILESOF PIPE. AFTER THE APRIL 1996 SURVEY, IT WAS DECIDED TO TAKE THE 12" PORTIONOUT OF SERVICE UNTIL FURTHER TESTING COULD BE CONDUCTED. IN ORDER TO TAKETHIS SECTION OF PIPE OUT OF SERVICE, CROSSOVER PIPING AND VALVES WEREINSTALLED FROM THE NEW 16" PIPE TO THE REMAINING 60 MILES OF 10" LINE SYSTEMFOR CONTINUED SERVICE TO SCPC'S SALE FOR RESALE AND INDUSTRIAL CUSTOMERS.THE 16" AND 10" PIPELINES OPERATED IN PARRALLEL WITH THE CROSSOVERS OPENLIMITED TO THE M.A.O.P. OF THE 10" SECTION FROM APRIL1996 TILL NOVEMBER 1997,SCPC COMPLETED THE CONSTRUCTION OF THE GROVER COMPRESSOR STATION WHICH WASDESIGNED TO DISCHARGE INTO THE NEW 16" LINE. THE MANAGER OF MEASUREMENT ANDCOMPRESSION ASSIGNED RESPONSIBILITIES TO MEASUREMENTS TECHNICIANS TO SEPERATETHE 16" FROM THE 10" EXCEPT AT ONE REGULATED CROSSOVER FROM THE 16" ATREGULATING STATION 11 - 70 TO ALLOW FOR THE GROVER COMPRESSOR STATION TOINCREASE THE PRESSURE ON THE 16" LINE TO THE M.A.O.P. THE WORK WAS REPORTEDTO BE COMPLETED AT ALL CROSSOVER 0N NOVEMBER 14TH AND THE GROVER COMPRESSORSTATION STARTED ADDITIONAL UNITS TO RAISE THE PRESSURE ON THE 16" PORTION TOAPPROXIMATELY 950 PSIG. AFTER THE REGULATED CROSSOVER AT STATION 11 - 70WAS CHECKED TO INSURE PROPER OPERATION ON THE MORNING OF NOVEMBER 15TH THE16" PIPELINE WAS CLEARED FOR OPERATION UP TO THE M.A.O.P. THE INCIDENTOCCURRED ON THE 10" LINE A SYSTEM IN A FIELD IN THE MIDDLE OF A DAIRY FARMNEAR STATION 11 - 90 AS A RESULT OF INADVERTENTLY LEAVING A 4" CROSSOVER VALVEOPEN AT REGULATING STATION 11 - 30. THIS VALVE BEING OPENED ALLOWEDUNRESTRICTED FLOW OF NATURAL GAS FROM THE 16" LINE TO A 10" SECTION OF LINEWITH A M.A.O.P. OF 821 PSIG. THE LINE RUPTURED AT AN ESTIMATED 1046 PSIGWHICH RESULTED IN THE LONGITUDINAL WELD OPEN ON FOR AN ESTIMATED DISTANCE OFFORTY FOUR FEET. A METALLURGICAL WAS CONDUCTED ON THE RUPTURED SECTION ANDIS ATTACHED FOR REVIEW. AS A RESULT OF HIS INCIDENT, SCPC NOW REQUIRES AWRITTEN PROCEDURE FOR ALL MAJOR PIPELINE MODIFICATIONS. THE LONG TIME,COMPETENT EMPLOYEES WHO WERE INVOVED IN THE INCIDENT HAVE BEEN DECIPLINEDAND ALL OTHER OPERATIONAL EMPLOYEES HAVE BEEN BRIEFED ON THIS INCIDENT TOHELP INSURE AN EVENT NEVER HAPPENS AGAIN. | 74000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
963 | 1998-01-05 | NV | other | UNKNOWN (CLARK COUNTY) | SOUTHWEST GAS CORP | ENCLOSED IS A GAS TRANSMISSION INCIDENT REPORT FOR AN INCIDENT WHICH OCCURREDON JANUARY 5, 1998. THE INCIDENT REPORT NUMBER PROVIDED TO SOUTHWEST GAS FROMDOT WHEN WE MADE OUR TELEPHONIC REPORT IS 418580. IF YOU HAVE ANY QUESTIONS,PLEASE GIVE ME A CALL. | 129860 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
964 | 1998-01-09 | LA | other | UNKNOWN (HOUMA COUNTY) | TENNESSEE GAS PIPELINE CO | UNKNKOWN THIRD PARTY WHO CAUSED DAMAGE. LOCATION IS NOT A WATER CROSSING, BUTIS OFFSHORE IN STATE WATERS. | 385000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
965 | 1998-01-08 | GA | other | UNKNOWN (COBB COUNTY) | ATLANTA GAS LIGHT CO | A 24" STEEL NATURAL GAS MAIN DEVELOPED A 4 1/4" STRESS CRACK AT A 12" STEELBRANCH CONNECTION WHEN THE FILLMATERIAL SUPPORT WAS WASHED AWAY DURING A WATERMAIN BREAK. | 47546 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
966 | 1998-01-21 | TX | other | UNKNOWN (HOWARD COUNTY) | WESTAR TRANSMISSION CO | ATTTACHED IS RSPA FORM F 7100.2 COVERING AN INCIDENT THAT OCCURRED NEARFORSAN, TEXAS ON JANUARY 21 1998. WE REPORTED THE INCIDENT TO THE NATIONALRESPONSE CENTER AT APPROXIMATELY 1602 HOURS CST ON JANUARY 21 1998 AND THEINCIDENT NUMBER ASSIGNED WAS 420718. WE REPORTED THIS INCIDENT BASED UPONOPERATOR JUDGMENT AT THE TIME IT WAS DISCOVERED. THE INCIDENT OCCURRED WHEN AROAD MAINTAINER OPERATED BY HOWARD COUNTY RD DEPARTMENT STRUCK OUR LINE. THERESULTING DAMAGE CAUSED A LOSS OF SERVICE TO APPROXIMATELY 97 ENERGASCUSTOMERS. THERE WERE NO FIRES, EXPLOSIONS, INJURIES OR FATALITIES AND THETOTAL PROPERTY DAMAGE IS ESTIMATED TO BE $8500. IF YOU REQUIRE INFORMATION,PLEASE FEEL FRE TO CALL ME AT (303)7633457 | 8500 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
967 | 1998-01-16 | AR | maintenance | UNKNOWN (CRAWFORD COUNTY) | NORAM GAS TRANSMISSION, A NORAM ENERGY COMPANY |  | 600000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
968 | 1998-01-16 | AR | maintenance | UNKNOWN (SEBASTAIN COUNTY) | NORAM GAS TRANSMISSION, A NORAM ENERGY COMPANY | PIPE NIPPLE ON OIL FILTER CASE SAMPLE PROBE BROKE AND VENTED OIL ONTO EXHAUSTMANIFOLD OF ENGINE #3 AND IGNITED. SAFETY SHUTDOWNS OPERATED AND SHUT DOWNENGINE. FIRE EXTINGUISHED BY STATION EMPLOYEE. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
969 | 1998-01-26 | LA | other | UNKNOWN ( COUNTY) | SEA ROBIN PIPELINE CO |  | 2500000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
970 | 1998-01-27 | TX | leaks and spills | UNKNOWN (HUDSPETH COUNTY) | EL PASO NATURAL GAS CO |  | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
971 | 1998-01-13 | OR | maintenance | UNKNOWN (JOSEPHINE COUNTY) | NORTHWEST PIPELINE CORP | ATTACHED IS AN INCIDENT REPORT, FORM 7100.2,CONCERNING A RUPTURE ON OUR GRANTSPASS LATERAL LOCATED IN JOSEPHINE COUNTY, OREGON. THE RUPTURE INFORMATION ISNECESSARY, PLEASE CONTACT ME. | 200000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
972 | 1997-10-21 | MS | maintenance | UNKNOWN (GEORGE COUNTY) | KOCH GATEWAY PIPELINE CO | ATTACHED PLEASE FIND YOUR REQUESTED RESUBMISSION OF THE WRITTEN REPORT FOR ALEAK WHICH OCCURRED ON OUR BAXTERVILLE 20" LINE. THE REPORT WAS MADE11/30/1997 TO LT. KOSHAR OF THE NATIONAL RESPONSE CENTER. THE REPORT NUMBER IS409967. WE APOLOGIZE FOR SENDING THE REPORT TO YOU TO INITIALLY ON ANINCORRECT FORM. SHOULD YOU REQUIRE ADDITIONAL INFORMATION PLEASE CALL ME AT(312)9887102. | 140000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
973 | 1997-01-11 | MS | maintenance | UNKNOWN (GEORGE COUNTY) | KOCH GATEWAY PIPELINE CO | ATTACHED PLEAS FIND YOUR REQUESTED RESUBMISSION OF THE WRITTEN REPORT FOR ALEAK WHICH OCCURRED ON OUR PIPELINE NEAR LUCEDALE, MISSISSIIPPI, IN GEORGECOUNTY. THE REPORT WAS MADE AT 7:24 AM.CENTRAL TIME, ON 10/21/1997 TO LT.KOSHAR OF THE NATIONAL RESPONSE CENTER. THE REPORT NUMBER 408257. WEAPOLOGIZE FOR SENDING THE REPORT TO YOU INITIALY ON AN INCORRECT FORM. | 60397 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
974 | 1998-01-30 | LA | leaks and spills | UNKNOWN ( COUNTY) | EQUITABLE RESOURCES (A.K.A EQUITABLE GAS CO) | PIPELINE REPAIR PROCEDURE WEST CAMERON 198 02/02/1998 JET OUR ATOUND THE PIPEAT THE LEAK LOCATION TO VERIFY ORIGIN OF LEAK. ULTRASONICALLY INSPECT THEPIPE AT VARIOUS LOCATION TDETERMINE GENERAL CONDITION OF PIPE MATERIAL.INSTALL A NEW PRE-TESTED PIPE SPOOL COMPLETE WITH FLANGS AT THE LEAKLOCATION. OPEN THE SUB-SEA VALVES AT THE TEXAS EASTERN TIE-IN AND PLACESYSTEM BACK IN SERVICE. MONITOR AND INSPECT FOR LEAKS DURING REPRESURIZATIONAND FOR SEVERAL DAYS THEREAFTER. | 700000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
975 | 1998-01-26 | LA | leaks and spills | UNKNOWN (OFFSJORE COUNTY) | EQUITABLE RESOURCES (A.K.A EQUITABLE GAS CO) | PIPELINE REPAIR PROCEDURE WEST CAMERON 198 1/27/1998 BLOWN DOWN THE 12"PIPELINE BACK TO THE 198 "A" PLATFORM. REMOVE CONCRETE COATING, CLEAN PIPE TOBARE METAL, AND ULTRASONICALLY INSPECT AT VARIOUS LOCATION OF PIPE TODETERMINE GENERAL CONNDITION OF PIPE MATERIAL; INSTALL REPAIR CLAMP. OPENTHE SUB-SEA VALVES AT THE TEXAS EASTERN TIE IN AND PLACE SYSTEM BACK INSERVICE. MONITOR AND INSPECT FOR LEAKS DURING REPRESSURIZATION AND FORSEVERAL DAYS THERE AFTER. | 200000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
976 | 1998-02-07 | WV | leaks and spills | UNKNOWN (KANAWHA COUNTY) | COLUMBIA GAS TRANSMISSION CORP | HEATER COIL IN A DIRECT FIRED HEATER. | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
977 | 1997-11-19 | LA | maintenance | UNKNOWN (ST MARY PARISH COUNTY) | COLUMBIA GULF TRANSMISSION CO | UNDERCUT ON THE HOT TAP WELD AND STRESS ON THE BRANCH PIPING CAUSING A 3"CRACK ON THE PIPELINE. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
978 | 1997-10-08 | OK | other | UNKNOWN (CANADIAN COUNTY) | GPM GAS CORP | ON OCTOBER 8,1997, A COMPANY MAINTENANCE CREW BEGAN WORK TO REMOVE A NONUSED 6INCH TIE IN FROM A 12 INCH NATURAL GAS GATHERING SYSTEM DISCHARGE LINE. THELINE HAD BEEN ISOLATED AND DEPRESSURED ON OCTOBER 5, 1997. AN OPEN VENT WASLOCATED AT EACH ISOLATION VALVE AND AT THE WORK SITE. THE WORK WAS INITIATEDBY MONITORING THE OPEN VENT AT THE WORK SITE ON THE END OF THE 6INCH TIE IN.ONLY TESIDUAL HYDROCARBON VAPORS WERE OBSERVED. AS A RESULT, THE CREW LIT THETOP OF THE VENT WITH A CUTTING TORCH AND THEN BEGAN REMOVING THE 6 INCH PIPE.THE NON-USED TIE-IN WOULD BE CUT OFF WITH THE TORCH ALLOWING A WELD CAP TO BEINSTALLED TO CAP THE 12INCH LINE. AFTER CUTTING APPROXIMATELY 3/4 OF THE6INCH PIPE, THE CONTROLLED FIRE BEGAN TO INCREASE ABRUPTLY. AS A RESULT, ALLWORKERS AT THE SITE WERE ORDERED TO EVACUATE UPWIND. SECONDS LATER, A LARGEUNCONTROLLED FIRE DESTROYED AN UNMANNED BACKHOE TRACTOR PARKED AT THE EDGE OFTHE EXCAVATION AND HEAT DAMAGED APPROXIMATELY 20 FEET OF EXCAVATED 12 INCHPIPE. THERE WERE NO INJURIES OR OTHER DAMAGES OCCURRED. THE FIRE WASALLOWED TO BURN ITSELF OUT. | 70000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
979 | 1998-03-01 | AK | other | UNKNOWN ( COUNTY) | ENSTAR NATURAL GAS CO | ON SUNDAY MORNING MARCH 1, 1998, AT 9:46 AM AST, ENSTAR WAS NOTIFIED BY THEANCHORAGE FIRE DEPARTMENT ( AFD OF A POWER POLE FIRE AND NATURAL GAS LEAK ATFIRST STREET AND POST ROAD, ANCHORAGE, ALASKA. A SERVICE MAN WAS DISPATCHEDTO THE LOCATION. A SUPERVISOR AND A DISTRIBUTION CREW ALSO RESPONDED. A 34.5KV ELECTRICAL TRANSMISSION LINE HAD BEEN SEVERED ON POLE AND ELECTRIC CURRENTFROM THE DOWNED POWER LINE OR POLE SWITCHING GEAR CARSED A FAILURE IN A 2"HDPE, 60 PSI, NATURAL GAS DISTRIBUTION MAIN ADJACENT TO THE POLE. AT 10:32 AM,AFD WAS NOTIFIED OF AN EXPLOSION AND FIRE AT MUNICIPAL LIGHT & POWER'S (ML&P)POWER PLANT BUILDING LOCATED APROXIMATELY 1 BLOCK WEST OF THE POLE FIRE.ADDITIONAL ENSTAR EMPLOYEES AND SUPERVISORS WERE CALLED IN TO SHUT DOWN TWO,275 PSI, 6" STEEL TRANSMISSION LINES FEEDING THE POWER PLANT. NATURAL GAS TOTHE POWER PLANT WAS SHUT DOWN AT 2:35 PM AND THE FIRE WAS CONTAINED. UPONINVESTIGATION, IT WAS DETERMINED THAT A LINE TO GROUND FAULT ON THE ML&P34.5 KV ELECTRICAL SYSTEM TRAVELED THE PATH OF LEAST RESISTANCE, THE ENSTARSTEEL TRANSMISSION PIPELINE, BACK TO THE GROUND GRID AT THE ML&P POWER PLANT.THE POWER POLE WAS IN CLOSE PROXIMITY TO ENSTAR'S STEEL TRANSMISSIONPIPELINE. EVIDENCE OF ELECTRICAL CURRENT ENTERING THE STEEL PIPELINE NEAR THEPOWER POLE AS WELL AS EXITING THE PIPELINE THE PIPELINE NEAR THE POWER PLANTWAS DISCOVERED. PRESSURE TESTING OF THE PIPELINES REVEALED THE SOUTHERN 6",275 PSI WAS INTACT. NO LEAKS WERE FOUND IN IT. IT WAS PRESSURE TESTED TO 425PSI AND PLACED BACK IN SERVICE. THE NORTHERN 6", 275 PSI PIPELINE AND 3/4"STEEL, 275 PSI SERVICE LINE CONNECTED TO IT FAILED A 100 PSI PRESSURE TEST.THEY WERE ABANDONED IN PLACE. AT LEAST ONE IDENTIFIED HOLE, AND ONE OR MOREADDITIONAL HOLES WERE BURNED IN THE 275 PSI 6" STEEL PIPELINE AND 3/4" STEELSERVICE LINE FEEDING THE POWER PLANT WHEN THE 34.5 KV POWER LINE FAILED.NATURAL GAS LEAKED UNDERGROUND THOUGH THESE HOLES BEFORE THE EXPLOSION ATML&P POWER PLANT. IT IS BELIEVED THAT NATURAL GAS ENTERED THE BUILDINGTHROUGH UNDERGROUND ELECTRICAL CONDUITS AND OR AROUND THE LOOSE FITTINGSIDING OF THE BUILDING WHERE IT WAS IGNITED BY ONE OF NUMEROUS IGNITIONSOURCES INSIDE THE BUILDING. | 2000000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
980 | 1997-11-10 | TX | other | UNKNOWN (MOORE COUNTY) | EL PASO NATURAL GAS CO | AT1:17 PM ON NOVEMBER 10 1997, EL PASO'S" DUMAS LINE NO. 1102 DUMAS NO. 1102WAS HIT AND PUNCTURED BY A SEISMOGRAPH CREW LOCKHARG GEOPHYSICAL CO. WORKINGIN THE VICINITY OU PIPELINE APPROXIMATELY 12 MILES SOUTH OF OUR DUMAS PLANT.A HOLE 1-1/2 IN DIAMETER WAS MUNCTURED IN OUR DUMAS AND AMARILLO PLANTS WERESHUT DOWN AND THE PIPELINE SEGMENT WAS ISOLATED WITH IN 2 HOURS OFDISCOVERY. 14 MILES OF PIPELINE WERE BLOWN DOWN AND THE PIPELINE WASREPAIRED WITH A 5 FOOT PUP AND WAS BACK IN SERVICE BY THE NEXT DAY. | 57843 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
981 | 1998-01-11 | LA | other | UNKNOWN ( COUNTY) | FOREST OIL CORP |  | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
982 | 1998-02-25 | LA | other | UNKNOWN (ST. JAMES PARISH COUNTY) | WILLIAM FIELD SERVICES | ON FEBRUARY 25, 1998 AT APPROXIMATELY 6:45 AM, WILLIAMS FIELD SERVICES COMPANY(WFS) PERSONNEL WERE NOTIFIED BY A LOCAL CITIZEN THAT GAS WAS VENTING AT VALVESETTING 62-40 (LOCATED ON THE NORTH END OF DUAL 20" PIPELINES CROSSING THEMISSISSIPPI RIVER). WFS PERSONNEL WERE DISPATCHED TO VALVE SETTING 62 - 40 TOINVESTIGATE AND DISCOVERED THAT THE AUTOMATED VALVES ON THE TWO (2) 20" RIVERCROSSING LINES WERE CLOSED.PERSONNEL WERE THEN DISPATCHED TO VALVE ON THE MOSTWESTERLY 20" PIPELINE WAS DOWN TO 75 PSIG AND FALLING AND THE PIPELINE WASSECURED AND ISOLATED. THE EASTERLY PIPELINE WAS HOLDING WAS PRESSURE ANDRETURNED TO SERVICE. AT THE PRESENT TIME, RIVER DEPTH AND CURRENTS HAVEPREVENTED AN INVESTIGATION OF THE WESTERLY 20" PIPELINE CROSSING. WFS PLANS AFULL INVESTIGATION AS SOON AS RIVER CONDITIONS ALLOW. A SUPPLEMENTAL INCIDENTREPORT WILL BE SUBMITTED UPON COMPLETION OF THE INVESTIGATION. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
983 | 1998-02-20 | MS | other | UNKNOWN ( COUNTY) | KOCH GATEWAY PIPELINE CO |  | 59433 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
984 | 1998-02-26 | TX | maintenance | UNKNOWN ( COUNTY) | TENNESSEE GAS PIPELINE CO |  | 78000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
985 | 1998-03-08 | GA | other | UNKNOWN (FULTON COUNTY) | SOUTHERN NATURAL GAS CO | RUN SWITCHING INSTRUMENTATION EQUIPMENT AT FULTON INDUSTRIAL METER STATIONWAS STRUCK BY LIGHTENING CAUSING A SMALL FIRE WHICH MIGRATED TO THE STATION'SMETER RUNS DUE TO MELTED SEAL COMPONENTS. A LARGER FIRE ENSUED RESULTING INSIGNIFICANT STATION DAMAGE. THE FIRE WAS CONTAINED AND EXTINGUISHED WITH NOINJURIES, AND NO DAMAGE TO PROPERTY OTHER THAN SOUTHERN'S. | 60000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
986 | 1998-03-20 | LA | other | UNKNOWN ( COUNTY) | COLUMBIA GULF TRANSMISSION CO | A TRAWLING NET BROKE THE 1" POWER GAS LINE FROM THE VALVE OPERATOR. THEBROKEN POWER GAS LINE WAS REMOVED AND THE 1" UNIONS WERE PLUGGED. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
987 | 1998-03-28 | LA | leaks and spills | UNKNOWN ( COUNTY) | SOUTHERN NATURAL GAS CO | CORRODED PART WAS ABOVE WATER ON PLATFORM | 202000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
988 | 1998-03-20 | TX | other | UNKNOWN (FAYETTE COUNTY) | OASIS PIPELINE CO |  | 227400 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
989 | 1998-04-02 | KY | maintenance | UNKNOWN ( COUNTY) | TENNESSEE GAS PIPELINE CO | TENNESSE WAS INVESTIGATING A LOW POTENTEAL AREA WHEN WORKERS HEARD GAS LEAK ATTHIS LOCATION AND ISOLATED VALVE SECTION 107-3 TO 108-3. | 64000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
990 | 1998-05-08 | TX | leaks and spills | UNKNOWN (MOORE COUNTY) | WEST TEXAS GAS INC |  | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
991 | 1998-05-12 | TX | maintenance | UNKNOWN (MOORE COUNTY) | WEST TEXAS GAS INC | METHOD OF PIPELINE CONNECTION CAUSED 22" PIPELINE JOINT TO SEPARATE FROMDRESSER COUPLING. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
992 | 1998-05-06 | OH | other | UNKNOWN (MONROE COUNTY) | TEXAS EASTERN TRANSMISSION CORP | THE PIPELINE RUPTURE WAS DUE TO THE FORCES OF A SOIL SLIPPAGE ALONG AHILLSIDE.TEXAS EASTERN IS RELOCATING THE PIPELINE OUTSIDE THE AREA OF THE SOILSLIP. | 3400000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
993 | 1998-04-08 | LA | other | UNKNOWN ( COUNTY) | FLORIDA GAS TRANSMISSION CO | THE PORTION OF THE LATERAL WITH LEAK HAS BEEN TAKEN OUT OF SERVICE UNTIL AREPAIR CAN BE MADE. THE CAUSE OF THE LEAK WILL REMAIN UNKNOWN UNTIL THEREPAIR WORK COMMENCES DUE TO THE DEPTH OF THE WATER OVER THE PIPELINE AT THELEAK LOCATION. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
994 | 1998-03-24 | TX | maintenance | UNKNOWN ( COUNTY) | HOUSTON PIPELINE CO | GASKET FAILURE | 45000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
995 | 1998-03-07 | NM | other | UNKNOWN (CHAVES COUNTY) | PUBLIC SERVICE COMPANY OF NEW MEXICO - GAS SVCS | UPON ARRIVAL I OBSERVED THAT A VEHICLE FULLY ENGULFED IN FLAMES AND THE DRIVEROF THE VEHICLE HAD BEEN TRANSPORTED TO THE HOSIPTAL IN ROSWELL, NM. FURTHERINVESTIGATION SHOWED THANT THE VEHICLE WAS TRAVELING EASTBOUND ON STATE ROAD560. FOR AN UNKNOWN REASON THE VEHICLE TRAVELED OFF THE ROAD AND INTO THEWEST BOUND BARDITCH. THE VEHICLE THEN STRUCK A GAS PIPE LINE VALVE AND THENAN ELECTRIC POLE. WHEN THE VEHICLE STRUCK THE GAS PIPE LINE VALVE, IT KNOCKEDTHE VALVE OFF THE PIPE. A SPARK FROM THE VEHICLE IGNITED THE GAS AND FULLYENGULFED THE VEHICLE. THE DRIVER MANAGED TO ESCAPE FROM THE VEHICLE. THEDRIVER SUSTAINED BURNS ON HIS ARMS AND LEGS. THE VEHICLE WAS BURNEDCOMPLETELY AND NO IDENTIFICATION COULD BE MADE OF THE VEHICLE. | 10000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
996 | 1998-04-02 | OK | maintenance | UNKNOWN (COAL COUNTY) | NORAM GAS TRANSMISSION, A NORAM ENERGY COMPANY | THESE ARE THE REMARKS | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
997 | 1998-04-08 | OK | other | UNKNOWN (COAL COUNTY) | NORAM GAS TRANSMISSION, A NORAM ENERGY COMPANY | FAILURE OCCURRED IN BEND THAT WRINKLED DUE TO OVERBURDEN LOAD IN HIGH BANK OFMUDDY BOGGY CREEK. | 400000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
998 | 1998-04-20 | LA | other | UNKNOWN ( COUNTY) | ANR PIPELINE CO | A REPAIR SLEEVE INSTALLED ON AUGUST 31, 1990 WAS LEAKING. FOUND HAIRLINECRACK ON PIPE HAD OPENED AND PROPAGATED. THE REPAIR SLEEVE WAS UNABLE TOCONTAIN THE PRESSURE. | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
999 | 1998-05-05 | TX | maintenance | UNKNOWN ( COUNTY) | NORTHERN NATURAL GAS CO (ENRON) |  | 300000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1000 | 1998-04-10 | IA | other | UNKNOWN (WRIGHT COUNTY) | NORTHERN NATURAL GAS CO (ENRON) |  | 58000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1001 | 1998-04-22 | CA | other | UNKNOWN (SAN BENITO COUNTY) | PACIFIC GAS & ELECTRIC CO |  | 4000000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1002 | 1998-05-11 | TX | leaks and spills | UNKNOWN ( COUNTY) | ANR PIPELINE CO |  | 325000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1003 | 1998-05-04 | TX | other | UNKNOWN ( COUNTY) | ANR PIPELINE CO |  | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1004 | 1998-05-19 | WV | other | UNKNOWN (JACKSON COUNTY) | COLUMBIA GAS TRANSMISSION CORP |  | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1005 | 1998-03-27 | LA | other | UNKNOWN ( COUNTY) | BASIN EXPLORATION INC |  | 600000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1006 | 1998-05-18 | TX | leaks and spills | UNKNOWN ( COUNTY) | WILLIAMS ENERGY GROUP-FIELD SERVICES |  | 75000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1007 | 1998-06-02 | LA | other | UNKNOWN (IBERVILLE COUNTY) | SOUTHERN NATURAL GAS CO | A CATALYTIC GAS SENSOR IN A COMPRESSOR BUILDING GAS DETECTOR MALFUNCTIONED,INDICATING A FALSE PRESENCE OF NATURAL GAS AT A LEVEL WHICH CAUSED THEAUTOMATED COMPRESSOR STATION'S EMERGENCY SHUTDOWN (ESD) SYSTEM TO ACTIVATE.THIS RESULTED IN A RELEASE OF GAS TO THE ATOMOSPHERE THROUGH THE STATION'SBLOWDOWN PIPING. THE ASSOCIATED NOSE OF THE HIGH PRESSURE GAS RELEASEATTRACTED THE ATTENTION OF LOCAL EMERGENCY RESPONSE PERSONNEL WHO INITIATED APRECAUTIONARY EVACUATION OF NEARBY RESIDENTS AND BLOCKED TRAFFIC ON A PARISHROAD. THE EMERGENCY RESPONSE PERSONEL ACTED OF THEIR OWN ACCORD WITHOUT ANYDECLARTION OF AN EMERGENCY FROM SOUTHERN'S COMPRESSOR STATION EMPLOYEES. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1008 | 1998-06-06 | TX | other | UNKNOWN (HIDALGO COUNTY) | PG & E TEXAS PIPELINE, L.P. | PAVING COMPANY USING A MAINTAINER AT THE INTERSECTION OF POLK ST & I ROAD INPHARR, TEXAS HIT A 2" TAP ON A 12" TRANSMISSION LINE. THIS IN TURN SPLIT THEWELD ON THE 2" TO 12" CONNECTION. LINE PRESSURE WAS REDUCED TO 20#'S AND A12" SPLIT-SLEEVE CLAMP WAS INSTALLED. | 5000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1009 | 1998-05-30 | SC | maintenance | UNKNOWN (AIKEN COUNTY) | SOUTH CAROLINA PIPELINE CORP | FAILURE OCCURRED IN ERW WELD. METALLURGICAL CONSULTANTS INC HAS DETERMINEDTHE MOST PROBABLE CAUSE TO BE HOOK CRACKS IN THE ERW WELD AREA. ON MAY 30,1998, AT APPROXIMATELY 1:02 PM, SOUTH CAROLINA PIPEINE CORPORATION EXPERIENCEDA FAILURE ON 10" LINE L IN AIKEN COUNTY BETWEEN OUR SOUTHERN COMPRESSORSTATION 12-10 AND AIKEN NORTH COMPRESSOR STATION 12-20. THE SPECIFIC LOCATIONOF THE FAILURE WAS ON THE DOWNSTREAM SIDE OF THE CASING BENEATH HWY #421 NEAR#118 BYPASS. SIX PEOPLE HAVE BEEN TREATED FOR INJURIES AS A RESULT OF THEFAILURE. FOUR OF THE INJURIES WERE A RESULT OF A FAMILY TRAVELING IN ANAUTOMOBILE DOWN HWY #421 AT THE TIME OF THE FAILURE. THE FORCE OF THE NATURALGAS ESCAPING FROM THE FAILED PIPE HURLED DEBRIS AND MUD ONTO THE CAR. ANOTHERINDIVIDUAL INJURED HER FOOT WHILE LEAVING HER HOUSE AFTER SHE HEARD THE NOISEAS RESULT OF THE FAILURE. ONE PERSON WAS HOSPITALIZED OVERNIGHT AS A RESULTOF THE INCIDENT DUE TO A COMPLAINT OF FUMES FROM THE ESCAPING NATURAL GAS.AT THE TIME OF THE INCIDENT, SCPC WAS RUNNING THREE SOLAR SATURN TURBINESCOMPRESSING NATURAL GAS INTO THE NORTH SYSTEM IN PREPARTION FOR EXPECTEDELECTRIC TURBINNE GENERATION LATER THAT DAY. THE PRESSURE AND FLOW RATE PRIORTO THE INCIDENT ON THE DISCHARGE SIDE OF SOUTHERN COMPRESSOR STATION INTO THENORTH SYSTEM WAS 1000.5 AND FLOWING 4785.94 MCFH AT 1:01 PM. | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1010 | 1998-06-19 | MS | other | UNKNOWN (LAMAR COUNTY) | GAYLORD CONTAINER LTD | ROAD GRADING MACH WAS DIGGING DITCH ALONGSIDE OF ROAD AND CUT TO DEEP ANDSTRUCK 8" GAS LINE WITH BLADE, CUTTING A 3" X 1/4" INCH GASH IN PIPELINE | 3000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1011 | 1998-05-19 | LA | maintenance | UNKNOWN ( COUNTY) | SEA ROBIN PIPELINE CO | A RECENTLY INSTALLED SUBSEA ASSEMBLY DEVELOPED A LEAK IN THE HEAT EFFECTEDWELD ZONE NEAR THE GIRTH WELD ON THE 2" BRANCH OF A 6X6X2 REDUCING TEE. THELEAK WAS DUE TO A TEAR IN THE TEE MATERIAL APPARENTLY CAUSED DURINGSAND-CEMENT BAG COVER INSTALLATION. A METALLURGICAL ANALYSIS IS UNDERWAY TOBETTER DETERMINE THE CAUSE OF THE TEAR. | 150000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1012 | 1998-06-15 | TX | other | UNKNOWN (GALVESTON COUNTY) | TRANSTEXAS TRANSMISSION CORP | DAMAGE WAS APPARENTLY CAUSED BY UNKNOWN FORCES (PERHAPS SHRIMP NETS) DRAGGINGOFF THE ANCHOR WEIGHTS OF THE PIPELINE, ALLOWING IT TO FLOAT UP NEAR THESURFACE WHERE AN UNKNOWN MOTOR VESSEL CAUSED EXTENSIVE PROPERTY DAMAGE. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1013 | 1998-06-06 | LA | other | UNKNOWN ( COUNTY) | KOCH GATEWAY PIPELINE CO | MINOR BUBBLES DISCOVERED MISS. RIVER REMOTE X-ING NEAR BANK. UNABLE TO VERIFYCAUSE/POSSIBLE FUTURE REPAIR COSTS W/O JEOPARDIZING DIVER SAFETY. BECAUSE OFLIMITED NEED FOR LINE, WE MAY NOT REPAIR IT OR PUT IT BACK IN SERVICE.REPORTED TO NRC JUST IN CASE WE DO & COSTS JUSTIFY REPORTING. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1014 | 1998-07-23 | LA | other | UNKNOWN ( COUNTY) | MID LOUISIANA GAS CO | SUPPLEMENTAL REPORT TO BE FILED AFTER PIPE IS INSPECTED & REPAIR ATTEMPTED.INSPECTION & REPAIR WILL BE DELAYED UNTIL RIVER LEVEL FALLS TO LEVEL SAFE FORDIVER TO WORK. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1015 | 1998-07-07 | LA | other | UNKNOWN (CONCORDIA COUNTY) | MID LOUISIANA GAS CO | SUPPLEMENTAL REPORT TO BE FILED AFTER PIPE IS INSPECTED AND REPAIR ATTEMPTED.INSPECTION AND REPAIR WILL BE DELAYED UNTIL RIVER LEVEL FALLS TOLEVEL SAFE FOR DIVER TO WORK. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1016 | 1998-07-07 | TX | other | UNKNOWN (TARRANT COUNTY) | LONE STAR PIPELINE CO (TRANSMISSION DIVISION) | THIRD PARTY CONTRACTOR CUT THE PIPELINE WHILE TRENCHING. | 450000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1017 | 1998-07-21 | WY | other | UNKNOWN (CAMPBELL COUNTY) | WILLISTON BASIN INTERSTATE PIPELINE CO | THIS INCIDENT OCCURRED AT A RECEIPT POINT WITH A GATHERING SYSTEM OPERATOR. ARELIEF VALVE ON THE GATHERING SYSTEM OPERATED AND CAUGHT FIRE. THE HEAT FROMTHE FIRE DESTROYED WILLISTON BASIN'S RECEIPT STATION. PIPELINE HAS BEENREPAIRED AND SYSTEM IS BACK TO NORMAL. | 415350 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1018 | 1998-07-15 | AR | other | UNKNOWN (UNION COUNTY) | NORAM GAS TRANSMISSION, A NORAM ENERGY COMPANY | LIGHTNING STRUCK METER STATION PIPING. THE INSULATING GASKET ON THE OUTLETSIDE OF THE LOWER METER TUBE ISOLATION VALVE FAILED. IGNITION OCCURRED WHERETHE GASKET FAILED. | 80000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1019 | 1998-07-11 | WV | other | UNKNOWN (WETZEL COUNTY) | CNG TRANSMISSION CORP | WHILE EXCAVATING FOR A NEW PIPELINE IL-492, A PACE PIPELINE TRACK HOE OPERATORWAS BACKFILLING NEW DITCH. SPOIL PILE WAS LOCATED OVER TOP OF EXISTING IL-342WHICH PARALLELS PLANNED TL-492. WHILE REQUIRING DIRT FROM SPOIL PILE, THEEQUIPMENT OPERATOR DUG INTO EXISTING TL-342. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1020 | 1998-07-15 | AL | other | UNKNOWN (CONECUH COUNTY) | CONECUH - MONROE COUNTIES GAS DIST | AT 4:50 PM THE GAS DISTRICT RECEIVED NOTICE BY TELEPHONE OF A GAS LEAK FROMTHE OCCUPANT OF 45687 HIGHWAY 31. THE LOCATION WAS SOUTH OF CASTLEBERRY INCONECUH COUNTY, ALABAMA. SEVERAL DISTRICT PERSONNEL LEFT THE OFFICE TORESPOND TO THE SCENE. THEY DISCOVERED THAT A CREW INSTALLING FIBER OPTICCABLE USING A BULLDOZER WITH VIBRATORY PLOW UNIT HAD DAMAGED THE GAS LINE ONTHE EAST SIDE OF HIGHWAY 31 AT APPROXIMATELY MILEPOST 79.7. GAS WAS LEAKINGAND ESCAPING UP THROUGH THE GROUND. IT WAS UNSURE AT THIS TIME IF MAIN ORSERVICE WAS DAMAGED. THE PRESSURE ON THE LINE WAS APPROXIMATELY 320 PSI. TWOEMPLOYEES PULLED THEIR TRUCKS INTO POSITION TO HELP BLOCK TRAFFIC ON HWY 31.ANOTHER EMPLOYEE UNLOADED A TRENCHER FROM ITS TRAILER AND PULLED IT CLOSE TOTHE LEAK AREA. AT APPROXIMATELY 5:10, THE GAS IGNITED CAUSING A FIRE. THEFIRE BURNED THE EMPLOYEE ON THE TRENCHER. AN AMBULANCE WAS CALLED AND HE WASTAKEN TO THE HOSPITAL IN BREWTON, ALABAMA. THE FIRE ALSO DAMAGED THEDISTRICT'S TRENCHER, AND HEAVILY DAMAGED THE CONTRACTOR'S BULLDOZER AND ROLLOF FIBER OPTIC CABLE. OTHER DISTRICT PERSONNEL CLOSED MAIN LINE VALVES TOSTOP THE GAS FLOW, WHILE OTHERS BEGAN GOING TO CUSTOMER METERS AND LOCKING THESERVICE VALVES. A TOTAL OF 52 CUSTOMERS WAS AFFECTED. ALSO RESPONDING TO THESITE WAS THE CONECUH COUNTY EMERGENCY MANAGEMENT AGENCY DIRECTOR AND UNITSFROM SEVERAL LOCAL FIRE DEPARTMENT. AT 6:10 PM THE INCIDENT WAS REPORTED TOTHE NATIONAL RESPONSE CENTER IN WASHINGTON, D.C. THE ALABAMA PUBLIC SERVICECOMMISSION WAS ALSO CONTACTED. LAW ENFORCEMENT PERSONNEL BLOCKED THE HIGHWAYUNTIL ALABAMA DEPARTMENT OF TRANSPORTATION PERSONNEL STARTED DETOURING TRAFFICAROUND THE INCIDENT SITE. THE FIRE WAS ALLOWED TO BURN UNTIL THE SUPPLY OFGAS WAS EXHAUSTED. ON THURSDAY MORNING, 7/16/1998, AT 9:00 PM, DISTRICPERSONNEL BEGAN EXCAVATING THE AREA AROUND THE DAMAGED PIPELINE. IT WASDISCOVERED THAT THE PLOW HAD TWISTED AND BROKEN LOOSE A 3/4' SERVICE LINE FROMITS TAPPING TEE. THE SERVICE LINE SERVES THE RESIDENCE AT 45687 HIGHWAY 31.WHEN THE GAS FLAME HAD SUBSIDED ENOUGH, DISTRICT PERSONNEL SHUT OFF THETAPPING TEE AND WELDED THE SERVICE LINE TO THE TEE. SINCE IT APPEARED THATTHE PLOW HAD CROSSED THE GAS MAIM PRIOR TO STRICKING THE SERVICE LINE,DISTRICT PERSONNEL DUG OUT ALONG THE LENGTH OF THE MAIN TO SEE IF THERE WASANY MORE DAMAGE TO THE LINE OR COATING DAMAGE. IT WAS DISCOVERED THE PLOW HADMADE A GOUGE NEAR THE TAPPING TEE 0.050' DEEP, AND A 26'-27' LONG INDENTION ATLEAST 3/4' DEEP AT THE DEEPEST POINT. COATING DAMAGE WAS ALSO EVIDENT ALONG65'-70 OF THE LINE. THE DECISION WAS MADE AT THIS TIME TO REPLACEAPPROXIMATELY 74' OF 6' STEEL PIPE. THE SITE WAS EXCAVATED ON THURSDAYAFTERNOON. ON FRIDAY MORNING 7/17/1998, DISTRIC PERSONNEL BEEN PREPARING THEMAIN FOR INSTALLATION OF TWO STOPPER FITTINGS. THROUGHOUT FRIDAY AND SATURDAY,STOPPER FITTINGS WERE INSTALLED, GAS FLOW STOPPED, THE DAMAGED SECTION OFPIPELINE WAS REMOVED, AND THE NEW SECTION WAS WELDED INTO PLACE. A NEWTAPPING TEE AND SECTION OF 3/4' SERVICE LINE INSTALLED FOR THE SERVICE TO45687 HIGHWAY 31. BY 6:00 PM SATURDAY 7/18/98, NORMAL PIPELINE OPERATION WASRESUMED AND THE SITE BACKFILLED AND LEVELED. | 170000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1021 | 1998-07-17 | IN | other | UNKNOWN (MONROE COUNTY) | INDIANA GAS CO INC | A CONTRACTOR WORKING FOR THE MONROE COUNTY HIGHWAY DEPARTMENT WAS INSTALLINGGUARD RAILING FOR A COUNTY BRIDGE. A TRUCK-MOUNTED PILE DRIVER WAS BEING USEDTO INSTALL ALUMINUM POSTS TO WHICH THE GUARD RAILING WOULD BE ATTACHED. ATAPPROXIMATELY 1:00 PM ON JULY 17, 1998, ONE OF THE ALUMINUM POSTS THEY WEREINSTALLING STRUCK AND DAMAGED AN INDIANA GAS CO. 8-INCH STEEL PIPELINE, WITH ANORMAL OPERATING PRESSURE OF 275 PSIG. NATURAL GAS BEGAN TO ESCAPE FROM THE3-INCH X .5 INCH HOLE IN THE PIPELINE AND FOUND A SOURCE OF IGNITION IN THECONTRACTOR'S TRUCK ENGINE. THE RESULTANT FIRE DESTROYED THE TRUCK, ANDDAMAGED OVER HEAD TELEPHONE LINES. AS THE SYSTEM WAS ISOLATED BY TWO (2)VALVES, 97 CUSTOMERS LOST GAS SERVICE. SERVICE WAS RESTORED AFTER REPAIRSWERE MADE. FACILITY LOCATE REQUESTS WERE MADE ON APRIL 27, 1998. INDIANA GASCO. MARKED THE FACILITIES AS REQUESTED ON APRIL 28, 1998. NO SUBSEQUENTLOCATE REQUESTS WERE MADE. THE TIME FRAME BETWEEN THE ONLY LOCATE REQUEST ANDTHE ACTUAL CONSTRUCTION WAS EIGHTY (80) DAYS. INDIANA LAW STATES THAT THENOTICE OF INTENT TO EXCAVATE IS VALID FOR A PERIOD FROM TWO TO TWENTY CALENDARDAYS AFTER THE REQUEST IS RECEIVED. A NEW NOTICE IS REQUIRED AFTER TWENTYCALENDER DAYS IF THE EXCAVATION HAS NOT STARTED. | 150000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1022 | 1998-07-06 | OR | other | UNKNOWN ( COUNTY) | PACIFIC GAS TRANSMISSION CO | 14:15-A PG&E GT-NW EMPLOYEE DOING ROUTINE MAINTENANCE DISCOVERED A NATURAL GASLEAK NEAR THE STANFIELD, OREGON CITY METER STATION MAINLINE "A" TAP. IT WASNOT APPARENT IF THE LEAK WAS COMING FROM THE MAINLINE OR THE METER STATIONSERVICE PIPING. PHYSICAL SIGNS AT THE LEAK SITE REVEALED AN APPROXIMATE 9'DIAMETER SOIL DISTRUBANCE AT THE GROUND SURFACE BLOWING NATURAL GAS. THEREWERE NO OTHER PHYSICAL SIGNS OF GROUND DISTURBANCE AT THE SITE. PG&E GT-NWWAS AT THIS SITE ON 7/3/98 DOING ROUTINE MAINTENANCE AND THERE WAS NOINDICATION OF A LEAK. 14:30- PG&E GT=NW GAS CONTROL WAS INFORMED OF THELEAK. PIPELINE EMERGENCY PROCEDURES AND NOTIFICATIONS WERE INTITATED. THEDECISION WAS MADE TO ISOLATE AND BLOWDOWN MAINLINE "A" FROM MLV 8-2 TO MLV 8-3AND TO CONTINUE SERVICE OF THE STANFIELD METER THROUGH THE MAINLINE "B" TAP.CREWS WERE DISPATCHED TO MLV 8-2 AND MLV 8-3 WHICH WERE 5.3 MILES UPSTREAM AND12.4 MILES DOWNSTREAM RESPECTIVELY TO PREPARE FOR VALVE SECTION ISOLATIONPROCEDURES. 14:45-PG&E GT-NW CREWS SECURED THE LEAK SITE BY MANNING THE SITEON A CONTINOUS BASIS. THE LEAK SITE IS A RURAL LOCATION CLASS 1 AREA. | 139000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1023 | 1998-07-23 | TX | maintenance | UNKNOWN ( COUNTY) | ANR PIPELINE CO | PACKING ON 20' CHECK VALVE STEM WAS LEAKING, 30I-20 TAP. | 150000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1024 | 1998-07-23 | LA | maintenance | UNKNOWN ( COUNTY) | TENNESSEE GAS PIPELINE CO | LEAK DEVELOPED IN STEM PACKING ON A SUBSEA CHECK VALVE. | 70000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1025 | 1998-07-17 | IL | other | UNKNOWN (MORGAN COUNTY) | PANHANDLE EASTERN PIPELINE CO | DUE TO A LEAKING VALVE, GAS ACCUMULATED IN A DEHY CONTRACTOR TOWER WHERE ANOUTSIDE CONTRACTOR WAS USING A CUTTING TORCH. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1026 | 1998-07-27 | AZ | other | UNKNOWN (PIMA COUNTY) | EL PASO NATURAL GAS CO | A ROAD GRADER OPERATED BY THE BUREAU OF LAND MANAGEMENT STRUCK THE 4 1/2 INCHLINE 2122 CAUSING A SIX INCH CUT ON THE PIPELINE. THERE WERE TWO TAPS THATWERE SHUT IN. THE PIPE WAS REPAIRED BY INSTALLING A 12-FOOT SECTION OF PIPE.THIS LINE WAS BACK IN SERVICE BY 7:05 PM. DOT CASE #447798 | 25000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1027 | 1998-08-08 | LA | leaks and spills | UNKNOWN ( COUNTY) | ANR PIPELINE CO | INTERNAL CORROSION - PINHOLE LEAT AT 9 O'CLOCK POSITION. | 58000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1028 | 1998-08-03 | FL | other | UNKNOWN ( COUNTY) | FLORIDA GAS TRANSMISSION CO | LIGHTING STORM IN VICINITY OF COMPRESSOR STATION INITIATED A STATION ESD ANDIGNITED GAS RELEASED AT BLOWDOWN SILENCER UNITS. | 263000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1029 | 1998-08-02 | AL | other | UNKNOWN (ST. CLAIR COUNTY) | SOUTHERN NATURAL GAS CO | SOUTHERN'S CONTRACTOR, WORKING ON REPLACEMENT OF A PIPELINE ADJACENT TO THEONE DAMAGED, WAS PLACING PAD DIRT WITH A FRONT END LOADER. DURING A TURN, THEMACHINERY'S BUCKET CUT INTO THE SPOIL AT THE 24" NORTH MAIN LOOP PIPELINE. ATOOTH ON THE BUCKET GOUGED A HOLE INTO THE LINE ALLOWING GAS TO RELEASE. | 65500 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1030 | 1998-08-02 | TX | maintenance | UNKNOWN (GUADALUPE COUNTY) | OASIS PIPELINE CO | LEAK RESULTED FROM A CRACK WHICH DEVELOPED IN THE BODY OF A MAINLINE VALVE. | 347361 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1031 | 1998-08-14 | FL | other | UNKNOWN (TAYLOR COUNTY) | FLORIDA GAS TRANSMISSION CO | A COMPRESSOR STATION ESD WAS INITIATED DURING A LIGHTNING STORM IN THEVICINITY OF THE STATION. A LIGHTNING IGNITED THE GAS RELEASED AT THE ESDBLOWDOWN SILENCER UNITS. | 14738000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1032 | 1998-08-28 | TX | leaks and spills | UNKNOWN (NUECES COUNTY) | AIR LIQUIDE AMERICA CORP. | DETAILED METALLURGICAL FAILURE ANALYSIS BEING CONDUCTED ON FAILED SECTION OFPIPELINE. SUPPLEMENTAL REPORT WILL BE ISSUED. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1033 | 1998-08-18 | PA | other | UNKNOWN (CAMBRIA COUNTY) | PEOPLES NATURAL GAS CO | LINE LOCATOR AND CONSTRUCTION COMPANY THAT CAUSED DAMAGE DISAGREE OVER WHETHERACCURATE SITE LOCATION WAS SUBMITTED BY CONSTRUCTION COMPANY. | 60000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1034 | 1989-08-22 | KY | other | UNKNOWN (BOONE COUNTY) | UNION LIGHT HEAT & POWER CO | WHILE EXCAVATING, A CONTRACTOR DUG INTO A TRANSMISSION PRESSURE GAS MAIN. | 84396 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1035 | 1998-08-28 | LA | leaks and spills | UNKNOWN ( COUNTY) | ANR PIPELINE CO | A PINHOLE LEAK AT 5 O'CLOCK POSITION CONSISTENT WITH INTERNAL CORROSION. | 98400 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1036 | 1998-08-26 | LA | leaks and spills | UNKNOWN ( COUNTY) | TENNESSEE GAS PIPELINE CO | LEAK CAUSED BY INTERNAL CORROSION. | 250000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1037 | 1998-08-25 | TX | other | UNKNOWN (VAL VERDE COUNTY) | WEST TEXAS GAS INC | UNDERGROUND CREEK CROSSING WAS WASHED OUT AND PIPELINE SEPARATION WAS CAUSEDBY THE FORCE OF THE WATER OR DEBRIS BEING TAKEN DOWNSTREAM. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1038 | 1998-09-06 | MN | other | UNKNOWN (CARLTON COUNTY) | GREAT LAKES GAS TRANSMISSION CO | AS STATED ABOVE, THE RUPTURE OCCURRED DUE TO FAILURE IN THE LONG SEAM OF THEPIPE DETERMINED TO BE AT THE SITE OF A CRACK. GREAT LAKES CONTINUES TO HAVEITS CONSULTANTS INVESTIGATE THE FAILURED PIPE SEGMENTS UNTIL A DEFINITVE CAUSECAN BE DETERMINED. IT SHOULD BE NOTED THAT THE REPAIRED PIPE SEGMENT, AS WELLAS THE ENTIRE VALVE SECTION, WAS SUCCESSFULLY HYDROSTATICALLY PRESSURE TESTEDAND SUBSEQUENTLY PLACED INTO SERVICE ON SEPTEMBER 21, 1998. | 1414000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1039 | 1998-09-17 | LA | leaks and spills | UNKNOWN ( COUNTY) | TENNESSEE GAS PIPELINE CO | LEAK CAUSED BY INTERNAL CORROSION | 105000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1040 | 1998-09-20 | LA | maintenance | UNKNOWN ( COUNTY) | TENNESSEE GAS PIPELINE CO | LEAK DEVELOPED IN LOCKING LEVER OF A SUBSEA CHECK VALVE. | 65000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1041 | 1998-09-30 | LA | other | UNKNOWN ( COUNTY) | TENNESSEE GAS PIPELINE CO | HURRICANE GEORGES CAUSED MUDSLIDE WHICH DAMAGED PIPE. | 3000000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1042 | 1998-09-29 | OK | other | UNKNOWN (TEXAS COUNTY) | WESTERN GAS INTERSTATE CO | DIRT CONTRACTOR MOVED LOCATIONS WITHOUT GIVING OPERATOR NOTICE OF CHANGE. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1043 | 1998-10-02 | LA | other | UNKNOWN ( COUNTY) | SOUTHERN NATURAL GAS CO | SHEER JOINT/LOAD LIMITING CONNECTOR (INSTALLED ON PIPELINE IN 1989) FAILED DUETO MUDSLIDE LOADS DURING HURRICANE GEORGES. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1044 | 1998-10-06 | LA | other | UNKNOWN ( COUNTY) | SOUTHERN NATURAL GAS CO | A THIRD PARTY WORK BARGE BROKE FREE DUE TO HURRICANE GEORGES AND RAN AROUNDON STONE ISLAND IN BLACK BAY, LA. THE BARGE RESTED OVER SOUTHERN'S 10" BLACKBAY PIPELINE AND ITS WEIGHT ULTIMATELY CAUSED IT TO REST ON THE PIPELINERESULTING IN A RUPTURE AND SUBSEQUENT FIRE. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1045 | 1998-09-23 | LA | leaks and spills | UNKNOWN ( COUNTY) | DUKE ENERGY CORP | EFFORTS TO LOCATE, ISOLATE, AND REPAIR THE LEAK WERE IMPACTED BY HURRICANEGEORGES. | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1046 | 1998-10-06 | TX | leaks and spills | UNKNOWN ( COUNTY) | WILLIAMS FIELD SERVICES | INTERNAL CORROSION | 200000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1047 | 1998-09-03 | TX | leaks and spills | UNKNOWN (FT BEND COUNTY) | KOCH GATEWAY PIPELINE CO | CORROSION CAUSED REDUCTION OF THE WALL THICKNESS TO THE POINT OF FAILURE. | 250000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1048 | 1998-10-12 | MS | maintenance | UNKNOWN (HANCOCK COUNTY) | TENNESSEE GAS PIPELINE CO | VALVE LEAKED RESULTING IN GAS ENTERING WORK AREA. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1049 | 1998-10-12 | TX | other | UNKNOWN (FREESTONE COUNTY) | LONE STAR PIPELINE CO (TRANSMISSION DIVISION) | 8" PIPELINE BLEW OUT (END TO END). | 54986 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1050 | 1998-10-08 | MN | other | UNKNOWN (WRIGHT COUNTY) | MINNEGASCO INC | ROAD GRADER ON REPAVING PROJECT CUT GRADE DOWN TO LEVEL OF PIPE AND HIT TEE,PULLING PIPE OUT OF NORMAC FITTING. | 60000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1051 | 1998-10-26 | IA | other | UNKNOWN (TAMA COUNTY) | NORTHERN NATURAL GAS CO (ENRON) | A 3RD PARTY CONTRACTOR SEVERED THE LINE WHILE EXCAVATING IN A FARMERS FIELD,NNG WAS NOT NOTIFIED OF THE EXCAVATION ACTIVITES. | 52000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1052 | 1998-10-29 | TN | other | UNKNOWN (MADISON COUNTY) | WILLIAMS GAS PIPELINE - TEXAS GAS | ON THURSDAY, OCTOBER 29, 1998, AT 3:19 PM, CENTRAL STANDARD TIME, WILLIAMS GAS PIPELINE, TEXAS GAS SUSTAINED AN IN-SERVICE FAILURE ON ITS RIPLEY JACKSON 8" NO. 1 LINE IN MADISON COUNTY, TENNESSEE. THE LOCATION OF THE INCIDENT WAS APPROXIMATELY 2.5 MILES WEST OF THE CITY OF JACKSON, TENNESSEE. THE FAILURE OCCURRED IN THE CENTER OF CUB CREEK AT LINE MILEPOST 33+2612, WHICH IS 5.22 MILES FROM THE TERMINUS OF THE 8"LINE. SERVICE WAS INTERRUPTED TO TWO OF WGP-TEXAS GASS DELIVERY POINTS. FROM CONVERSATIONS WITH THE LOCAL DISTRIBUTION COMPANY, WE UNDERSTAND 628 LDC CUSTOMERS, INCLUDING 6 OR 8 INDUSTRIAL USERS, LOST GAS SERVICE. FULL GAS SERVICE WAS RESTORED TO THE WGP-TEXAS GAS DELIVERY POINTS BY 7:32AM CST, ON OCTOBER 30, 1998. AN ONGOING METALLURICAL INVESTIGATION HAS CONCLUDED THE FOLLOWING. THE FAILURE INITIATED IN A SEGMENT OF PIPE CONTAINING A DENT AND GOUGES CREATED BY OUTSIDE FORCES. THE DENT AND GOUGE DAMAGE, PRESUMABLY CAUSED BY EXCAVATING EQUIPMENT, EXTENDED 111" IN LENGTH ALONG THE LONGITUDINAL AXIS OF THE 8" PIPE. THE FAILURE RESULTED IN A 25" LENGTH OF PIPE BEING SEPARATED FROM THE CONTIGUOUS PIPELINE SYSTEM. THE LINE PIPE WAS CATHODICALLY PROTECTED. MINERAL DEPOSITS STRONGLY SUGGEST A LONG-TERM, UNDERGROUND EXPOSURE AFTER THE OUTSIDE-FORCE DAMAGE OCCURRED. THE METALLURGICAL EVALUATION HAS RULED OUT ANY INVOLVEMENT OF THE LONGITUDINAL OR GIRTH WELD SEAMS. PROPERTY DAMAGE WAS CONFINED TO TEXAS GAS FACILITIES. THE INCIDENT OCCURRED IN A CREEK BED LOCATED IN AN AGRICULTURAL AREA BEING UTLIZED AS PASTURE GROUND. PERMANENT REPAIRS TO THE PIPELINE, INCLUDING CLEANUP AND BANK RESTORATION WERE COMPLETED ON NOVEMBER 6, 1998. THE COMPANYS ONE-CALL RECORDS DO NOT INDICATE NOTIFICATION OF PLANNED EXCAVATIONS IN THIS AREA. LINE MARKERS ARE MAINTAINED AT THE CREEK CROSSING. THESE MARKERS CONTAIN WARNING LANGUAGE, THE COMPANY NAME, AND 24-HOUR TELEPHONE INFORMATION. | 96838 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1053 | 1998-09-29 | LA | maintenance | UNKNOWN ( COUNTY) | CHEVRON USA INC | UNDER STATIC CONDITIONS AFTER HURRICANE GEORGES, MECHANICAL FLANGE CONNECTIONSEPARATED FROM PIPELINE RESULTING IN NATURAL GAS RELEASE. | 600000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1054 | 1998-11-30 | LA | leaks and spills | UNKNOWN ( COUNTY) | TENNESSEE GAS PIPELINE CO | INTERNAL CORROSION LEAK | 82000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1055 | 1998-12-13 | NM | other | UNKNOWN (MCKINLEY COUNTY) | EL PASO NATURAL GAS CO | A RATE CHANGE WAS NOTICED AT BLUEWATER COMPRESSOR STATION AND THEN A FIRE WASDISCOVERED ON THE PIPELINE RIGHT-OF-WAY AT THE SAME TIME. A RUPTURE OCCURREDON THE TIE-IN TO A MAINLINE VALVE ON LINE 1300. THE FIRE BURNED FORAPPROXIMATELY 4 HOURS CAUSING DAMAGE TO POWER LINES, A CELL PHONE TOWER, AND ASTORAGE SHED. SERVICE WAS CURTAILED TO APPROXIMATELY 75 HOMES IN THE TOP OFTHE WORLD SUBDIVISION. | 150000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1056 | 1998-12-06 | LA | other | UNKNOWN ( COUNTY) | TENNESSEE GAS PIPELINE CO | UNKNOWN DUE TO DAMAGED PIPE BEING UNRECOVERABLE FROM SITE DURING RUPTUREINVESTIGATION. | 750000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1057 | 1998-12-02 | OK | other | UNKNOWN (MCCLAIN COUNTY) | ONEOK GAS TRANSPORTATION, LLC | AT APPROXIMATELY 1:40PM CST ON DECEMBER 2, 1998, AN EMPLOYEE OF ONEOK GASTRANSPORTATION, LLC. (OGT) WAS INJURED BY A 20" PIPELINE CLEANING PIG THATRAPIDLY EXITED A 20" RECEIVER BARREL ON PIPELINE A-1300, LOCATED NORTWEST OFPURCELL, OKLAHOMA. PLEASE NOTE ATTACHEMENT "A" DESIGNATING ITEM NUMBERSREFERENCED BELOW, AND ATTACHMENT "B" WHICH IS AN ISOMETRIC ENGINEERING DRAWINGOF THE RECEIVER. THREE OGT EMPLOYEES, BOBO RENEGAR, LINDSEY SOUTHWARD, ANDJOHN FRYAR, WERE PIGGING A SECTION OF A-1300 20" FROM MAYSVILLE JUNCTION TOPURCELL JUNCTION. THEY ARRIVED AT PURCELL JUNCTION AND PULLED THE 20" FROMCUP PIG, AN ENDURO ADV-3CC-BL (36" O.A.L.), INTO THE RECEIVER, TRIPPING THEPIG SIGNAL (3) AT ABOUT 1:20PM CST. THE A-1300 SIDE VALVE (1) WAS OPENED, ANDTHE 20"RECEIVER VALVE (2) WAS CLOSED. THE 8" KICKER GAS VALVE (6) WAS ALSOCLOSED. BLOWOFF VALVE (4) WAS OPEN ONE-HALF WAY, AND BLOWOFF VALVE (5) WASOPENED COMPLETELY. THE RECEIVER CLOSURE (7) WAS OPENED AND MOVED TO ONESIDE. AFTER FIVE MINUTES LINDSAY SOUTHWARD LOOKED INTO THE RECEIVER BARRELFROM A DISTANCE OF APPROXIMATELY 12 FEET DIRECTLY AWAY AND 6 FEET TO THE SIDEOF THE RECEIVER CLOSURE. HE NOTED THAT THE PIG WAS VISIBLE IN THE TRAP. WEESTIMATE THE DISTANCE FROM THE RECEIVER CLOSURE THREADS TO THE PIG NOSE TO BE3-4 FEET. BOB RENEGAR LOOKED INTO THE RECEIVER BARREL FROM THE IMMEDIATE EDGEOF THE CLOSURE OPENING, AND PUT HIS HEAD DOWN TO INSPECT THE AMOUNT OF SLUDGE,ETC., THAT THE PIG HAD MOVED. BOB MADE A COMMENT ON THE AMOUNT OF FLUIDS THATHAD BEEN MOVED. BOB MADE A COMMENT ON THE AMOUNT OF FLUIDS THAT HAD BEENMOVED, AND AT THAT TIME THE PIF SHOT OUT OF THE END OF THE RECEIVER HITTINGTHE GROUND AT APPROXIMATELY 23 FEET AND ROLLING TO A STOP AT 57 FEET FROM THERECEIVER. LINDSEY SOUTHWARD DESCRIBED THE NOISE THAT OCCURRED AS A DEEP CORKPOPPING SOUND. BOB RENEGAR FELL ON HIS BACK, HIT ABOVE THE RIGHT EYE BY THEPIG AND BLEEDING SEVERELY. NEITHER LINDSEY SOUTHWARD OR JOHN FRYAR WERESTANDING IN A POSITION TO BE STRUCK BY THE PIG, AND WERE INJURED. LINDSEYSOUTHWARD AND JOHN FRYAR PROVIDED ASSISTANCE TO BOB RENEGAR UNTIL MEDICALPERSONNEL ARRIVED, AND TRAVELED TO THE HOSPITAL WITH HIM, WHERE HE WASADMITTED FOR TREATMENT OF SEVERE HEAD INJURIES WHICH ULTIMATELY REQUIREDCORRECTIVE SURGERY. SCOTT HARDY, AN EMPLOYEE OF ONEOK, INC. ARRIVED AT THESITE TO SECURE THE SITE BY CLOSING THE RECEIVER CLOSURE (7) AND CLOSINGBLOWOFF (4) AND (5). FOLLOWING THE ACCIDENT, OGT HAS PERFORMED ANINVESTIGATION TO DETERMINE THE CAUSE OF THE ACCIDENT. INPUT HAS BEEN SOUGHTFROM THE OKLAHOMA CORPORATION COMMISSION'S PIPELINE SAFETY STAFF, AS SEVERALOF THEIR INSPECTORS HAVE SIGNIFICANT PIPELINE OPERATIONS EXPERIENCE. ALSO,REPRESENTATIVES FROM NORSTROM VALVES, INC AND MYLON C. JACOBS SUPPLY HAVEINSPECTED THE 20" RECEIVER VALVE (2). THE INITIAL REPORT FROM NORSTROMINDICATES THAT THE RECEIVER VALVE (2) DOES HAVE MINIMAL LEAKAGE, BUT ISOPERATING PROPERLY AND EFFECTIVELY CONTROLS GAS FLOW FROM THE PURPOSES OFPIGGING OUR PIPELINES. FURTHER, THE BLOWOFF VALVE (4) WAS STILL COMPLETELYOPEN AND WOULD HAVE VENTED ANY GAS THAT HAD LEAKED PAST THE RECEIVER VALVE (2)IS OPERATING PROPERLY. DESPITE OUR EFFORTS TO DETERMINE THE CAUSE OF THEACCIDENT, WE HAVE NOT FOUND THE ANSWER. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1058 | 1998-12-10 | OK | other | UNKNOWN (HUGHES COUNTY) | CENTRAL OKLAHOMA OIL & GAS CO. | ON DECEMBER 10, 1998, CENTRAL OKLAHOMA OIL AND GAS CORP. (OPERATOR) WAS IN THEPROCESS OF REWORKING ONE OF ITS EXISTING UNDERGROUND NATURAL GAS STORAGE WELLSLOCATED IN THE STUART NATURAL GAS STORAGE FACILITY IN HUGHES COUNTY,OKLAHOMA. AT APPROXIMATELY 1:30 PM, WHILE THE OPERATOR WAS PULLING ITS 5 1/2INCH PRODUCTION STRING OUT OF THE WELL. OPERATOR EXPERIENCED A GAS "KICK" INTHE WELL. IN ORDER TO MAINTAIN WELL CONTROL, OPERATOR IMMEDIATELY CLOSED THEPIPE RAM (HYDRILL) BLOWOUT PREVENTER AROUND THE JOINT OF PIPE WAS BEING PULLEDFROM THE WELL. IMMEDIATELY AFTER THE PIPE RAM BLOWOUT PREVENTER WAS CLOSED,OPERATOR INSTALLED A SWEDGE (CAP) ON THE TOP OF THE EXPOSED JOINT OF PIPEEXTENDING THROUGH THE RIG FLOOR. HOWEVER, SOME THE THREADS AT THE TOP OF THEJOINT OF PIPE WERE CRIMPED, AND THUS THE SWEDGE COULD NOT BE COMPLETELYSCREWED DOWN ONTO THE PIPE. AS A RESULT, THE SWEDGE DID NOT HOLD; AND THUS ITWAS BLOWN OFF THE TOP OF THE PIPE AS A RESULT OF THE GAS PRESSURE IN THEPIPE. OPERATOR THEN CLOSED THE BLIND RAM BLOWOUT PREVENTER. HOWEVER, BECAUSEOPERATOR WAS REMOVING A BLAST JOINT AT THE TIME OF THE GAS "KICK", WHICH ISTHICKER THAN THE NORMAL PRODUCTION LINER THAT WAS BEING REMOVED, THE BLINDRAMS DID NOT SHEER OFF THE PIPE AND SEAL THE WELL. AS A RESULT, THE WELLFLOWED INTO THE ATMOSPHERE UNTIL THE WELL WAS BROUGHT BACK INTO CONTROL. APRESSURE CONTROL COMPANY WAS CONTACTED TO ASSIST OPERATOR IN BRINGING THE WELLBACK INTO CONTROL. BECAUSE IT WAS NEARLY DARK BY THE TIME THE PRESSURECONTROL COMPANY ARRIVED, A DECISION WAS MADE TO WAIT UNTIL DAYBREAK THE NEXTMORNING TO RIG UP EQUIPMENT TO BRING THE WELL BACK INTO CONTROL. THE WELL WASBROUGHT BACK INTO CONTROL BY 4PM THE FOLLOWING DAY. THERE WERE NO FIRES, NOPERSONAL INJURIES AND NO PROPERTY DAMAGE OTHER THAN THE LOSS OF AN ESTIMATED7-10 MMCF OF GAS. AS A SAFETY PRECAUTION, DURING THE ENTIRE INCIDENT, ASAFETY PERIMETER OF APPROXIMATELY ONE (1) MILE WAS ESTABLISHED AROUND THEWELL. OTHER THAN NECESSARY PERSONNEL, NO ONE WAS PERMITTED WITHIN AREA.MOREOVER, WITHIN AN AREA APPROXIMATELY THREE (3) MILES DOWNWIND, APPROXIMATELYTHRITY-FOUR (34) PERSONS WERE EVACUATED UNTIL THE WELL WAS BROUGHT BACK INTOCONTROL. DURING THE ENTIRE INCIDENT, DETECTION EQUIPMENT WAS USED TO MONITORTHE AREA AROUND THE WELLBORE TO ENSURE THAT THE GAS WAS DISSIPATING AND NOTSETTLING IN LOW AREAS. LOCAL SHERIFF AND POLICE DEPARTMENTS ASSISTED INPROTECTING THE AREA, AND FIRE EQUIPMENT WAS ALSO AVAILABLE. LOCAL AND AREAOFFICALS PROVIDED PROMPT ASSISTANCE AND SUPPORT DURING THIS TIME. ALTHOUGHTHE FOREGOING INCIDENT DID NOT OCCUR ON OPERATOR'S PIPELINE, THE FOREGOINGWELL IS A PART OF OPERATOR'S TOTAL STORAGE SYSTEM. THEREFORE, OPERATOR ISSUBMITTING THIS INCIDENT REPORT IN THE EVENT IT IS REQUIRED. | 20000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1059 | 1998-12-10 | CA | other | UNKNOWN (KING COUNTY) | SOUTHERN CALIFORNIA GAS CO | PIPELINE WAS MISLOCATED. SPECIAL EQUIPMENT REQUIRED TO MOVE BULL DOZER OFF OFDAMAGED PIPELINE. | 350000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1060 | 1998-11-14 | IL | leaks and spills | UNKNOWN (CHAMPAIGN COUNTY) | PEOPLES GAS LIGHT & COKE CO |  | 345000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1061 | 1998-09-23 | TX | leaks and spills | UNKNOWN (WHARTON COUNTY) | TRUNKLINE GAS CO | LEAK OCCURRED DUE TO LOSS OF WALL THICKNESS RESULTING FROM INTERNAL CORROSION. | 400000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1062 | 1998-12-07 | IL | leaks and spills | UNKNOWN (KANKAKEE COUNTY) | NATURAL GAS PIPELINE CO OF AMERICA | FAILURE OF THE 24' DIAMETER CLASS "C" DRIP RESULTED IN A FIRE. INTENSE HEATFROM THE FIRE EVENTUALLY CAUSE THE 36" DIAMETER CARRIER PIPE TO RUPTURE. | 396100 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1063 | 1998-11-23 | WY | maintenance | UNKNOWN (FREMONT COUNTY) | K N ENERGY INC(KANSAS NEBRASKA GAS CO) | ON NOVEMBER 23, 1998 AT 1:12PM, AN AGENT OF KN ENERGY, MR. DOUG THACKER,REPORTED TO YOU A GAS LEAK ON THE NORTHERN GAS COMPANY (NGC) 16' INTRASTATEPIPELINE. AT 11:30AM ON NOVEMBER 23,1998 THE GAS LEAK WAS CONFIRMED ON THENGC 16' INTRASTATE PIPELINE IN FREMONT COUNTY, SOUTHEAST OF THE TOWN OFRIVERTON. THE GAS LEAK WAS REPAIRED WITH REPLACEMENT PIPE AND PLACED BACK INSERVICE ON NOVEMBER 25, 1998 AT 8AM. EVEN THOUGH THIS INCIDENT DID NOTREQUIRE FEDERAL REPORTING, IT WAS ALSO TELEPHONICALLY REPORTED TO THE NATIONALRESPONSE CENTER BY MR. DOUG THACKER, AS PER YOR RECOMMENDATION. | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1064 | 1998-12-17 | PA | leaks and spills | UNKNOWN (ARMSTRONG COUNTY) | CNG TRANSMISSION CORP | THIS LETTER PRESENTS MY PRELIMINARY FINDINGS REGARDING THE CAUSE OF THERUPTURED OF CNG'S 26-INCH PIPELINE WHICH OCCURRED ON DECEMBER 17, 1998 NEARELDERTON, PENNSYLVANIA. THE RUPTURE WAS CAUSED BY EXTERNAL CORROSION WHICHHAD TAKEN PLACE ON THE BOTTOM OF THE PIPELINE. THE MOST SEVERELY CORRODEDAREA, WHICH CORRESPONDS TO ORIGIN OF THE RUPTURE, WAS ONLY ABOUT 13 INCHES INLENGTH. OTHER THINNED AREAS, NOT AS SEVERELY AFFECTED, WERE FOUND OVER ABOUTA 6-FOOT LONG REGION ALONG THE BOTTOM OF THE PIPE. MEASUREMENTS OF THEREMAINING WALL THICKNESS WITHIN THE ORIGIN REGION PRODUCED VALVES IN SOMELOCATIONS AS SMALL AS 0.087 RO 0.099 INCH. MY RSTRENG CALCULATION BASED ONTHE MEASUREMENTS OVER THE 13-INCH ORIGIN REGION INDICATED A BURST PRESSURE OF876 PSIG. THIS AGREES REASONABLY WELL WITH THE PRESSURE LEVEL AT THE TIME OFTHE INCIDENT 917 PSIG (STATED BY CNG PERSONNEL AT THE RUPTURE SITE). A ROUGH,PRELIMINARY MAP OF REMAINING WALL THICKNESS CONTOURS IS ATTACHED AS IS ADIAGRAM OF THE OVERALL RUPTURE. ABOUT 33.7 FEET OF PIPE INVOLVING TWO JOINTSWERE AFFECTED. | 500000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1065 | 1998-12-16 | TX | maintenance | UNKNOWN ( COUNTY) | AQUILA SOUTHWEST (EX. CLAJON GAS CO) |  | 15000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1066 | 1999-01-17 | LA | other | UNKNOWN ( COUNTY) | TRUNKLINE GAS CO |  | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1067 | 1999-01-02 | OR | maintenance | UNKNOWN (UMATILLA COUNTY) | NORTHWEST PIPELINE CORP |  | 500000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1068 | 1998-12-21 | OR | other | UNKNOWN (JEFFERSON COUNTY) | PG&E GAS TRANSMISSION-NORTHWEST |  | 57000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1069 | 1999-01-17 | LA | leaks and spills | UNKNOWN (OFFSHORE LA COUNTY) | COLUMBIA GULF TRANSMISSION CO | SUSPECT BACTERIA CORROSION. INSTALLED TWO REPAIR CLAMPS AT X=231850.28 ANDX=1367347.55 Y=235176.30. | 350000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1070 | 1999-02-02 | AL | other | UNKNOWN (TALLADEGA COUNTY) | CHILDERSBURG GAS BOARD | AT APPROXIMATELY 7:45 AM, THE BOARD AFTER HOURS OPERATOR WAS NOTIFIED BY THECHILDERSBURG POLICE THAT LINCOLN POLICE HAD CALLED REPORTING AN EXPLOSION ATTHE HOLIDAY INN EXPRESS IN LINCOLN. AT APPROXIMATELY 7:50 AM, BOARDEMPLOYEES, JERRY CARPENTER, GENERAL FOREMAN, AND TONY KELLEY, SERVICETECHNICIAN, DISPATCHED EN ROUTE TO THE SCENE. UPON ARRIVING, JERRY CARPENTERWAS TOLD THAT ONE PERSON HAD BEEN TRANSPORTED TO TALLADEGA HOSPITAL. BOARDEMPLOYEES, MICHEAL MADDOX, GENERAL MANAGER, AND DAVID MARTIN, ASSISTANT TO THEFOREMAN, LEFT AT APPROXIMATELY 8:05 AM. UPON ARRIVING AT THE SCENE, JERRYCARPENTER CHECKED THE GAS METER FOUND ABSOLUTELY NO GAS FLOWING THROUGH THEMETER AND NO EVIDENCE OF FIRE OR GAS LEAK. TURNED THE GAS OFF AND LOCKED OFFAT METER AT 8:13 AM BY JERRY CARPENTER. AT 8:35 AM MICHAEL MADDOX CALLED THEOFFICE AND TOLD EMPLOYEES TO NOTIFY THE PUBLIC SERVICE COMMISSION OFFICE OFPIPELINE SAFETY THAT THERE HAD BEEN SOME TYPE OF EXPLOSION AT THE HOLIDAY INNAT LINCOLN. AT 8:50 AM THE OFFICE WAS CONTACTED BY HAROLD DUNSON OF THEPUBLIC SERVICE COMMISSION AND TOLD THAT HE WAS EN ROUTE TO THE SCENE. ATAPPROXIMATELY 8:40 AM MICHAEL MADDOX AND JERRY CARPENTER FROM THE BOARDACCOMPANIED OFFICER DENNIS ALLBRITTON OF THE CITY OF LINCOLN POLICE DEPARTMENTTO TALLADEGA HOSPITAL TO GET A STATEMENT AND WITNESS THE CONDITIONOF THE INJURED PERSON. UPON ARRIVAL AT THE HOSPITAL THE INJURED PERSON WASINTERVIEWED BY OFFICER ALLBRITTON. HIS NAME IS TIMOTHY JAMES OF DAMRONPLUMBING INC. OF CHATTANOOGA, TENNESSEE. MR. JAMES TOLD THE INVESTIGATORTHAT HE WAS PREPARING TO LIGHT THE WATER HEATERS IN THE UITLITY ROOM OF THEHOTEL. HE STATED THAT HE WAS TOLD BY MR. GAYA TO TURN THE GAS ON AT THEMETER AND BEGIN POURING THE PLUMBING LINES. HE STATED THAT HE HAD TAKEN THEPIPING APART IN THE ROOM AND PURGED THE LINES FOR 2 TO 3 MINUTES. HE THENSAID THAT HE TURNED THE VALVE IN THE BUILDING OFF. HE THEN ATTEMPTED TO PLUGINTO AN ELECTRICAL OUTLET THE ELECTIC IGNITOR FOR THE WATER HEATERS. THEEXPLOSION OCCURRED AT THAT TIME. AB EXACT COPY OF THE STATEMENT CAN BEOBTAINED FROM THE POLICE DEPARTMENT OF THE CITY OF LINCOLN, PHONE NUMBER(205)763-7777. ACCORDING TO THE DOCTOR, MR. JAMES HAD RECEIVED SUPERFICIALBURNS ON HIS NECK, HANDS, AND FACE. HE IS EXPECTED TO RECOVER FULLY WITHOUTCOMPLICATION OR SCARS. MR. JAMES WAS RELEASED AROUND 11 AM. HE RETURNED TOTHE JOB SITE AND GAVE FURTHER STATEMENTS TO PUBLIC SERVICE COMMISSIONREPRESENTATIVE, HAROLD DUNSON, AND THE STATE FIRE MARSHALL. MICHAEL MADDOXAND JERRY CARPENTER RETURNED TO THE SCENE AND AWAITED THE ARRIVAL OF THEPUBLIC SERVICE COMMISSION AND THE STATE FIRE MARSHALL WAS ALREADY ON THESCENE. MR. JOHN, THE STATE FIRE MARSALL, AND HAROLD DUNSON WITH THE PUBLICSERVICE COMMISSION DECIDED IT WOULD BE BETTER FOR AN INDEPENDENT PERSON TO DOTHE PRESSURE TEST ON THE PLUMBING INSIDE THE BUILDING. ALABAMA GAS INTALLADEGA WAS CONTACTED AND ASKED TO RUN THE PRESSURE TEST. THE GASTECHNICIAN TESTED THE PLUMBING AT 6 INCH WATER COLUMN FOR APPROXIMATELY 10MINUTES, NO LEAKS WERE FOUND. RESULTS FROM THESE TEST CAN ALSO BE OBTAINEDFROM THE OFFICE OF PIPELINE SAFETY, STATE OF ALABAMA PUBLIC SERVICE COMMISSIONOR STATE OF ALABAMA OFFICE OF STATE FIRE MARSHALL. AFTER EXAMINING THE METERAT THE SITE, IT WAS APPARENT THAT ABOUT 300 CUBIC FEET OF GAS HAD PASSEDTHROUGH THE METER. BY THE STATEMENT GIVEN AND THE EVIDENCE SEEN, IT ISCONCLUDED THAT AN EXCESS AMOUNT OF GAS WAS ALLOWED INTO THE UTILITY ROOM ANDPROPER TIME NOT ALLOWED FOR VENTING. AS A RESULT, INSERTION OF THEELECTRICAL PLUG CREATED A SPARK WHICH IGNITED THE GAS IN THE ROOM. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1071 | 1999-01-25 | TX | other | UNKNOWN (POLK COUNTY) | MIDCON TEXAS PIPELINE CORP. | EXTEME VARIATIONS IN TRINITY RIVER WATER ELEVATIONS MAY HAVE BEEN ACONTRIBUTING FACTOR. | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1072 | 1999-02-02 | TX | leaks and spills | UNKNOWN (GREGG COUNTY) | TEJAS GAS CORP | MICROALLOYING INTERNATIONAL, INC. WAS COMMISSIONED TO INVESTIGATE THE FAILUREOF A NATURAL GAS PIPELINE FOR TEJAS LLS. THE PIPELINE IS FABRICATED FROM 20OF A NATURAL GAS PIPELINE FOR TEJAS LLC. THE PIPELINE IS FABRICATED FROM 20INCH DIAMETER, 0.312 INCH WALL API 5L GRADE X-60 ERW PIPE. THE PIPE WASMANUFACTURED BY STUPP AND INSTALLED IN JANUARY 1981. ON FEBRUARY 2, 1999 AT9:45 AM LOCATED AT 2,000 FEET NORTHEAST OF THE INTERSECTION OF HIGHWAY 149 ANDFM 2906 IN GREGG COUNTY, TEXAS. OPERATING PRESSURE AT THE TIME OF FAILURE WAS740 PSIG AND THE GAS FLOW RATE AT THE TIME OF FAILURE WAS REPORTED TO BE 10MMCF. SYSTEM DESIGN PRESSURE IS 1348 PSIG. ON SITE INVESTIGATION, BY BOTHTRANSOK AND MICROALLOYING PERSONNEL, REVEALED THAT IN EXCESS OF 20 FEET OF THEPIPELINE WAS TORN FROM THE ORIGINAL INSTALLATION. THE ACTUAL DEBRIS CONSISTEDON ONE SECTION OF PIPE WHICH UNRAVELED IN A SPIRAL PATTERN AS SHOWN INF FIGURE1. THE PRELIMINARY ON SITE INVESTIGATION SHOWED THAT THE RUPTURE MOST LIKELYINITIATED AT THE LOWEST POINT OF THE INSTALLATION WHERE CONDENSATION ANDMOISTURE WOULD BE EXPECTED TO COLLECT. THIS REGION IS SHOWN IN FIGURE 2 WHICHALSO SHOWS THAT SEVERE LOCALIZED CORROSION IS ALIGNED AT THE BOTTOM (SIXO'CLOCK INSTALLED POSITION) OF THE PIPE. THE LOCALIZED CORROSION EXTENDEDAPPROXIMATELY 18 INCHES ALONG THE BOTTOM OF THE PIPE AND WAS SEVERAL INCHESACROSS AT THE WIDEST SECTION. THE ERW WELD ON THIS PARTICULAR SEGMENT WASALIGNED NEAR THE ELEVEN O'CLOCK IN THE INSTALLED POSITION. THE SPIRAL TEAREXHIBITED A DUCTILE FRACTURE SURFACE WITH LOCALIZED DISTORTION NEAR THEFRACTURE SURFACE AND A 45 DEGREE SHEAR SEPARATION ANGLE ALONG THE LENGTH OFTHE TEAR. THERE WERE NO SIGNS OF CORROSION ALONG THE SPIRAL TEAR. THREESECTIONS OF THE DAMAGED PIPE WERE DISPATCHED TO HOUSTON FOR FURTHER ANALYSIS.THE SECTIONS ANALYZED INCLUDE THE LOW POINT REGION WITH LOCALIZED CORROSION,AND TWO SECTIONS REMOVED FROM THE SPIRAL TEAR SEGMENT. | 150000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1073 | 1999-01-30 | LA | other | UNKNOWN (EAST CARROLL PARISH COUNTY) | SOUTHERN NATURAL GAS CO | COMPANY WAS NOTIFIED BY THE PUBLIC OF A LARGE COLUMN OF WATER BLOWING IN THEAIR IN EAST CARROLL PARISH LOUISIANA. EMPLOYEES DISPATCHED TO THE SITEDETERMINED THE CAUSE TO BE A LEAK ON THE 22" NORTH MAIN PIPELING IN LONG LAKEBAYOU. THE AREA HAD RECEIVED 8" OF RAIN PRIOR TO THE LEAK CAUSING FLASHFLOODING AND RAPID CURRENTS IN THE BAYOU. IT IS BELIEVED THAT THE HIGH WATERCONDITIONS CAUSED EXCESSIVE STRESSES ON AND ULTIMATE CRACKING OF A GIRTH WELD30' EAST OF THE BAYOU'S WEST BANK. DIVERS LATER CONFIRMED A 1/2" WIDE CRACKIN THE GIRTH WELD, APPROXIMATELY 17" LONG. THE DECISION WAS MADE TO LEAVE THELINE OUT OF SERVICE UNTIL APRIL 1999, WHEN REPLACEMENT OF LINE HAD BEENPREVIOUSLY SCHEDULED. A METALLURGICAL ANALYSIS WILL BE PERFORMED ON THECRACKED WELD WHEN THE FAILED SEGMENT CAN BE REMOVED. | 165000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1074 | 1999-01-13 | TX | other | UNKNOWN (POLK COUNTY) | MIDCON TEXAS PIPELINE CORP. | EXTREME VARIATIONS IN TRINITY RIVER WATER ELEVATIONS MAY HAVE BEEN ACONTRIBUTING FACTOR. | 200000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1075 | 1999-01-03 | VA | other | UNKNOWN (WYTHE COUNTY) | EAST TENNESSEE NATURAL GAS CO | FIRE FROM NEARBY NATURAL GAS PIPELINE FACILITY DAMAGED EAST TENNESSEE NATURALGAS METER STATION. | 125000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1076 | 1999-02-24 | PA | maintenance | UNKNOWN (POTTER COUNTY) | NATIONAL FUEL GAS SUPPLY CORP | GASKET ON BACK OF VALVE FAILED. THIS FILLED THE COMPRESSOR STATION WITH GAS.THE GAS IGNITED AND BURNT IN THE COMPRESSOR STATION. | 5000000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1077 | 1998-03-29 | TX | leaks and spills | UNKNOWN (POLK COUNTY) | NATURAL GAS PIPELINE CO OF AMERICA | COMPLEX INTERACTION OF SOIL ENVIRONMENT, PIPE MATERIALS, AND OPERATINGCONDITIONS. | 112036 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1078 | 1999-02-26 | WA | other | UNKNOWN (SKAMANIA COUNTY) | NORTHWEST PIPELINE CORP | EXCESSIVE RAIN. LAND MOVEMENT | 4000000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1079 | 1999-03-07 | MI | maintenance | UNKNOWN ( COUNTY) | CONSUMERS POWER CO | CAUSE OF FAILURE WAS LACK OF FUSION IN THE LONGITUDINAL WELD OF A LENGTH OF12" PIPE. | 700000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1080 | 1999-03-03 | NJ | maintenance | UNKNOWN (ESSEX COUNTY) | TRANSCO GAS PIPELINE CORP | INVESTIGATION FOUND THE LEAK TO BE IN A CRACK IN THE WALL OF THE 36" LINE PIPEWHERE THE HOT TAP NIPPLE IS CONNECTED. THE HOT TAP CONNECTION INCLUDING THELINE PIPE CONTAINING THE PIPE IS BEING SENT TO THE METALLURGIST. RESULTS OFTHE METALLURGICAL EXAMS WILL BE FORWARDED IN A SUPPLEMENTAL REPORT DESCRIBINGTHE CAUSE OF THE LEAK. | 80000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1081 | 1999-02-28 | CA | other | UNKNOWN (BUTTE COUNTY) | WILD GOOSE STORAGE INC | WE HAD BEEN OPERATING THE PIPELINE FOR 6 MONTHS AT 1400 PSI. BECAUSE THEOPERATING PRESSURE WOULD BE INCREASING IN THE NEAR FUTURE THE DECISION WASMADE TO BLOCK IN THE WELLS ALLOWING THE PIPELINE PRESSURE TO INCREASE TO ITSMAXIMUM WORKING PRESSURE. WHEN THE PIPELINE REACHED A PRESSURE OF 1580 WEDISCOVERED A LEAK BETWEEN TWO FLANGES. THE PRESSURE WAS REDUCED INTO PG&E'SDISTRIBUTION LINE. THE GASKET WAS IN EXCELLENT CONDITION , THE LEAK MAY HAVEBEEN CAUSED BY IMPROPER TARQUING METHODS. FLANGES WERE HYDRAULICALLY TARQUEDUSING SPECIAL EQUIPMENT. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1082 | 1999-03-23 | LA | other | UNKNOWN ( COUNTY) | COLUMBIA GULF TRANSMISSION CO | A TRAWLING NET DAMAGED THE BLEEDER VALVE ON THE 16" CHECK VALVE SHAFT COVERAND PULLED THE OPERATOR OFF THE 12" VALVE THEREFORE DAMAGING THE VALVESYSTEM. THE BLEEDER VALVE AND NIPPLE ON THE 16" CHECK VALVE WERE REPLACED ANDTHE STEM AND OPERATOR ON THE 12" VALVE WERE REPLACED. | 70000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1083 | 1999-05-13 | TX | leaks and spills | UNKNOWN (ORANGE COUNTY) | MIDCON TEXAS PIPELINE CORP. |  | 45000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1084 | 1999-05-12 | WI | other | UNKNOWN (GREEN COUNTY) | NORTHERN NATURAL GAS CO (ENRON) |  | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1085 | 1999-05-28 | OK | leaks and spills | UNKNOWN (GRADY COUNTY) | ONEOK GAS TRANSPORTATION, LLC | APPARENT CAUSE- INTERNAL CORROSION. LAB TESTING PENDING. TELEPHONIC REPORT#485403APPARENT CAUSE-- INTERNAL CORROSION. LAB TEST PENDING. TELEPHONIC REPORT #485403 | 70000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1086 | 1999-05-20 | LA | maintenance | UNKNOWN ( COUNTY) | COLUMBIA GULF TRANSMISSION CO | DEFECT ON 24" CHECK VALVE AT BOTTOM OF RISER. | 60000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1087 | 1999-06-13 | IL | leaks and spills | UNKNOWN (LIVINGSTON COUNTY) | NORTHERN ILLINOIS GAS CO | AT THE ANCONA STATION, A 12" NATURAL GAS DRIP RUPTURED AND IGNITED RESULTING IN PROPERTY DAMAGE TO THE STATION FACILITIES. THE DRIP IS USED TO COLLECT LIQUIDS FROM THE GATHERING SYSTEM. PRELIMINARY INVESTIGATION SHOWS INTERNAL CORROSION AS THE CAUSE OF THE FAILURE. | 1800000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1088 | 1999-07-10 | TX | leaks and spills | UNKNOWN (PANOLA COUNTY) | NATURAL GAS PIPELINE CO OF AMERICA | INTERNAL CORROSION OF THE CARRIER PIPE | 361000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1089 | 1999-07-18 | WV | other | UNKNOWN (BROOKE COUNTY) | COLUMBIA GAS TRANSMISSION CORP |  | 80000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1090 | 1999-08-26 | TX | other | UNKNOWN (KENT COUNTY) | SPUR, CITY OF | STATE CONTRACTOR WAS WIDENING ROAD AND CUTTING A BAR DITCH AND HIT LINE WITH THE CATERPILLAR. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1091 | 1999-08-23 | WV | leaks and spills | UNKNOWN (MARSHALL COUNTY) | COLUMBIA GAS TRANSMISSION CORP | ON 8/23/99 16" STORAGE LINE 29104 RUPTURED, WITH AN ENSUING FIRE. PRELIMINARY ASSESSMENT OF THE DAMAGE IS 5-7 ACRES OF FARMLAND BURNED, HEAT DAMAGE TO A GARAGE, ROOF DAMAGE TO A MOBILE HOME, AND DAMAGE TO A GRAVEL STATE ROAD (FISH RIDGE ROAD). THERE WERE NO INJURIES. | 71000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1092 | 1999-08-14 | TX | other | UNKNOWN (JACKSON COUNTY) | TRUNKLINE GAS CO | THE PIPELINE FAILED IN A COMPRESSIVE MODE AS A RESULT OF THE PIPELINE HEATING AND EXPANDING APPROXIMATELY 30 INCHES. THE HEATING WAS CAUSED BY THE PRESENCE OF IRON SULFIDE INSIDE THE PIPELINE AND A SUBSEQUENT EXOTHERMIC REACTION THAT RESULTED WHEN AIR WAS INTRODUCED DURING EVACUATION OF THE PIPELINE FOR MAINTENANCE WORK. THE DISCOVERY THAT THE PIPELINE HAD FAILED IN THIS MODE WAS MADE AFTER THE MAINTENANCE WORK WAS COMPLETED AND DURING THE PURGING OPERATION WITH GAS AT APPROXIMATELY 50 PSIG. THE PIPELINE WAS FOUND TO HAVE FAILED IN TWO LOCATIONS APPROXIMATELY 1,300 FEET APART. | 500000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1093 | 1999-08-16 | MI | other | UNKNOWN (GOGEBIC COUNTY) | GREAT LAKES GAS TRANSMISSION CO | A LIGHTNING STRIKE CAUSED THE MAIN LINE VALVE (WHICH IS NORMALLY CLOSED) TO CYCLE PARTIALLY OPEN. THIS PARTIALLY OPEN CONDITION CAUSED VIBRATION IN THE MAIN LINE VALVE ASSEMBLY TO OCCUR. THIS VIBRATION SUBSEQUENTLY CAUSED A CRACK TO DEVELOP IN THE HEAT-AFFECTED ZONE ADJACENT TO A 2-INCH GIRTH WELD ON A 12"X12" EXTRUDED TEE FITTING SITUATED ON THE VALVE BLOWOFF. THE PROPERTY DAMAGE ESTIMATE INCLUDES $154,423 FOR THE COST OF GAS BLOWN DOWN AND PURGED TO FACILITATE THE REPAIR. | 163000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1094 | 1999-08-11 | TX | leaks and spills | UNKNOWN (CRANE COUNTY) | DYNEGY MIDSTREAM SERVICES, L.P. | THERE WERE NO SIGNS OF OUTSIDE PIPELINE CORROSION OR DAMAGE OF ANY TYPE. CORROSION COUPONS DO NOT INDICATE ANY PROBLEMS ASSOCIATED WITH THE CORROSION PROGRAM. PIPELINE OPERATION WAS NORMAL, NO PRESSURE FLUCTUATIONS WERE NOTED AT THE TIME OF FAILURE. ACCORDING TO THE METALLURGICAL INVESTIGATION, MILD ACIDIC. CORROSION ATTACKED THE PIPE WALL FROM THE INSIDE THINNING THE WALLS OF THE PIPE AT THE 12 OCLOCK POSITION. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1095 | 1999-09-23 | LA | leaks and spills | UNKNOWN (nan COUNTY) | BASIN EXPLORATION INC |  | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1096 | 1999-08-15 | LA | other | UNKNOWN (PLAQUEMINES COUNTY) | MID LOUISIANA GAS CO | DRAGLINE CAUGHT PIPE WITH ONE TOOTH OF BUCKET. | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1097 | 1999-09-01 | TX | other | UNKNOWN (HUDSPETH COUNTY) | EL PASO NATURAL GAS CO | AT APPROXIMATELY 4:30 PM, SEPT 1, 1999 THREE EL PASO NATURAL GAS EMPLOYEES RECEIVED SECOND DEGREE BURNS TO THEIR FACES AND WRISTS WHEN A FLASH FIRE OCCURRED AFTER PLACING A BLIND FLANGE BACK ON A 6-INCH BLOWOFF. A 12-INCH BYPASS BEING INSTALLED WHEN GAS WAS IGNITED WHEN WELDING A PUP TO LEVEL A 2-INCH VALVE OPERATOR TO VALVE 20 1/2. THE EMPLOYEES WERE TREATED ON SITE AND RUSHED TO THE HOSPITAL WHERE THEY STAYED OVERNIGHT. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1098 | 1999-09-13 | AZ | other | UNKNOWN (GREENLEE COUNTY) | EL PASO NATURAL GAS CO | AT 9:30 AM A FARMER PLOWING A FIELD HIT AND PUNCTURED THE 6 5/8 INCH PIPELINE BETWEEN VALVE 2 AND VALVE 3. BOTH VALVES WERE SHUT-IN TO ISOLATE THE SEGMENT. HIGHWAY 75 FROM MILE MARKERS 395 TO 400 WAS CLOSED AND THE NEARBY VALLEY VIEW TRAILER PARK WAS EVACUATED. AT 11:15 AM, THE LINE WAS BLOWN DOWN AND THE AREA MADE SAFE. THE HIGHWAY WAS THEN REOPENED AND THE RESIDENTS WERE LET BACK INTO THEIR HOMES BY 11:30. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1099 | 1999-09-12 | NM | maintenance | UNKNOWN (SAN JUAN COUNTY) | EL PASO NATURAL GAS CO | ON SEPT 12, 1999, GAS CONTROL RECEIVED A CALL AT 8:05 PM FROM THE SHIPROCK POLICE ABOUT A RUPTURE ON OUR PIPELINE. EPNG PERSONNEL RESPONDED TO THE CALL AND ISOLATED THE SEGMENT BEWTEEN VALVES 2 1/2 AND VALV3 3. REPAIR CREWS WERE ON SITE THE NEXT MORNING AND REPLACED THE SEGMENT WITH 2 JOINTS OF PIPE. THE LINE WAS BACK IN SERVICE BY THE EVENING OF SEPT. 13. NRC # 498467 | 174800 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1100 | 1999-09-08 | TX | other | UNKNOWN (nan COUNTY) | NORTHERN NATURAL GAS CO (ENRON) | A 2" THREADED PIPE NIPPLE AND VALVE THAT WAS ATTACHED TO A 12" PIPELINE TEE AND FLANGE WAS CAUGHT BY A FISHING NET. THE PIPE NIPPLE WAS BENT SLIGHTLY AT ITS THREADED CONNECTION, RESULTING IN A SMALL LEAK. | 150000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1101 | 1999-09-23 | TN | other | UNKNOWN (OBION COUNTY) | WILLIAMS GAS PIPELINE - TEXAS GAS | ON THURSDAY, SEPTEMBER 23, 1999, AT 1:00 A.M. CENTRAL STANDARD TIME. WILLIAMS GAS PIPELINE-TEXAS GAS SUSTAINED AN IN-SERVICE FAILURE ON ITS 26" MAINLINE SYSTEM. NO. 2 PIPELINE IN OBION COUNTY, TENNESSEE. THE LOCATION OF THE INCIDENT WAS MILEPOST 346+5181, WHICH IS APPROXIMATELY 2.75 MILES NORTHEAST OF THE CITY OF KENTON, TENNESSEE, AND APPROXIMATELY ONE MILE DOWNSTREAM OF TEXAS GAS KENTON, TN, COMPRESSOR STATION. THERE WERE NO INJURIES OR FATALITIES RESULTING FROM THIS INCIDENT. THERE WERE NO SERVICE INTERUPTIONS AS A RESULT OF THE FAILURE. TEXAS GAS STAFF METALLURGIST HAS DETERMINED THE FAILURE WAS INITIATED BY A STRESS CORROSION CRACK THAT EXTENDED 5 5/8" ALONG THE LONGITUDINAL AXIS OF THE PIPE. THE FAILURE RESULTED IN A 29-FOOT LENGTH OF PIPE BEING SEPARATED FROM THE CONTIGOUS PIPELINE SYSTEM. THE PIPELINE SYSTEM HAS BEEN UNDER CATHODIC PROTECTION SINCE ITS CONSTRUCTION IN 1952. THE LINE HAD BEEN HYDROSTATICALLY TESTED IN 1964 AND 1985. PROPERTY DAMAGE WAS CONFINED TO TEXAS GAS FACILITIES. THE INCIDENT OCCURRED IN A FIELD DEDICATED TO CROP FARMING WHERE THERE WERE NO DWELLINGS WITHIN THE PIPELINE CORRIDOR. ESTIMATED COST OF REPAIR AND GAS LOSS ARE DEFINED AS FOLLOWS: GAS LOSS: $305,000, MATERIAL $4,000, LABOR $3,000, EQUIPMENT $750, X-RAY $600, TOTAL COST OF DAMAGE AND REPAIR - 312,750. AFTER THE IN-SERVICE FAILURE DESCRIBED ABOVE, COMPANY PERSONNEL HYDROSTATICALLY RETESTED TWO BLOCK VALVE SECTIONS (APPROX. 20 MILES) OF THE LINE PIPE DOWNSTREAM OF THE KENTON COMPRESSOR STATION. ONE TEST FAILURE OCCURRED WHICH WAS ATTRIBUTED TO STRESS CORROSION CRACKING. THE ENTIRE 20-MILE SEGMENT WAS SUCCESSFULLY RETESTED TO 100% SPECIFIED MINIMUM YIELD STRENGTH BY OCTOBER 18, 1999. PERMANENT REPAIRS AT THE SITE OF THE SERVICE FAILURE CONSISTED OF REPLACEMENT OF APPROXIMATELY 80 OF LINE PIPE. POST-TEST CLEAN-UP ACTIVITIES ARE UNDERWAY. IT IS ANTICIPATED THE LINE WILL BE RETURNED TO SERVICE WITHIN A WEEK. | 312750 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1102 | 1999-09-25 | LA | leaks and spills | UNKNOWN (nan COUNTY) | SEA ROBIN PIPELINE CO | A PINHOLE LEAK WAS DETECTED VISUALLY AS BUBBLES ON THE WATER SURFACE. ISOLATION VALVES WERE CLOSED TO INACTIVATE THE PIPELINE. A REPAIR CLAMP WAS INSTALLED WAS COST OF REPAIRS ONLY. | 200000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1103 | 1999-10-05 | NV | other | UNKNOWN (CLARK COUNTY) | SOUTHWEST GAS CORP | WHILE AN OPERATOR WITH ACME ELECTRIC WAS OPERATING A FRONT END LOADER, HE STRUCK AND DAMAGED AN 8" STEEL PSIG GAS MAIN. THE CONTRACTOR DID HAVE A CURRENT USA (ONE CALL) TICKET BUT WAS WORKING OUTSIDE OF THE SPECIFIED AREA. THE GAS MAIN LOCATE WAS CORRECT AND PERMANENT LINE MARKERS WERE VISIBLE. THERE WAS NO IGNITION OF GAS OR INJURIES AS A RESULT OF THE INCIDENT. A TOTAL OF 128,891 THERMS OF GAS LOST. THERE WERE 62 CUSTOMER OUTAGES INCLUDING THE JAMES HARDIE GYPSUM PLANT DUE TO THE DAMAGE. THE JAMES HARDIE GYPSUM PLANT IS MAKING AN ALLEGED LOSS OF PRODUCTION CLAIN OF $141,130. | 182100 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1104 | 1999-09-20 | MT | other | UNKNOWN (JEFFERSON COUNTY) | MONTANA POWER CO | A SEMI TRACTOR TRAILER RIG ROLLED FROM A TRUCK STOP DOWN AN EMBANKMENT AND INTO THE CITY GATE STATION AT MP 26.6 ON THE MPC 4" EAST HELENA-BOULDER NATURAL GAS TRANSMISSION LINE. THE IMPACT DESTROYED THE GATE STATION BUILDING AND BROKE PIPING INSIDE THE YARD. HIGH PRESSURE GAS BLEW BUT DID NOT IGNITE. THE TOWN OF BOULDER (500 CUSTOMERS) WAS RENDERED OUT OF GAS AND HAD TO BE RELIT. NO INJURIES OCCURRED. | 114000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1105 | 1999-10-16 | TX | other | UNKNOWN (nan COUNTY) | COASTAL OIL & GAS CORP (SUBSIDIARY OF ANR PROD CO) | FITTING WAS NOT PROPERLY TIGHTENED AT THE NEW PIPELINE TIE-IN | 74287 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1106 | 1999-10-27 | LA | leaks and spills | UNKNOWN (CAMERON COUNTY) | WILLIAM FIELD SERVICES | LEAK WAS CAUSED BY INTERNAL BACTERIAL CORROSION AT THE 5:30 POSITION. | 250000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1107 | 1999-10-26 | TX | maintenance | UNKNOWN (nan COUNTY) | WILLIAM FIELD SERVICES | A 12" VALVE BODY BLEED ORIFICE HAD BEGUN TO LEAK AS A RESULT OF FLATTENED THREADS ON THE ORIFICE SCREW. THE AFFECTED VALVE WAS 12" TAP VALVE. THE VALVE BODY ORIFICE THREADS WERE RE-DRILLED TO ACCEPT A LARGER 3/4" SCREW TO SECURE THE ORIFICE FROM LEAKING. | 60000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1108 | 1999-11-03 | OK | other | UNKNOWN (BRYAN COUNTY) | ENOGEX INC (EX. MUSTANG FUEL CORP) | DIAPHRAM RUPTURE DUE TO WEATHER FATIGUE CAUSED DUMP VALVE FAILURE ON ESD VENT VALVE, CAUSING ESD VENT TO OPEN AND RELEASE GAS. | 73000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1109 | 1999-11-13 | AK | other | UNKNOWN (nan COUNTY) | BP EXPLORATION ( ALASKA), INC | CRACK IN A GIRTH WELD. A FAILURE ANALYSIS WILL BE PERFORMED ON WELD TO DETERMINE CAUSE. SUPPLEMENTAL INFO:WIND INDUCED VIBRATION OF THE ELEVATED PIPELINE CREATED HIG CYCLIC STRESSES CAUSING A FATIGUE FAILURE OF A GIRTH WELD. THE WIND INDUCED VIBRATION WAS OF THE SECOND MODE, ONE THOUGHT TO EXIST BUT HAD NEVER BEEN WITNESSED ON NORTH SLOPE ALASKA PIPELINES. A COPY OF THE COMPLETE FAILURE ANALYSIS HAS BEEN ENCLOSED. | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1110 | 1999-11-17 | AR | other | UNKNOWN (WASHINGTON COUNTY) | ARKANSAS WESTERN GAS CO | A THIRD PARTY CONTRACTOR WAS CUTTING IN A NEW SUBDIVISION STREET WITH A LARGE EARTH MOVER WHEN IT SEVERED A 4 1/2" STEEL TRANSMISSION LINE. THE GAS IGNITED SEVERELY DAMAGING THE EARTH MOVER. | 90000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1111 | 1999-11-11 | IA | other | UNKNOWN (FAYETTE COUNTY) | NORTHERN NATURAL GAS CO (ENRON) | TILLING CONTRACTOR CHANGED PLANS WITHOUT SUBMITTING NEW LOCATE REQUEST OR NOTIFYING NNG. CONTRACTOR HIT LINE WITH TILLING PLOW. | 145184 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1112 | 1999-11-11 | OK | other | UNKNOWN (LE FLORE COUNTY) | OKLAHOMA NATURAL GAS CO | LANDOWNER/DEVELOPER CUT THE LINE WHILE EXCAVATING. THE OPERATOR BROKE HIS LEG BY JUMPING OFF THE DOZER AND WAS SUBSEQUENTLY HOSPITALIZED. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1113 | 1999-11-11 | CA | other | UNKNOWN (COLUSA COUNTY) | PACIFIC GAS & ELECTRIC CO | OUR INVESTIGATION DISCLOSED THAT APPROXIMATELY 1406 HOURS ON NOVEMBER 11, 1999, A RECLAMATION DISTRICT NUMBER 1004 EQUIPMENT OPERATOR HIT A 12-INCH STEEL NATURAL GAS TRANSMISSION PIPELINE NEAR THE INTERSECTION OF GRIDLEY AND BUTLER ROAD, ALLOWING GAS TO ESCAPE. THERE WAS NO REQUEST TO LOCATE AND MARK OUR FACILITIES. WE WERE NOTIFIED OF THIS INCIDENT AT 1415 HOURS BY THE COLUSA COUNTY SHERIFFS DEPARTMENT AND IMMEDIATELY DISPATCHED PERSONNEL TO THE SCENE. COMPANY PERSONNEL ARRIVED ON THE SCENE AT 1515 HOURS. THE FLOW OF GAS WAS CONTROLLED AT 1533 HOURS BY CLOSING VALVES. PERMANANET REPAIRS WERE COMPLETED AT 2010 HOURS ON NOVEMBER 13, 1999. THERE WAS NO INTERRUPTION OF SERVICE TO CUSTOMERS. THERE WERE NO INJURIES OR FATALITIES AS A RESULT OF THIS INCIDENT. DAMAGE TO COMPANY PROPERTY IS ESTIMATED TO BE $103,000; THERE WAS NO THIRD PARTY PROPERTY DAMAGE. | 103000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1114 | 1999-11-09 | KS | leaks and spills | UNKNOWN (MIAMI COUNTY) | PANHANDLE EASTERN PIPELINE CO | FAILURE IN AREA OF GENERAL CORROSION. | 300000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1115 | 1999-11-24 | CA | other | UNKNOWN (ALAMEDA COUNTY) | PACIFIC GAS & ELECTRIC CO |  | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1116 | 1999-12-09 | MS | leaks and spills | UNKNOWN (COVINGTON COUNTY) | KOCH GATEWAY PIPELINE CO | SMALL EXTERNAL CORROSION PIT LEAKING IN CASING UNDER ROAD. RELEASE DID NOT CAUSE A THREAT TO PUBLIC SAFETY BUT WAS REPORTED DUE TO REPAIR COST EXCEEDING $50,000 REPORTING LIMIT. | 120000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1117 | 1999-12-18 | TX | other | UNKNOWN (THOMPSONVILLE COUNTY) | TEJAS GAS OPERATING LLC | TEXAS ONE CALL LAW PROCEDURES NOT FOLLOWED BY CONTRACTOR. SEE ATTACHEMENT "A" | 200000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1118 | 2000-01-01 | MI | leaks and spills | UNKNOWN (GRAND TRAVERSE COUNTY) | MICHIGAN CONSOLIDATED GAS CO (MICHCON) | TWO SNOWMOBILERS IN THE PIPELINE RIGHT OF WAY HAD MECHINCAL PROBLEMS. THEY WERE USING A CIGARETTE LIGHTER TO SEE WITH. WE HAVENT BEEN ABLE TO DETERMINE IF GASOLINE VAPOR OR LEAKING NATURAL GAS FIRST IGNITED CAUSING THE INJURIES. BOTH WERE TREATED AND RELEASED. | 2000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1119 | 1999-12-22 | OK | maintenance | UNKNOWN (LATIMER COUNTY) | RELIANT ENERGY - ARKLA | PIPE SETTING ON ROCK LEDGE, WHICH CAUSED DENT AND PUNCTURE IN PIPE. NO CORROSION FOUND. SMALL LEAK LOCATED, NO DAMAGE TO PROPERTY EXCEPT PIPELINE. | 80000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1120 | 1999-12-20 | CA | other | UNKNOWN (SAN BENITO COUNTY) | PACIFIC GAS & ELECTRIC CO |  | 122000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1121 | 2000-01-24 | MA | other | UNKNOWN (MIDDLESEX COUNTY) | TENNESSEE GAS PIPELINE CO | MAIN LINE VALVE DID NOT FULLY CLOSE CAUSING OPERATOR TO VENT TO ATMOSPHERE, RESULTING IN LOCAL AUTHORITIES EVACUATING NEARBY VICINITY. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1122 | 1999-12-10 | TX | other | UNKNOWN (LIVE OAK COUNTY) | HOUSTON PIPELINE CO | THE UNKNOWN ACCUMULATION OF LIQUID FUMES IN THE TRENCH AREA. IGNITED BY WELDERS CUTTING TORCH. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1123 | 1999-12-31 | TX | leaks and spills | UNKNOWN (nan COUNTY) | NORTHERN NATURAL GAS CO (ENRON) |  | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1124 | 2000-01-11 | NJ | other | UNKNOWN (HUNTERDON COUNTY) | COLUMBIA GAS TRANSMISSION CORP | WHILE DRIVING A PIECE OF PIPE IN THE GROUND TO ANCHOR A DRILLING MACHINE, A CONTRACTOR PUNCTURED THE PIPELINE. | 70000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1125 | 2000-02-01 | LA | maintenance | UNKNOWN (OUACHITA COUNTY) | TENNESSEE GAS PIPELINE CO | APPARENT FAILURE IN A WELD. | 190000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1126 | 2000-01-27 | LA | leaks and spills | UNKNOWN (nan COUNTY) | RELIANT ENERGY - ARKLA | PIPE FAILED IN BOTTOM OF SMALL CREEK, INITAL EVALUATION APPEARS THAT ERROSION CORR. CAUSED GENERAL THINNING OF THE PIPE WALL ON TOP. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1127 | 2000-02-02 | TX | leaks and spills | UNKNOWN (POLK COUNTY) | NATURAL GAS PIPELINE CO OF AMERICA (KMI) | INTERACTION OF SOIL ENVIRONMENT PIPE MATERIAL AND OPERATING CONDITIONS | 129000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1128 | 2000-02-18 | NY | maintenance | UNKNOWN (ONONDAGA COUNTY) | TENNESSEE GAS PIPELINE CO | CRACK IN PIPE WALL DUE TO MANUFACTURING DEFECT (DETERMINED AFTER EXCAVATION). | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1129 | 2000-02-11 | PA | other | UNKNOWN (CLARION COUNTY) | CNG TRANSMISSION CORP | ON FRIDAY, FEBRUARY 11, 2000, CNG TRANSMISSION PIPELINE LN-200 WAS STRUCK BY A CONTRACTORS DOZER WORKING FOR TEXAS KEYSTONE, INC WHILE EXCAVATING A DRAINAGE POND/PIT FOR A NEW PRODUCTION WELL. TEXAS KEYSTONE PLACED A ONE-CALL NOTICE AFTER THE INCIDENT BUT NO PRIOR NOTICATION PERTAINING TO THE SUBJECT EXCAVATION SITE WAS MADE ANY TIME IN ADVANCE OF THE PLANNED EXCAVATION AS REQUIRED BY ACT 287. | 75000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1130 | 2000-02-05 | TX | other | UNKNOWN (FREESTONE COUNTY) | TXU LONE STAR PIPELINE | FAILED PORTION OF PIPE WAS SENT TO LAB FOR ANALYSIS TO IDENTIFY ROOT CAUSE OF FAILURE. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1131 | 2000-01-27 | TX | other | UNKNOWN (WISE COUNTY) | TXU LONE STAR PIPELINE | FAILED PORTION OF PIPE SENT TO LAB FOR ANALYSIS TO IDENTIFY ROOT CAUSE OF FAILURE. THIRD PARTY CONTRACTOR WAS WORKING IN PIPELINE RIGHT OF WAY BUT IT IS NOT KNOWN IF THIS IS A CONTRIBUTING FACTOR AT THIS TIME. SUPPLEMENTAL INFORMATION : METALLURGICAL TESTING CONCLUDED THAT FAILURE WAS RESULT OF RECENT MECHANICAL DAMAGE BY OUTSIDE FORCE. SOURCE OF DAMAGE IS UNKNOWN. | 130000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1132 | 2000-01-29 | FL | leaks and spills | UNKNOWN (BREVARD COUNTY) | FLORIDA GAS TRANSMISSION CO (ENRON) |  | 263000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1133 | 2000-02-23 | MI | other | UNKNOWN (CLARE COUNTY) | ANR PIPELINE CO | THERE WERE SEVERAL MECHANISMS, COMBINED, THAT CONTRIBUTED TO THE RUPTURE OF THE 12" LINCOLN PIPELINE. THE CONTRIBUTING FACTORS WERE: FROST HEAVE; MISMATCH OF PIPE ENDS DUE TO HIGH-LOW DURING TIE-IN OF A 15-FOOT REPLACEMENT IN 1993 (NOTE: THE HIGH-LOW WAS WITHIN ACCEPTABLE LIMITS IMPOSED BY SECTION 6.3.2 OF API STANDARD 1104 AT THE TIME OF REPLACEMENT).; RESIDUAL FORCES APPLIED DURING CLAMPING OF THE PIPE REPLACEMENT ENDS TO THE EXISTING PIPELINE; UNUSUALLY COLD CLIMATE ON THE DAY OF THE RUPTURE; AND NON-HOMOGENEOUS MATERIAL IN THE WELD METAL AT THE ORIGIN OF THE FRACTURE THAT REDUCED EFFECTIVE WALL THICKNESS (NONFUSION/SLAG), BUT WAS WITHIN API STANDARD 1104 ACCEPTANCE CRITERIA. | 297000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1134 | 2000-02-18 | TX | other | UNKNOWN (EL PASO COUNTY) | SOUTHERN UNION GAS CO | THIRD PARTY CONTRACTOR EXVACATING FOR DRAINAGE IMPROVEMENTS RELATED TO DEVELOPMENT OF COMMERCIAL PROPERTY FAILED TO CALL FOR UTILITY LOCATIONS PRIOR TO EXCAVATING. EQUIPMENT STRUCK AND DAMAGED 16" WRAPPED STEEL GAS MAIN CAUSING LEAKAGE. ISOLATION OF MAIN BY CLOSING MAIN LINE VALVES MITIGATED LEAKAGE. DAMAGE TEMPORARY REPAIRED WITH A WELD SLEEVE. DAMAGED SECTION OF PIPE WILL BE REMOVED AND REPLACED WITH NEW PIPE AS PERMANENT REPAIR. | 79000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1135 | 2000-02-27 | PA | leaks and spills | UNKNOWN (POTTER COUNTY) | TENNESSEE GAS PIPELINE CO | STRESS CORROSION CRACKING AUGMENTED BY A BEND IN THE PIPE. | 143000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1136 | 2000-02-23 | LA | leaks and spills | UNKNOWN (CAMERON COUNTY) | WILLIAMS ENERGY GROUP-FIELD SERVICES | LEAK WAS CAUSED BY INTERNAL BACTERIAL CORROSION AT THE 5:30 POSITION. | 120000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1137 | 2000-02-25 | TX | other | UNKNOWN (NOLAN COUNTY) | TXU LONE STAR PIPELINE |  | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1138 | 2000-03-16 | MS | other | UNKNOWN (COVINGTON COUNTY) | KOCH GATEWAY PIPELINE CO | VERY SMALL RELEASE WAS DETECTED USING LEAK DETECTION EQUIPMENT. BECAUSE OF THE PROXIMITY OF THE RELEASE TO A ROAD, A NEW CROSSING IS REQUIRED TO MAKE THE REPAIR. RELEASE DID NOT CAUSE A THREAT TO PUBLIC SAFETY BUT WAS REPORTED DUE TO COST EXCEEDING $50,000 REPORTING THRESHOLD. | 110000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1139 | 2000-03-15 | MS | other | UNKNOWN (WARREN COUNTY) | KOCH GATEWAY PIPELINE CO | VERY SMALL RELEASE WAS DETECTED USING LEAK DETECTION EQUIPMENT. BECAUSE OF THE PROXIMITY OF THE RELEASE TO ROAD, A NEW CROSSING IS REQUIRED TO MAKE THE REPAIR. RELEASE DID NOT CAUSE A THREAT TO PUBLIC SAFETY BUT WAS REPORTED DUE TO REPAIR COST EXCEEDING $50,000 REPORTING THRESHOLD. | 130000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1140 | 2000-03-08 | NV | other | UNKNOWN (CLARK COUNTY) | SOUTHWEST GAS CORP | WHILE AN OPERATOR WITH M&M CONSTRUCTION WAS GRADING FOR A WALL WITH A D-9 CAT, HE STRUCK AND DAMAGED A 16" STEEL; 300 PSIG GAS MAIN. THE CONTRACTOR DID HAVE A CURRENT USA (ONE CALL) TICKET. THE GAS MAIN LOCATE WAS CORRECT AND PERMANENT LINE MARKERS WERE VISIBLE. THERE WAS NO IGNITION OF GAS OR INJURIES AS A RESULT OF THE INCIDENT. A TOTAL OF 197,141 THERMS OF GAS WAS LOST. THERE WERE 2 CUSTOMER OUTAGES INCLUDING A PARTIAL OUTAGE AT THE SAGUARO POWER PLANT AND PABCO GYSUM PLANT DUE TO THE DAMAGE. | 76170 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1141 | 2000-03-22 | TX | leaks and spills | UNKNOWN (KARNES COUNTY) | PG & E TEXAS PIPELINE, L.P. | PG&E TEXAS PIPELINE, LP WAS NOTIFIED THAT A PIPELINE NORTH OF OUR BURNELL COMPRESSOR STATION HAD BLOWN OUT AND WAS ON FIRE. EMPLOYEES VERIFIED THAT THIS WAS OUR EAST SADF 20" (THE SITE OF THE BLOWOUT WAS APPROXIMATELY 8 MILES SOUTH OF KENEDY, TX ON US HWY 181), AND IMMEDIATELY SHUT DOWN COMPRESSOR UNITS AND CLOSED ISOLATION VALVES TO SECURE THE AREA. WORK BEGAN THE SAME DAY, MARCH 22, 2000 TO GET THE ROAD REPAIRS COMPLETED TO US HWY 81 AND THE EAST SADF 20" PIPELINE RETURNED TO SERVICE. THE PIPE FROM THE BLOWOUT IS BEING ANALYZED BY SOUTHWEST RESEARCH TO DETERMINE THE CAUSE OF THE BLOWOUT. | 360000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1142 | 2000-03-22 | MS | other | UNKNOWN (JEFFERSON DAVIS COUNTY) | KOCH GATEWAY PIPELINE CO | MINOR RELEASE UNDER ROAD. RELEASE DID NOT CAUSE A THREAT TO PUBLIC SAFETY BUT WAS REPORTED DUE TO REPAIR COST EXCEEDING $50,000 REPORTING LIMIT. | 78771 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1143 | 2000-03-27 | OK | leaks and spills | UNKNOWN (GRAY COUNTY) | NATURAL GAS PIPELINE CO OF AMERICA (KMI) | INTERACTION OF SOIL ENVIRONMENT, PIPE MATERIAL AND OPERATING CONDITIONS. | 150000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1144 | 2000-03-30 | CA | other | UNKNOWN (KERN COUNTY) | PACIFIC GAS & ELECTRIC CO | A SEMITRAILER DROVE OFF THE ROAD, KNOCKING DOWN THE CHAIN LINK FENCE SURROUNDING THE STATION. THE TRUCK THEN STRUCK AND DEMOLISHED THE BUILDING THAT HOUSED SCADA CONTROLS FOR PLS 3. A RADIO ANTENNA ON TOP OF THE BUILDING WAS KNOCKED DOWN AND STRUCK THE SENSING LINE TO BLOW OFF VALVE A ON LINE 300-A. | 200000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1145 | 2000-04-24 | LA | leaks and spills | UNKNOWN (nan COUNTY) | ANR PIPELINE CO | SUSPECTED INTERNAL CORROSION - PINHOLE LEAK AT THE 5 OCLOCK POSITION | 79000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1146 | 2000-04-26 | LA | leaks and spills | UNKNOWN (nan COUNTY) | TENNESSEE GAS PIPELINE CO | LEAK UPSTREAM OF CHECK VALVE AT SIX OCLOK POSITION. | 150000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1147 | 2000-05-02 | MS | other | UNKNOWN (WASHINGTON COUNTY) | WILLIAMS GAS PIPELINE - TEXAS GAS | FLASH FIRE ONLY NO FAILURE. ON TUESDAY MAY 2, 2000 AT 12:10 P.M. CENTRAL STANDARD TIME, AN INCIDENT OCCURRED DURING A TURBINE CONSTRUCTION PROJECT AT THE WILLIAMS GAS PIPELINE-SOUTHCENTRAL COMPRESSOR STATION AT GREENVILLE, MS. THE LOCATION OF THE INCIDENT WAS NEAR MILEPOST 114+0046 ON THE COMPANYS MAINLINE SYSTEM PIPELINE IN WASHINGTON COUNTY, MS. A FLASH FIRE OCCURRED WHEN CONTRACTOR EMPLOYEES WERE BEGINNING TO INSTALL AN ISOLATION CAP ON A 26-INCH DIAMETER NATURAL GAS LINE. NO FATALITIES RESULTED FROM THIS EVENT, ALTHOUGH ONE COMPANY EMPLOYEE AND FIVE CONTRACTOR EMPLOYEES WERE INJURED. ALL THE INJURED WERE TRANSPORTED TO DELTA REGIONAL HOSPITAL IN GREENVILLE WHERE THEY WERE LISTED IN STABLE CONDITION AND HAVE CONTINUED TO IMPROVE. THE FIRE OR POLICE DEPARTMENTS WERE NOT DISPATCHED. THE FIRE EXTINGUISHED ITSELF. ALL WILLIAMS GAS PIPELINE-SOUTHCENTRAL FACILITIES WERE IMMEDIATELY SECURE AND THERE WAS NO DANGER TO THE SURROUNDING AREA. THERE WERE NO SERVICE INTERRUPTIONS AS A RESULT OF THE INCIDENT. EVIDENCE AVAILABLE HAS NOT ALLOWED DETERMINATION OF CAUSE AT THIS TIME. THE CAUSE OF THE INCIDENT CONTINUES TO BE INVESTIGATED. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1148 | 2000-05-07 | OK | other | UNKNOWN (ATOKA COUNTY) | NATURAL GAS PIPELINE CO OF AMERICA (KMI) | A FIRE OCCURRED IN THE STATIONS SERVICE BUILDING. THE BUILDING WHICH HOUSES THE GENERATORS, AIR COMPRESSORS CONTROL ROOM TECH. SHOP BREAK ROOM OFFICE AND STORAGE AREA WAS HEAVILY DAMAGED. WITH THE EXCEPTION OF THE TWO GENERATORS ALL CONTENTS OF THE BUILDING WERE DESTROYED. | 1950000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1149 | 2000-05-18 | KY | other | UNKNOWN (PIKE COUNTY COUNTY) | COLUMBIA GAS TRANSMISSION CORP | IN 1999 THIS PIPELINE WAS RELOCATED TO THE CURRENT LOCATION AT THE REQUEST OF THE SURFACE MINING COMPANY. A ROW OF TREES WAS LEFT IN PLACE AS A BUFFER BETWEEN THE MINE AREA AND COLUMBIAS RIGHT-OF-WAY. THE RELOCATION WAS COMPLETED IN NOVEMBER 1999 AND COLUMBIA NOTIFIED THE SURFACE MINING COMPANY THAT THE PIPELINE HAD BEEN RELOCATED, WHERE NEW PIPELINE WAS LOCATED AND WAS IN SERVICE. ON 5/18/00, THERE WAS AN ENROACHMENT ON COLUMBIAS RIGHT-OF WAY BY SURFACE MINING COMPANY. THE SURFACE MINING COMPANY HAD REMOVED THE ROW OF TREES "BUFFER" WITH A LOADER/EXCAVATOR AND STRUCK COLUMBIAS PIPELINE, APPROXIMATELY 50 FEET FROM AN EXISTING PIPELINE MARKER, RESULTING IN THE IGNITION OF NATURAL GAS AND SUBSEQUENT FIRE. | 59800 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1150 | 2000-05-13 | PA | other | UNKNOWN (PERRY COUNTY COUNTY) | TEXAS EASTERN TRANSMISSION CORP (DUKE) | THE EMERGENCY SHUTDOWN DEVICE (ESD) ACTIVATED AT COMPRESSOR STATION BY LIGHTING STRIKE TO COMPRESSOR UNIT GAS MONITOR. ALL EQUIPMENT OPERATED PROPERLY WITH THE EXCEPTION OF A SUCTION VALVE THAT DID NOT CLOSE AUTOMATICALLY. THIS ALLOWED GAS TO CONTINUE VENTING TO ATMOSPHERE IN A CONTROLLED MANNER UNTIL THE VALVE WAS MANUALLY CLOSED (57 MINUTES ELAPSED TIME). | 99000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1151 | 2000-06-19 | TX | leaks and spills | UNKNOWN (nan COUNTY) | NATURAL GAS PIPELINE CO OF AMERICA (KMI) | A LEAK OCCURRED ON THE ISLAND 16" LATERAL, 18.5 MILES FROM THE BEACH. | 217243 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1152 | 2000-06-03 | MN | other | UNKNOWN (OTTERTAIL COUNTY) | VIKING GAS TRANSMISSION CO | ON JUNE 3, 2000 THE WEEKEND DUTY PERSON WAS MAKING ROUNDS PERFORMING ROUTINE INSPECTIONS IN VIKINGS SOLAR CENTAUR GAS TURBINE COMPRESSOR PACKAGE WHEN HE DISCOVERED A 3/8 FITTING ON THE HIGH PRESSURE SEAL OIL LUBE SYSTEM LEAKING. THE STATION DISTRICT FOREMAN AND WEEKEND DUTY PERSON INITIATED A NORMAL SHUTDOWN OF THE UNIT SO REPAIRS COULD BE MADE. AS THE UNIT WAS SHUTTING DOWN THE FITTING BROKE AND OIL SPRAYED ON SOME PART OF THE ENGINE UNIT AND A VAPOR CLOUD STARTED TO APPEAR. THE DISTRICT FOREMAN PUSHED THE FAST STOP ON THE GAS TURBINE UNIT AND EXITED THE BUILDING. THE FIRE IS BELIEVED TO HAVE STARTED WHEN HIGH PRESSURE OIL SPRAY CONTACTED THE TURBINE EXHAUST. THE BUILDING FIRE DETECTION VENTILATION SYSTEM. EMERGENCY RESPONSE AGENCIES WERE IMMEDIATELY NOTIFIED AND THREE FIRE DEPARTMENTS RESPONDED AND THE FIRE WAS EXTINGUISHED WITH FOAM. THE BUILDING WAS SECURED AND DAMAGE ASSESSMENT BEGAN. ALL DAMAGE WAS CONTAINED WITHIN THE TURBINE BUILDING. REPAIRES TO THE TURBINE SKID, ELECTRICAL CONTROL SYSTEM AND BUILDING PANELS ARE CURRENTLY UNDERWAY. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1153 | 2000-06-17 | LA | other | UNKNOWN (nan COUNTY) | TENNESSEE GAS PIPELINE CO | A LEAK WAS REPORTED AND DETERMINED TO BE ON A TENNESSEE GAS PIPELINE FACILITY AT 10 A.M. ON 6/17/00 ON THE 507K-100 LINE (26" LINE) IN THE WC 177A. | 600000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1154 | 2000-06-14 | WY | other | UNKNOWN (NATRONA COUNTY) | NORTHERN GAS CO | THIRD PARTY EXCAVATION DAMAGE--A DOZER WITH RIPPER STRUCK A HOLE IN THE MAINLINE DAMAGING A SECTION OF PIPELINE. THIS SECTION WAS REPLACED WITH 14 FEET OF 0.25W X-52 16" PIPE. | 53230 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1155 | 2000-06-22 | TX | leaks and spills | UNKNOWN (BRAZORIA COUNTY) | FLORIDA GAS TRANSMISSION CO (ENRON) | PIPELINE FAILURE THE RESULT OF LOCALIZED STRESS CORROSION CRACKING OF PIPE EXTERNAL SURFACE.PIPELINE FAILURE THE RESULT OF LOCALIZED STRESS CORROSION CRACKING OF PIPE EXTERNAL SURFACE. | 65000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1156 | 2000-07-05 | LA | other | UNKNOWN (nan COUNTY) | SOUTHERN NATURAL GAS CO | A TUGBOAT, OCEAN SCRAMBLER, STRUCK THE MARKED 14" ROMERE PASS TRANSMISSION PIPELINE CAUSING THE RUPTURE. SUBSEQUENTLY, THE M/V LADY MELINDA ARRIVED AND THEN IGNITION OCCURRED. | 500000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1157 | 2000-07-05 | LA | leaks and spills | UNKNOWN (nan COUNTY) | TENNESSEE GAS PIPELINE CO | A LEAK WAS REPORTED AND DETERMINED TO BE ON A TENNESSEE GAS PIPELINE FACILITY AT 12:10P.M. ON 7/5/2000 ON THE 507A-3200 LINE IN EC BLOCK 33C. | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1158 | 2000-06-29 | LA | other | UNKNOWN (nan COUNTY) | COLUMBIA GULF TRANSMISSION CO | 1/2 BODY BLEED VALVE ON 16" BLOCK VALVE BROKEN OFF BY A TRAWLER. | 57000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1159 | 2000-07-02 | IN | maintenance | UNKNOWN (RANDOLPH COUNTY) | ANR PIPELINE CO | A 30" GIRTH WELD WAS LEAKING AT THE 6 OCLOCK (1/8" WIDE X 1-1/4" LONG). | 75000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1160 | 2000-07-02 | PA | leaks and spills | UNKNOWN (BEDFORD COUNTY) | COLUMBIA GAS TRANSMISSION CORP | THIS FAILURE OCCURRED IN AN ISOLATED AREA WITH NO IGNITION SOURCE OR FIRE. THE RUPTURE WAS CONTAINED WITHIN ONE JOINT OF PIPE ADJACENT TO PIPELINE EQUIPMENT ASSOCIATED WITH A STORAGE WELL. THE FORCE OF THE RUPTURE DESTROYED THE WELL SITE PIPELINE EQUIPMENT. THE PRELIMINARY RESULTS FROM THE ON-GOING INVESTIGATION INDICATE MICROBIOLOGICALLY INFLUENCED CORROSION (MIC). | 250000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1161 | 2000-07-07 | TX | leaks and spills | UNKNOWN ( COUNTY) | NATURAL GAS PIPELINE CO OF AMERICA (KMI) | A SMALL PINHOLE LEAK WAS DISCOVERED ON THE HIGH ISLAND 16" LATERAL. PRODUCTION WAS SHUT IN FOR PART OF THE WEEKEND. | 92823 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1162 | 2000-07-07 | FL | other | UNKNOWN (LAKE COUNTY) | FLORIDA GAS TRANSMISSION CO (ENRON) | A LIGHTNING STRIKE AT OR NEAR THE REGULATOR/METERING STATION RESULTED IN THE FAILURE OF A PRESSURE TRANSMITTER DIAPHRAGM. | 208000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1163 | 2000-07-03 | TX | leaks and spills | UNKNOWN (MATAGORDA COUNTY) | PG & E TEXAS PIPELINE, L.P. | PIPELINE RUPTURED @ 795 PSIG. METALLURGICAL EXAM REVEALED INTERNAL CORROSION. | 47900 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1164 | 2000-08-02 | WI | other | UNKNOWN (OCONTO COUNTY) | ANR PIPELINE CO | CONTRACTOR HIT 16" MARINETTE LATERAL. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1165 | 2000-07-18 | WY | other | UNKNOWN (ALBANY COUNTY) | NORTHERN GAS CO | THE MAINLINE BLOCK VALVE AT HERRICK LANE (UPSTREAM OF LARAMIE TBS) WAS INADVERTENTLY LEFT CLOSED AFTER MAINTENANCE. GAS CONTROL TECHNICIANS(S) DID NOT RESPOND TO THE LOSS OF PRESSURE AND FLOW AT THE TBS. GAS SERVICE WAS LOST TO THE CITY OF LARAMINE. (POPULATION 27000; APPROXIMATELY 10177 METERS) AT APRROXMATELY 1 A.M. SERVICE WAS RESTORED TO THE TBS AT 6 AM. GAS SERVICE WAS RESTORED TO THE MAJORITY OF CUSTOMERS BY 7/21/00. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1166 | 2000-07-21 | TX | leaks and spills | UNKNOWN (nan COUNTY) | NATURAL GAS PIPELINE CO OF AMERICA (KMI) | A SMALL PINHOLE LEAK WAS DISCOVERED ON THE HIGH ISLAND 16" LATERAL. | 137500 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1167 | 2000-07-21 | AZ | other | UNKNOWN (MARICOPA COUNTY) | EL PASO NATURAL GAS CO | THE BUCKET TEETH ON A FRONT END LOADER EXCAVATING IN THE ROCKLAND MATERIALS YARD PUNCHED TWO HOLES IN THE PIPELINE. THE ESCAPING GAS IGNITED. BURNING THE OPERATOR ON 70% OF HIS BODY. THE OPERATOR WAS ABLE TO GET TO A NEARBY DITCH WITH WATER IN IT. THE VALVES ON BOTH SIDES OF THE INCIDENT SITE WERE CLOSED AND THE FIRE EXTINGUSHED ITSELF BY 3:00PM. THE OPERATOR IS CURRENTLY IN THE PHOENIX BURN CENTER. THE LOADER OPERATOR DIED ON SEPTEMBER 9, 2000 | 155000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1168 | 2000-07-15 | LA | other | UNKNOWN (CAMERON COUNTY) | LOUISIANA RESOURCES PIPELINE CO, L.P. | MARSH FIRE OF UNKNOWN ORIGIN CONSUMED WOODEN CREOSOTE PLATFORM WHICH SUPPORTED THE SUBJECT PIPELINE VALVE SETTING/SCRAPER RECEIVER STATION | 72000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1169 | 2000-08-19 | NM | leaks and spills | UNKNOWN (EDDY COUNTY) | EL PASO NATURAL GAS CO | AT APPROXIMATELY 5:27 A.M. (MST) ON AUGUST 19, 2000 EL PASOS 30-INCH LINE 1103 RUPTURED. GAS CONTROL NOTICED A PRESSURE DROP AND DETERMINED THAT A FAILURE HAD OCCURRED. PECOS RIVER DISTRICT AND JAL DISTRICT PERSONNEL DISPATCHED TO THE SITE. VALVES 6 & 6 3/4 & 6 1/2 WERE SHUT-IN ISOLATING THE SECTION. THE FIRE WAS OUT AT APPROXIMATELY 6:36 A.M. THERE WERE TWELVE FATALITIES ASSOCIATED WITH THIS INCIDENT. | 998296 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1170 | 2000-08-16 | IL | other | UNKNOWN (CHRISTIAN COUNTY) | PANHANDLE EASTERN PIPELINE CO | MODIFICATIONS WERE MADE TO THE CROSSOVER PIPING BETWEEN TWO LINES TO ACCOMADATE IN-LINE INSPECTIONS. THE MODIFICATIONS DID NOT TAKE INTO ACCOUNT THAT AN UNKNOWN DRESSER COUPLING MIGHT HAVE BEEN INSTALLED ON THE EXISTING UNCOVERED CROSSOVER PIPING. AS THE LINE WAS BEING PRESSURED BACK UP AFTER CONSTRUCTION, THE MODIFIED CROSSOVER PIPE CAME OUT OF THE DRESSER COUPLING. CONTRIBUTING FACTORS TO THE INCIDENT WERE THAT THE MAIN LINE WAS CHECKED FOR DRESSER COUPLINGS, THE CROSSOVER WAS NOT AND THAT THE CONCRETE SUPPORT INSTALLED FOR THE 90 DEGREE ELBOW WAS NOT DESIGNED TO WITHSTAND THE FORCES THAT ARE EXERTED ON ELBOWS IN A LINE WITH COUPLINGS. STANDARD OPERATING PROCEDURES HAVE BEEN MODIFIED TO PREVENT A REOCCURENCE. | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1171 | 2000-08-25 | LA | leaks and spills | UNKNOWN (nan COUNTY) | ANR PIPELINE CO | A PINHOLE LEAK WAS DISCOVERED AT THE 6:00 POSITION ON THE BODY OF PIPE. | 54000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1172 | 2000-08-29 | MS | leaks and spills | UNKNOWN (COVINGTON COUNTY) | KOCH GATEWAY PIPELINE CO | SMALL RELEASE WAS DISCOVERED ON KOCHS HATTIESBURG 8" PIPELINE (TPL 387). THE DIFFICULT WORKING TERRAIN SURROUNDING THE RELEASE WILL MAKE THE REPAIR COST EXCEED THE $50,000 REPORTING LIMIT. RELEASE DID NOT CAUSE A THREAT TO PUBLIC SAFETY. | 80500 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1173 | 2000-08-16 | TX | leaks and spills | UNKNOWN (nan COUNTY) | NATURAL GAS PIPELINE CO OF AMERICA (KMI) | A SMALL PINHOLE LEAK WAS DISCOVERED ON THE HIGH ISLAND 16"LATERAL. | 157324 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1174 | 2000-08-14 | TX | leaks and spills | UNKNOWN (BRAZOS COUNTY) | MITCHELL GAS SERVICES LP | 1:23 A.M. OUR 12" PIPELINE LEAKED DUE TO INTERNAL CORROSION. DUE TO THE CLASS I LOCATION, SURROUNDING HOMES WERE EVACUATED AND TRAFFIC WAS REROUTED. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1175 | 2000-08-04 | TX | other | UNKNOWN (BEE COUNTY) | KINDER MORGAN TEXAS PIPELINE CO | A LEAK WAS FOUND ON A 2" SIDETAP ON INDEX 50. THE APPARENT CAUSE WAS THAT THE MAINLINE, OVER TIME, HAD SETTLED WHILE THE BRACE FOR THE 2" VALVE WAS HELD IN POSITION BY A BRACE. THIS EXERTED FORCE ON THE NIPPLE BETWEEN THE VALVE AND THE MAINLINE RESULTING IN A CRACK NEAR THE WELD ON THE 2" NIPPLE. | 98700 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1176 | 2000-08-19 | LA | leaks and spills | UNKNOWN (nan COUNTY) | ANR PIPELINE CO | EXTERNAL CORROSION ON RISER CLAMP ON THE PLATFORM | 119000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1177 | 2000-08-28 | TX | maintenance | UNKNOWN (GAINES COUNTY) | EL PASO NATURAL GAS CO | LEAK WAS DISCOVERED IN A FARMERS FIELD AFTER EPNG WAS INFORMED OF DARKENED SOIL IN THE VICINITY OF OUR LINE 1102. AN EXPLORATORY HOLE WAS DUG AND OF HAZARDOUS GAS DETECTOR DETERMINED A LEAK EXISTED. THE LINE WAS EXCAVATED AND THE LEAK WAS DETERMINED TO BE A MECHANICAL CLAMP ON AN OLD LEAK. THE LEAK WAS ADJACENT TO THE LONG SEAM OF THE 30" O.D. DSAW PIPE. IN THE INTEREST OF SAFETY IT WAS DECIDED TO REPAIR THE LEAK BY REMOVING A JOINT OF THE 30" PIPE AND REPLACING IT WITH 30" PIPE OF EQUAL OR GREATER STRENGTH. IT WAS NECESSARY TO BLOW DOWN 13 MILES OF PIPELINE IN ORDER TO REPAIR THE PIPELINE. CUSTOMERS WERE SERVICED WITH VOLUME BOTTLES WHILE REPAIRS WERE MADE. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1178 | 2000-09-12 | TX | other | UNKNOWN (nan COUNTY) | TXU LONE STAR PIPELINE | PIPELINE WAS STRUCK BY A LOCAL CONTRACTOR WITH A BULLDOZER WHILE PREPARING LAND FOR FARMING ACTIVITIES. TXU PIPELINE SERVICES DID NOT RECEIVE PRIOR NOTICE OF THIS ACTIVITY. | 142000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1179 | 2000-09-26 | TX | leaks and spills | UNKNOWN (HIDALGO COUNTY) | TENNESSEE GAS PIPELINE CO | A RUPTURE WAS REPORTED ON THE TGP LINE 407D-100, SULLIVAN CITY LINE, AT 2:12 A.M. ON 9-26-00. THE EXACT CAUSE IS STILL UNDER INVESTIGATION | 136000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1180 | 2000-09-27 | TX | maintenance | UNKNOWN (HANSFORD COUNTY) | NATURAL GAS PIPELINE CO OF AMERICA (KMI) | COMPANY PERSONNEL WERE INFORMED BY ONEOK PERSONNEL OF A POTENTIAL LEAK ON OUR PIPELINE. AFTER INVESTIGATION, IT WAS DETERMINED THAT THERE WAS A LEAK ON THE #2 MAINLINE. NOTIFICATION WERE MADE, THE PIPELINE SECTION WAS SHUT DOWN, DRAWN DOWN, AND BLOWN DOWN FOR EXCAVATION. INSPECTION OF THE PIPE REVEALED A PINHOLE LEAK IN THE BUTT WELD LOCATED AT RECHAIN 2039+26. THE DEFECTIVE WELD WAS CUT OUT AND A 5 5" PUP INSTALLED. | 54043 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1181 | 2000-10-03 | KS | other | UNKNOWN (CHASE COUNTY) | PANHANDLE EASTERN PIPELINE CO | BOLTS HOLDING THE VALVE BONNET ON TO THE TOP OF A 2" WKM SAF-T SEAL GATE VALVE FAILED ALLOWING BOTH THE BONNET AND THE GATE SLAB TO BE BLOWN FROM THE VALVE BODY. | 209500 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1182 | 2000-09-29 | LA | leaks and spills | UNKNOWN (nan COUNTY) | COLUMBIA GULF TRANSMISSION CO | METAL LOSS NEAR GIRTH WELD | 250000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1183 | 2000-10-12 | TX | maintenance | UNKNOWN (JACKSON COUNTY) | TENNESSEE GAS PIPELINE CO | A LEAK WAS LOCATED BETWEEN MLVS 12 & 13. A SIX INCH LONG CRACK WAS FOUND ON A PRESSURE WELD. THE EXACT CAUSE IS STILL UNDER INVESTIGATION. | 72000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1184 | 2000-10-28 | LA | maintenance | UNKNOWN (RAPIDES COUNTY) | KOCH GATEWAY PIPELINE CO | VALVE BODY CRACKED VENTING NATURAL GAS TO ATMOSPHERE. NRC REPORT #546637VALVE BODY CRACKED VENTING NATURAL GAS TO ATMOSPHERE. NRC REPORT #546637 | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1185 | 2000-10-30 | LA | leaks and spills | UNKNOWN (nan COUNTY) | ANR PIPELINE CO | POSSIBLE INTERNAL CORROSION @ 6 OCLOCK POSITION 5 FEET WEST OF FIELD JOINT. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1186 | 2000-11-13 | CO | other | UNKNOWN (SAN MIGUEL COUNTY) | ROCKY MOUNTAIN NATURAL GAS CO INC | HYDROCARBON FREEZE-OFF IN ABOVE-GROUND LINE CAUSED PRESSURE LOSS IN LINE, CAUSING LOSS OF GAS SUPPLY TO THE TOWNS OF TELLURIDE, MOUNTAIN VILLAGE, AND NEARBY AREAS. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1187 | 2000-11-16 | TX | leaks and spills | UNKNOWN (nan COUNTY) | WILLIAMS ENERGY GROUP-FIELD SERVICES | ON 11-16-00 A PRODUCER FLYING TO A PLATFORM NOTICED THE APPARENT SIGN OF A SUBSEA GAS LEAK. HE CALLED THE WFS AREA MANAGER TO REPORT THE LEAK. THE AREA MANAGER CALLED THE NRC AND REPORTED THE INCIDENT. THE LINE SEGMENT WAS THEN SHUT-IN AT THE PLATFORM DOWNSTREAM OF THE LEAK, AFTER WHICH THE UPSTREAM PLATFORMS WERE SHUT-IN TO ISOLATE THE LEAK. DIVERS WERE DISPATCHED TO LOCATE THE EXACT LOCATION AND NATURE OF THE LEAK. THE LEAK WAS VERIFIED AS A CRACKED FORGED-ON END CONNECTOR (BIG INCH MARINE BRAND). THE END CONNECTOR WAS FROM A PREVIOUS REPAIR THAT WAS COMPLETED IN 1994. REPAIRS WERE MADE BY REMOVING A 39 SEGMENT AND REPLACING WITH A NEW SEGMENT. THE PIPELINE SEGMENT WAS BACK IN SERVICE ON 12-8-00. THE FAILED CONNECTOR WAS SENT TO A BATON ROUGE COMPANY TO PERFORM A METALLURGICAL ANALYSIS. | 730000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1188 | 2000-11-23 | LA | other | UNKNOWN (GRANT COUNTY) | TRUNKLINE GAS CO | COMPRESSOR STATION COMMERCIAL POWER FAILED. UNINTERRUPTED POWER SYSTEM TO THE CONTROLS OF THE AUXILIARY GENERATOR FAILED, SO AC POWER WAS NOT AVAILABLE TO PUMPS OR ELECTRICALLY OPERATED LOADING VALVES. GAS TURBINE CONTINUED TO RUN UNTIL LUBRICATING OIL HIGH TEMPERATURE SAFETY SHUT IT DOWN. THE CENTRIFUGAL COMPRESSOR REMAINED PRESSURIZED AFTER SHUT DOWN, SINCE AC POWER WAS NOT AVAILABLE TO OPERATE THE ISOLATION AND BLOW DOWN VALVES. ABOUT 15 MINUTES AFTER SHUT DOWN, THE GRAVITY FED CENTRIFUGAL COMPRESSOR SEAL OIL TANKS EMPTIED ALLOWING GAS PRESSURE TO BACK INTO THE OIL DRAIN SYSTEM, FORCING OIL & GAS THROUGHOUT THE SYSTEM. GAS PRESSURE ALSO CAUSED A DRESSER COUPLING ON THE SHAFT BEARING DRAIN LINE BETWEEN THE CENTRIFUGAL COMPRESSOR & TURBINE TO SEPARATE. OIL VAPOR & NATURAL GAS BEING FORCED OUT OF THE OIL SUMP VENT & FROM THE SEPARATED DRESSER COUPLING WAS IGNITED. PROBABLE SOURCE OF THE IGNITION WAS EXPOSED HOT METAL ON THE TURBINE EXHAUST. THE MAJORITY OF PROPERTY LOSS IS DUE TO DISMANTLING AND INSPECTION OF THE GAS TURBINE TO CHECK FOR DAMAGE, BEFORE PUTTING IT BACK IN SERVICE. | 900000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1189 | 2000-12-04 | TX | other | UNKNOWN (CHAMBERS COUNTY) | EL PASO FIELD SERVICES | 8:48-OCC RECEIVED TELEPHONE CALL FROM ART MANGUS IN BAYTOWN, TX CONCERNING A LINE RUPTURE AND GAS BLOWING TO THE ATMOSPHERE. HIS TELEPHONE NUMBER IS 281-383-7453. 8:50PM OCC CONTROLLERS BEGAN NOTIFYING OPERATIONS PERSONNEL FOLLOWED BY OTHER KEY COMPANY PERSONNEL, HPL GAS CONTROL, TGP GAS CONTROL, AND DOW GAS CONTROL. ADVISED HPL TO BEGIN SHUTTING RECEIPTS AND DELIVERIES IN THE SHIP CHANNEL AREA AS NEEDED. 9:01PM OCC CONTROLLERS BEGAN NOTIFYING CUSTOMERS IN THE SHIP CHANNEL AREA OF THE SITUATION AND ADVISED THEM TO SWITCH TO ALTERNATE FUEL SOURCES IF NEEDED. BEGAN SHUTTING IN RECEIPTS AND DELIVERIES IN THE SHIP CHANNEL AREA THAT WERE REMOTE CONTROLLED FROM THE OCC. 9:15PM OCC ISSUED STATION 809 UNITS A REMOTE STOP COMMAND, REMOTE FAILED AND GERRY TREVINO AND FRANK REEVES WERE NOTIFIED TO SHUT DOWN THE UNITS.9:40PM STATION 812-1A REMOTELY PINCHED DOWN ATTEMPTING TO REDUCE VOLUME INTO THE SHIP CHANNEL AREA. 9:45PM STATION 809 UNITS SHUT DOWN PER GERRY TREVINO. 9:45PM RECEIVED CALL FROM BEACH CITY FIRE DEPARTMENT REPORTING 40 FLUME OF NATURAL GAS BUT NO FIRE AT HIGHWAY 565 AND NEEDLEPOINT ROAD (FM2354). THEY REPORTED THAT THE AREA HAD BEEN PARTIALLY EVACUATED AT THIS TIME.10:07 PM MAINLINE VALVE 816 CLOSED. 10:15 PM RECEIVED UPDATE FROM JOHN D CARTER THAT RUPTURE APPEARS TO BE ON THE 30"A/S LINE BETWEEN BLOCK VALVES.10:20 PM MAINLINE VALVE 815 CLOSED. SEGMENT IS ISOLATED AND BEING DEPRESSURIZED. VERIFIED BY JOHN D CARTER.10:25PM JOHN STERRETT NOTIFIED THE OCC THAT THE DOT NATIONAL RESPONSE CENTER HAD BEEN NOTIFIED. 10:38PM JOHN STERRETT NOTIFIED THE OCC THAT THE TEXAS RAILROAD COMMISSION HAD BEEN NOTIFIED. 11:38PM BEGAN WITHDRAWAL FROM MOSS BLUFF TO BRING THE LINEPACK ON THE EAST END BACK TO NORMAL.11:41PM 812-1A REGULATOR OPENED BACK UP TO 100%. 11:45PM BEGAN BRINGING CUSTOMERS BACK ON-LINE IN THE SHIP CHANNEL AREA.12:00AM STATION 809 #1B UNIT BACK LINE. 12:05AM BEGAN RECEIVING GAS FROM TGP SABINE TO HELP BRING EAST END LINE PACK BACK UP.1:30AM OCC NOTIFIED THAT M/L VALVE HAS BEEN TAKEN OUT OF SERVICE TO INSTALL AN AIR MOVER. 4:45 AM SYSTEM BACK TO NORMAL OPERATING PRESSURES AND CUSTOMERS ARE BACK ON-LINE WITH THE EXCEPTION OF THE CUSTOMERS WITHIN THE SEGMENT THAT IS ISOLATED. DURING THIS INCIDENT THERE WAS NUMEROUS AND CONSTANT COMMUNICATIONS WITH EPFS PERSONNEL, HPL PERSONNEL, AND CUSTOMERS CONCERNING THE ON-GOING SITUATION. | 2200000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1190 | 2000-11-28 | TN | other | UNKNOWN (SUMNER COUNTY) | TENNESSEE GAS PIPELINE CO | A MAINTENANCE CREW WAS PERFORMING WORK IN COMPRESSOR BUILDING "D", WHEN AN EXPLOSION/FLASH FIRE OCCURRED. APPARENTLY, GAS FROM THE COMPRESSOR MIGRATED INTO A CRANKCASE AND WAS IGNITED BY A SPARK, CAUSING THE EXPLOSION/FLASH FIRE. A POSSIBLE SOURCE OF IGNITION, THAT HAS BEEN IDENTIFIED, IS A WELDING MAINTENANCE ACTIVITY ON AN OIL LUBRICATION LINE, CONNECTED TO THE CRANKCASE. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1191 | 2000-11-25 | MS | leaks and spills | UNKNOWN (ATTALA COUNTY) | SOUTHERN NATURAL GAS CO | A LEAK WAS LOCATED ON THE NORTH MAIN LOOP, AT MP 137.3 EXTERNAL CORROSION IS THE APPARENT CAUSE. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1192 | 2000-11-18 | MN | leaks and spills | UNKNOWN (DOUGLAS COUNTY) | NORTHERN NATURAL GAS CO (ENRON) | APPARENT CAUSE OF INCIDENT WAS A CORROSION LEAK WHICH DEVELOPED IN THE FIRE TUBE OF THE INDIRECT GAS HEATER. THE ETHYLENE GLYCOL/WATER MIXTURE CAUGHT FIRE INSIDE THE HEATER. HEAT FROM THE BURNING GLYCOL MIXTURE CAUSED THE CONTROL TUBING ON THE PRESSURE CONTROLLER TO FAIL. GAS AT APPROX 15 PSIG WAS RELEASED FROM THE CONTROL TUBING AND CONTROLLER BODIES. NO OTHER PRESSURE CONTAINING PIPING FAILED. THE FIRE CAUSED RELIEF VALVE TO FAIL OPEN BUT THE VENTED GAS DID NOT IGNITE. | 129000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1193 | 2000-11-20 | CO | other | UNKNOWN (MONTROSE COUNTY) | TRANS - COLORADO PIPELINE CO | THERE WAS A FALSE EMERGENCY SHUTDOWN AT THE OLATHE COMPRESSOR STATION DUE TO FAILURE OF THE CONTROL PANEL. IN ADDITION, THE CONTROL PANEL ONLY SENT A PARTIAL ESD SIGNAL, LEAVING THE COMPRESSOR INLET VALVE OPEN, UNDETECTED, FOR ABOUT 5 HOURS. THIS ALLOWED VENTING OF PIPELINE GAS TO ATMOSPHERE. NOTICE OF SITUATION WAS RECEIVED FROM A PRIVATE PARTY AND SUBSEQUENTLY CORRECTED. | 92000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1194 | 2000-11-27 | TX | other | UNKNOWN (KNOX COUNTY) | TXU LONE STAR PIPELINE | KNOX COUNTY MAINTAINER WAS GRADING WHEN MAINTAINER HIT LINE U10. LINE U10 WAS APPROXIMATELY 16" DEEP. | 58900 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1195 | 2000-11-30 | TX | other | UNKNOWN (WEBB COUNTY) | PG & E TEXAS PIPELINE, L.P. | A THIRD-PARTY TELEPHONE COMPANY WAS PLANNING TO LAY FIBER-OPTIC CABLE IN THE VICINITY OF A PG&E NGL MARKETING, L.P. 6" PRODUCT LINE AND A PG & E TEXAS PIPELINE, L.P. 20" NATURAL GAS LINE WHICH PARALLEL EACH OTHER. THE TELEPHONE COMPANY CONTACTED PGE TEXAS PIPELINE COMPANY PERSONNEL ON NOVEMBER 29TH REGARDING THE PLANNED EXCAVATION. PGE TEXAS PIPELINE COMPANY PERSONNEL MET WITH TELEPHONE COMPANY PERSONNEL THE FOLLOWING MORNING AND PROCEEDED TO THE JOB SITE TO LOCATE THE TWO PIPELINES. UPON ARRIVING AT THE SITE AT APPROXIMATELY 9:30 A.M. EXCAVATION EQUIPMENT WAS IDLE. IT WAS DETERMINED BY PGE TEXAS PIPELINE COMPANY PERSONNEL THAT EXCAVATION WORK HAD BEGUN PRIOR TO THE MORNING OF NOVEMBER 30TH AND THAT THE 6" PRODUCT LINE HAD BEEN CROSSED. PGE TEXAS PIPELINE COMPANY PERSONNEL BEGAN REMOVING LINE-FINDING EQUIPMENT FROM THEIR VEHICLES TO VERIFY THE CROSSING DEPTH OF THE 6" LINE AND TO LOCATE AND DETERMINE THE DEPTH OF COVER ON THE 20" LINE. TELEPHONE COMPANY PERSONNEL INSTRUCTED THE OPERATOR OF A ROCK-SAW TRACTOR TO MOVE HIS EQUIPMENT OUT OF THE WAY IN ORDER TO FACILITATE LINE SPOTTING. AT APPROXIMATELY 9:45 A.M. AN EXPLOSION WITH NO IGNITION OCCURRED ON THE 20" GAS LINE. PRELIMINARY INVESTIGATION INDICATES THAT THE ROCK- SAW GOUGED THE PIPELINE THUS CAUSING THE ENSUING EXPLOSION. THE OPERATOR OF THE TRACTOR WAS BLOWN OFF THE EQUIPMENT AND DIED ONSITE. ANOTHER TELEPHONE COMPANY EMPLOYEE RECEIVED HEAD AND EYE INJURIES. | 133000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1196 | 2000-12-06 | IN | other | UNKNOWN (LAPORTE COUNTY) | ANR PIPELINE CO | A CRACKED THREAD ON A 1/2" X 11-1/2" LONG PIPE NIPPLE THAT WAS PART OF A BELOW GRADE BODY BLEED SYSTEM WAS LEAKING. | 95061 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1197 | 2000-12-09 | KS | leaks and spills | UNKNOWN (RENO COUNTY) | PANHANDLE EASTERN PIPELINE CO | SELECTIVE SEAM CORROSION IN AN EFW WELD SEAM. ACCELERATED CORROSION RATE EXPERIENCED IN THE SEAM DUE TO VARYING CHEMISTRY BETWEEN THE SEAM WELD METAL AND THE PIPE PARENT METAL. CORROSION IN THE PIPE BODY WAS LIGHT, BUT VERY DEEP AT THE WELD SEAM. | 750000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1198 | 2000-12-16 | IL | other | UNKNOWN (MONTGOMERY COUNTY) | ILLINOIS POWER CO | WHILE CONDUCTING A ROUTINE INSPECTION OF THE PLANT FACILITIES AT THE HILLSBORO STORAGE FIELD ON SATURDAY, DECEMBER 16, 2000, THE PLANT OPERATOR ON DUTY OBSERVED THE SIGHT GAUGE ON THE WATER SEPARATOR TANK AND DETERMINED THAT WATER SHOULD BE TRANSFERRED TO THE PRODUCED WATER HOLDING TANK. THE OPERATOR PROCEEDED TO MANUALLY OPERATE THE CONTROLLER ON A PNEUMATIC VALVE TO TRANSFER THE WATER. WHEN THE OPERATOR NO LONGER HEARD WATER FLOWING THROUGH TRANSFER LINE, HE MANUALLY OPERATED THE CONTROLLER TO CLOSE THE VALVE. AT THIS TIME, THE OPERATOR HEARD ABNORMAL SOUNDS COMING FROM THE AREA OF THE PRODUCED WATER HOLDING TANK. SECONDS LATER, THE OPERATOR HEARD A VIOLENT ROAR NEAR THE PLANT REGULATOR BUILDING. IMMEDIATELY THEREAFTER, THE PLANT LIGHTING WAS DISRUPTED. REALIZING THE POSSIBILITY A SERIOUS EVENT HAD OCCURED, THE OPERATOR SCANNED THE IMMEDIATE AREA WITH A FLASHLIGHT AND NOTICED LARGE PIECES OF METALLIC DEBRIS NEAR THE PLANT REGULATOR BUILDING. THE EMERGENCY SHUTDOWN SYSTEM (ESD) WAS ENGAGED AT APPROXIMATELY 11:50PM. THE OPERATOR NOTIFIED GAS DISPATCH THAT THE ESD HAD BEEN ENGAGED AND REQUESTED ASSISTANCE. UPON ARRIVAL, PLANT PERSONNEL OBSERVED THE PRODUCED WATER HOLDING TANK HAD BEEN DISLODGED. THE 50,000 GALLON WATER HOLDING TANK WAS DISLODGED FROM ITS FOUNDATION AND MOVED APPROXIMATELY 300 FEET CAUSING DAMAGE TO THE FIELDS REGULATOR STATION, 2 GAS DEHYDRATION TOWERS, AND NEARBY CABLE TRAYS. A NEARBY PRIMARY ELECTRIC LINE WAS ALSO DAMAGED. IN ACCORDANCE WITH COMPANY PROCEDURES, APPROPRIATE STATE AND FEDERAL AGENCIES WERE NOTIFIED BY TELEPHONE WITHIN THE REQUIRED TIME. THE FOLLOWING DAY, ILLINOIS POWERS CLAIMS PERSONNEL WERE NOTIFIED OF THE INCIDENT DESCRIBED ABOVE. SUBSEQUENTLY A DAMAGE ASSESSMENT WAS REQUESTED. ON MONDAY, DECEMBER 18, CLAIMS, GAS SUPPLY, AND ICC PIPELINE SAFETY PERSONNEL ARRIVED ON SITE TO CONDUCT AN ASSESSMENT OF THE DAMAGE AND DETERMINE POSSIBLE CAUSE. THE TEAM DECIDED TO RETAIN THE SERVICES OF AN INDEPENDENT DAMAGE ASSESSMENT SPECIALIST. ON TUESDAY, DECEMBER 19, PACKER ENGINEERING, INC. REPRESENTATIVES ARRIVED TO BEGIN THEIR INVESTIGATION. RESULTS OF THEIR INVESTIGATION ARE PENDING. CONDITIONS AT THE TIME OF THE INCIDENT WERE AS FOLLOWS: TEMPERATURE 5 DEGREES F.WIND VELOCITY 35 MPH GUSTING TO 40-45 MPH. WIND DIRECTION NORTHWEST. WIND CHILL FACTOR APPROXIMATELY MINUS 35 TO 45 DEGREES F. | 1000000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1199 | 2000-06-28 | MS | other | UNKNOWN (JEFFERSON DAVIS COUNTY) | AIM PIPELINE CO | ON 06-28-00 SHORTLY BEFORE 5:47 P.M. THE FRM PIPELINE, AN 8 INCH HIGH PRESSURE GAS PIPELINE THAT RUNS EAST AND WEST FROM TRANSCO TO THE GEORGIA PACIFIC PAPER MILL, RUPTURED RELEASING NATURAL GAS TO THE ATMOSPHERE. AT 5:47P.M. JAMES DICKENS, A LOCAL LANDOWNER AND RESIDENT, NOTIFIED THE PRENTISS VOLUNTEER FIRE DEPARTMENT AND DEFS GAS CONTROL OF THE PIPELINE RUPTURE. AT 5:50 P.M. GAS CONTROL NOTIFIED JIM BERTELMAN, DEFS MEASUREMENT SUPERVISOR OF THE RUPTURE WHO IN TURN NOTIFIED MICHAEL SMALL, DEFS FIELD OPERATOR AND BUTCH HEMPHILL. DEFS SYSTEM SUPERVISOR AT 6:15 P.M. THE LINE IGNITED. THE PRENTISS VFD WAS ONSITE; HOWEVER, NO EFFORTS WERE MADE TO EXTINGUISH THE FIRE AS THE FIRE WAS ALLOWED TO BURN UNDER CONTROL. AT 6:55 P.M. THE LINE WAS SHUT-IN AND ISOLATED BY CLOSING THE MAIN PIPELINE BLOCK VALVES. AT 8:27 P.M. THE FUEL HAD BEEN CONSUMED AND THE FIRE WAS CONTAINED WITHIN THE BELLHOLE. DEFS PERSONNEL REMAINED ONSITE UNTIL THE LINE WAS REPAIRED THE FOLLOWING DAY, 06-29-00. AS A PRECAUTIONARY MEASURE, THE PRENTISS VFD EVACUATED THREE NEARBY RESIDENCES. ALL THREE WERE ALLOWED TO RETURN TO THEIR HOMES BEFORE 7:45 P.M. (NOTE: THERE WERE NO INJURIES AND NO MAJOR PROPERTY DAMAGE ASSOCIATED WITH THIS INCIDENT.) THE RUPTURE IN THE PIPE MEASURED SIX INCHES BY THREE INCHES. THE RUPTURE POINT IN THE LINE WAS IN A LOW-LYING AREA ON THE BOTTOM OF THE LINE APPROXIMATELY TWO INCHES FROM A JOINT WELD. AN EXTERNAL INSPECTION OF THE LINE DID NOT REVEAL FURTHER DAMAGE. A 53 FOOT SECTION OF LINE WAS REPLACED AND THE LINE WAS READY TO BE PUT BACK INTO SERVICE ON THE P.M. OF 6-29-00. THE LINE WAS PURGED, SLOWLY PRESSURIZED AND RETURNED TO SERVICE ON 6-30-00. | 107500 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1200 | 2000-12-29 | IL | leaks and spills | UNKNOWN (PIKE COUNTY) | PANHANDLE EASTERN PIPELINE CO | GENERAL CORROSION IN THE PIPE BODY AT THE LOCATION OF AN OVERBEND. COMPARISON OF COATING AT THE OVERBEND TO COATING ON THE ADJACENT PIPE INDICATES THAT THE COATING AT THE OVERBEND WAS DISBONDED. CONJECTURE IS THAT COATING WAS MANUALLY APPLIED AFTER INSTALLATION OF THE OVERBEND. | 1030000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1201 | 2000-12-26 | CA | other | UNKNOWN (SOLANO COUNTY) | PACIFIC GAS & ELECTRIC CO | DESILVA CONSTRUCTION HIT 32" STEEL TRANSMISSION LINE 2010 WITH D6 GRADER WHILE GRADING FOR ROAD. | 150000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1202 | 2001-01-03 | NC | other | UNKNOWN (ANSON COUNTY) | NORTH CAROLINA NATURAL GAS CORP | CONTRACTOR WAS EXCAVATING, IN VIOLATION OF PROCEDURES, WHEN HE STRUCK 2-INCH LATERAL OFF OF 16 INCH TRANSMISSION LINE. | 2159963 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1203 | 2001-01-04 | MS | other | UNKNOWN (BOLIVAR COUNTY) | WILLIAMS GAS PIPELINE - TEXAS GAS | ON THURSDAY, JANUARY 4, 2001, AT APPROXIMATELY 8:00 AM CENTRAL STANDARD TIME, WILLIAMS GAS PIPELINE -- SOUTHCENTRAL (TEXAS GAS TRANSMISSION) WAS NOTIFIED THAT GAS WAS HEARD BLOWING IN A FIELD APPROXIMATELY 5 MILES WEST OF SHELBY, MS, AND 1 MILE SOUTH OF US HIGHWAY 32. THE COMPANY PROMPTLY DETERMINED THAT THE GAS WAS LEAKING FROM THE COMPANYS EIGHTEEN-INCH SYSTEM (EIS) #2 PIPELINE, NEAR MILEPOST 121+2948 IN BOLIVAR COUNTY , MS (SECTION 18, TOWNSHIP 19 NORTH, RANGE 7 WEST). THERE WAS NO DEATHS OR INJURIES RESULTING FROM THIS INCIDENT. ALSO, THERE WAS NO FIRE AT OR NEAR THE PIPELINE FACILITY. THERE WERE NO SERVICE INTERRUPTIONS AS A RESULT OF THIS INCIDENT. EVIDENCE AVAILABLE HAS NOT ALLOWED DETERMINATION OF CAUSE AT THIS TIME. THE CAUSE OF THE INCIDENT CONTINUES TO BE UNDER INVESTIGATION. PROPERTY DAMAGE WAS CONFINED TO COMPANY FACILITIES. THE INCIDENT OCCURRED IN A CROP FIELD WHERE THERE WERE NO DWELLINGS WITH THE PIPELINE CORRIDOR. THE COST OF REPAIR AND GAS LOSS ARE ESTIMATED AS FOLLOWS: GAS LOSS 106,000, MATERIAL 1,000, LABOR 3,000, EQUIPMENT 750, X-RAY 1,500, TOTAL COST 112,250EST. ADDITIONAL COMMENTS: COMPANY PERSONNEL FOUND THE DAMAGED PIPE SECTION TO HAVE A 40-INCH BURIAL DEPTH. ONCE UNCOVERED, A FRACTURE (APPROXIMATELY 30 INCHES LONG CIRCUMFERENTIALLY) WAS OBSERVED IN A WRINKLE BEND SITUATED ON THE TOP OF THE PIPE. ON FRIDAY, JANUARY 5, 2001, COMPANY PERSONNEL RETURNED THE EIS #2 TO SERVICE AFTER CUTTING OUT AND REPLACING THE DAMAGED PIPE SECTION WITH APPROXIMATELY 12 FEET OF 18-INCH PRETESTED PIPE FROM STOCK. | 106000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1204 | 2001-01-04 | MO | maintenance | UNKNOWN (CASS COUNTY) | PANHANDLE EASTERN PIPELINE CO | CIRCUMFERENTIAL SPLIT IN A SHARP WRINKLE BEND. | 365000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1205 | 2001-01-16 | AL | leaks and spills | UNKNOWN (TUSCALOOSA COUNTY) | SOUTHERN NATURAL GAS CO | A LEAK WAS LOCATED ON THE NORTH MAIN SYSTEM, AT MP 157.2, AFTER DEAD VEGETATION WAS FOUND. FURTHER INVESTIGATION WITH GAS DETECTION INSTRUMENTS AND EXCAVATION REVEALED A SMALL LEAK ON THE 2ND NORTH MAIN PIPELINE. A LOCALIZED EXTERNAL CORROSION HOLE IS THE APPARENT CAUSE. | 217850 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1206 | 2001-01-15 | UT | other | UNKNOWN (UTAH COUNTY) | QUESTAR GAS COMPANY | ON JANUARY 15, 2001, AT APPROXIMATELY 0625 A QUESTAR GAS COMPANY PHONE OPERATOR RECEIVED NOTIFICATION THAT A QUESTAR LINE WAS BLOWING. A QUESTAR EMPLOYEE ARRIVED ON-SCENE AND VERIFIED THAT THE BLOWING LINE WAS A 20 INCH HIGH PRESSURE (300 PSI) STEEL PIPELINE AND IT HAD BEEN HIT BY A FRONT END LOADER (1997 CATERPILLAR 980 G CAT). THE SECTION OF LINE THAT WAS DAMAGED WAS AN ABOVEGROUND SPAN THAT WENT ACROSS A RAVINE (APPROXIMATELY 20 ACROSS). INVESTIGATION REVEALED THAT SOME TIME DURING THE PREVIOUS NIGHT, A FRONT END LOADER HAD BEEN STOLEN FROM A NEARBY SAND AND GRAVEL PIT. IT IS BELIEVED THAT THE FRONT END LOADER WAS HOT WIRED AND USED TO PULL TWO TRUCKS FROM THE MUD IN THE HILLS ABOVE THE SCENE OF THE INCIDENT. THE FRONT END LOADER WAS THEN ROLLED DOWN THE HILL WHERE IT STRUCK THE PIPELINE WHERE IT CROSSED THE RAVINE. THIS RESULTED IN AN APPROXIMATE 9 INCH BY 3 INCH TEAR IN THE PIPELINE. THE TOTAL PROPERTY DAMAGE INCLUDING COST OF LOST GAS IS $300,838.00, OF WHICH $277,838.00 IS THE MARKET VALUE OF THE LOST GAS, AND $23,000.00 WAS THE COST OF THE REPAIR. | 300838 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1207 | 2001-01-25 | LA | other | UNKNOWN (CAMERON COUNTY) | BASIN EXPLORATION INC |  | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1208 | 2001-01-16 | ID | other | UNKNOWN (MONTPELIER COUNTY) | NORTHWEST PIPELINE CORP (WGP) | A TEAM OF NORTHWEST PIPELINE CORPORATION EMPLOYEES WERE IN THE PROCESS OF PURGING AND PACKING THE PEGRAM COMPRESSOR STATION PIPING AFTER THE COMPLETION OF A CONSTRUCTION PROJECT. DURING THE PURGE PROCESS THREE EMPLOYEES WERE FOUND INSIDE THE UNIT #1 VALVE BUILDING. THE PURGING PROCESS WAS QUICKLY TERMINATED AND THE THREE MEN WERE REMOVED FROM THE BUILDING. TWO HAD VITAL SIGNS AND THE THIRD HAD NO VITAL SIGNS. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1209 | 2001-01-29 | KS | maintenance | UNKNOWN (MIAMI COUNTY) | WILLIAMS GAS PIPELINE CENTRAL, INC. | CRACKED WELD. INCOMPLETE PENETRATION IN ACETYLENE TYPE WELD. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1210 | 2001-02-04 | MT | other | UNKNOWN (JEFFERSON COUNTY) | MONTANA POWER CO | A CONTRACTOR DIGGING WITH AN LARGE TRACK MOUNTED EXCAVATOR HIT THE MPC EAST HELENA TO BOULDER 8" NATURAL GAS TRANSMISSION LINE AT MP 1.96. THE IMPACT OF THE EXCAVATOR TOOTH PUNCTURED THE LINE AND IMMEDIATELY NATURAL GAS BEGAN BLOWING. HIGH PRESSURE GAS BLEW BUT DID NOT IGNITE. TWO FARM TAP CUSTOMERS WERE LOST AS A RESULT. NO INJURIES OCURRED.A CONTRACTOR DIGGING WITH AN LARGE TRACK MOUNTED EXCAVATOR HIT THE MPC EAST HELENA TO BOULDER 8" NATURAL GAS TRANSMISSION LINE AT MP 1.96. THE IMPACT OF THE EXCAVATOR TOOTH PUNCTURED THE LINE AND IMMEDIATELY NATURAL GAS BEGAN BLOWING. HIGH PRESSURE GAS BLEW BUT DID NOT IGNITE. TWO FARM TAP CUSTOMERS WERE LOST AS A RESULT. NO INJURIES OCCURRED. | 150000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1211 | 2001-02-08 | TX | maintenance | UNKNOWN (nan COUNTY) | TXU LONE STAR PIPELINE | DURING INSTALLATION OF A HOT TAP CONNECTION FOR CITY OF AUSTINS SAND HILL POWER PLANT, THE CONTRACTOR GOUGED A HOLE IN THE PIPE. | 55000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1212 | 2001-03-10 | TX | other | UNKNOWN (nan COUNTY) | SEACREST CO LLC | APPARENTLY A SUBSEA OBJECT DRUM OVER THE GATHERING LINE CAUSING A LEAK ON A COATED PIPE IN THE 3 OCLOCK POSITION. | 75000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1213 | 2001-02-28 | LA | other | UNKNOWN (nan COUNTY) | EL PASO FIELD SERVICES | DETERMINED TO BE A PROBABLE PIPELINE INCIDENT AT 1015 CST WHEN NOTIFIED THAT THE PIPELINE PRESSURE WAS ZERO. AT ABOUT 0330 CST, A BOAT HIT A PRODUCTION PLATFORM AND SEVERED THE PIPELINE RISER, WHICH WAS ATTACHED TO THE PLATFORM. THE ABOVE COST ESTIMATE INCLUDES LOSS OF GAS, REPAIR OF PIPELINE, REPLACEMENT OF A COMMUNICATION HUB, AND PRODUCERS ESTIMATE OF PLATFORM AND EQUIPMENT DAMAGE, INCLUDING THE LOSS OF A PARKED HELICOPTER. THE INCIDENT WAS CONSIDERED SAFE WHEN SUBSEA BLOCK VALVE WAS CLOSED. ALSO, SEE ATTACHED RECORDS OF EVENTS. | 7550600 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1214 | 2001-02-03 | TX | maintenance | UNKNOWN (GULF OF MEXICO COUNTY) | EL PASO FIELD SERVICES | EPFS TELEPHONED THE RAILROAD COMMISSION OF TEXAS WITHIN 2 HOURS OF THE DETERMINATION THAT THE LEAK WAS ON AN EPFS LINE. IN REGARDS TO THE ABOVE MENTIONED LEAK, THE FOLLOWING IS A SUMMARY OF EVENTS THAT OCCURRED: ON FEBRUARY 4, 2001, A HELICOPTER PILOT WITH THE TNRCC HELICOPTER PATROL NOTICED BUBBLES IN THE WATER AROUND AN UNMANNED PLATFORM. THE PIPELINE ASSOCIATED WITH THIS PLATFORM IS AN 8" NATURAL GAS TRANSMISSION LINE WITH AN OPERATING PRESSURE OF 300 PSIG THAT WAS RECENTLY ACQUIRED BY EL PASO FIELD SERVICES FROM COASTAL. CODY MILBURN, AN EL PASO FIELD SERVICES REPRESENTATIVE WAS NOTIFIED AND MR. MILBURN THEN SET UP A DIVE BOAT TO BE DISPATCHED IN ORDER TO INVESTIGATE THE BUBBLES. THE PLATFORM WAS IN 30 FEET OF WATER AND IS LOCATED APPROXIMATELY SIX (6) MILES OFFSHORE. AT THE TIME THAT THE BUBBLES WERE SEEN, THERE WAS NO SHEEN ON THE WATER. THE 8" LINE WAS SUBSEQUENTLY BLOCKED IN ON FEBRUARY 4 UNTIL THE POSSIBLE LEAK COULD BE LOCATED AND VERIFIED THAT IT BELONGED TO EL PASO FIELD SERVICES. WHEN THIS DETERMINATION WAS MADE, THE LINE WAS RE-PRESSURIZED ON FEBRUARY 6 IN ORDER TO ASCERTAIN OF THE CORRECT LINE AND LOCATION AND THEN BLOCKED IN AGAIN SO THAT REPAIRS COULD BE MADE. REPAIRS WERE COMPLETED ON FEBRUARY 7 AND THE LINE PUT BACK INTO SERVICE ON FEBRUARY 8, 2001. ELI GUZMANN OF THE TEXAS RAILROAD COMMISSION WAS NOTIFIED BY THE AREA MANAGER OVER THESE ASSETS, J.R. LOGAN, ABOUT THE EVENTS LEADING UP TO THE ACTIONS. WE ARE CURRENTLY IN THE PROCESS OF FILLING OUT FORM RSPA F7100.2 IN ORDER TO MEET REQUIREMENTS OF THE RAILROAD COMMISSION. | 97336 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1215 | 2001-03-05 | LA | other | UNKNOWN (nan COUNTY) | MID LOUISIANA GAS CO | SOMETHING (3RD PARTY) STRUCK PIPELINE MAKING A PIN SIZE HOLE AT 3 OCLOCK POSITION. DO NOT KNOW WHO OR WHAT HIT PIPE. | 30000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1216 | 2001-03-28 | CO | other | UNKNOWN (EL PASO COUNTY) | PEOPLES NATURAL GAS CO | DEVELOPER WAS LEVELING SITE FOR CONSTRUCTION OF TOWNHOMES. TRANSMISSION LINE WAS STRUCK BY EARTHMOVER. | 140000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1217 | 2001-03-19 | OK | other | UNKNOWN (CANADIAN COUNTY) | DUKE ENERGY FIELD SERVICES INC | A FIELD OPERATOR ARRIVED AT WEST YUKON BOOSTER THE MORNING OF MARCH 19TH, 2001. THE OPERATOR WAS CHECKING THE EQUIPMENT AT THE BOOSTER WHEN HE FOUND THE TEMPERATURE OF THE GLYCOL IN THE DEHYDRATOR WAS AT 50 F, WELL BELOW NORMAL OPERATING TEMPERATURE. AFTER A CLOSER INSPECTION OF UNIT, LEVELS, AND ALARMS, HE DETERMINED THE BURNER TUBE WAS NOT OPERATING. AT APPROXIMATELY 8:50 A.M., HE RESTARTED THE UNIT BY RE-IGNITING THE BURNER TUBE AND THEN PROCEEDED WITH HIS ROUNDS. APPROXIMATELY 5 MINUTES LATER HE HEARD A GURGLING NOISE FROM THE DEHYDRATOR AND SAW LIQUID BEING RELEASED FROM THE 2" VENT. AT THAT INSTANT, THE LIQUID/VAPOR IGNITED AND BEGAN TO BURN. THE FEILD OPERATOR IMMEDIATELY SHUT DOWN THE UNIT. AFTER SEVERAL MINUTES, THE LIQUID AND VAPOR RELEASE FROM THE 2" VENT STOPPED. A RESIDUAL FIRE STILL BURNED ON THE EXTERIOR OF THE UNIT AND ON THE LIQUID TRAPPED INSIDE THE UNITS DIKED AREA. ANOTHER OPERATOR HAD ARRIVED TO ASSIST AND TOGETHER THEY EXTINGUISHED THE RESIDUAL FIRE USING TWO 30# PORTABLE FIRE EXTINGUISHERS. THE YUKON FIRE DEPARTMENT WAS CALLED AND ARRIVED AT APPROXIMATELY 9:20 A.M. THE FIRE DEPARTMENT APPLIED WATER TO THE DEHYDRATOR UNIT TO ASSIST COOLING AND PREVENT RE-IGNITION. NO INJURIES OCCURRED. DAMAGE COST IS ESTIMATED AT $15,000. PRELIMINARY INVESTIGATION REVEALED THE FLAME IN THE BURNER TUBE WAS SOMEHOW EXTINGUISHED AND THE FLAME SENSOR FAILED TO DETECT IT. THE SENSOR IS CONFIGURED TO SHUT DOWN THE UNIT IN THE EVENT OF A "FLAME OUT" AND SIGNAL AN OPERATIONAL UPSET ALARM. THE GLYCOL PUMPS CONTINUED TO CIRCULATE GLYCOL THROUGH THE CONTACT TOWER AND BACK TO THE DEHYDRATOR UNIT. WITH THE BURNER TUBE NOT HEATING THE GLYCOL, IT COOLED TO THE POINT WHERE NATURAL GAS CONDENSATE WAS NOT SEPARATING FROM THE GLYCOL IN THE CONTACT TOWER. NATURAL GAS CONDENSATE THEN BEGAN TO ENTER THE DEHYDRATOR UNIT WITH THE GLYCOL. THE CONDENSATE ACCUMULATED ON TOP OF THE GLYCOL DUE TO ITS LOWER SPECIFIC GRAVITY. WHEN THE OPERATOR RE-STARTED BURNER TUBE IT HEATED THE GLYCOL/CONDENSATE MIXTURE CAUSING THE CONDENSATE TO RAPIDLY EVAPORATE INSIDE THE DEHYDRATOR UNTIL ENOUGH PRESSURE BUILT UP TO "BURP" LIQUID FROM THE 2" VENT. SOME OF THE CONDENSATE CONTACTED THE BURNER TUBE EXHAUST STACK AND IGNITED. AN INVESTIGATION TEAM HAS BEEN ASSEMBLED AND IS CURRENTLY CONDUCTING A THROUGH INVESTIGATION OF THIS INCIDENT. | 15000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1218 | 2001-03-22 | FL | other | UNKNOWN (LAKE COUNTY) | FLORIDA GAS TRANSMISSION CO (ENRON) | ON MARCH 22, 2001 AT APPROXIMATELY 0800, GAS VENTING FROM A BLOWDOWN SILENCER ADJACENT TO THE FGT 24" MAINLINE IGNITED DURING A PLANNED PIPELINE BLOWDOWN. THE FIRE WAS EXTINGUISHED BY CLOSURE OF THE BLOWDOWN VALVE APPROXIMATELY 40 MINUTES AFTER THE GAS IGNITION. DAMAGE FROM THE FIRE WAS LIMITED TO THE SILENCER, A BACKHOE, AND SEVERAL ADJACENT POWER LINES. THE CAUSE OF THE GAS IGNITION IS NOT KNOWN. | 105000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1219 | 2001-03-29 | TX | other | UNKNOWN (GAINES COUNTY) | ONEOK GAS TRANSPORTATION, LLC | COUNTY MAINTAINE STRUCK AND RUPTURED PIPELINE WHILE GRADING BAR DITCH. | 42000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1220 | 2001-03-17 | AZ | other | UNKNOWN (YAVAPAI COUNTY) | EL PASO NATURAL GAS CO | A MALFUNCTION OF A LIMIT SWITCH FAILED TO CLOSE THE #2 ELECTRIC UNIT SUCTION VALVE. THIS CAUSED THE #2 UNIT VENT TO REMAIN OPEN AFTER THE UNIT WAS DROPPED OF LINE ON SATURDAY, MARCH 17; HOWEVER, THE SIGNAL WAS PASSED ON TO THE DISCHARGE VALVE TO CLOSE. THE CLOSED DISCHARGE VALVE CAUSED THE VENT TO OPEN AND VENT GAS TO THE ATMOSPHERE. | 534000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1221 | 2001-03-29 | TX | leaks and spills | UNKNOWN (MCMULLEN COUNTY) | HOUSTON PIPELINE CO |  | 40000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1222 | 2001-04-06 | LA | leaks and spills | UNKNOWN (nan COUNTY) | DYNEGY MIDSTREAM SERVICES, L.P. | PIN HOLE LEAK AT THE 3 OCLOCK POSITION. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1223 | 2001-03-13 | TX | maintenance | UNKNOWN (HARRIS COUNTY) | HOUSTON PIPELINE CO | WHILE BOLTING UP A FLANGE TO CONNECT A LINE TO THE 4" TAP VALVE, A LEAK WAS DISCOVERED IN THE WELDOLET ON THE TAP VALVE. | 117500 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1224 | 2001-03-30 | PA | leaks and spills | UNKNOWN (CHESTER COUNTY) | COLUMBIA GAS TRANSMISSION CORP | A LEAK AT A ROAD CROSSING (PA 401/CONESTOGA ROAD) WAS DISCOVERED BY A MOTORIST AND REPORTED TO COLUMBIA. A PRELIMINARY FAILURE INVESTIGATION SUGGESTS THE LEAK OCCURRED IN AN AREA OF LOCALIZED EXTERNAL CORROSION WHICH WAS ATMOSPHERICALLY EXPOSED IN THE ROAD CASING. | 88000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1225 | 2001-04-04 | LA | other | UNKNOWN (ST MARTIN COUNTY) | LOUISIANA INTRASTATE GAS CO, L.L.C. | CONTRACTOR WAS USING A DOZER TO PERFORM EARTHWORK AND LAND LEVELING OVER THE PIPELINE. THE CARTHERN COVER OVER THE PIPELINE WAS EVENTUALLY REMOVED. THE DOZER BLADE PUNCTURED A HOLE IN THE 10" PIPELINE. CONTRACTOR DID NOT MAKE THE PROPER ONE CALL NOTIFICATION, FOR THE STATE OF LA. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1226 | 2001-04-07 | IL | other | UNKNOWN (DOUGLAS COUNTY) | PANHANDLE EASTERN PIPELINE CO | A CONTROL SYSTEM FAILURE SHUT ALL OF THE UNITS COMPRESSING THIS LINE DOWN. PRESSURE INCREASED UNTIL RELIEF VALVE OPERATED. RELIEF VALVE OPERATED NORMALLY TO PREVENT PRESSURE FROM EXCEEDING MAOP+10%. INCIDENT REPORT IS BEING SUBMITTED BECAUSE GAS LOSS EXCEEDED $50,000. MODIFICATIONS ARE BEING MADE TO PREVENT REOCCURRENCE. | 109620 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1227 | 2001-04-05 | LA | leaks and spills | UNKNOWN (TERREBONNE COUNTY) | WILLIAMS ENERGY GROUP-FIELD SERVICES | CORROSION TECH NOTICED A SHEEN IN THE MARSH WHILE WORKING AT THE MOSQUITO BAY PIPELINE MANIFOLD PLATFORM. STATE AND FEDERAL AGENCIES WERE NOTIFIED. A UNIFIED INCIDENT COMMAND STRUCTURE WAS ACTIVATED. BOOMS WERE DEPLOYED TO ISOLATE AND CONTAIN THE CONDENSATE PRODUCT. FOLLOWING THE CLEAN UP, THE LEAK WAS LOCATED. THE AREA OF PIPE IN THE VICINITY OF THE LEAK WAS RADIOGRAPHICALLY AND ULTRASONICALLY INSPECTED WITH NO FURTHER EVIDENCE OF CORROSION FOUND. THE CIRCUMFERENCE OF THE LINE NEAR THE LEAK WAS CLEANED AND CLAMPED. SAFETY AND ENVIRONMENTAL MEASURES WERE MONITORED THROUGHOUT THE PROCESS. THE LINE WAS RETURNED TO SERVICE. | 1250000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1228 | 2001-04-04 | KS | other | UNKNOWN (BUTLER COUNTY) | WILLIAMS GAS PIPELINE CENTRAL, INC. | WHILE INSTALLING AN ELECTRIC LINE, AN OUTSIDE CONTRACTOR PUNCTURED THE LINE WITH A TRENCHER. | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1229 | 2001-04-05 | OK | other | UNKNOWN (HARPER COUNTY) | WILLIAMS GAS PIPELINE CENTRAL, INC. | BACKHOE TRACTOR FELL INTO EXCAVATION DURING THE RECLAIM OF A SETTING RESULTING IN THE FATALITY OF AN CENTRL EMPLOYEE | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1230 | 2001-04-04 | TX | other | UNKNOWN (EL PASO COUNTY) | SOUTHERN UNION GAS CO | COMPANY PERSONNEL RESPONDED TO A BLOWING GAS SITUATION AT 2:25 AM MST ON APRIL 4, 2001. CONFLICTING REPORTS OF UNDERGROUND LEAKS, POSSIBLE EXPLOSIONS, AND NUMEROUS GAS ODOR REPORTS NECESSITATED A THOROUGH AND CAUTIOUS INVESTIGATION IN CONJUCTION WITH LOCAL PUBLIC SAFETY OFFICIALS TO PROTECT EMERGENCY RESPONDERS AND THE PUBLIC. PERSONNEL TOOK NUMEROUS SURFACE AND SUBSURFACE GAS READINGS AT LOCATIONS THROUGHOUT THE AREA. NO NATURAL GAS WAS FOUND EXCEPT THAT BEING RELEASED FROM THE RELIEF VALVE INTO THE ATMOSPHERE IN THE IMMEDIATE AREA. DUE TO THE REMOTE LOCATION OF THE INCIDENT, THE PROPERTIES OF NATURAL GAS, AND ATMOSPHERIC CONDITIONS THERE WAS NO THREAT TO THE PUBLIC. IT WAS DETERMINED THAT THE RELEASE OF GAS WAS SOLELY DUE TO A BLOWING RELIEF VALVE. THERE WERE NO LEAKS, EXPLOSIONS, OR GAS IN THE SURROUNDING AREAS. THE INVESTIGATION SHOWED THAT THE RELIEF VALVE WAS BLOWING DUE TO AN INCREASE IN DELIVERY PRESSURE ABOVE THE NORMAL OPERATING PRESSURE. DUE TO THE LARGE PRESSURE DROP THE TEMPERATURE AT THE VALVE DROPPED SIGNIFICANTLY AND MAY HAVE THE RELIEF VALVE TO FREEZE IN THE OPEN POSITION. THREE SUBSEQUENT TESTS OF THE RELIEF VALVE HAVE SHOWN THAT IT IS FUCTIONING PROPERLY. | 120000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1231 | 2001-04-16 | KS | maintenance | UNKNOWN (CLOUD COUNTY) | NATURAL GAS PIPELINE CO OF AMERICA (KMI) | DEAD VEGETATION DISCOVERED 04/13/01 ON FLYOVER. USED LEL DETECTOR ON 04/16/01 TO CONFIRM LEAK. LINE WAS ISOLATED AND PRESSURE WAS DRAWN DOWN TO 319 PSIG. A 1/2-INCH PENETRATOR WAS FOUND IN A LONG SEAM, ABOUT 1/8 INCH FROM THE GIRTH WELD. A FULL CIRCUMFERENCE SLEEVE WAS INSTALLED, AND THE LINE WAS RETURNED TO SERVICE ON 04/19/01. | 81000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1232 | 2001-04-25 | LA | other | UNKNOWN (BOSSIER COUNTY) | RELIANT ENERGY GAS TRANSMISSION | CONTRACTOR INSTALLING GATHERING LINE STRUCK LINE ST-10 WITH BACKHOE BUCKET PUNCTURING PIPELINE. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1233 | 2001-04-27 | LA | leaks and spills | UNKNOWN (ACADIA COUNTY) | WILLIAMS FIELD SERVICES | AIR PATROL NOTICED BUBBLES IN A FLOWING CREEK. STATE & FEDERAL AGENCIES WERE NOTIFIED. A AFFECTED SEGMENT OF PIPELINE WAS ISOLATED AND BLOWN DOWN. REPAIRS OR OTHER MEASURES WILL OCCUR IN THE NEAR FUTURE. A SUPPLEMENTAL FF7100.2 REPORT WILL BE SUBMITTED WHEN FUTURE ACTIONS ARE COMPLETED. 406.5 FEET OF PIPE WAS REPLACED, COMPLETE 8/31/01 | 450000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1234 | 2001-05-04 | TX | other | UNKNOWN (SUTTON COUNTY) | EL PASO NATURAL GAS CO | GROUND SETTLEMENT AT 6"X 20" TIE-IN RESULTED IN REDUCTION IN UNDERLYING STRUCTURAL SUPPORT FOR TIE-IN. | 252176 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1235 | 2001-05-11 | LA | other | UNKNOWN (IBERIA COUNTY) | TENNESSEE GAS PIPELINE CO | A LEAK WAS LOCATED AFTER A FARMER HIT THE PIPELINE WITH A DITCHING MACHINE. | 52000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1236 | 2001-05-13 | LA | other | UNKNOWN (nan COUNTY) | SEA ROBIN PIPELINE CO | FISHING NET BROKE A GREASE FILLING OFF FROM A SWIVEL FLANGE. | 630000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1237 | 2001-05-21 | WV | other | UNKNOWN (GRANT COUNTY) | COLUMBIA GAS TRANSMISSION CORP | DURING CIS SURVEY, CREW SMELLED GAS. FURTHER INVESTIGATION INDICATED A LEAK IN THE LINE. LINE PRESSURE WAS LOWERED UNTIL PIPE COULD BE UNCOVERED AND EXAMINED. EXAMINATION OF PIPE INDICATED A LEAK CAUSED BY DENT FROM THE LINE SITTING ON A ROCK. | 149200 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1238 | 2001-05-24 | LA | other | UNKNOWN (nan COUNTY) | DYNEGY MIDSTREAM SERVICES, L.P. | UNKNOWN OUTSIDE FORCE | 130000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1239 | 2001-05-24 | KS | other | UNKNOWN (PHILLIPS COUNTY) | KINDER MORGAN GP, INC. | A COUNTY MAINTAINER WAS GRADING THE ROAD AND CUT INTO THE PIPELINE, WHICH CROSSED UNDER THE ROAD. | 69000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1240 | 2001-06-16 | TX | other | UNKNOWN (PANOLA COUNTY) | GULF SOUTH PIPELINE CO | THE COMPRESSOR FRAME EXPERIENCED MECHANICAL FAILURE IN THE CROSSHEAD AREA WHICH LOOSENED THE COMPRESSOR ROD PACKING GLAND. GAS PRESSURE ESCAPED BY THE PACKING GLAND AND IGNITED BEFORE THE UNIT SHUT DOWN. THE UNIT SHUTDOWN ON VIBRATION AND THE STATION FIRE AND GAS DETECTION "EMERGENCY SHUTDOWN SYSTEM" ACTIVATED AND SHUTDOWN THE STATION. FAILURE OCCURRED DUE TO LIQUID GETTING INTO THE UNIT. | 125000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1241 | 2001-06-13 | FL | other | UNKNOWN (ESCAMBIA COUNTY) | GULF SOUTH PIPELINE CO | METALLURGICAL STUDY IS CURRENTLY BEING PERFORMED. A CAUSE WILL BE DETERMINED ONCE THE ANALYSIS IS COMPLETED. SEE ATTACHED INCIDENT SKETCH 6/13/2001 FOR DETAILS OF THE INCIDENT AREA. ADDITIONAL SUPPLEMENTAL REPORT(S) WILL BE FILED AS INFORMATION BECOMES AVAILABLE. SUPPLEMENTAL 12-13-2002- AS WAS STATED IN OUR INITIAL INCIDENT RESPONSE TO THE FAILURE THAT OCCURRED ON JUNE 13, 2001 ON OUR 8" LINE FEEDING THE TWO NAVAL BASES IN PENSACALA, WE SHIPPED OFF THE SECTION OF PIPE TO A THIRD PARTY FOR A METALLURGICAL EVALUATION OF THE FAILURE. THE PIPE WS EVALUATED BY KIEFNER AND ASSOCIATES, INC IN WORTHINGTON - OHIO. THE FAILURE OCCURRED WHILE A READY-MIX TRUCK WAS UNLOADING CONCRETE FOR A CONCRETE SLAB. THE REAR AXLES OF THE READY-MIX TRUCK WERE POSITIONED APPROXIMATELY ALMOST PARALLEL TO AND OVER THE PIPELINE. THE LINE WAS OPERATING AT APPROXIMATELY 300 PSIG AT THE TIME OF THE FAILURE. AN 8.2 FOOT SEGMENT OF FAILED PIPE WAS ANALYZED TO DETERMINE MATERIAL PROPERTIES, CHEMICAL PROPERTIES, AND TO CHARACTERIZE THE FRACTURE AREA. TWO ADDITIONAL 1-FOOT SEGMENTS WERE REMOVED FROM THE PIPELINE ADJACENT TO THE FAILURE TO PROVIDE MATERIAL FOR MECHANICAL TESTING. THE PIPE WAS 8.625 INCH OD, 0.203 INCH WT FURNACE LAP WELDED PIPE. THE CONSLUSIONS FROM THE TESTING PROVIDED BY KIEFNER AND ASSOCIATES INC, STATED THAT THE LAP-WELD SEAM WAS NOT CONTRIBUTING FACTOR TO THE FAILURE OF THE IRON PIPE. AN AREA OF MECHANICAL DAMAGE WAS LOCATED IN THE CENTER OF THE FRACTURE. THE MECHANICAL DAMAGE WAS PRESENT PRIOR TO THE FRACTURE, AS INDICATED BY THE MATCHING SMEARED METAL PATTERN APPEARING ON BOTH SIDES OF THE FRACTURE. THE PREEXISTING MECHANICAL DAMAGE LOCATED AT THE CENTER OF THE PIPELINE FRACTURE IS CONSIDERED TO BE A CONTRIBUTING FACTOR TO THE FAILURE. THE FINAL REPAIR CONSISTED OF REPLACING 3,200 FT OF 8" LINE. | 518140 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1242 | 2001-06-14 | WI | other | UNKNOWN (COLUMBIA COUNTY) | NORTHERN NATURAL GAS CO (ENRON) | LEAK RESULTED FROM SUSPECTED LIGHTING STRIKING PIPELINE. | 42000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1243 | 2001-06-19 | AR | other | UNKNOWN (LOGAN COUNTY) | RELIANT ENERGY GAS TRANSMISSION | THIRD PARTY CONTRACTOR CALLED IN LOCATE REQUEST. COMPANYS PIPELINE IN AREA IDENTIFIED ON LOCATE WAS MARKED. CONTRACTOR STRUCK ANOTHER ONE OF COMPANYS PIPELINES WHILE WORKING OUTSIDE THE AREA IDENTIFIED ON THE LOCATE. | 89000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1244 | 2001-06-20 | OH | other | UNKNOWN (MONTGOMERY COUNTY) | ANR PIPELINE CO | THIRD PARTY/LANDOWNER HIT THE PIPELINE AS HE WAS EXCAVATING IN THE AREA FOR THE PURPOSE OF BURYING ANIMAL CARCASSES. A LEAK WAS LOCATED AND REPAIRED. | 506539 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1245 | 2001-07-08 | WV | other | UNKNOWN (WYOMING COUNTY) | COLUMBIA GAS TRANSMISSION CORP | LINE KA-14 WAS A SUSPENDED CROSSING OF THE GUYANDOTTE RIVER. THE CATACLYSMIC FLOODING OF THE GUYANDOTTE RIVER COMPLETELY WASHED OUT THE PIPELINE. THE FAILURE RESULTED FROM THE EXTREME EXTERNAL FORCES ASSOCIATED WITH THE FLOODING. ABOUT 200 FEET OF PIPELINE WAS WASHED OUT. A CREW WAS DISPATCHED TO THE AREA. HOWEVER, DUE TO MANY WASHED OUT ROADS AND BRIDGES AND DANGEROUS FLOODING CONDITIONS, IT TOOK 5 HOURS FOR THE CREW TO REACH SHUT OFF VALVES ON BOTH SIDES OF THE PIPELINE WASHOUT. | 53800 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1246 | 2001-08-15 | KS | maintenance | UNKNOWN (HASKELL COUNTY) | NORTHERN NATURAL GAS CO (ENRON) | GAS WAS IGNITED INSIDE A METER BUILDING. THE EXACT CAUSE CANNOT BE DETERMINE SUSPECTED TO BE GAS LEAKING FROM A FLANGE THAT WAS IGNITED BY LIGHTING. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1247 | 2001-07-23 | TX | other | UNKNOWN (BROOKS COUNTY) | TENNESSEE GAS PIPELINE CO | AT APPROXIMATELY 3:20 PM ON 7/23/01, HAAS ANDERSON CONTRACTOR WAS DIGGING A HOLE WITH A 950 FRONT END LOADER/EXCAVATOR TO BURY A DEBRIS. THEY STRUCK THE TGP 26" 400-2 SAN SALVADOR LINE AND PUNCTURED A HOLE AT APPROXIMATE MP 403-2+9.26. | 194560 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1248 | 2001-07-25 | LA | maintenance | UNKNOWN (LAFOURCHE COUNTY) | TEXAS EASTERN TRANSMISSION CORP (DUKE) | A TAP VALVE, A 2-INCH WKM GATE VALVE, WAS BEING CLOSED TO INITIATE THE ABANDONMENT OF A LATERAL WHEN THE VALVE BONNET SEPARATED FROM THE BODY OF THE VALVE DUE TO A GASKET FAILURE RESULTING IN GAS RELEASE TO ATMOSPHERE. | 200000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1249 | 2001-08-14 | AK | other | UNKNOWN (nan COUNTY) | BP PIPELINES (ALASKA), INC | WIND-INDUCED VIBRATION OF THE ELEVATED PIPELINE CREATING HIGH CYCLIC STRESSES MAY HAVE CAUSED A FATIGUE FAILURE OF A GIRTH WELD. A COMPLETE FAILURE ANALYSIS WILL BE CONDUCTED. | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1250 | 2001-07-25 | TX | other | UNKNOWN (GREGG COUNTY) | VOYAGEUR PIPELINE LLP | BUILDING CONTRACTOR CONSTRUCTING A DRIVEWAY ENTRANCE TO NEW RETAIL STORE DUG TOO DEEP WITH ROTO MIXER, LINE WAS MARKED PREVIOUS DAY. | 6600 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1251 | 2001-07-29 | IN | other | UNKNOWN (SPENCER COUNTY) | SOUTHERN INDIANA GAS & ELECTRIC CO | AN ELECTRICAL STORM APPEARS TO HAVE CAUSED DAMAGE TO A REGULATOR FEEDING A 1-INCH PIPELINE NEAR A GAS WELLHEAD. LEAKING NATURAL GAS (FROM THE REGULATOR) IGNITED FROM AN UNKNOWN SOURCE. FLAMES FROM THE FIRE THEN ENGULFED TWO -(2) NEARBY 3" VALVES, DESTROYING THE FLANGE GASKET MATERIAL THUS ALLOWING GAS LEAKING FROM THESE AREAS TO FEED THE EXISTING FIRE. | 5000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1252 | 2001-08-03 | LA | leaks and spills | UNKNOWN (nan COUNTY) | COLUMBIA GULF TRANSMISSION CO | GAS DETECTOR INDICATED GAS LEAK DURING CASING VENT LEAKAGE SURVEY. PIN HOLE LEAK FOUND NEXT TO CASING SPACER DUE TO ATMOSPHERIC CORROSION. | 78000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1253 | 2001-08-09 | OK | maintenance | UNKNOWN (BRYAN COUNTY) | NATURAL GAS PIPELINE CO OF AMERICA (KMI) | DEAD VEGETATION DISCOVERED AND CONFIRMED TO BE GAS LEAKAGE-FOUND LEAK ON WELD. | 135600 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1254 | 2001-08-20 | TX | other | UNKNOWN (REFUGIO COUNTY) | KINDER MORGAN TEXAS PIPELINE CO | THIRD PARTY GOUGED INDEX 153 WHILE LAYING 3" FIBERGLASS PIPELINE AND DID NOT NOTIFY KMTP, CAUSING LINE TO LEAK. | 16680 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1255 | 2001-08-11 | AZ | leaks and spills | UNKNOWN (COCONINO COUNTY) | EL PASO NATURAL GAS CO | EPNG LINE L1200 RUPTURED AT MP 286+5040, AT APPROXIMATELY 5:00 A.M. (MST) ON 8/11/01. THE EXACT CAUSE IS STILL UNDER INVESTIGATION. HOWEVER, STRESS CORROSION CRACKING (SCC) IS SUSPECTED. | 737500 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1256 | 2001-08-14 | FL | leaks and spills | UNKNOWN (ORANGE COUNTY) | FLORIDA GAS TRANSMISSION CO (ENRON) | ELECTRICAL INTERFERENCE FROM ADJACENT TELEPHONE CABLE CAUSED LOCALIZED LOSS OF EFFECTIVE PIPELINE CATHODIC PROTECTION. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1257 | 2001-08-21 | LA | other | UNKNOWN (ST MARY COUNTY) | GULF SOUTH PIPELINE CO | CONTRACTOR USING A TREE GRINDER ON AMPHIBIOUS EXCAVATOR WAS CLEANING RIGHT OF WAY FOR WILLIAMS FIELD SERVICES AND INADVERTENTLY SET GRINDER DOWN ON 20" PIPELINE AND PUNCTURED THE PIPELINE. THE PIPELINE WAS BURIED ONLY 6" BELOW SOIL BY DESIGN FOR ARMY CORP OF ENGINEERS LEAVE CROSSING. | 50832 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1258 | 2001-09-07 | MT | other | UNKNOWN (nan COUNTY) | MONTANA POWER CO | A CONTRACTOR DIGGING WITH AN LARGE TRACK MOUNTED EXCAVATOR HIT THE MPC 3" DILLION TO BARRETTS NATURAL GAS TRANSMISSION LINE AT MP 55.7. THE IMPACT OF THE EXCAVATOR TOOTH PUNCTURED THE LINE AND NATURAL GAS BEGAN BLOWING IMMEDIATELY. HIGH PRESSURE GAS ESCAPED BUT DID NOT IGNITE. APPROXIMATELY 90 FARM TAP CUSTOMERS AS WELL AS ONE LARGE INDUSTRIAL CUSTOMER LOST NATURAL GAS SERVICE. NO INJURIES OCCURRED.A CONTRACTOR DIGGING WITH AN LARGE TRACK MOUNTED EXCAVATOR HIT THE MPC 3" DILLION TO BARRETTS NATURAL GAS TRANSMISSION LINE AT MP 55.7. THE IMPACT OF THE EXCAVATOR TOOTH PUNCTURED THE LINE AND NATURAL GAS BEGAN BLOWING IMMEDIATELY. HIGH PRESSURE GAS ESCAPED BUT DID NOT IGNITE. APPROXIMATELY 90 FARM TAP CUSTOMERS AS WELL AS ONE LARGE INDUSTRIAL CUSTOMER LOST NATURAL GAS SERVICE. NO INJURIES OCCURRED.A CONTRACTOR DIGGING WITH AN LARGE TRACK MOUNTED EXCAVATOR HIT THE MPC 3" DILLION TO BARRETTS NATURAL GAS TRANSMISSION LINE AT MP 55.7. THE IMPACT OF THE EXCAVATOR TOOTH PUNCTURED THE LINE AND NATURAL GAS BEGAN BLOWING IMMEDIATELY. HIGH PRESSURE GAS ESCAPED BUT DID NOT IGNITE. APPROXIMATELY 90 FARM TAP CUSTOMERS AS WELL AS ONE LARGE INDUSTRIAL CUSTOMER LOST NATURAL GAS SERVICE. NO INJURIES OCCURRED. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1259 | 2001-08-26 | LA | other | UNKNOWN (nan COUNTY) | ANR PIPELINE CO | A LEAK WAS LOACTAED AFTER GAS BUBBLES WERE REPORTED IN EI 266 IN AREA OF PLIDCO REPAIR CLAMP INSTALLED IN 1987. | 75000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1260 | 2001-08-26 | LA | other | UNKNOWN (nan COUNTY) | TENNESSEE GAS PIPELINE CO | A SHRIMPERS NET, APPARENTLY SNAGGED A SUBSEA ASSEMBLY, UNDER THE VALVE GUARD AT SIDE VALVE 523M-102, IN SHIP SHOAL BLOCK 198G. | 70000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1261 | 2001-08-31 | LA | other | UNKNOWN (nan COUNTY) | SOUTHERN NATURAL GAS CO | A LEAK WAS LOCATED ON THE 12" WEST DELTA BLOCK 30 LINE, AT MP 13.90, AFTER BUBBLES WERE SPOTTED IN THE PIPE DITCH. PIPE IS IN THE MARSH UNDER SEVERAL FEET OF MUD. LINE WILL BE ISOLATED AND THE REPAIR MADE BY INSTALLING A LEAK CLAMP. THE REPAIR IS PENDING, AFTER APPROVAL FOR A CORPS OF ENGINEERS PERMIT IS GRANTED. | 90000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1262 | 2001-09-03 | LA | leaks and spills | UNKNOWN (OUACHITA COUNTY) | MID LOUISIANA GAS CO | FAILURE UNDER INVESTIGATION. PIPE SENT TO LAB FOR ANALYSIS. HISTORICAL RECORDS AND PIPELINE OPERATIONS BEING REVIEWED. | 450000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1263 | 2001-09-17 | PA | other | UNKNOWN (LANCASTER COUNTY) | U G I CORP | WHILE EXCAVATING A PROPERLY MARKED PIPELINE TO EXPOSE A CONTROL FITTING, UGIS CONTRACTOR HIT AN ADJACENT SERVICE PUNCH TEE THAT THE CONTRACTOR HAD PREVIOUSLY INSTALLED. THE SERVICE PUNCH TEE WAS TORN PARTIALLY FROM THE MAIN PIPELINE. GAS SUBSEQUENTLY ESCAPED. FINDINGS INDICATE THE CONTRACTOR WAS USING POWERED EXCAVATING EQUIPMENT TOO CLOSE TO THE PIPELINE. | 80000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1264 | 2001-07-24 | TX | other | UNKNOWN (NUCES COUNTY) | CROSSTEX PIPELINE CO | TRAIN DERAILED OFF TRACK WHICH CAUSED ONE TRAIN CAR TO LAND ON PIPELINE CROSSING A DRAINAGE DITCH. | 124000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1265 | 2001-09-21 | ID | other | UNKNOWN (KOOTENAI COUNTY) | NORTHWEST PIPELINE CORP (WGP) | WHILE ATTEMPTING TO REPAIR A 2" WKM GATE VALVE AT THE MCGUIRE METER STATION, THE TOP OF THE VALVE CAME APART DUE TO A BROKEN STEM IN THE INTERIOR OF THE VALVE. | 64215 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1266 | 2001-09-25 | LA | leaks and spills | UNKNOWN (BEINVILLE COUNTY) | GULF SOUTH PIPELINE CO | THE PIPE WILL BE TAKEN TO A METALLURGIST TO DETERMINE THE CAUSE OF THE INCIDENT. 11-19-2001 - BASED ON THE ANALYSIS FROM METALLURGICAL CONSULTANTS, INC. THE FAILURE WAS CAUSED BY INTERNAL CORROSION. THE INTERNAL CORROSION APPEARS TO BE THE RESULTS OF (MIC) MICROBIOLOGICALLY INDUCED CORROSION. | 115850 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1267 | 2001-10-09 | VA | maintenance | UNKNOWN (LOUDOUN COUNTY) | COLUMBIA GAS TRANSMISSION CORP | THE PIPELINE LEAK WAS CAUSED BY A GIRTH WELD FAILURE OF A RECENTLY CONSTRUCTED PIPELINE SECTION. THE FORMAL FAILURE INVESTIGATION HAS NOT BEEN COMPLETED. HOWEVER, PRELIMINARY RESULTS INDICATE THAT THIS FAILURE WAS CAUSED BY A COMBINATION OF CONSTRUCTION AND PRESSURIZATION STRESS ACTING UPON A HYDROGEN CRACK. | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1268 | 2001-10-18 | LA | other | UNKNOWN (nan COUNTY) | TENNESSEE GAS PIPELINE CO | BUBBLES REPORTED BY WORK BOAT IN SP. BLK. 39 AREA, APPROXIMATELY 300 FEET WEST OF 526A-2400 LINE. POSSIBLE STRESS CRACK DUE TO MUD SLIDE ACTIVITY IN THE AREA. | 275000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1269 | 2001-10-16 | LA | other | UNKNOWN (nan COUNTY) | TENNESSEE GAS PIPELINE CO | A LEAK WAS LOCATED AFTER GAS BUBBLES WERE REPORTED APPROXIMATELY 20 FEET WEST OF THE EMPIRE WATERWAY CROSSING. AFTER FURTHER INVESTIGATION, IT WAS DETERMINED THAT THE AREA HAD BEEN SCOURED DUE TO EROSION, AND THE PIPE HAD BECOME EXPOSED. | 570000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1270 | 2001-10-24 | LA | leaks and spills | UNKNOWN (nan COUNTY) | TENNESSEE GAS PIPELINE CO | A LEAK WAS LOCATED AFTER GAS BUBBLES WERE REPORTED IN WC 53, 1/2 MILE NORTHEST OF THE WC BLK. 53 PLATFORM. INVESTIGATIVE DIVE REVEALED A 2" ELL ON THE BYPASS LINE AROUND SV 821E-114A WAS LEAKING. INTERNAL CORROSION IS THE APPARENT CAUSE. | 123000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1271 | 2001-11-07 | MD | other | UNKNOWN (ALLEGHANY COUNTY) | COLUMBIA GAS OF MARYLAND INC | WILDFIRE BURNING ON THE MOUNTAINSIDE CROSSED OVER THE AREA OF THE PIPELINE AND IGNITED SMALL LEAKS THAT WERE ON A REGULAR MONITORING SCHEDULE. SERVICE WAS INTERRUPTED TO 70 CUSTOMERS WHILE AREA WAS SECURED AND 21 SECTION OF PIPE WAS REPLACED. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1272 | 2001-10-12 | OK | other | UNKNOWN (nan COUNTY) | TRANSOK INC | AT 0105 HRS A DROP IN PRESSURE WAS EXPERIENCED ON TRANSOK LINE #31. THE DROP IN PRESSURE WAS THE RESULT OF A RUPTURE. THE ESCAPING GAS IGNITED AND A FIRE RESULTED. THE INCIDENT IS UNDER INVESTIGATION TO IDENTIFY CAUSE. AFTER DETERMINATION A SUPPLEMENTAL REPORT WILL FOLLOW. 1-17-02 AFTER FURTHER INVESTIGATION, IT WAS CONCLUDED THA THE CAUSE OF THE TRANSOK LINE #31 RUPTURE AND SUBSEQUENT FIRE WAS DUE TO A WELD FAILURE RESULTING FROM TENSILE OVERLOAD. THE ULTIMATE FAILURE OCCURRED AS A RESULT OF A COMBINATION OF THE FOLLOWING CAUSAL FACTORS: EXCESSIVE LOADING ON THE PIPE DUE TO PIPE MISALIGNMENT, RESIDUAL MAGNETIC FIELDS, AND EXTERNAL LOADING CAUSED BY SETTLING OF BACKFILL AND SIGNIFICANT RAINFALL. | 107500 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1273 | 2001-12-07 | LA | maintenance | UNKNOWN (WINN COUNTY) | GULF SOUTH PIPELINE CO | HAIRLINE FRACTURE DEVELOPED IN THE PIPE WALL DUE TO ELEVATED HARDNESS. THE LOCATION ALREADY HAD A REINFORCING SLEEVE OVER THE PIPE. THE PIPE STOPPED LEAKING WHEN THE PRESSURE WAS REDUCED. THE LOCATION WAS REMOTE AND WAS NEVER CONSIDERED UNSAFE. | 89634 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1274 | 2001-09-20 |  | other | UNKNOWN (nan COUNTY) | WILLIAMS FIELD SERVICES | BUBBLES WERE REPORTED ON GALVESTON BLOCK 419. INVESTIGATION DETERMINED A 12" VALVE WAS LEAKING. THE VALVE AND ASSOCIATED PIPE WERE REMOVED AND REPLACED WITH A SPOOL OF NEW, PRE-TESTED PIPE OF SAME GRADE, AND THE LINE RETURNED TO SERVICE. | 250000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1275 | 2001-12-07 | PA | maintenance | UNKNOWN (FAYETTE COUNTY) | COLUMBIA GAS TRANSMISSION CORP | ON 12/7/2001 LINE 1804 RUPTURED IN THE VICINITY OF A SIDE CONNECTION. THERE WERE NO INJURIES. | 348000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1276 | 2001-12-10 | PA | other | UNKNOWN (ALLEGHENY COUNTY) | COLUMBIA GAS OF PENNSYLVANIA | SEWER CONTRACTOR PERFORMING EMERGENCY REPAIR HIT 16 STEEL LINE. LINE WAS HIT WITH TOOTH OF EXCAVATION EQUIPMENT CAUSING 2X3 GASH IN PIPE. | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1277 | 2001-11-13 | KS | leaks and spills | UNKNOWN (LAFAYETTE COUNTY) | WILLIAMS GAS PIPELINE CENTRAL, INC. | ROAD SALT SPILLED ON TO LINE CAUSING CORROSION. THE CORROSION OCCURRED WHERE ROAD ALS AND GRIME SPILLED DOWN ON THE LINE. THIS BRIDGE CROSSING WAS SCHEDULED TO BE REPLACED WITH A ROAD BORE IN 2002. HOWEVER, BECAUSE OF THE LEAK, THIS PROJECT WILL BEGIN IN DECEMBER 2001. THE COST OF THIS PROJECT WILL BE BETWEEN $800,000 AND $1,000,000. | 800000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1278 | 2001-11-05 | AR | other | UNKNOWN (GARLAND COUNTY) | RELIANT ENERGY GAS TRANSMISSION | COMPANY EMPLOYEE AND TWO CONTRACT EMPLOYEES WERE AT THE JESSIEVILLE SCRAPER TRAP YARD TO INSERT AND RUN A 16" CLEANING PIG IN COMPANYS 16" PIPELINE, BT-1-AS, LOCATED IN RURAL GARLAND COUNTY, ARKANSAS ON NOVEMBER 5, 2001. COMPANYS EMPLOYEE REMOVED THE 16" LAUNCHER FROM SERVICE BY CLOSING ALL ASSOCIATED VALVES AND BLOWING DOWN THE LAUNCHER. AFTER THE BLOWDOWN WAS COMPLETED COMPANY EMPLOYEE NOTICED UNRELATED LEAKAGE FROM A 4" KICKER LINE VALVE, AND USING A HIGH-PRESSURE GREASE GUN, GREASED THE 4" VALVE. COMPANYS EMPLOYEE AND THE TWO CONTRACT EMPLOYEES OPENED THE SCRAPER TRAP DOOR AND INSERTED THE PIG. BEFORE THE LAUNCHER DOOR COULD BE SHUT THE PIG WAS EJECTED FROM THE OPEN END OF THE LAUNCHER STRIKING BOTH CONTRACT EMPLOYEES. BOTH CONTRACT EMPLOYEES WERE TAKEN TO ST. JOSEPH HOSPITAL IN HOT SPRINGS, ARKANSAS. ONE BEING TREATED IN THE EMERGENCY ROOM AND RELEASED AND THE OTHER ADMITTED WITH A BROKEN LEG. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1279 | 2001-10-23 | OK | other | UNKNOWN (TULSA COUNTY) | OKLAHOMA NATURAL GAS CO | EXCAVATOR USING A TRACKHOE DAMAGED ONGS 18-INCH PIPELINE. | 55000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1280 | 2001-12-12 | KS | other | UNKNOWN (MITCHELL COUNTY) | WILLIAMS GAS PIPELINE CENTRAL, INC. | LEAK IS INSIDE CASING. UNKNOWN CAUSE. NEW XING WILL EXCEED $50,000. LEAK WILL BE INVESTIGATED AFTER REPAIRS. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1281 | 2001-12-06 | KS | other | UNKNOWN (SMITH COUNTY) | WILLIAMS GAS PIPELINE CENTRAL, INC. | LEAK IS DETECTED INSIDE CASING. UNKNOWN CAUSE. NEW ROAD XING WILL EXCEED 50,000.00. LEAK WILL BE INVESTIGATED AFTER REPAIRS. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1282 | 2001-11-06 | CA | other | UNKNOWN (TEHAMA COUNTY) | PACIFIC GAS & ELECTRIC CO | LUBE OIL MIST RELEASED FROM A CRACKED 1/4- IN PIPE NIPPLE FLASHED WHEN THE TURBINE UNIT REACHED OPERATING TEMP. COMPRESSOR STATION SHUT DOWN SAFETY- NO RELEASE OF GAS. TURBINE SKID, COMPRESSOR AND COMPRESSOR BUILDING SEVERELY DAMAGED. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1283 | 2001-12-06 | LA | leaks and spills | UNKNOWN (TERREBONNE COUNTY) | WILLIAMS ENERGY GROUP-FIELD SERVICES | A TEMPORARY LEAK CLAMP WAS INSTALLED; LINE HAS BEEN SHUT-IN AND WILL NOT BE BROUGHT BACK INTO SERVICE UNTIL AN ASSESSMENT OF THE LINES CONDITION IS DETERMINED. | 450000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1284 | 2001-11-21 | TX | leaks and spills | UNKNOWN (nan COUNTY) | NATURAL GAS PIPELINE CO OF AMERICA (KMI) | A SMALL PINHOLE LEAK WAS DISCOVERED ON THE BOTTOM OF THE PIPE NEAR THE 6 OCLOCK POSITION. A LEAK CLAMP WAS INSTALLED. | 162350 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1285 | 2001-12-16 | CA | other | UNKNOWN (SONOMA COUNTY) | PACIFIC GAS & ELECTRIC CO | IT IS SUSPECTED THAT A CONTRACTOR EXCAVATING OVER THE LINE DAMAGED THE LINE ENOUGH TO SIGNIFICANTLY WEAKEN IT TO THE EXTENT THAT IT RUPTURED DAYS AFTER THE DAMAGE. | 120000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1286 | 2001-06-30 | LA | leaks and spills | UNKNOWN (TERREBONNE COUNTY) | WILLIAMS ENERGY GROUP-FIELD SERVICES | AERIAL PATROL NOTICED SHEEN IN MARSH. STATE AND FEDERAL AGENCIES WERE NOTIFIED. BOOMS WERE DEPLOYED TO ISOLATE AND CONTAIN PRODUCT. ALL RELEASED PRODUCT WAS RECOVERED. LINE THEN WAS BLOWN DOWN AND REPAIRED. | 300000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files
1287 | 2001-12-12 | MI | other | UNKNOWN (nan COUNTY) | MICHIGAN CONSOLIDATED GAS CO (MICHCON) | FAILURE OF SEALING ELEMENT OF STOPPLE. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/flagged-data-files