## incident_gas_distribution_mar20
| Date | State | Cause of Loss | Name of Installation | Name of Owner | Text | Loss Estimated ($)
0 | 2004-02-27 | AZ | leaks and spills | UNKNOWN (MARICOPA COUNTY ) | SOUTHWEST GAS CORP | <P>SOUTHWEST GAS EXPERIENCED A GAS LEAK ON A 4" PE MAIN THAT WAS INSTALLED IN JOINT TRENCH WITH A 12" WATER MAIN. THE GAS LINE WAS BELOW THE WATER LINE AND AS A RESULT SOUTHWEST GAS USED VALVES TO CONTROL THE LEAK. WE WERE UNABLE TO DETERMINE THE CAUSE DU | 0
1 | 2004-02-21 | UT | natural disasters | UNKNOWN (UTAH COUNTY ) | QUESTAR GAS COMPANY | PERSONNEL FROM THE UTAH STATE FIRE MARSHAL'S OFFICE DETERMINED THAT THE FIRE WAS CAUSED AS A RESULT OF SNOW SLIDING OFF THE ROOF OF THE STRUCTURE AND IMPACTING THE NATURAL GAS METER. THE IMPACT OF THIS SNOW DISPLACED THE METER ASSEMBLY BREAKING THE PIPE | 230
2 | 2004-02-15 | GA | maintenance | UNKNOWN (MUSCOGEE COUNTY ) | ATMOS ENERGY CORPORATION | FRACTURED PIPE UNEARTHED ON FEB.20TH 2004. THE SECTION OF PIPE WHERE THE FRACTURE WAS FOUND WAS TAKEN INTO CUSTODY BY THE GEORGIA PSC FOR METALLURGICAL ANALYSIS, WHICH BEGAN ON MARCH 15, 2004. THE METALLURGICAL ANALYSIS OF THE PIPES REVEALED A STRESS FRA | 0
3 | 2004-02-17 | CO | other | UNKNOWN (SAN MIGUEL COUNTY ) | KINDER MORGAN RETAIL |  | 427
4 | 2004-03-05 | TX | sabotage | UNKNOWN (TRAVIS COUNTY ) | TEXAS GAS SERVICE COMPANY | A CONTRACTOR STRUCK A 12" STEEL NATURAL GAS MAIN WITH A 36" AUGER ATTACHMENT FROM THE REAR OF A DRILLING TRUCK CAUSING NATURAL GAS TO ESCAPE. THE LOCAL FIRE DEPARTMENT TEMPORARILY CLOSED A SECTION OF RM 620 UNTIL THE AREA WAS BROUGHT UNDER CONTROL. TEXA | 58564
5 | 2004-02-01 | MI | technical failure | UNKNOWN (LIVINGSTON COUNTY ) | CONSUMERS ENERGY CO | ON FEBRUARY 1, 2004 AN EMPLOYEE WAS INVESTIGATION A POSSIBLE GAS LEAK ON A PLASTIC MAIN LOCATE IN THE STREET ROW. DURING THE LEAK INVESTIGATION PROCEDURE THE EMPLOYEE, FOLLOWING COMPANY STANDARDS, BEGAN TO CHECK FOR GAS IN THE GROUND BEGINNING AT THE HOU | 10
6 | 2004-03-18 | VA | technical failure | UNKNOWN (nan COUNTY ) | RICHMOND DEPT OF PUBLIC UTILITIES, CITY OF | ON THURSDAY, 03/19/2004 AT APPROXIMATELY 2240 HOURS, HENKELS & MCKOY CREW #8 WAS KILLING TWO GAS SERVICES TO 1709 AND 1711 NORTH 21ST STREET. THE SERVICE TO 1711 NORTH 21ST STREET WAS KILLED AND THE CREW WAS WORKING TO KILL THE SERVICE TO 1709 NORTH 21ST | 0
7 | 2004-04-13 | MA | other | UNKNOWN (NORFOLK COUNTY ) | BAY STATE GAS CO | APRIL 21 2006 ----------------- THE INCIDENT WAS INVESTIGATED BY THE MASSACHUSETTS STATE FIRE MARSHALLS OFFICE , TROOPER MARK VARKAS. SEE THE ATTACHED REPORT. THE INCIDENT HAS BEEN DETERMINED TO BE ACCIDENTAL. IT IS BELIEVED THE HOMEOWNER, WHILE HAMME | 10
8 | 2004-03-26 | PA | other | UNKNOWN (LANCASTER COUNTY ) | UGI UTILITIES INC | AT 20:20 (APPROXIMATELY) MARCH 26, 2004 AN EXPLOSION OCCURRED AT THE RESIDENCE OF 403 SOUTH QUEEN STREET, LANCASTER, PENNSYLVANIA DUE TO AN UNKNOWN IGNITION SOURCE. A UGI UTILITY, INC (UGI) EMERGENCY RESPONDER WAS IN THE PROCESS OF INVESTIGATION AN INSID | 0
9 | 2004-04-03 | IN | technical failure | UNKNOWN (VANDERBURGH COUNTY ) | SOUTHERN INDIANA GAS & ELECTRIC CO | AT APPROXIMATELY 7:42 AM ON 4/3/04. VECTREN RECEIVED NOTICE THAT A THIRD PARTY HAD MISTAKENLY TURNED A GAS SERVICE VALVE AND RUPTURED A 1/2" PE PLASTIC SERVICE LINE AT 33007 LINCOLN AVE. IN EVANSVILLE IN. THE SERVICE HAD BEEN INSTALLED THROUGH A PREVIOUS | 0
10 | 2004-04-27 | AK | other | UNKNOWN (nan COUNTY ) | ENSTAR NATURAL GAS CO | ON TUESDAY MORNING, APRIL 27, 2004 AT APPROXIMATELY 9:30 AM ADT, ENSTAR NATURAL GAS COMPANY WAS NOTIFIED OF A STRUCTURE FIRE AT 6304 BIRCH LANE, NORTH KENAI, ALASKA. AN ENSTAR SERVICEMAN WAS DISPATCHED TO THE SCENE. UPON ARRIVAL THE SERVICEMAN FOUND A R | 10
11 | 2004-04-01 | OH | sabotage | UNKNOWN (LUCAS COUNTY ) | COLUMBIA GAS OF OHIO INC | A THIRD PARTY CONTRACTOR DIRECTIONALLY BORED INTO AN UNDERGROUND 2-INCH PLASTIC MEDIUM PRESSURE GAS MAIN. THE THIRD PARTY CONTRACTOR NOTIFIED COLUMBIA GAS OF OHIO VIA THE ONE CALL SYSTEM AT 14:08 ON 04/01/04. COLUMBIA PERSONNEL ARRIVED AT THE SITE AT APP | 100
12 | 2004-04-06 | IL | other | UNKNOWN (LASALLE COUNTY ) | NORTHERN ILLINOIS GAS CO | SUPPLEMENTAL REPORT FILED TO INDICATE SUM THE TOTAL ESTIMAGED DAMAGES. ************************************************************************** FIRE/EXPLOSION ORIGINATED INSIDE THE HOUSE (STILL UNDER CONSTRUCTION), NEAR THE GARAGE AREA. FLAMES SPRE | 0
13 | 2004-04-25 | PA | other | UNKNOWN (ALLEGHENY COUNTY ) | T W PHILLIPS GAS & OIL CO | FIRE DESTOYED SINGLE FAMILY HOME AT 342 MOYHEND STREET, SPRINGDALE, PA 15144. SINGLE OCCUPANT, DAVID HUMMEL, WAS INJURED IN FIRE AND TAKEN TO LOCAL HOSPITAL. ALTHOUGH NO DIRECT INFORMATION, ACCORDING TO NEWS REPORTS, MR. HUMMEL IS IN CRITICAL CONDITION. | 0
14 | 2004-04-26 | IL | other | UNKNOWN (COOK COUNTY ) | NORTHERN ILLINOIS GAS CO | SUPPLEMENTAL REPORT SUBMITTED WITH THE 3 PROPERTY DAMAGE SUBCATEGORIES SUMMING UP TO THE TOTAL VALUE. ****************************************************************************** HOMEOWNER OF MOBILE HOME WAS HEATING GREASE IN MICROWAVE. GREASE CONTA | 0
15 | 2004-04-28 | IL | other | UNKNOWN (WILL COUNTY ) | NORTHERN ILLINOIS GAS CO | SUPPLIMENTAL REPORT SUBMITTED WITH THE 3 PROPERTY DAMAGE SUBCATEGORIES SUMMING UP TO THE TOTAL VALUE. **************************************************************************** MULCH FIRE ORIGINATED NEAR THE METER SET. THE METER SET (SERVICE REGULA | 0
16 | 2004-06-18 | WI | sabotage | UNKNOWN (LACROSSE COUNTY ) | NORTHERN STATES POWER CO, A WISCONSIN CORPORATION DBA XCEL ENERGY | THE 5/8" PE SERVICE FEEDING THE BUILDING WAS PUNCTURED BY A CURB STAKE INSTALLED BY CONCRETE PAVING CONTRACTOR (JAMES CAPE AND SONS, CO.). GAS FROM THE PUNCTURED SERVICE MIGRATED INTO THE BUILDING AND WAS IGNITED BY AN UNKNOWN SOURCE CAUSING THE EXPLOSIO | 1000
17 | 2004-04-28 | IL | other | UNKNOWN (WILL COUNTY ) | NORTHERN ILLINOIS GAS CO | SUPPLEMENTAL REPORT SUBMITTED WITH THE 3 PROPERTY DAMAGE SUBCATEGORIES SUMMING UP TO THE TOTAL VALUE. ****************************************************************************** FIRE WAS STARTED BY ELECTRICAL SHORT. FIRE SPREAD TO THE LOCATION WHE | 0
18 | 2004-05-17 | AK | other | UNKNOWN (KENAI PENINSULA BOROUGH COUNTY ) | ENSTAR NATURAL GAS CO | ON MONDAY MORNING, MAY 17, 2004 AT APPROXIMATELY 11:00 PM ADT, ENSTAR NATURAL GAS COMPANY WAS NOTIFIED OF A STRUCTURE FIRE AT 36235 SCHULTZ COURT, SOLDOTNA, ALASKA. AN ENSTAR SERVICEMAN WAS DISPATCHED TO THE SCENE. UPON ARRIVAL THE SERVICEMAN FOUND A RE | 10
19 | 2004-05-19 | AK | other | UNKNOWN (nan COUNTY ) | ENSTAR NATURAL GAS CO | ON WEDNESDAY MORNING, MAY 19, 2004 AT APPROXIMATELY 3:37 AM ADT, ENSTAR NATURAL GAS COMPANY WAS NOTIFIED OF A STRUCTURE FIRE AT 16346 E BREADFORD DR, PALMER, AK. AN ENSTAR SERVICEMAN WAS DISPATCHED TO THE SCENE. UPON ARRIVAL THE SERVICEMAN FOUND A RESI | 10
20 | 2004-04-13 | LA | sabotage | UNKNOWN (TERREBONNE COUNTY ) | SOUTH COAST GAS CO INC |  | 410
21 | 2004-05-07 | AZ | technical failure | UNKNOWN (MARICOPA COUNTY ) | SOUTHWEST GAS CORP | SERVICE WAS INSTALLED BY DIRECTIONAL BORE THROUGH SEWER LATERAL. DURING SEWER LATERAL, CLEAN OUT ROTOR STUCK AND DAMAGED THE GAS SERVICE LINE. GAS MIGRATED THROUGH SEWER LATERAL INTO MOBILE HOME. THERE WAS IGNITION OF NATURAL GAS AND ONE MOBILE HOME WAS | 0
22 | 2004-04-09 | NY | sabotage | UNKNOWN (ULSTER COUNTY ) | CENTRAL HUDSON GAS & ELECTRIC CORP | C.M. APPLER AND SONS, INC. WAS REMOVING BLACKTOP AND CURBING FROM THE DRIVEWAY TO 7 TILLSON AVENUE IN HIGHLAND. THIS CONTRACTOR, UTILIZING AN EXCAVATOR, PULLED UP CURBING AND A 3/4" STEEL NATURAL GAS SERVICE LINE OPERATING AT 30 PSIG. THE SERVICE LINE S | 200
23 | 2004-05-14 | NY | other | UNKNOWN (ST LAWRENCE COUNTY ) | ST LAWRENCE GAS CO INC | GAS SERVICE INSTALLED IN 1993 UTILIZING PNEUMATIC BORING TOOL. LOCATIONS OF SEWER LATERALS WERE UNATTAINABLE OR UNKNOWN AT THE TIME OF GAS SERVICE INSTALLATION. BORING TOOL APPARENTLY PENETRATED A SHALLOW SEWER LATERAL (40" DEEP) TO RESIDENCE AT 1000 ME | 100
24 | 2004-05-12 | TX | sabotage | UNKNOWN (COLLIN COUNTY ) | COSEAY GAS | THIRD PARTY EXCAVATOR CUT 3/4" SERVICE LINE BETWEEN STREET AND HOUSE WHILE DRILLING PIER HOLES FOR SCREENING WALL. FLASH FIRE OCCURRED, HOWEVER, EXCESS FLOW VALVE ACTIVATED SHUTTING OFF THE FLOW OF GAS ALMOST IMMEDIATELY. | 0
25 | 2004-06-22 | WA | technical failure | UNKNOWN (KING COUNTY ) | PUGET SOUND ENERGY | DURING A PURGING OPERATION RELATED TO A MAIN REPLACEMENT PROJECT, AN EMPLOYEE OF A PUGET SOUND ENERGY CONTRACTOR SUFFERED BURNS WHEN THE PURGE GAS IGNITED. THE INCIDENT OCCURRED WHEN THE VALVE CONTROLLING INJECTION OF THE PURGE GAS WAS OPENED BEFORE A VE | 0
26 | 2004-05-12 | PA | maintenance | UNKNOWN (WESTMORELAND COUNTY ) | DOMINION PEOPLES | ON MAY 12, 2004 AT 9:40 AM, A REPORT OF AN ODOR OF GAS WAS RECEIVED BY DOMINION PEOPLES FROM CORDIA COMMONS, A NURSING HOME IN NORTH HUNTINGDON TOWNSHIP, WESTMORELAND COUNTY, PA. DOMINION PEOPLES PERSONNEL ARRIVED AT THE SCENE, PERFORMED THE INITIAL LEAK | 0
27 | 2004-05-20 | CA | sabotage | UNKNOWN (ORANGE COUNTY ) | SOUTHERN CALIFORNIA GAS CO | CONTRACTOR WORKING FOR CITY OF GARDEN GROVE STRUCK 3" PE MAIN WITH BACKHOE. CREW EXCAVATED CONTROL EXCAVATIONS AND PROCEEDED TO INSTALL TEMPORARY BY PASS. AT APPROXIMATELY 13:00, ESCAPING GAS IGNITED, DAMAGING BACKHOE AND OVERHEAD UTILITY LINES. FACILIT | 5000
28 | 2004-06-04 | KY | sabotage | UNKNOWN (FAYETTE COUNTY ) | COLUMBIA GAS OF KENTUCKY INC | AT APPROXIMATELY 11:55 AM ON JUNE 4, 2004 THE COLUMBIA GAS OF EENTUCKY (CKY) EMERGENCY LINE RECEIVED A CALL FROM THE LEXINGTON FIRE DEPARTMENT. THE CALLER STATED THAT A GAS LINE AT 741 SOUTH LIMESTONE SREET HAD BEEN DAMAGED RESULTING IN A FIRE AND INJURY | 0
29 | 2004-07-23 | IN | other | UNKNOWN (ALLEN COUNTY ) | NORTHERN INDIANA PUBLIC SERVICE CO | AT APPROXIMATELY 12:35 AM THE OWNER OF ERNIE'S RESTAURANT WAS USING HIS VEHICLE TO JUMP-START ANOTHER VEHICLE WHEN HIS VEHICLE SURGED FORWARD AND STRUCK THE GAS METER SET FOR THE ADJACENT FURNITURE STORE AND CONTINUED THROUGH THE BUILDING WALL. THE METER | 1070
30 | 2004-05-25 | LA | sabotage | UNKNOWN (LAFOURCHE COUNTY ) | SOUTH COAST GAS CO INC |  | 56
31 | 2004-06-07 | LA | sabotage | UNKNOWN (TERREBONNE COUNTY ) | SOUTH COAST GAS CO INC |  | 182
32 | 2004-06-08 | LA | sabotage | UNKNOWN (TERREBONNE COUNTY ) | SOUTH COAST GAS CO INC |  | 350
33 | 2004-05-10 | CA | sabotage | UNKNOWN (RIVERSIDE COUNTY ) | SOUTHERN CALIFORNIA GAS CO | CONTRACTOR WORKING FOR CALTRANS STRUCK MAIN WITH TRACKHOE, RIPPING OFF A ONE INCH NIPPLE. FACILITIES HAD BEEN RECENTLY RELOCATED FOR CALTRANS, AND CALTRANS WAS AWARE OF LOCATION. DAMAGE CAUSED BY CONTRACTOR ERROR. | 30000
34 | 2004-06-09 | MO | sabotage | UNKNOWN (JACKSON COUNTY ) | MISSOURI GAS ENERGY | THE DEVELOPER'S EXCAVATOR WAS GRADING FOR SIDEWALK INSTALLATION WHEN A TOOTH FROM A BULL DOZER STRUCK OUR 12 INCH HIGH PRESSURE MAIN. THE EXCAVATOR INDICATED THAT HE WAS MOVING ROCKS AND HAD NOT INTENDED TO DIG. THE EXCAVATOR HAD NOT MADE A FACILITY LOC | 58951
35 | 2004-06-15 | NJ | natural disasters | UNKNOWN (CAMDEN COUNTY ) | PUBLIC SERVICE ELECTRIC & GAS CO | AT 19:02 ON TUESDAY JUNE 15, 2004, PSE&G RECEIVED AN EMERGENCY GAS LEAK CALL FROM THE CAMDEN FIRE DEPARTMENT. THE CALL WAS DISPATCHED TO A SERVICE TECHNICIAN AT 19:04. THE TECHNICIAN ARRIVED ON SITE AT 19:19. UPON ARRIVAL, THE TECHNICIAN CONFIRMED THAT | 200
36 | 2004-06-24 | VA | other | UNKNOWN (nan COUNTY ) | RICHMOND DEPT OF PUBLIC UTILITIES, CITY OF | ON JUNE 24, 2004 SOMEONE ALLEGEDLY BROKE INTO THE CRAWLSPACE OF A VACANT HOME LOCATED AT 4705 CASTLEWOOD ROAD. THEY APPARENTLY STOLE COPPER HOUSE PIPE FEEDING THE GAS HOT WATER HEATER. THE OPEN END OF THE GAS PIPE ALLOWED GAS TO FLOW FREELY INTO THE CRA | 2000
37 | 2004-06-29 | OH | sabotage | UNKNOWN (MIAMI COUNTY ) | VECTREN ENERGY DELIVERY OF OHIO | A CONSTRUCTION CREW WAS EXCAVATING FOR WATER MAIN INSTALLATION WHEN THEIR TRENCHER HIT THE VECTREN'S 8 INCH GAS LINE AND IGNITED THE EXCAPING GAS CAUSING A BRIEF EXPLOSION AND ENSUING FIRE. THE FIRE DESTROYED THE TRENCHER AND CAUSED DAMAGE TO OVERHEAD CO | 2960
38 | 2004-07-05 | CA | other | UNKNOWN (TULARE COUNTY ) | SOUTHERN CALIFORNIA GAS CO | FIRE ORIGINATING AT PALLET FACTORY SPREAD ACROSS STREET TO HOMES. WALL FROM BURNING HOME TOPPLED, BREAKING METER SET ASSEMBLY AND RISER. FIRE IGNITED ESCAPING GAS. NO FIRE DAMAGE ATTRIBUTED TO ESCAPING GAS. | 0
39 | 2004-07-15 | NY | other | UNKNOWN (nan COUNTY ) | NATIONAL FUEL GAS DISTRIBUTION CORP - NEW YORK | SEE ATTACHED REPORTS (1) NEW YORK PUBLIC SERVICE COMMISSION 30 DAY REPORT (2) EXPERT FORENSIC ENGINEERING REPORT PREPARED BY ENGINEERING AND FIRE INVESTIGATIONS INC. | 0
40 | 2004-07-26 | WA | sabotage | UNKNOWN (PIERCE COUNTY ) | PUGET SOUND ENERGY | CONTRACTOR VERTICALLY AUGERING FOR GUARD RAIL POSTS AS PART OF MAJOR BRIDGE CONSTRUCTION PROJECT. UTILITY LOCATOR PAINT MARKS NOT PRESERVED WHEN PAVEMENT WAS REMOVED BY ANOTHER CONTRACTOR MAKING IT IMPOSSIBLE TO DETERMINE THEIR ACCURACY WITH CERTAINTY. | 1029
41 | 2004-08-06 | LA | sabotage | UNKNOWN (nan COUNTY ) | SOUTH COAST GAS CO INC |  | 120
42 | 2004-08-20 | LA | sabotage | UNKNOWN (ASSUMPTION COUNTY ) | PIERRE PART NATURAL GAS INC |  | 145
43 | 2004-08-02 | OH | leaks and spills | UNKNOWN (FRANKLIN COUNTY ) | COLUMBIA GAS OF OHIO INC | COMPANY CREW WAS WORKING IN AN EXCAVATION ON A LEAK REPAIR INVOLVING A PLASTIC ELBOW THAT WAS LEAKING AT THE JOINT. IN PREPARATION TO INSTALL A BY-PASS THAT WOULD ENABLE THE COMPANY TO MAKE REPAIRS, THE CREW CONTINUED WITH THE EXCAVATION OF THE PIPELINE | 8700
44 | 2004-09-08 | AZ | other | UNKNOWN (NAVAJO COUNTY ) | UNISOURCE ENERGY SERVICES | AT APPROXIMATELY 09:57 ON 9/8/04, A VEHICLE DRIVEN BY AN UNKNOWN PERSON (HIT-AND-RUN) WAS DRIVING IN THE ALLEY BETWEEN 2ND STREET AND 3RD STREET AND CAMPBELL AND HICKS IN WINSLOW ARIZONA WHEN IT STRUCK A RESIDENTIAL NATURAL GAS SERVICE RISER AND CAUSED TH | 72
45 | 2004-08-03 | NV | sabotage | UNKNOWN (CLARK COUNTY ) | SOUTHWEST GAS CORP | AN EXPLOSION AND FIRE OCCURRED AT 2819 GLENDEVON CIRCLE DUE TO THE FAILURE OF A 1" PE FITTING (PE GAS TUBING TEE). THE LEAK WAS CAUSED BY THIRD PARTY DAMAGE. SPECIFICALLY, ONE OR MORE EXCAVATORS CREATED AT LEAST ONE EXCAVATION BELOW SOUTHWEST'S PE GAS T | 175
46 | 2004-08-21 | PA | leaks and spills | UNKNOWN (CLEARFIELD COUNTY ) | NATIONAL FUEL GAS DISTRIBUTION CORP - NEW YORK | AT 8:45 AM ON AUGUST 21,2004, AN EXPLOSION OCCURRED AT 48 WOODLAND LANE IN SANDY TOWNSHIP NEAR BUBOIS, PENNSYLVANIA. FIRE FOLLOWED THE EXPLOSION, WHICH CONSUMED MUCH OF THE EXPLOSION DEBRIS THAT REMAINED IN AND AROUND THE HOUSE FOUNDATION. MR. AND MRS, | 0
47 | 2004-08-19 | CA | other | UNKNOWN (LOS ANGELES COUNTY ) | SOUTHERN CALIFORNIA GAS CO | ELECTRIC TRANSFORMER FAILED, ENERGIZING WATER LINE THAT ARCED ONTO GAS MAIN, CREATING HOLE THAT ALLOWED WATER TO ENTER GAS MAIN, CAUSING SIGNIFICANT CUSTOMER OUTAGES. NOTE: INCIDENT BECAME REPORTABLE AT APPROXIMATELY 10:30 ON 8/20/04 WHEN FURTHER WATE | 0
48 | 2004-08-21 | PA | natural disasters | UNKNOWN (PA COUNTY ) | EQUITABLE RESOURCES (A.K.A EQUITABLE GAS CO) | A 16" STEEL GAS MAIN PULLED OUT OF A 16" STEEL COUPLER. | 0
49 | 2004-09-02 | WA | maintenance | UNKNOWN (KING COUNTY ) | PUGET SOUND ENERGY | A PSE EMPLOYEE WAS PERFORMING A PRELIMINARY LEAK INVESTIGATION IN RESPONSE TO A GAS ODOR CALL. AS HE WAS WORKING NEAR THE HOUSE WHERE THE ODOR CALL ORIGINATED, THE HOUSE NEXT DOOR EXPLODED AND BURNED. THE SOLE RESIDENT WAS BURNED, REQUIRING HOSPITALIZAT | 344
50 | 2004-09-01 | CT | other | UNKNOWN (FAIRFIELD COUNTY ) | YANKEE GAS SERVICES CO | ON WED., 9/1/04 AT 1442 THE YANKEE GAS DISPATCHER RECEIVED A CALL FROM THE NORWALK FIRE DEPT. THERE WAS AN ODOR OF GAS AT THE GAS METERS IN THE BASEMENT. DISPATCH WAS INFORMED THAT THE FIRE DEPT HAD PUT OUT A STRUCTURE FIRE ABOUT AN HOUR PRIOR TO THE CA | 0
51 | 2004-06-23 | UT | other | UNKNOWN (SALT LAKE COUNTY ) | QUESTAR GAS COMPANY | A PLUMBING COMPANY WAS PERFORMING MAINTENANCE ON A LEAKING WATER SERVICE LINE. THE PLUMBING COMPANY CALLED THE ONE CALL SYSTEM. THE LINE WAS ACCURATELY LOCATED. THE PLUBMING COMPANY EXCAVATED THE HOLE TO REPAIR THE WATER LINE. THE WATER LEAK WAS LOCA | 50
52 | 2004-08-28 | WA | other | UNKNOWN (KING COUNTY ) | PUGET SOUND ENERGY | PLUMBER WORKING FOR PRIVATE PARTY WAS PREPARING TO SOLDER A COPPER JOINT IN A WATER SERVICE. ONE-CALL HAD CORRECTLY LOCATED A NEARBY 5/8" POLYETHYLENE GAS SERVICE AND IT HAD BEEN SAFELY EXPOSED. THE PLUMBER FAILED TO USE A HEAT SHIELD TO PROTECT THE PE | 0
53 | 2004-09-09 | CA | other | UNKNOWN (KERN COUNTY ) | SOUTHERN CALIFORNIA GAS CO | VEHICLE BEING CHASED ON HIGHWAY LOST CONTROL, FLIPPED NUMEROUS TIMES, EJECTING PASSENGERS. VEHICLE CAME TO REST ON PRIMARY REGULATION OF METER SET ASSEMBLY, APPROXIMATELY 50' FROM ROADWAY. FIVE FATALITIES, NONE RELATED TO RELEASE OF GAS. | 500
54 | 2004-09-22 | LA | sabotage | UNKNOWN (TERREBONNE COUNTY ) | SOUTH COAST GAS CO INC | THOMPSON CONSTRUCTION HIT OUR LINE WORKING FOR SCHLUMBER. IN DOING CONSTRUCTION THEY HIT THE WATER LINE. WHILE HELPING THE WATER DISTRICT REPAIR THEIR LINE THEY HIT THE GAS LINE. | 333
55 | 2004-08-27 | NM | leaks and spills | UNKNOWN (LEA COUNTY ) | ZIA NATURAL GAS CO |  | 3387
56 | 2004-08-23 | IL | other | UNKNOWN (COOK COUNTY ) | PEOPLES GAS LIGHT & COKE CO | ON MONDAY, AUGUST 23, 2004, A TWO_MAN DISTRIBUTION DEPARTMENT CREW WAS ASSIGNED TO RENEW AN 1-1/2" STEEL CATHODICALLY PROTECTED SERVICE PIPE (INSTALLED IN 1965) WITH 5/8" POLYETHYLENE PLASTIC. DURING THE SERVICE PIPE RENEWAL PROCESS ONE OF THE TWO CREW M | 0
57 | 2004-08-29 | PA | other | UNKNOWN (WESTMORELAND COUNTY ) | DOMINION PEOPLES | ON AUGUST 29, 2004 AT 10:37 PM, DOMINION PEOPLES RECEIVED A REPORT FROM 911 THAT A VEHICLE HAD COLLIDED INTO OUR REGULATOR STATION FACILITY LS-3414 LOCATED AT ARONA ROAD, IRWIN, WESTMORELAND COUNTY, PA. DOMINION PEOPLES PERSONNEL ARRIVED AT THE SCENE, FO | 10
58 | 2004-08-14 | LA | sabotage | UNKNOWN (nan COUNTY ) | SOUTH COAST GAS CO INC |  | 247
59 | 2004-08-20 | LA | sabotage | UNKNOWN (LAFOURCHE COUNTY ) | SOUTH COAST GAS CO INC |  | 0
60 | 2004-06-14 | UT | other | UNKNOWN (SALT LAKE COUNTY ) | QUESTAR GAS COMPANY | VEHICLE WAS SOUTHBOUND ON 700 EAST. VEHICLE RAN OFF ROAD TO THE RIGHTSIDE AT ABOUT 4700 SOUTH AND 700 EAST. VEHICLE RAN OVER VEGETATION, STOP SIGN AND APARTMENT SIGN. VEHICLE CONTINUED OFF ROAD SOUTHBOUND UNTIL IT HIT A FOUR-METER HEADER ATTACHED TO TH | 200
61 | 2004-07-23 | LA | sabotage | UNKNOWN (ASSUMPTION COUNTY ) | PIERRE PART NATURAL GAS INC |  | 367
62 | 2004-07-14 | NM | sabotage | UNKNOWN (SANTA FE COUNTY ) | PUBLIC SERVICE COMPANY OF NEW MEXICO - GAS SVCS | SUPPLEMENTAL: HORIZON UTILITIES AND EXCAVATING HIT A CAPPED GAS STUB THAT THEN CAUSED A RELEASE OF GAS RESULTING IN DAMAGE TO A NEARBY MOBILE HOME. DAMAGE TO PRIVATE PROPERTY/MOBILE HOME AND CONTENTS IS REVISED TO AN ESTIMATED VALUE OF $35,000. NO PH | 312
63 | 2004-08-08 | AK | other | UNKNOWN (nan COUNTY ) | ENSTAR NATURAL GAS CO | ON SUNDAY AFTERNOON, AUGUST 8, 2004 AT APPROXIMATELY 12:56 PM ADT, ENSTAR NATURAL GAS COMPANY WAS NOTIFIED OF A STRUCTURE FIRE AT LOT 15, BLOCK 2 SKYLINE ESTATES (TWILIGHT DRIVE) WASILLA, ALASKA. AN ENSTAR SERVICEMAN WAS DISPATCHED TO THE SCENE. UPON AR | 10
64 | 2004-08-14 | VA | sabotage | UNKNOWN (PRINCE WILLIAM COUNTY ) | WASHINGTON GAS LIGHT CO | CONTRACTOR PRK DRILLING & BLASTING, WERE BLASTING IN PREPARATION OF SEWER MAIN INSTALLATION IN THE VICINITY OF WASHINGTON GAS FACILITIES WHICH CAUSED THE 12" PLASTIC GAS MAIN TO BE SEVERED BY THE EXPLOSION. THIS CAUSED A LOSS OF GAS SERVICE TO APPROXIMAT | 29600
65 | 2004-07-31 | IL | other | UNKNOWN (COOK COUNTY ) | NORTHERN ILLINOIS GAS CO | STRUCTURE FIRE CAUSED THE ROOF AND THE CUSTOMER FUEL LINE TO COLLAPSE WHICH THEN DAMAGED THE GAS METER WHICH WAS LOCATED INSIDE THE STURCTURE. | 0
66 | 2004-08-09 | MD | other | UNKNOWN (MONTGOMERY COUNTY ) | WASHINGTON GAS LIGHT CO | THE NATURAL GAS METER WAS DAMAGED BY A FIRE THAT STARTED IN A SINGLE FAMILY RESIDENCE. THE ROCKVILLE CITY FIRE DEPARTMENT THAT THE PRIMARY CAUSE OF THE FIRE WAS FLAMMABLE MATERIAL STORED NEAR THE WATER HEATER. IGNITION FROM THE WATER HEATER CAUSED THE F | 35
67 | 2004-09-18 | PA | natural disasters | UNKNOWN (ALLEGHENY COUNTY ) | EQUITABLE RESOURCES (A.K.A EQUITABLE GAS CO) | AN 12" STEEL GAS MAIN FAILED AS A RESULT OF HEAVY RAINS. PIPELINE SECTION IS PHYSICALLY SEPARATED AND ABANDONED. | 0
68 | 2004-09-21 | PA | sabotage | UNKNOWN (BERKS COUNTY ) | PPL GAS UTILITIES CORP | TOWNSHIP WAS GRADING DIRT ROADWAY AND SHOULDER WITH A FRONT END LOADER. THE PIPELINE IN THE SHOULDER OF THE ROAD WAS STRUCK AND PUNCTURED. LEAK SITE WAS SECURED, AND GAS ALLOWED TO VENT WHILE A TEMPORARY BYPASS INSTALLED TO MAINTAIN GAS SERVICE WHILE RE | 69283
69 | 2004-06-05 | NY | other | UNKNOWN (nan COUNTY ) | CONSOLIDATED EDISON CO OF NEW YORK | THIS IS THE FOLLOW UP TO THE VERBAL REPORT OF AN INCIDENT ON JUNE 5, 2004 AT 23:45 HOURS HOURS AT 52-15 VAN DAM STREET IN QUEENS, NEW YORK. COMPANY PERSONNEL RESPONED TO A NEW YORK CITY FIRE DEPARTMENT REPORT OF A BUILDING FIRE IN PROGRESS WITH GAS INVOL | 0
70 | 2004-09-21 | PA | natural disasters | UNKNOWN (ALLEGHENY COUNTY ) | COLUMBIA GAS OF PENNSYLVANIA | IN ALLEGHENY COUNTY, CRECENT TOWNSHIP AN 8-INCH CROSS COUNTRY LINE KNOWN AS D-74 IN THE AREA OF RIVERVIEW ROAD, THERE WAS A LANDSLIDE WHICH CAUSED A SEPARATION OF A COMPRESSION COUPLING ON A HILLSIDE. IT WAS A TWO WAY FEED AND COULD BE ISOLATED BY A VALV | 390000
71 | 2004-09-18 | PA | natural disasters | UNKNOWN (ALLEGHENY COUNTY ) | DOMINION PEOPLES | ON SEPTEMBER 18, 2004, DOMINION PEOPLES DISCOVERED A BROKEN GAS PIPELINE (#P-1163) CAUSED BY A MUDSLIDE FROM EARTH MOVEMENT DUE TO HEAVY RAINS ON SEPTEMBER 17, 2004. DOMINION PEOPLES PERSONNEL ARRIVED AT THE SCENE, ASSESSED AND MONITORED THE SITUATION & | 3000
72 | 2004-09-21 | PA | natural disasters | UNKNOWN (ALLEGHENY COUNTY ) | DOMINION PEOPLES | ON SEPTEMBER 21, 2004, DOMINION PEOPLES DISCOVERED AN 8" BROKEN GAS PIPELINE CAUSED BY A LANDSLIDE FROM EARTH MOVEMENT DUE TO HEAVY RAINS ON SEPTEMBER 17, 2004. DOMINION PEOPLES PERSONNEL ARRIVED AT THE SCENE ASSESSED AND MONITORED THE SITUATION AND DISC | 21276
73 | 2004-10-14 | AK | other | UNKNOWN (nan COUNTY ) | ENSTAR NATURAL GAS CO | ON THURSDAY EVENING, OCTOBER 14, 2004 AT APPROXIMATELY 8:34PM ADT, ENSTAR NATURAL GAS COMPANY WAS NOTIFIED OF A STRUCTURE FIRE AT LOT 11, BLOCK 2 FREEMAN ANTHONY SUBDIVISION (6825 W BLONDELL DR) WASILLA, ALASKA. AN ENSTAR SERVICEMAN WAS DISPATCHED TO THE | 10
74 | 2004-09-16 | CA | other | UNKNOWN (ORANGE COUNTY ) | SOUTHERN CALIFORNIA GAS CO | ELDERLY WOMAN INVOLVED IN AUTO ACCIDENT WITH ANOTHER VECHICLE LOST CONTROL, LEFT ROAD AND CAME TO REST ON TOP OF METERSET ASSEMBLY. DAMAGE TO METER SET RESULTED IN ESCAPING GAS WHICH DID NOT CONTRIBUTE TO DRIVER'S INJURIES. | 0
75 | 2004-07-08 | LA | sabotage | UNKNOWN (TERREBONNE COUNTY ) | SOUTH COAST GAS CO INC |  | 396
76 | 2004-07-15 | LA | sabotage | UNKNOWN (LAFOURCHE COUNTY ) | SOUTH COAST GAS CO INC |  | 187
77 | 2004-09-26 | IL | other | UNKNOWN (DEKALB COUNTY ) | NORTHERN ILLINOIS GAS CO | SUPPLEMENTAL REPORT SUBMITTED WITH THE 3 PROPERTY DAMAGE SUBCATEGORIES SUMMING UP TO THE TOTAL VALUE. ***************************************************************************** MULCH/LANDSCAPING FIRE DAMAGED THE METER SET THUS CAUSING A RELEASE OF | 0
78 | 2004-09-20 | MD | other | UNKNOWN (BALTIMORE COUNTY ) | BALTIMORE GAS & ELECTRIC CO | ACCORDING TO BATTALLION CHIEF MARK EWERS AND FIRE INVESTIGATOR #4 FOR THE BALTIMORE COUNTY FIRE DEPARTMENT, THE POINT OF FIRE ORIGINATED AT THE SOFFIT REAR OF BUILDING FROM THE SERVICE CABLES AFTER THE ELECTRICAL METER BOXES. THE HEAT AND/OR FIRE CAUSED | 0
79 | 2004-08-16 | VA | sabotage | UNKNOWN (LOUDOUN COUNTY ) | WASHINGTON GAS LIGHT CO | THE TOWN OF LEESBURG WAS PERFORMING MAINTENANCE ON A SEWER LINE WHEN THEY RUPTURED A 2" GAS MAIN. WHILE MOVING THE BACKHOE AFTER RUPTURING THE PLASTIC GAS LINE, THE LINE IGNITED CAUSING DAMAGE TO A DUMP TRUCK AND A BACKHOE. THE FIRE DEPARTMENT WAS ON TH | 331
80 | 2004-09-14 | NY | technical failure | UNKNOWN (SARATOGA COUNTY ) | NIAGARA MOHAWK POWER CORP | OPERATING GAS CREW INCORRECTLY DISASSEMBLED MAIN VALVE WHILE IN SERVICE TO SUCH POINT WHERE THE VALVE CORE WAS EJECTED BY THE PRESSURE OUT OF THE HOUSING. BLOWING GAS FROM THE HOUSING EVENTUALLY IGNITED, SOURCE UNKNOWN. | 13467
81 | 2004-09-25 | WV | sabotage | UNKNOWN (PUTNAM COUNTY ) | UNION OIL & GAS INC | ADELPHIA CABLE USING WALK BEHIND TRENCHER CUT INTO 2 INCH NATURAL GAS PIPELINE. PIPELINE WAS MARKED AND GAS COMPANY INVESTIGATION DETERMINES INCIDENT DUE TO ADELPHIA OPERATOR ERROR. | 0
82 | 2003-07-15 | MN | sabotage | UNKNOWN (nan COUNTY ) | CENTENNIAL UTILITIES | EXCAVATION CONTRACTOR WAS WORKING AT THE ADJACENT ADDRESS TO THE ONE CALLED IN FOR LOCATES. | 75
83 | 2003-08-21 | MN | sabotage | UNKNOWN (ANOKA COUNTY ) | CENTENNIAL UTILITIES | THE 4" LINE THAT WAS HIT MADE A HUGE CHANGE IN DEPTH BETWEEN THE POTHOLES ON EITHER SIDE OF EXCAVATION. THIS LINE WAS REPLACED AS PART OF THE ROAD REPLACEMENT PROJECT THAT WAS ONGOING. | 500
84 | 2004-05-10 | MN | other | UNKNOWN (HENNEPIN COUNTY ) | CENTERPOINT ENERGY MINNEGASCO | HOMEOWNER DISCONNECTED GAS CONNECTION TO WATER HEATER DRIP LEG, PLUGGED WATER HEATER VENT WITH RAGS, ALLOWING GAS TO FILL THE HOUSE AND IGNITE WITH A CIGARETTE LIGHTER. HOUSE EXPLODED SERIOUSLY INJURING HOME OWNER. | 0
85 | 2004-07-13 | MI | sabotage | UNKNOWN (WAYNE COUNTY ) | DTE ENERGY - MICHCON | RELEASE AND IGNITION OF NATURAL GAS FROM SERVICE LINE. MISS DIG WAS CALLED AND SITE WAS STAKED ACCURATELY. CONTRACTOR FAILED TO HAND EXPOSE NATURAL GAS FACILITY PRIOR TO USING POWER EQUIPMENT. THIS INCIDENT WAS CAUSED BY A CONTRACTOR WHEN THEY RUPTURED | 0
86 | 2004-10-07 | KS | other | UNKNOWN (JOHNSON COUNTY ) | KANSAS GAS SERVICE | A DELIVERY TRUCK BACKED INTO THE METER SETTING AND CRACKED THE METER AROUND THE METER SPUD. APPARENTLY NATURAL GAS WAS DRAWN INTO THE BUILDING THROUGH A VENT AT THE SIDE OF THE BUILDING WHICH WAS APPARENTLY IGNITED BY SOME UNDETERMINED SOURCE LOCATED INS | 0
87 | 2004-09-17 | TX | sabotage | UNKNOWN (HARRIS COUNTY ) | CENTERPOINT ENERGY | CENTERPOINT ENERGY CONTRACTOR DAMAGED A 4" H.P. STEEL MAIN WITH A BORING TOOL WHILE INSTALLING A NEW GAS MAIN. | 27295
88 | 2004-10-11 | SD | other | UNKNOWN (nan COUNTY ) | MONTANA - DAKOTA UTILITIES CO | FIRE OF UNKNOWN ORIGIN IN BASEMENT OF STORAGE AREA OF BUILDING SPREAD TO VICINITY OF METER SET, DESTROYING METER SET. GAS TO METER SET WAS TURNED OFF OUTSIDE OF BUILDING. FIRE DEPARTMENT DETERMINED THAT NATURAL GAS WAS NOT SOURCE OF FIRE. DAMAGE TO MET | 200
89 | 2004-10-05 | AL | leaks and spills | UNKNOWN (MARSHALL COUNTY ) | MARSHALL COUNTY GAS DISTRICT |  | 0
90 | 2004-10-21 | LA | sabotage | UNKNOWN (ASSUMPTION COUNTY ) | PIERRE PART NATURAL GAS INC |  | 125
91 | 2004-10-11 | WI | other | UNKNOWN (WASHINGTON COUNTY ) | WISCONSIN GAS CO | ON THE MORNING OF OCTOBER 11, 2004, COMPANY'S CONTRACTOR CREW (ARBY CONSTRUCTION) PROCEEDED TO INSTALL A 6X6X6 TEE IN AN EXISTING 35#, 6", PE DISTRIBUTION MAIN. A 1&1/4" BY-PASS WAS CONSTRUCTED AROUND THE PROPOSED TEE CUT IN LOCATION TO AVOID CUSTOMER OU | 10000
92 | 2004-10-12 | NJ | sabotage | UNKNOWN (MIDDLESEX COUNTY ) | PUBLIC SERVICE ELECTRIC & GAS CO | AT 1500 HOURS ON TUESDAY, OCTOBER 12, 2004,A PSE&G SERVICE TECHNICIAN CALLED IN TO THE COMPANY TO REPORT THAT WHILE HE WAS WORKING AT A CUSTOMER'S HOME ON PROSPECT STREET, EDISON ON A SERVICE CALL, A NEIGHBOR INFORMED HIM THAT THERE WAS A SMELL OF NATURAL | 5000
93 | 2004-10-23 | MD | natural disasters | UNKNOWN (BALTIMORE COUNTY ) | BALTIMORE GAS & ELECTRIC CO | AT 11:15 ON 10/23/04, B/C/F/D CALLED TO REPORT A FURNACE EXPLOSION AT 4247 CARDWELL AVE. BGE'S FIRST RESPONDER ARRIVED TO FIND A LARGE WATER LEAK FROM AN APPARENT WATER MAIN BREAK AT THE INTERSECTION OF BELAIR RD & CARDWELL AVE. FOUND WATER IN CUSTOMER'S | 0
94 | 2004-11-02 | OH | other | UNKNOWN (HAMILTON COUNTY ) | CINCINNATI GAS & ELECTRIC CO | ATTEMPTIMG TO COMMIT SUICIDE, AN INDIVIDUAL USED A SAW TO CUT THROUGH THE OUTLET METER SWIVEL PIPING WHICH CAUSED GAS TO ESCAPE INSIDE A SINGLE FAMILY RESIDENCE RESULTING IN AN EXPLOSION. THERE WAS NO FIRE OR PERSONAL INJURY RESULTING FROM THE EXPLOSION. | 0
95 | 2004-10-20 | IL | sabotage | UNKNOWN (DUPAGE COUNTY ) | NORTHERN ILLINOIS GAS CO | THIRD PARTY CONTRACTOR WAS CONDUCTING DIRECTIONAL DRILLING OPERATIONS AND STRUCK A 4-INCH GAS LINE. GAS MIGRATED INTO THE STRUCTURE. EXPLOSION OCCURRED. | 4650
96 | 2004-10-30 | NM | other | UNKNOWN (DONA ANA COUNTY ) | PUBLIC SERVICE COMPANY OF NEW MEXICO | ACCORDING TO THE DONA ANA COUNTY SHERIFF'S DEPARTMENT REPORT, ON OCTOBER 30, 2004, MARIO DELGADO, DRIVING A 2005 SUZUKI MOTORCYCLE, APPROACHED A CURVE AT OR AROUND 201 S ALVAREZ ST AND FAILED TO MAINTAIN HIS LANE OF TRAFFIC. MR. DELGADO LEFT THE ROADWAY | 0
97 | 2004-11-01 | AR | sabotage | UNKNOWN (PULASKI COUNTY ) | CENTERPOINT ENERGY ARKLA | CONTRACTOR DAMAGED 4"STL MAIN WHILE BORING UNDER SHACKLEFORD RD TO INSTALL FIBER. THE COST ESTIMATE FOR PUBLIC/PRIVATE DAMAGE WAS ESTIMATED AT $40000 TO INCLUDE THE REPLACEMENT OF THE TRAFFIC SIGNAL AND PAVING REPAIR. | 15752
98 | 2004-10-23 | VA | other | UNKNOWN (LOUDON COUNTY ) | WASHINGTON GAS LIGHT CO | DURING THE PROCESS OF REPLACING A WATER METER A TYLER MECHANCIAL EMPLOYEE WAS SOLDERING A COPPER WATER LINE WITH AN ACETYLENE TORCH. THE WORK WAS DONE IN THE AREA OF AN EXPOSED 2" - 55 PSI PLASTIC GAS SERVICE LINE IN AN OPEN EXCAVATION. THE METER AND RE | 78
99 | 2004-11-01 | IA | technical failure | UNKNOWN (MONTGOMERY COUNTY ) | MIDAMERICAN ENERGY COMPANY | GAS SERVICE TO MINSA CORPORATION WAS TURNED OFF AT THE METER SET AT THE CUSTOMER'S REQUEST SO THE CUSTOMER COULD WELD ON THE CUSTOMER'S PIPING. MINSA CORPORATION CALLED BACK BECAUSE GAS WAS LEAKING THROUGH. THE SERVICEMAN SHUTOFF THE OUTLET VALVE OF THE | 0
100 | 2004-11-08 | OK | sabotage | UNKNOWN (ROGERS COUNTY ) | OKLAHOMA NATURAL GAS COMPANY | CONTRACTOR WORKING FOR DEVELOPER STRUCK ONG'S 4-INCH HIGH PRESSURE NATURAL GAS MAIN WITH A BACKHOE WHILE EXCAVATING FOR A SEWER LINE. THE EXCAVATOR DID NOT HAVE A LINE LOCATE REQUEST. THE BACKHOE RIPPED A 14"X4" GASH IN THE MAIN. THE SYSTEM HAD A TWO-W | 94000
101 | 2004-11-15 | AZ | other | UNKNOWN (SANTA CRUZ COUNTY ) | UNISOURCE ENERGY SERVICES | A VEHICLE HIT A SINGLE METER LOOP AS WELL AS A PHONE AND ELECTRIC METER PEDESTAL. THE BREAK OCCURRED AT THE METER BAR WHERE THE REGULATOR AND METER VALVE WAS STILL INTACT. THE ARCING ELECTRIC METER PEDESTAL IGNITED THE GAS, RESULTING IN DAMAGE TO VEHICL | 88
102 | 2004-11-29 | IN | sabotage | UNKNOWN (DEARBORN COUNTY ) | LAWRENCEBURG GAS COMPANY | THE HIGHWAY CONTRACTOR WAS WORKING ON A ROAD PROJECT THAT HAS BEEN ONGOING FOR SEVERAL MONTHS. ONE-CALL LOCATES WERE PROPERLY MADE AT MANY DIFFERENT TIMES FOR THIS CONTRACTOR. IN THIS PARTICULAR AREA, CONTRACTOR WAS IN PROCESS OF DOING LIME STABLIZATION | 24850
103 | 2004-09-28 | CO | sabotage | UNKNOWN (nan COUNTY ) | PUBLIC SERVICE CO OF COLORADO | ROAD EXCAVATION WORK HIT OLD BONNETED VALVE WHICH TORE PIPE CAUSING RUPTURE. | 54627
104 | 2004-11-19 | LA | sabotage | UNKNOWN (LAFOURCHE COUNTY ) | SOUTH COAST GAS CO |  | 337
105 | 2004-11-05 | TX | leaks and spills | UNKNOWN (BEXAR COUNTY ) | CITY PUBLIC SERVICE | GAS IGNITION OCCURRED WHEN THE CUSTOMER AT 4911 SWANN LANE FLIPPED A LIGHT SWITCH IN BATHROOM. AFTER INVESTIGATION, IT IS BELIEVED THAT THE SOURCE OF GAS ORIGINATED FROM A CRACKED POLYETHYLENE BUTT FUSION THAT MIGRATED UNDERGROUND TO THE HOUSE AND UNDER | 0
106 | 2004-12-03 | LA | sabotage | UNKNOWN (LAFOURCHE COUNTY ) | SOUTH COAST GAS CO |  | 911
107 | 2004-11-27 | MN | natural disasters | UNKNOWN (GOODHUE COUNTY ) | NORTHERN STATES POWER COMPANY DBA XCEL ENERGY | EARTH SETTLED UNDER STEEL-PE TRANSITION FITTING CAUSING LEAK IN PLASTIC SIDE OF COMPONENT. GAS MIGRATED ALONG THE SERVICE INTO THE HOUSE AND WAS IGNITED WHEN THE RENTER LIVING AT THE RESIDENCE LIT A LIGHTHER IN THE UTILITY ROOM. | 0
108 | 2004-11-16 | KY | sabotage | UNKNOWN (nan COUNTY ) | BURKESVILLE GAS COMPANY INC |  | 0
109 | 2004-10-26 | CA | leaks and spills | UNKNOWN (YOLO COUNTY ) | PACIFIC GAS & ELECTRIC COMPANY | THE ROOT CAUSE OF THIS INCIDENT WAS THAT A LEAK ON A 4-INCH DIAMETER PLASTIC MAIN AT A PREVIOUS SQUEEZE POINT MIGRATED TO THE RESIDENCE AND IGNITED. THE SOURCE OF IGNITION HAS NOT BEEN DETERMINED. THE GAS LEAK WAS CAUSED BY A PLASTIC PIPE SLOW CRACK GRO | 1000
110 | 2004-11-29 | MD | other | UNKNOWN (PRINCE GEORGES COUNTY ) | WASHINGTON GAS | THE FIRE LOCATION, A RESTAURANT, AT 9128-30 BALTIMORE AVENUE IN COLLEGE PARK , MARYLAND CAUGHT FIRE AS A RESULT OF SUSPECTED ARSON. UPON ARRIVAL OF WASHINGTON GAS PERSONNEL, THE FIRE WAS BURNING AT THE BUILDING WHERE THE GAS SERVICE (METER BUILD-UP)WAS L | 521
111 | 2004-12-04 | KS | maintenance | UNKNOWN (SEDGWICK COUNTY ) | KANSAS GAS SERVICE | AN INVESTIGATION REVEALED NATURAL GAS WAS ESCAPING FROM A MAIN AND APPARENTLY MIGRATED TO A NEARBY STRUCTURE WHERE IGNITION OCCURRED. | 0
112 | 2004-12-10 | CA | sabotage | UNKNOWN (YOLO COUNTY ) | PACIFIC GAS & ELECTRIC COMPANY | ON DECEMBER 10, 2004, A FOUR-INCH DIAMETER GAS DISTRIBUTION MAIN WAS STRUCK AND DAMAGED BY A THIRD PARTY EXCAVATOR, WHO WAS INSTALLING SANITARY SEWER MAIN, BY THE JACK AND BORE METHOD. THIS RESULTED IN A GAS LEAK. THE GAS MAIN IN QUESTION, WAS LOCATED A | 11100
113 | 2004-12-24 | AK | other | UNKNOWN (nan COUNTY ) | ENSTAR NATURAL GAS COMPANY | ON FRIDAY EVENING, DECEMBER 24, 2004 AT APPROXIMATELY 9:37 PM AST, ENSTAR NATURAL GAS COMPANY WAS NOTIFIED OF A STRUCTURE FIRE AT LOT 25, BLOCK 2 TURNAGAIN VIEW SUBDIVISION (2710 CUTWATER CIRCLE) ANCHORAGE, ALASKA. AN ENSTAR SERVICEMAN WAS DISPATCHED TO | 10
114 | 2004-12-07 | MN | other | UNKNOWN (DOUGLAS COUNTY ) | CENTERPOINT ENERGY | THE DAMAGE TO THE DISTRIBUTION SYSTEM THAT LEAD TO THE RUPTURE WAS NOT REPORTED TO CENTERPOINT ENERGY MINNESOTA GAS. THERE WERE EXCAVATORS WORKING FOR THE CITY OF ALEXANDRIA PERFORMING SEWER AND WATER CONSTRUCTION DURING THE DURING AND SUMMER OF 2004 NEAR | 0
115 | 2004-12-24 | PA | other | UNKNOWN (CAMBRIA COUNTY ) | DOMINION PEOPLES | ON DECEMBER 24, 2004 AT 4:20AM, DOMINION PEOPLES RECEIVED A REPORT FROM 911 THAT A VEHICLE HAD COLLIDED INTO A HOUSE AND CUSTOMER METER FACILITY LOCATED AT 106 FORREST HILLS DRIVE, JOHNSTOWN, ADAMS TOWNSHIP, CAMBRIA COUNTY, PA. DOMINION PEOPLES PERSONNEL | 0
116 | 2004-12-20 | PA | natural disasters | UNKNOWN (WASHINGTON COUNTY ) | COLUMBIA GAS OF PENNSYLVANIA INC | IN WASHINGTON COUNTY, FALLOWFIELD TOWNSHIP A 12-INCH LINE KNOWN AS D-7237 IN THE AREA OF FIFTH STREET AND KINDER AVE THERE WAS GROUND MOVEMENT, WHICH CAUSED A SEPARATION OF A COMPRESSION COUPLING ON A HILLSIDE. IT WAS A TWO WAY FEED AND COULD BE ISOLATED | 45000
117 | 2004-12-17 | IL | other | UNKNOWN (COOK COUNTY ) | NICOR GAS | AN UNKNOWN FLAMMABLE VAPOR INSIDE THE HOME CAUSED THE EXPLOSION. AS A RESULT OF THE IMPACT, THE NICOR GAS METERING FACILITIES, WHICH WERE LOCATED OUTDOORS, WERE DAMAGED THUS CAUSING A RELEASE OF NATURAL GAS WHICH WAS A SECONDARY FEED TO THE FIRE. NOTE: | 400
118 | 2004-12-09 | VA | other | UNKNOWN (FAIRFAX COUNTY ) | WASHINGTON GAS | THE CAUSE OF INCIDENT HAS BEEN DETERMINED TO BE ACCIDENTAL NATURE BY THE FAIRFAX COUNTY FIRE INVESTIGATIONS UNIT AND WAS CONTRIBUTED TO AN ELECTRICAL PROBLEM AT THE HOUSE PANEL. THE WASHINGTON GAS METER AND REGULATOR WERE DAMAGED DO TO HEAT EXPOSURE FROM | 0
119 | 2004-11-14 | KS | other | UNKNOWN (nan COUNTY ) | KANSAS GAS SERVICE | AN UNIDENTIFIED VEHICLE STRUCK THE METER SETTING DAMAGING THE METER SETTING AND CUSTOMER'S PIPING, THEN LEFT THE SCENE. APPARENTLY NATURAL GAS WAS IGNITED BY SOME UNDETERMINED SOURCE LOCATED INSIDE THE BUILDING. 7/27/2006 SUPPLEMENTAL REPORT CHANGED | 200
120 | 2004-12-21 | PA | sabotage | UNKNOWN (JEFFERSON COUNTY ) | NATIONAL FUEL GAS DISTRIBUTION CORPORATION | CONTRACTOR INSTALLING SEWER SYSTEM HIT AND SEVERED 3" PLASTIC 50 PSIG DISTRIBUTION MAIN WHICH NFG LOCATED WITHIN TOLERANCE. 609 CUSTOMERS LOST SERVICE AS A RESULT. | 250
121 | 2005-01-07 | NH | sabotage | UNKNOWN (ROCKINGHAM COUNTY ) | NORTHERN UTILITIES INC | WHILE GRINDING PAVEMENT/TRENCH FOR SEWER EXCAVATION, GRADING MACHINE HIT 6" PE IP GAS MAIN CAUSING IGNITION OF ESCAPING GAS AND ENVELOPING GRADING MACHINE. OPERATOR JUMPED TO ESCAPE INJURY. | 17400
122 | 2004-12-23 | CA | other | UNKNOWN (MONTEREY COUNTY ) | PACIFIC GAS & ELECTRIC COMPANY | CAR STRUCK AN ELECTRIC POLE IN SEASIDE, CA @ 0853 CAUSING ELECTRIC OUTAGE. PG&E EMPLOYEES ATTEMPTED SWITCHING OPERATIONS AT THE SEASIDE SUBSTATION TO RESTORE POWER. A SWITCHING EQUIPMENT FAILURE CAUSED A GROUND FAULT TO APPLY ABNORMAL VOLTAGE TO THE GAS | 0
123 | 2004-12-08 | LA | sabotage | UNKNOWN (LAFOURCHE COUNTY ) | SOUTH COAST GAS CO |  | 543
124 | 2004-12-17 | WA | sabotage | UNKNOWN (SPOKANE COUNTY ) | AVISTA UTILITIES | ON DECEMBER 17TH 2004 AT APPROXIMATELY 3:35 PM PST, A RAILROAD CONTRACTOR DUG INTO AVISTA'S 8-INCH HIGH PRESSURE DISTRIBUTION FEEDER NEAR SULLIVAN ROAD AT THE UNION PACIFIC RAILROAD OVER CROSSING (RAILROAD TRACKS RUN UNDERNEATH), NORTH OF THE SPOKANE RIVE | 65337
125 | 2004-11-12 | MO | other | UNKNOWN (GREENE COUNTY ) | SPRINGFIELD, MO MUNICIPAL GAS SYSTEM | CITY UTILITIES FILED A GAS INCIDENT REPORT WITH THE MISSOURI PUBLIC SERVICE COMMISION ON 12/08/04. SINCE THAT TIME, CITY UTILITIES RECEIVED NEW DAMAGE ESTIMATES FROM THE PROPERTY OWNER AT 1870 E PAGE. THE TOTAL ESTIMATED REPAIR COST IS $114,970.00. CIT | 0
126 | 2004-12-31 | OH | other | UNKNOWN (CLARK COUNTY ) | COLUMBIA GAS OF OHIO INC | THE CUSTOMER'S SERVICE LINE FAILED THE COH PRESSURE TEST, DROPPING FROM LINE PRESSURE TO ZERO IN APPROXIMATELY 3-4 SECONDS. COH EXCAVATED THE SERVICE LINE AND DISCOVERED LARGE ROCKS AND GRAVEL SURROUNDING IT IN THE TRENCH. CRACKS IN THE LINE WERE OBSERV | 0
127 | 2005-01-01 | AZ | leaks and spills | UNKNOWN (MARICOPA COUNTY ) | SOUTHWEST GAS CORPORATION | EXPLOSION AND FIRE AT COMMERICAL LAUNDRY COMPLEX LOCATED IN A STRIP MAILL AT 3918 N/W GRAND AVE. TWELVE APARTMENTS ON 39TH AVE/HAZLEWOOD AND SIX UNITS IN THE STRIP MALL WERE EVACUATED AFFECTING NINE PERSONS. THE CAUSE OF THE LEAK WAS DETERMINED TO BE DU | 5000
128 | 2004-11-18 | WI | sabotage | UNKNOWN (ST CROIX COUNTY ) | MIDWEST NATURAL GAS INC | EARTHMOVING EQUIPMENT OPERATED BY HOFFMAN CONSTRUCTION CO HIT AND SEVERED A 3 INCH PLASTIC MAIN (MEDIUM DENSITY PE) WITH AN MAOP OF 60 PSIG (OPERATING AT ABOUT 50 PSIG). THE GAS BEING RELEASED IGNITED WITHOUT DAMAGE TO THE EQUIPMENT OR OPERATOR (THE MACH | 230
129 | 2005-01-06 | IN | natural disasters | UNKNOWN (HAMILTON COUNTY ) | INDIANA GAS COMPANY INC | AFTER HEAVY RAINS, AN ICE LADEN TREE UPROOTED AND THE TREE ROOT BALL LIFTED METER SET BREAKING THE INLET TO THE METER BAR AND CAUSING A LEAK AT THE INLET TO THE RISER VALVE. ESCAPING GAS IGNITED CAUSING DAMAGE TO RESIDENTIAL STRUCTURE. IGNITION SOURCE U | 0
130 | 2005-01-19 | NE | other | UNKNOWN (DOUGLAS COUNTY ) | METROPOLITAN UTILITIES DISTRICT | THE HOUSE FIRE WAS STARTED FROM FUMES FROM THE FINISH PAINTERS WHOSE 5 GAL BUCKET OF LACQUER WAS IGNITED BY A HALOGEN LAMP. THE STRUCTURE CAUGHT FIRE AND THE HOUSE WAS ENGULFED BY FIRE. BETWEEN THE COLLAPSE OF THE STRUCTURE AND FIRE THE GAS SERVICE RISE | 0
131 | 2005-01-14 | IL | other | UNKNOWN (COOK COUNTY ) | NICOR GAS | A VEHICLE HIT THE GAS METER SET, CAUSING THE METER TO BE SHEARED OFF AT THE RISER THUS CAUSING A RELEASE OF NATURAL GAS. DRIVER OF THE VEHICLE LEFT THE SCENE PRIOR TO ARRIVAL OF EMERGENCY RESPONSE PERSONNEL. NO INJURIES REPORTED. | 867
132 | 2004-12-23 | IN | natural disasters | UNKNOWN (MARION COUNTY ) | CITIZENS GAS & COKE UTILITY | FROST AND THAW CYCLE IS BELIEVED TO BE MAJOR CONTRIBUTING FACTOR TO THE FAILURE OF STEEL-TO-PLASTIC COMPRESSION TRANSITION FITTING FOR 1/2" HIGH DENSITY PLASTIC SERVICE. THE DEEP FROST CAP ALLOWED GAS TO MIGRATE FROM THE FAILURE THROUGH THE CASING PIPE T | 0
133 | 2004-12-28 | MN | natural disasters | UNKNOWN (ANOKA COUNTY ) | CENTERPOINT ENERGY RESOURCES CORP DBA CENTERPOINT ENERGY MINNESOTA GAS | ANALYSIS OF THE FAILED PIPING INDICATES A DRESSER STYLE 90 COUPLER WAS USED TO JOIN THE ONE INCH IPS, DRISCOPIPE M7000 PE 3408 SERVICE LINE. THE ONE INCH PE ON THE OUTLET SIDE OF THE DRESSER COUPLING WAS FOUND TO HAVE INSUFFICIENT PENETRATION TO PROVIDE | 0
134 | 2005-01-14 | CA | sabotage | UNKNOWN (KERN COUNTY ) | PACIFIC GAS & ELECTRIC COMPANY | CONTRACTOR WAS EXCAVATING 24 FOOT DEEP TRENCH TO INSTALL SEWER MAIN, AND HAD EXPOSED THE 4" PG&E PLASTIC GAS LINE, BUT DURING THE INSTALLATION OF A TRENCH SHORING BOX THE EXCAVATOR CAUSED A PORTION OF THE ASPHALT TO BREAK AND FALL INTO THE EXCAVATION. TH | 3000
135 | 2004-09-22 | MT | sabotage | UNKNOWN (nan COUNTY ) | NORTHWESTERN ENERGY | A CONTRACTOR, FOR THE CITY, REPLACING WATER MAINS, HIT AN UN-MARKED STEEL SERVICE. LOCATES WERE CALLED INTO THE ONE CALL SYSTEM, AND OTHER MAINS AND SERVICES WERE MARKED. THE HIT SERVICE PULLED APART AT A MECHANICAL COUPLING. THE LEAKING GAS MIGRATED A | 0
136 | 2005-02-22 | TX | sabotage | UNKNOWN (TARRENT COUNTY ) | COSERV GAS | 2" LP GAS MAIN WAS DAMAGED BY EXCAVATOR INSTALLING WATER LINES. LP GAS TANKS WERE SHUT OFF TO ELIMINATE THE ESCAPING GAS. RESULTS OF DAMAGE CAUSED AN OUTAGE OF 50 CUSTOMERS. REPAIRES WERE MADE AND SERVICE RESTORED. | 0
137 | 2005-01-25 | IL | other | UNKNOWN (COOK COUNTY ) | NICOR GAS | THE METER SET (REGULATOR AND METER) MELTED AS A RESULT OF A HOUSE FIRE. CAUSE OF THE FIRE IS UNKNOWN. | 3237
138 | 2005-01-17 | TX | sabotage | UNKNOWN (HARRIS COUNTY ) | CENTERPOINT ENERGY | THIRD PARTY DAMAGED A 2" I.P. STEEL MAIN WITH A BACKHOE AND THE ESCAPING GAS WAS IGNITED. * ADDRESS WAS CORRECTED FROM 2615 CASON ST. TO 2612 WERLEIN ST. | 1513
139 | 2004-05-18 | TX | other | UNKNOWN (GALVESTON COUNTY ) | CENTERPOINT ENERGY | TREE LIMB FELL ON AND DAMAGED SERVICE REGULATOR WHILE THIRD PARTY WAS TRIMMING TREE. RESULTING IN LINE PRESSURE DOWNSTREAM. IGNITION OCCURRED INSIDE AND HOME OWNER WAS INJURED AND HOSPITALIZED. 4-25-05 ADDITIONAL RELEVANT INFORMATION - HOME OWNER PASSED | 0
140 | 2005-02-02 | NJ | other | UNKNOWN (CAMDEN COUNTY ) | SOUTH JERSEY GAS COMPANY | BASED ON THE CONCLUSION FOUND IN THE CAMDEN COUNTY FIRE MARSHALL REPORT (SEE ATTACHED) WE BELIEVE THE SHUT OFF VALVE WAS DEFECTIVE AND THAT THE MOST LIKELY IGNITION SOURCE COULD HAVE BEEN THE STANDING PILOT ON THE PORTABLE NATURAL GAS APPLIANCE WHICH WAS | 0
141 | 2005-01-27 | NJ | natural disasters | UNKNOWN (SALEM COUNTY ) | SOUTH JERSEY GAS COMPANY | AN UNDERWATER 6" PIPELINE CROSSING OF THE SALEM RIVER CONSTRUCTED IN 1955 FAILED IN SERVICE ON 1/27/05 DUE TO SCOURING OF PROTECTIVE COVER AND SUPPORT OF THE PIPELINE ACROSS THE CHANNEL BOTTOM. THIS LOCATION IS SUBJECT TO STRONG TIDAL CURRENTS RESULTING | 10000
142 | 2005-02-04 | IL | other | UNKNOWN (MCHENRY COUNTY ) | NICOR GAS | HOUSE FIRE CAUSED THE METER SET (REGULATOR AND METER) TO MELT THUS CAUSING THE RELEASE OF GAS. | 5687
143 | 2005-01-30 | NJ | other | UNKNOWN (UNION COUNTY ) | ELIZABETHTOWN GAS COMPANY | ON JANUARY 30, 2005 ELIZABETHTOWN GAS RESPONDED TO A CALL RECEIVED AT 3:39 AM FROM THE UNION TOWNSHIP POLICE DEPARTMENT. UPON ARRIVAL AT 3:48 AM COMPANY EMPLOYEES FOUND THE FIRE DEPARTMENT PUTTING OUT FIRES AT #744 AND #748 LEHIGH AVE, UNION NJ. COMPANY | 100
144 | 2005-02-08 | LA | sabotage | UNKNOWN (LAFOURCHE COUNTY ) | SOUTH COAST GAS CO |  | 177
145 | 2005-02-18 | LA | sabotage | UNKNOWN (LAFOURCHE COUNTY ) | SOUTH COAST GAS CO |  | 868
146 | 2005-02-07 | PA | sabotage | UNKNOWN (BUCKS COUNTY ) | PEO ENERGY COMPANY | A CONSTRUCTION COMPANY WAS EXCAVATING WITH A TRACK HOE TO INSTALL A WATER LINE FOR THE LOCAL SEWER AND WATER AUTHORITY WHEN THEY CONTACTED THE 3/4" STEEL GAS SERVICE WHICH FED 52 FERRY ST. WHEN THE TRACK HOE CAME IN CONTACT WITH THE GAS SERVICE, THE SERVI | 0
147 | 2005-02-08 | PA | maintenance | UNKNOWN (nan COUNTY ) | PECO ENERGY COMPANY | A 6 INCH STEEL MAIN ON THE HULMEVILLE ROAD BRIDGE OVER THE PENNSYLVANIA TURNPIKE HAD A SECTION FAILURE. THE GAS MAIN INCIDENT CAUSED THE SHUTDOWN OF THE PENNSYLVANIA TURNPIKE AND EVACUATION OF AREA RESIDENTS. | 39500
148 | 2005-02-08 | MI | other | UNKNOWN (EATON COUNTY ) | CONSUMERS ENERGY | ON FEBRUARY 8, 2005, A RESIDENT AT 3930 HARTFORD RD, LANSING, MICHIGAN, WAVERLY PARK APARTMENTS DROVE HIS VEHICLE INTO THE FRONT OF A 35 UNIT APARTMENT BUILDING SEVERING THE ABOVE GROUND SERVICE VALVE AND DIRECTING THE FLOW OF GAS INTO TO THE BUILDING. T | 3415
149 | 2005-02-09 | IN | leaks and spills | UNKNOWN (nan COUNTY ) | NORTHERN INDIANA PUBLIC SERVICE COMPANY | ON FEBRUARY 9, 2005 NIPSCO'S CENTRAL OPERATIONS RECEIVED A CALL FROM THE JASFER COUNTY SHERIFF'S DEPARTMENT REPORTING A HOUSE EXPLOSION AND FIRE AT THE ABOVE ADDRESS. UPON ARRIVAL OF NIPSCO PERSONNEL, IT WAS DISCOVERED THAT GAS WAS ESCAPING FORM AND UNDE | 56
150 | 2005-02-24 | TN | technical failure | UNKNOWN (COFFEE COUNTY ) | ELK RIVER PUBLIC UTILITY DISTRICT | EMPLOYEE WHILE IN THE PROCESS OF ABANDONING AN OLD 3/4" STEEL SERVICE WAS INVOLVED IN AN INCIDENT. AN IGNITION OCCURED IGNITING THE NATURAL GAS IN THE BELL HOLE. | 20
151 | 2005-02-06 | CA | natural disasters | UNKNOWN (EL DORADO COUNTY ) | AVISTA UTILITIES | AT APPROXIMATELY 09:30 A NATURAL GAS EXPLOSION OCCURRED AT THE ABOVE ADDRESS. THE LAKE VALLEY FIRE DEPARTMENT RESPONDED AND CONTACTED AVISTA UTILITIES AT 09:53. THE FIRE PERSONNEL SHUT OFF THE GAS AT THE SERVICE LOCKCOCK AT 10:30. AVISTA PERSONNEL ARRIVED | 1000
152 | 2005-02-02 | MA | natural disasters | UNKNOWN (SUFFOLK COUNTY ) | BOSTON GAS COMPANY DBA KEYSPAN ENERGY DELIVERY NEW ENGLAND | COLD TEMPERATURE WITH FROST CAUSED A BREAK IN THE NATURAL GAS MAIN. | 0
153 | 2005-02-23 | IN | other | UNKNOWN (MARION COUNTY ) | CITIZENS GAS & COKE UTILITY | ON FEBRUARY 23RD, 2005, AT APPROXIMATELY 1:56 PM, CITIZENS GAS & COKE UTILITY RECEIVED A CALL FROM WARREN TOWNSHIP FIRE DEPARTMENT INFORMING US OF A GAS METER THAT HAD BEEN STRUCK BY A VEHICLE AND RESULTED IN A FIRE. AT APPROXIMATELY 2:05 P.M., CITIZEN G | 220
154 | 2005-02-27 | IL | other | UNKNOWN (COOK COUNTY ) | NICOR GAS | METER SET LOCATED IN UTILITY/LAUDRY ROOM MELTED AS A RESULT OF THE INTENSE HEAT OF THE FIRE. CAUSE OF FIRE WAS DUE TO ELECTRICAL SHORT. | 100
155 | 2005-02-23 | NJ | other | UNKNOWN (HUNTERDON COUNTY ) | ELIZABETHTOWN GAS COMPANY | DISPATCH RECEIVED CALL FROM HUNTERDON COUNTY COMMUNICATIONS AT 17:23. RESPONDER ARRIVED AT 17:43. LAMBERTVILLE FIRE DEPT CLOSED CURB VALVE AT APPROXIMATELY 18:00. BASEMENT FIRE HAD BEEN EXTINGUISHED. METER WAS NOT IN PLACE. NOTE: FIRE INVESTIGATOR DI | 0
156 | 2005-03-03 | CT | other | UNKNOWN (nan COUNTY ) | YANKEE GAS SERVICES COMPANY | A TRACTOR TRAILER HAD CRASHED INTO A BUILDING LOCATED AT 39-41 MAPLE AVE AND THERE WAS DAMAGE TO OUR FACILITIES. ON THURSDAY MARCH 3, 2005 AT 12:40, A YANKEE GAS DISPATCHER RECEIVED A CALL FROM THE ENFIELD FIRE DEPARTMENT A YANKEE GAS METER & SERVICE MEC | 149
157 | 2005-03-21 | NY | other | UNKNOWN (nan COUNTY ) | CONSOLIDATED EDISON COMPANY OF NEW YORK INC | THIS IS THE FOLLOW-UP TO THE VERBAL REPORT OF AN INCIDENT ON MARCH 21, 2005 07:52 HOURS AT 938 EAST 163RD STREET IN BRONX, NEW YORK. COMPANY FORCES RESPONDED TO A REPORT (FROM THE NYPD) OF A POSSIBLE GAS EXPLOSION INSIDE A SUPERMARKET AND FOUND THE FDNY | 0
158 | 2005-03-27 | IL | other | UNKNOWN (WILL COUNTY ) | NICOR GAS | STRUCTURE FIRE AT A VACANT FARM HOUSE. PART OF THE WALL FELL ONTO THE METER SET, DAMAGING IT AND CAUSING A RELEASE OF NATURAL GAS. INCIDENT WAS ORIGINALLY REPORTED AT 17040 OAK AVENUE. ACTUAL ADDRESS IS 17024 OAK AVENUE. | 3020
159 | 2005-02-15 | LA | sabotage | UNKNOWN (TERREBONNE COUNTY ) | SOUTH COAST GAS CO |  | 72
160 | 2005-03-23 | PA | other | UNKNOWN (MONROE COUNTY ) | PPL GAS UTILITIES CORPORATION | A CAR LOST CONTROL ON BLUE VALLEY DRIVE (S R 512) AS ROAD CONDITIONS BEGAN TO DETERIORATE DURING A SNOWSTORM. THE VEHICLE SLID OFF THE ROAD AND RUPTURED A NATURAL GAS SERVICE. THE IMPACT RESULTED IN A FIRE THAT BURNED THE SIDE OF A HOUSE. | 1882
161 | 2005-04-01 | TX | sabotage | UNKNOWN (MEDINA COUNTY ) | CITY OF LYTLE | IRBY CONTRACTOR FOR CITY PUBLIC SERVICE RUPTURE 3" DISTRIBUTION GAS MAIN THAT SERVICE THE CITY OF LYTLE. SYSTEM WAS SHUT DOWN FOR REMOVAL OF BACK BUCKET AND REPAIR OF MAIN. HAVING THE CITY OF LYTLE WITHOUT GAS SERVICE. | 0
162 | 2005-03-16 | PA | sabotage | UNKNOWN (ALLEGHENY COUNTY ) | COLUMBIA GAS OF PENNSYLVANIA INC | CONTRACTOR INSTALLING CABLE IN ALLEGHENY COUNTY USING A DIRECTIONAL BORE MACHINE, HIT A 50 PSIG 2" PLASTIC NATURAL GAS MAIN CAUSING LEAKAGE. THE NATURAL GAS MIGRATED TO NEARBY RESIDENTS, 107 BERTLEY RIDGE DRIVE, WHICH IS APPROXIMATELY 50 FEET AWAY FROM T | 440
163 | 2005-03-30 | LA | sabotage | UNKNOWN (ASSUMPTION COUNTY ) | PIERRE PART NATURAL GAS COMPANY |  | 315
164 | 2005-04-12 | NC | other | UNKNOWN (GASTON COUNTY ) | PUBLIC SERVICE OF NORTH CAROLINA INCORPORATED (DBA PSNC ENERGY) | VEHICLE WAS TRAVELING WEST ON WILKINSON BLVD. OCCUPANT LOST CONTROL OF VEHICLE STRIKING POWER POLE AND 1" RELIEF VALVE AT STATION #RS01118 AT THE INTERSECTION OF CHURCH AND WILKINSON BLVD. VEHICLE CAME TO REST ON TOP OF RELIEF VALVE WITH NOSE OF VEHICLE | 2200
165 | 2005-03-23 | IL | maintenance | UNKNOWN (nan COUNTY ) | THE PEOPLES GAS LIGHT AND COKE COMPANY | ON MARCH 23, 2005, SOMETIME BEFORE 7:04 PM, A FIRE OCCURRED AT A BOILER LOCATED IN THE BASEMENT OF 7117 S EUCLID STREET, CHICAGO. ILLINOIS, A 24-UNIT APARTMENT BUILDING. AT APPROXIMATELY 7:04 PM, THE FIRE DEPARTMENT (CFD) NOTIFIED PEOPLES GAS OF A FIRE/E | 0
166 | 2005-04-06 | MA | other | UNKNOWN (SUFFOLK COUNTY ) | BOSTON GAS COMPANY DBA KEYSPAN ENERGY DELIVERY NEW ENGLAND |  | 0
167 | 2005-04-15 | AZ | other | UNKNOWN (PIMA COUNTY ) | SOUTHWEST GAS CORPORATION | A TWO VEHICLE CAR ACCIDENT RESULTED IN THE METER SET ASSEMBLY AT THIS ADDRESS BEING HIT. FACILITY DAMAGE WAS ISOLATED TO METER SET ASSEMBLY RESULTING IN AN OUTAGE OF ONE CUSTOMER. TWO FIREFIGHTERS REQUIRED HOSPITALIZATION AS A RESULT OF INHALATION OF BO | 10
168 | 2005-01-10 | MD | other | UNKNOWN (MONTGOMERY COUNTY ) | WASHINGTON GAS LIGHT | MONTGOMERY COUNTY FIRE AND RESCUE RECEIVED AN ALARM FOR AN ELECTRIC CLOTHES DRYER ON FIRE AT 17610 LONGVIEW LANE IN THE OLNEY MARYLAND AREA. UPON THE FIRE DEPARTMENT'S ARRIVAL, THEY FOUND THE ENTIRE HOUSE ENGULFED, INCLUDING THE REAR BUILDING WALL ON THE | 0
169 | 2005-03-29 | VA | sabotage | UNKNOWN (nan COUNTY ) | WASHINGTON GAS | LINEAL INDUSTRIES CO WAS INSTALLING FIBER-OPTIC LINES USING A DIRECTIONAL DRILL MACHINE. WHILE ATTEMPTING TO PULL THE LINES THE DRILL HEAD DAMAGED A 4" PLASTIC MAIN. THE HOLE WAS 14' 10" LONG ON THE UNDERSIDE OF THE MAIN. THIS SYSTEM WAS A ONE WAY FEED | 1913
170 | 2005-03-28 | MD | other | UNKNOWN (nan COUNTY ) | WASHINGTON GAS | INCIDENT UPDATE: PER THE REPORT OF INVESTIGATION COMPLETED BY LT. DALE EDNOCK, IT WAS CONCLUDED THAT THE CAUSE OF THE EXPLOSION AND ENSUING HOUSE FIRE WAS A NATURAL GAS LEAK. ALTHOUGH THE CAUSE OF THE EXPLOSION/FIRE IS NATURAL GAS, THE EXACT CAUSE FOR | 0
171 | 2005-04-16 | UT | natural disasters | UNKNOWN (IRON COUNTY ) | QUESTAR GAS COMPANY | EXCESSIVE SNOW LOAD AGAINST THE METER CREATED A "GLACIER" EFFECT (I.E. WHERE THE SNOW MELTS AND FREEZES, MELTS AND FREEZES). DUE TO EXCESSIVE STRESS AGAINST THE SERVICE LINE RISER, THE THREADS, JUST BELOW THE SERVICE REGULATOR, CRACKED. THE LEAKING GAS | 50
172 | 2005-04-15 | LA | other | UNKNOWN (nan COUNTY ) | SOUTH COAST GAS CO |  | 238
173 | 2005-04-18 | IL | other | UNKNOWN (COOK COUNTY ) | NICOR GAS | FIRE AT MULTIPLE STRUCTURES. METER SET RISER TO 5807 ROOSEVELT ROAD MELTED AS A RESULT OF THE STRUCTURE FIRE. | 1054
174 | 2005-04-18 | IL | other | UNKNOWN (OGLE COUNTY ) | NICOR GAS | VEHICLE ACCIDENT BETWEEN SEMI AND FARM TRACTOR. SEMI LEFT THE ROAD AND STRUCK THE 1ST STAGE REGULATOR, SHEARING OFF A PIPE NIPPLE ON THE DOWNSTREAM SIDE OF THE REGULATOR. THE 2 REPORTED INJURIES WERE A RESULT OF THE VEHICLE ACCIDENT. | 350
175 | 2005-04-09 | TX | other | UNKNOWN (ANGELINA COUNTY ) | CENTERPOINT ENERGY | VEHICLE RAN INTO THE METER INSTALLATION, DAMAGED THE SERVICE REGULATOR, CAUSING THE PRESSURE TO INCREASE ON THE HOUSELINE. | 150
176 | 2004-09-24 | TX | sabotage | UNKNOWN (DALLAS COUNTY ) | ATMOS ENERGY CORPORATION LONE STAR DIVISION | A THIRD PARTY EXCAVATOR DRILLING TO INSTALL ELECTRIC POLES DRILLED INTO A POLY GAS MAIN. | 42000
177 | 2005-03-11 | TX | other | UNKNOWN (DALLAS COUNTY ) | ATMOS ENERGY CORP MID-TEX DIVISION | A VEHICLE RAN OFF THE ROAD, OVER THE RISER, AND INTO THE RESIDENCE. THE ESCAPING GAS IGNITED AND CAUGHT THE VEHICLE AND HOUSE ON FIRE. | 0
178 | 2005-04-12 | MI | other | UNKNOWN (INGHAM COUNTY ) | CONSUMERS ENERGY COMPANY | THE FINAL INVESTIGATION DETERMINED THAT THE CAUSE OF THE INCIDENT WAS CARELESS SMOKING AROUND THE METER INSTALLATION. THE AREA SURROUNDING THE RISER LOCATION WAAS COVERED WITH DRY WOOD CHIPS AND IT APPEARS THAT SOMEONE THREW A LIT CIGARETTE BUTT ONTO THE | 100
179 | 2005-04-24 | CT | other | UNKNOWN (HARTFORD COUNTY ) | CONNECTICUT NATURAL GAS CORP | HOMEOWNER WAS PERFORMING MECHANICAL WORK ON OWNERS MOTORCYCLE. OWNER WAS IN THE BASEMENT COMPLETING THIS WORK. WHILE WORKING ON THE MOTORCYCLE THE MOTORCYLE TIPPED OVER SPILLING GASOLINE FROM ITS GAS TANK ONTO THE FLOOR OF THE BASEMENT. NEARBY WAS A KE | 20
180 | 2005-05-25 | AK | other | UNKNOWN (nan COUNTY ) | ENSTAR NATURAL GAS COMPANY | ENSTAR WAS NOTIFIED BY ANCHORAGE FIRE DEPARTMENT (AFD) OF A STRUCTURE FIRE AT 4521 PARSONS AVE, ANCHORAGE, AK AT 0507, ON 5/29/05. THE FIRE HAD BURNED THROUGHT ENSTAR'S HDPE RISER AND CAUSED A RELEASE OF NATURAL GAS. AFD CREWS PINCHED OFF THE RISER TO S | 50
181 | 2005-06-01 | AK | other | UNKNOWN (ANCHORAGE COUNTY ) | ENSTAR NATURAL GAS COMPANY | ENSTAR WAS NOTIFIED BY THE ANCHORAGE FIRE DEPARTMENT (AFD) OF A STRUCTURE FIRE AT 3324 AND 3230 ORION CIRCLE, ANCHORAGE, AK AT 0212, JUNE 1, 2005. ENSTAR CREWS RESPONDED TO FIND A 2-UNIT TOWNHOME FULLY ENGULFED IN FIRE. EACH UNIT WAS SERVED BY A SEPARAT | 100
182 | 2005-04-28 | PA | sabotage | UNKNOWN (ALLEGHENY COUNTY ) | DOMINION PEOPLES | ON APRIL 28, 2005, AT APPROXIMATELY 11:30 AM DOMINION PEOPLES RECEIVED A REPORT FROM 911 THAT A PIPELINE WAS HIT AND DAMAGED BY A CONTRACTOR BORING THE ROAD AT RT.8 AND SAXONBURG BOULEVARD, SHALER TOWNSHIP, ALLEGHENY COUNTY, PA. DOMINION PEOPLES PERSONNE | 2019
183 | 2005-05-23 | CO | sabotage | UNKNOWN (DOUGLAS COUNTY ) | PUBLIC SERVICE CO OF COLORADO | CONTRACTOR EXCAVATING IN AREA NOT LOCATED FOR PIPELINE. BACKHOE RUPTURED FOUR INCH PE GAS MAIN. BLOWING GAS IGNITED. FIRE DESTORYED BACKHOE. | 0
184 | 2005-05-18 | NJ | sabotage | UNKNOWN (BERGEN COUNTY ) | PUBLIC SERVICE ELECTRIC AND GAS | ON WEDNESDAY, MAY 18, 2005, AN EXTERMINATOR FROM HORIZON TERMITE AND PEST CONTROL CORPORATION WAS DRILLING HOLES FOR HOME TERMITE TREATMENT AT 80 W PROSPECT STREET IN WALDWICK, NEW JERSEY AND DRILLED INTO A 1/2" PS, 60 PSIG GAS SERVICE. THE TECHNICIAN IN | 0
185 | 2005-06-13 | AK | other | UNKNOWN (ANCHORAGE COUNTY ) | ENSTAR NATURAL GAS COMPANY | ENSTAR WAS NOTIFIED BY ANCHORAGE FIRE DEPARTMENT OF A STRUCTURE FIRE AT 4141 E. 66TH AVE AT 0153 ON JUNE 13, 2005. A SERVICEMAN AND CREW WERE DISPATCHED. THE STRUCTURE FIRE CAUSED ENSTAR'S HDPE RISER AND METER SET ASSEMBLEY TO LEAK GAS AND IGNITE. THE | 50
186 | 2005-06-06 | LA | sabotage | UNKNOWN (LAFOURCHE COUNTY ) | SOUTH COAST GAS CO |  | 898
187 | 2005-06-01 | CA | natural disasters | UNKNOWN (ORANGE COUNTY ) | SOUTHERN CALIFORNIA GAS COMPANY | ON JUNE 1, 2005 NUMEROUS GAS FACILITIES WERE DAMAGED WHEN A MAJOR LANDSLIDE OCCURRED IN THE CITY OF LAGUNA BEACH. A NUMBER OF HOMES SLIPPED OFF OF A HILLSIDE IN THE AREA OF FLAMINGO AND BLUEBIRD ROADS. GAS FACILITIES DAMAGED FROM THE LANDSLIDE INCLUDE 4 | 0
188 | 2005-06-05 | IL | natural disasters | UNKNOWN (MCHENRY COUNTY ) | NICOR GAS | LIGHTNING STRUCK THE HOUSE ON LOT 427 (9100 DURHAM DRIVE). HOUSE FIRE MELTED THE METER SET AND RISER, THUSE CAUSING A RELEASE OF GAS. FIRE DAMAGE ALSO SUSTAINED BY LOTS 425 AND 427. GAS FACILITIES HAD NOT YET BEEN INSTALLED AT LOT 425 AND LOT 426. | 600
189 | 2005-06-11 | CA | sabotage | UNKNOWN (SANTA BARBARA COUNTY ) | SOUTHERN CALIFORNIA GAS COMPANY | ON JUNE 11, 2005 AN 8" HIGH PRESSURE DISTRIBUTION SERVICE WAS DAMAGED BY CUSTOMER, CELITE CORPORATION. EMPLOYEE OF CELITE CORPORATION WAS GRADING FIRE ROAD WHEN HE STRUCK AND PUNCTURED THE SERVICE FOR CELITE CORPORATION, RESULTING IN ONE OUTAGE. INVESTI | 10000
190 | 2005-06-20 | LA | sabotage | UNKNOWN (LAFOURCHE COUNTY ) | SOUTH COAST GAS CO |  | 1170
191 | 2005-04-21 | TX | technical failure | UNKNOWN (HOUSTON COUNTY ) | CENTERPOINT ENERGY | GULF SOUTH PIPELINE LOST GAS SUPPLY TO THE CITY OF CROCKETT. FAILURE WAS DUE TO A CONTROL VALVE BEING LEFT IN THE CLOSED POSITION. | 0
192 | 2005-06-14 | CT | other | UNKNOWN (NEW HAVEN COUNTY ) | YANKEE GAS SERVICES | THE ONGOING STRUCTURE FIRE AT 49 EAST STREET CAUSED THE OUTSIDE METERSET ASSEMBLY (METER & REGULATOR) TO MELT RESULTING IN THE RELEASE OF NATURAL GAS AT A PRESSURE OF APPROXIMATELY 24 PSI. THE GAS IGNITED AND CONTRIBUTED TO THE EXISTING STRUCTURE FIRE UN | 335
193 | 2005-05-27 | AZ | leaks and spills | UNKNOWN (PIMA COUNTY ) | SOUTHWEST GAS | BRIEF DESCRIPTION AT 1552 HOURS ON MAY 27, 2005, SOUTHWEST GAS WAS NOTIFIED OF A FIRE AT 1841 SOUTH CAMPBELL AVENUE. UPON ARRIVAL AT 1614 HOURS, TWO APARTMENT UNITS WERE FOUND TO BE DAMAGED BY THE REPORTED FIRE. A LEAK INVESTIGATION WAS INITIATED AND | 0
194 | 2005-06-17 | MD | other | UNKNOWN (ANNE ARUNDEL COUNTY ) | BALTIMORE GAS & ELECTRIC COMPANY | ANNE ARUNDEL COUNTY FIRE INVESTIGATION BUREAU (FIB) OFFICER DOUG WILSON REPORTS THAT AN OUTSIDE FIRE IMPINGED ON THE GAS METER AND REGULATOR INSTALLATION CAUSING DAMAGE TO THE REGULATOR BODY, RELEASE AND THEN IGNITION OF NATURAL GAS. JUVENILES WERE WITNE | 0
195 | 2005-05-25 | MO | other | UNKNOWN (CLAY COUNTY ) | MISSOURI GAS ENERGY | AN OUT OF CONTROL VEHICLE, WHICH APPEARED TO BE TRAVELING AT A HIGH RATE OF SPEED, WENT THROUGH TWO FENCES, TRAVERSED A DITCH AND IMPACTED A REGULATOR STATION. A FOUR (4) INCH ELBOW WAS BROKEN OFF BELOW GROUND ON THE OUTLET SIDE OF THE REGULATOR STATION. | 2237
196 | 2005-03-24 | MD | other | UNKNOWN (PRINCE GEORGE'S COUNTY ) | WASHINGTON GAS | THE PRINCE GEORGES COUNTY FIRE DEPARTMENT'S INVESTIGATION IS UNDERWAY. THE METER WAS MISSING AT THE FIRE BOARDS ARRIVAL AS ADVISED. THE FIRE DEPARTMENT ALSO ADVISED THAT THEIR PERSONNEL TURNED THE GAS OFF AT THE HIGH PRESSURE STOPCOCK JUST INSIDE THE BU | 0
197 | 2005-06-16 | CT | leaks and spills | UNKNOWN (NEW HAVEN COUNTY ) | SOUTHERN CONNECTICUT GAS COMPANY | FROM F5-14 SHEAR FAILURE AT CONNECTION TO SERVICE TEE. THE INCIDENT OCCURRED WHEN A PLASTIC SERVICE FAILED AT THE CONNECTION TO A STEEL MAIN. THE PLASTIC PROTECTIVE SLEEVE APPARENTLY SLIPPED OUT OF POSITION DURING THE BACKFILLING OPERATION AND ALLOWED T | 0
198 | 2005-06-27 | TN | other | UNKNOWN (HAYWOOD COUNTY ) | BROWNSVILLE UTILITIES DEPARTMENT | ON JUNE 27, 2005 A 1995 PONYIAC GRAN AM CARRYING DONNA MANN (APPROX. AGE 60), TAYLOR KILLEN (AGE 10), AND KATIE LADEWELL (AGE 11) WAS TRAVELING NORTH ON STATE ROUTE 76. THE VEHICLE VEERED OFF THE WEST SIDE OF THE ROAD AND TRAVELED 165' ON THE SHOULDER OF | 700
199 | 2005-06-27 | IN | sabotage | UNKNOWN (VANDERBURGH COUNTY ) | SOUTHERN INDIANA GAS AND ELECTRIC COMPANY | EXCAVATOR WORKING ON ROADS PULLED A 1 1/4" STEEL SERVICE FROM A COMPRESSION COUPLING AT THE SERVICE TEE. GAS ESCAPING TO ATMOSPHERE WAS IGNITED BY AN UNDETERMINED IGNITION SOURCE. TWO INDIVIDUALS WERE BURNED. ONE OF THE INDIVIDUALS WAS ADMITTED TO THE | 0
200 | 2005-06-23 | OK | sabotage | UNKNOWN (HASKELL COUNTY ) | OKLAHOMA NATURAL GAS COMPANY | EXCAVATOR DAMAGED ONG'S 4 INCH HIGH PRESSURE DISTRIBUTION LINE THAT SERVES THE TOWN OF STIGLER, OKLAHOMA. 1623 ACCOUNTS WERE LOST DUE TO THIS INCIDENT. | 1989
201 | 2005-06-28 | TN | sabotage | UNKNOWN (nan COUNTY ) | MEMPHIS LIGHT GAS & WATER DIVISION | ON JUNE 28, 2005, STABILIZATION INC., WAS WORKING APPROXIMATELY 100' NORTH OF GEORGE R JAMES RD. ON REED HOOKER RD WHEN THEIR 55-250 PULVIMIXER PUNCTURED A 8" PE GAS LINE. THE RELEASE OF GAS WAS FOLLOWED BY IGNITION RESULTING IN DAMAGE TO THE PULVIMIXER | 2979
202 | 2005-06-28 | IL | technical failure | UNKNOWN (COOK COUNTY ) | NICOR GAS | EMPLOYEE WAS CONDUCTING A SCHEDULED ROUTINE LEAK REPAIR. WHILE IN THE PROCESS OF REMOVING THE TAP CONNECTION FROM THE MAIN TO THE SERVICE LINE, AN UNAPPROVED NON-INTRINSICALLY SAFE TOOL WAS USED TO REMOVE BOLTS FROM THE TEE CONNECTION, CAUSING IGNITION O | 0
203 | 2005-06-17 | WV | other | UNKNOWN (MCDOWELL COUNTY ) | WELCH GAS COOPERATIVE ASSOCIATION | STATEMENT BY RONNIE CLEMINS, OPERATIONS MANAGER OF WELCH GAS CO-OP, FIRE AT AMBULANCE AUTHORITY 6/17/05 - 1:10 PM WELCH CITY DISPATCHER CALLS FOR GAS TRUCK #3 OR #4 TO GO TO THE AMBULANCE AUTHORITY AT MAITLAND AND CUT GAS OFF. THE BUILDING WAS ON FIRE | 50
204 | 2005-06-06 | TX | sabotage | UNKNOWN (HARRIS COUNTY ) | CENTERPOINT ENERGY | THIRD PARTY DAMAGED A 12" H.P. STEEL MAIN WITH A BORING TOOL WHILE INSTALLING A WATER MAIN. | 6759
205 | 2005-07-05 | NM | other | UNKNOWN (DONA ANA COUNTY ) | PUBLIC SERVICE COMPANY OF NEW MEXICO | A MOTORIST LOST CONTROL OF THE VEHICLE THEY WERE DRIVING, WENT OFF THE ROADWAY AND ROLLED OVER STRIKING GAS METER SET WHICH RESULTED IN TEH DRIVER BEING HOSPITALIZED. SUPPLEMENTAL: NATURAL GAS WAS NOT THE CAUSE OF THE INJURY RESULTING IN HOSPITALIZAT | 100
206 | 2005-07-09 | IL | other | UNKNOWN (WILL COUNTY ) | NICOR GAS | PEOPLE CUTTING DOWN A TREE DROPPED A LARGE BRANCH ON AN OVERHEAD POWER LINE. THE POWER LINE FELL TO THE GROUND AND ARCED ONTO AN UNDERGROUND STEEL MAIN LOCATED UNDER THE POWER LINE. NATURAL GAS IGNITED. | 2500
207 | 2005-07-10 | IL | other | UNKNOWN (WILL COUNTY ) | NICOR GAS | MULCH FIRE DAMAGED THE REGULATOR AND METER CAUSING A RELEASE OF NATURAL GAS WHICH THEN FUELED THE ON-GOING FIRE. | 500
208 | 2005-07-02 | LA | sabotage | UNKNOWN (TERREBONNE COUNTY ) | SOUTH COAST GAS CO |  | 1293
209 | 2005-07-11 | MD | sabotage | UNKNOWN (nan COUNTY ) | BALTIMORE GAS AND ELECTRIC COMPANY | ON JULY 11, 2005 AT APPROXIMATELY 11:50 AM, A CONTRACTOR WORKING TO INSTALL A NEW 48 INCH SEWER LINE AT BELAIR RD. AND HAMILTON AVE. IN BALTIMORE CITY, STRUCK THE BGE 20" NATURAL GAS MAIN WITH A HIGHHOE TARMAC. THE STROKE PRODUCED A HOLE 10" BY 12" AND A | 65000
210 | 2005-01-27 | AZ | leaks and spills | UNKNOWN (MARICOPA COUNTY ) | SOUTHWEST GAS CORPORATION | PL# 2005-5601 ODOR COMPLAINT CALLED IN. CONSTRUCTION CREW RESPONDED, IDENTIFIED AND ISOLATED LEAK AREA AND SHUT DOWN A SEGMENT OF 4" MAIN. LEAK WAS DUE TO A CRACK ON 4" NORDSTROM LUBE VALVE. OUTAGE OF 11,017 CUSTOMERS CONTRIBUTED TO PROPERTY DAMAGE TOT | 0
211 | 2005-07-21 | NJ | other | UNKNOWN (CUMBERLAND COUNTY ) | SOUTH JERSEY GAS COMPANY | ON JANUARY 24, 1994, R&T CASTELLINI COMPANY, THE COMPANY'S QUALIFIED DISTRIBUTION CONTRACTOR FOR THE CUMBERLAND DIVISION, CONSTRUCTED A NEW 3/4" POLYETHYLENE RESIDENCIAL SERVICE LATERAL EXTENSION FOR A PROPERTY AT 708 SHAR LANE BOULEVARD, IN MILLVILLE, NE | 200
212 | 2005-07-19 | MN | sabotage | UNKNOWN (BETRAMI COUNTY ) | AQUILA | CONTRACTOR WAS EXCAVATING FOR INSTALLATION OF A SEWER LINE. THE 6" GAS MAIN AND A TELEPHONE CONDUIT WERE IN THE EXCAVATION. IN THE PROCESS OF EXPOSING AND SUPPORTING THE TELEPHONE CONDUIT THE CONTRACTOR PUNCTURED THE GAS MAIN. THE LINE HAD BEEN ACCURAT | 16859
213 | 2005-07-30 | WA | sabotage | UNKNOWN (PIERCE COUNTY ) | PUGET SOUND ENERGY | PSE RESPONDED TO A REPORT FROM THE CITY OF PUYALLUP FIRE DEPARTMENT OF A DAMAGED GAS MAIN. THE CONTRACTOR HAD PUNCTURED A 6" PE GAS MAIN WHILE EXCAVATING IN A STATE HIGHWAY. CITY OF PUYALLUP POLICE AND FIRE DEPARTMENTS CLOSED THE HIGHWAY. PSE DETERMINE | 43767
214 | 2005-07-07 | TX | maintenance | UNKNOWN (GALVESTON COUNTY ) | TEXAS GAS SERVICE COMPANY | THE REGULATORAND MONITOR PILOT LINES WERE FILLED WITH A FOREIGN LIQUID FROM THE GAS SUPPLY CAUSING THE REGULATOR AND MONITOR TO FAIL OPEN. THE 14" LINE EXPERIENCED A LEAK LOCATED AT A JOINT WELD FROM THE OVERPRESSURIZATION. TWO SECTIONS OF THE LINE, TOT | 5835
215 | 2005-07-26 | TX | other | UNKNOWN (YOUNG COUNTY ) | TEXAS GAS SERVICE | A FREIGHTLINER WAS PARKED ON THE SIDE OF THE ROADWAY IN THE 1300 BLK OF HWY 16 SOUTH ON TOP OF A HILL. THE UNATTENDED VEHICLE ROLLED SOUTH DOWN A HILL STRIKING A GAS RISER AND AN ELECTRICAL POLE. THE ESCAPING GAS IGNITED AND ENGULFED THE CAB OF THE TRUC | 4155
216 | 2005-07-22 | LA | sabotage | UNKNOWN (ASSUMPTION COUNTY ) | PIERRE PART NATURAL GAS CO. |  | 124
217 | 2005-09-01 | AK | other | UNKNOWN (nan COUNTY ) | ENSTAR NATURAL GAS COMPANY | ANCHORAGE FIRE DEPARTMENT CALLED ENSTAR NATURAL GAS TO REPORT A STRUCTURE FIRE AT 2621 LYVONA LANE, ANCHORAGE AK, AT 0054 ON 9/1/05. THE STRUCTURE FIRE CAUSED THE GAS METER, REGULATOR AND HDPE RISER TO MELT, CAUSING A RELEASE OF NATURAL GAS. ENSTAR RESP | 50
218 | 2005-08-03 | IL | other | UNKNOWN (JO DAVIES COUNTY ) | NICOR GAS | STRUCTURE FIRE AT THIS ADDRESS. METER SET WAS OFF AND LOCKED PRIOR TO STRUCTURE FIRE. RISER, REGULATOR AND METER WERE DAMAGED AS A RESULT OF THE FIRE, THUS CAUSING A RELEASE OF NATURAL GAS. | 500
219 | 2005-08-10 | IL | other | UNKNOWN (HENDERSON COUNTY ) | NICOR GAS | STRUCTURE FIRE ORIGINATED AT NEIGHBORING HOUSE AND SPREAD TO THIS (WS 1ST 3S CLAY)ADDRESS. THE METER SET WAS DAMAGED AS A RESULT OF THE INTENSE HEAT AND FLAMES THUS CAUSING A RELEASE OF NATURAL GAS. | 500
220 | 2005-08-25 | CO | sabotage | UNKNOWN (JEFFERSON COUNTY ) | COLORADO NATURAL GAS INC. | HOMEOWNDER BEGAN INSTALLING A RETAINING WALL THE PRIOR DAY OF THE EXPLOSION, 8-24-05 AT 13:00. HOMEOWNDER AND FRIEND WERE USING 1/2 INCH DIAMETER BY 3 FEET LONG REBAR TO ANCOR WALL TO GROUND. THE WALL ULTIMATELY CONSISTED OF 4 TIERS OF RAIL ROAD TIES. T | 180
221 | 2005-08-12 | WY | natural disasters | UNKNOWN (CAMPBELL COUNTY ) | KINDER MORGAN RETAIL | THERE WERE ADDITIONAL COSTS THAT WERE NOT INCLUDED WITH THE FIRST REPORT WHICH WAS LABLED "ORIGINAL" AND "FINAL". SEE SECTION 5C. A TORNADO HIT THE TOWN OF WRIGHT WY. (SPECIFICALLY THE COTTONWOOD MOBILE HOME PARK OF 112 HOMES) CAUSING DAMAGE TO THE G | 132
222 | 2005-08-06 | CT | other | UNKNOWN (NEW HAVEN COUNTY ) | YANKEE GAS SERVICES | THE ONGOING STRUCTURE FIRE AT 2104 NORTH BROAD STREET CAUSED THE 2 INCH OUTSIDE SERVICE RISER TO MELT RESULTING IN THE RELEASE OF NATURAL GAS AT A PRESSURE OF APPROXIMATELY 55 PSIG. THE GAS IGNITED AND CONTRIBUTED TO THE EXISTING STRUCTURE FIRE UNTIL THE | 335
223 | 2005-09-13 | NE | other | UNKNOWN (DOUGLAS COUNTY ) | METROPOLITAN UTILITIES DISTRICT | METROPOLITAN UTILITIES DISTRICT ID# 12390 SUPPLEMENTAL REPORT REPORT FROM: MICHAEL G. CONRAD, CLAIMS ADJUSTER ADDRESS OF INCIDENT: 7003 N. 113TH PLZ., LOT 494, OMAHA NE 68142 DATE/TIME OF INCIDENT: SEPTEMBER 13, 2005, 2140 HOURS NRC REPORT#: | 0
224 | 2005-08-02 | TN | sabotage | UNKNOWN (RUTHERFORD COUNTY ) | ATMOS ENERGY | ON AUGUST 2, 2005, ATMOS ENERGY CORPORTATION, IN MURFREESBORO, TENNESSEE EXPERIENCED A RUPTURE OF A TWO-INCH NATURAL GAS PIPELINE RESULTING IN IGNITION OF GAS HOSPITALIZATION OF ONE ATMOS EMPLOYEE. | 467
225 | 2005-08-27 | MI | other | UNKNOWN (KENT COUNTY ) | MICHIGAN CONSOLIDATED GAS COMPANY/DTE ENERGY | A CAR SPED THROUGH THE SOUTH PARKING LOT OF 2720 28TH STREET SE,, ACROSS LANDSCAPED AREA, AND STRUCK THE WEST SIDE OF THE BUILDING THE METER ASSEMBLY AT 2730 28TH STREET SE, COMING TO REST AGAINST THE WEST WALL OF THE BUILDING AND ATOP THE SERVICE LINE RI | 0
226 | 2005-08-26 | CA | sabotage | UNKNOWN (LOS ANGELES COUNTY ) | SOUTHERN CALIFORNIA GAS COMPANY | CPUC?DOT REPORTABLE INCIDENT 58TH & WEST J14, LANCASTER NARRATIVE ON AUGUST 26, 2005, A 2" PLASTIC MEDIUM PRESSURE MAIN WAS PUNCTURED BY A CONTRACTOR USING A BACKHOE TO EXCAVATE FOR UTILITY CONDUITS. THERE WAS A USA REQUEST FOR THIS AREA, AND FACI | 0
227 | 2005-09-15 | NC | other | UNKNOWN (NEW HANOVER COUNTY ) | PIEDMONT NATURAL GAS (DBA NCNG) | A PERSON DRIVING A CAR STRUCK A METER SET AND CAUSED A GAS LEAK IN THE PIPING ON THE 60 PSIG SIDE OF THE SERVICE REGULATOR. THE GAS IGNITED AND A FIRE RESULTED. THE TWELVE PEOPLE IN THE BUILDING EVACUATED AFTER THE INCIDENT OCCURRED AND THERE WERE NOT R | 200
228 | 2005-08-16 | GA | other | UNKNOWN (WHITEFIELD COUNTY ) | WATER LIGHT & SINKING FUN DBA DALTON UTILITIES | ON AUGUST 16, 2005, DALTON UTILITIES PERSONNEL WERE CALLED TO THE SCENE OF A FIRE AT THE COUNTRY INN'S & SUITES LOCATED AT 903 WEST BRIDGE RD. THE DALTON FIRE DEPARTMENT WAS IN TEH PROCESS OF EXTINGUISHING A FIRE NEAR THE GAS METER WHEN DALTON UTILITIES | 41
229 | 2005-08-22 | MO | sabotage | UNKNOWN (CASS COUNTY ) | MISSOURI GAS ENERGY | CONTRACTOR, CALLED TEAM EXCAVATING, WHILE DIGGING WITH A TRACK HOE TO INSTALL SEWER MAIN LINE HIT A GAS SERVICE LINE THAT WAS 1 1/4 INCH PE MATERIAL. THE SERVICE WAS CUT IN TWO AND GAS WAS BLOWING. THE OPERATOR LEFT HIS TRACK HOE IN PLACE AND WHILE CALL | 639
230 | 2005-09-20 | LA | sabotage | UNKNOWN (LAFOURCHE COUNTY ) | SOUTH COAST GAS |  | 449
231 | 2005-09-19 | LA | sabotage | UNKNOWN (LAFOURCHE COUNTY ) | SOUTH COAST GAS CO |  | 295
232 | 2005-09-22 | LA | sabotage | UNKNOWN (LAFOURCHE COUNTY ) | SOUTH COAST GAS CO |  | 756
233 | 2005-09-07 | MA | other | UNKNOWN (nan COUNTY ) | BOSTON GAS COMPANY DBA KEYSPAN ENERGY DELIVERY NEW ENGLAND | A KEYSPAN SERVICEMAN RESPONDING TO AN ODOR CALL FOUND FIRE DEPARTMENT AND POLICE DEPARTMENT PERSONNEL AT THE SCENE INVESTIGATING A SUSPECTED SUICIDE. THE POLICE REPORTEDLY FOUND GAS LEAKING FROM A DISCONNECTED CUSTOMER-OWNED PIPE. THE CASE OF DEATH IS B | 0
234 | 2005-09-07 | IL | other | UNKNOWN (DUPAGE COUNTY ) | NICOR GAS | STRUCTURE FIRE CAUSED WALL TO COLLAPSE ONTO METER SET THUS DAMAGING IT AND CAUSING A RELEASE OF GAS. HOUSE WAS UNDER RENOVATION. GAS HAD BEEN TURNED OFF AT THE METER SET PRIOR TO THE STRUCTURE FIRE. NOTE: THIS INCIDENT WAS REPORTED AS 29W560 POINT O | 500
235 | 2005-09-16 | OK | other | UNKNOWN (OKLAHOMA COUNTY ) | OKLAHOMA NATURAL GAS COMPANY | MOTORCYCLE DRIVER TRAVELING AT A HIGH RATE OF SPEED LOST CONTROL AND VEERED OFF THE ROAD INTO ONG'S DISTRICT REGULATOR STATION. THE DRIVER WAS DEAD AT THE SCENE. THE IMPACT BENT THE GUARD RAIL SURROUNDING THE DISTRICT REGULATOR STATION AND PUSHED THE GU | 15
236 | 2005-09-14 | CA | other | UNKNOWN (FRESNO COUNTY ) | PACIFIC GAS & ELECTRIC COMPANY | THE FIRE IS SUSPECTED TO HAVE STARTED AT UNIT 122, AND DUE TO THE WOOD SIDING AND SHAKE ROOFS, THE FIRE CARRIED OVER TO UNIT 123. BOTH STRUCTURES WERE APPROXIMATELY 15 FEET APART WITH THE GAS METER SETS LOCATED ON ADJACENT WALLS. THE GAS METER SET LOCAT | 200
237 | 2005-09-15 | MT | sabotage | UNKNOWN (PARK COUNTY ) | NORTHWESTERN ENERGY | 5/4/09 - THIS WILL BE THE FINAL REPORT FOR THIS INCIDENT. A THIRD PARTY CONTRACTOR THAT WAS EXCAVATING FOR A SEWER PROJECT FOR THE CITY OF LIVINGSTON DAMAGED A SERVICE LINE THAT CAUSED THE INCIDENT. THIS INCIDENT REPORT SHOULD NOW BE CONSIDERED CLOSED W | 0
238 | 2005-10-18 | IL | other | UNKNOWN (COOK COUNTY ) | NICOR GAS | A STRUCTURE FIRE AT THE RESIDENCE DESTROYED THE HOME AND ALSO MELTED THE METER SET WHICH WAS LOCATED IN THE BASEMENT. | 500
239 | 2005-10-13 | LA | sabotage | UNKNOWN (TERREBONNE COUNTY ) | SOUTH COAST GAS |  | 336
240 | 2005-10-20 | PA | technical failure | UNKNOWN (ALLEGHENY COUNTY ) | EQUITABLE GAS COMPANY | AN EQUITABLE GAS CREW WAS IN THE PROCESS OF PURGING A NEWLY INSTALLED 4" PLASTIC MAIN LINE BEFORE PLACING IT INTO SERVICE. AN EQUITABLE GAS EMPLOYEE WAS IN THE EXCAVATION MONITORING GAS FLOW AT TEH PURGE SITE, WHEN A FLASH FIRE OCCURRED. THE EQUITABLE G | 0
241 | 2005-10-10 | AL | other | UNKNOWN (JEFFERSON COUNTY ) | ALABAMA GAS CORPORATION | THERE HAVE BEEN PUBLIC REPORTS BY THE INVESTIGATING FIRE DEPARTMENT THAT THE SERVICE LINE RUPTURED BY EXTERNAL FORCES FROM FALLING DEBRIS AFTER RESIDENCE CAUGHT FIRE. | 0
242 | 2005-09-28 | LA | sabotage | UNKNOWN (LAFOURCHE COUNTY ) | SOUTH COAST GAS |  | 155
243 | 2005-10-12 | LA | sabotage | UNKNOWN (TERREBONNE COUNTY ) | SOUTH COAST GAS |  | 655
244 | 2005-08-29 | MD | other | UNKNOWN (PRINCE GEORGE'S COUNTY ) | WASHINGTON GAS | THE BOWIE FIRE DEPARTMENT RESPONDED TO A HOUSE FIRE. WASHINGTON GAS WAS NOTIFIED AT 6:38AM, AND ARRIVED AT 7:09AM TO FIND GAS OFF AND THE FIRE EXTINGUISHED. THE FIRE DEPARTMENT DETERMINED THAT THE FIRE WAS DUE TO A MALFUNCTION IN THE ELECTRICAL AIR COND | 100
245 | 2005-09-30 | LA | natural disasters | UNKNOWN (WASHINGTON COUNTY ) | WASHINGTON PARISH GAS UTILITY DISTRICT #2 | EMERGENCY RESPONDER DID NOT FOLLOW PROCEDURE AS DESCRIBED WITHIN OPERATIONS, MAINTENANCE & EMERGENCY MANUAL IN ACCORDANCE WITH 193.605(B)(9). RESPONDER WAS CALLED AT 8:30PM ON 9/30/2005 WITH REPORT OF GAS SMELL. HE WAS FOUND AT 12:00AM ON 10/1/05. THE | 0
246 | 2005-10-14 | IN | sabotage | UNKNOWN (JOHNSON COUNTY ) | INDIANA GAS COMPANY, INC. | THIRD PARTY CONTRACTOR PERFORMING ROADWORK FOR ROADWAY APPROACH TO SUBDIVISION DAMAGED A 6" PE MAIN. CONTRACTOR HAD PREVIOUSLY REMOVED 31" OF COVER PRIOR TO DAMAGING THE PIPE. OPERATOR OF MACHINERY WAS ADMITTED TO HOPSITAL FOR 2ND AND 3RD DEGREE BURNS T | 7000
247 | 2005-09-27 | NY | sabotage | UNKNOWN (NASSAU COUNTY ) | KEYSPAN ENERGY DELIVERY LONG ISLAND (KEYSPAN GAS EAST CORP, DBA) | ON SEPTEMBER 27, 2005, A THIRD PARTY CONTRACTOR DAMAGED A 2" 60# PLASTIC GAS MAIN WHILE TRENCHING ON THE NORTH SIDE OF JERICHO TURNPIKE IN NEW HYDE PARK, NY. THE MACHINE THAT HIT THE GAS MAIN WAS A SMALL MAN OPERATED TRENCHING MACHINE. NATURAL GAS ESCAP | 0
248 | 2005-10-10 | MD | sabotage | UNKNOWN (nan COUNTY ) | BALTIMORE GAS & ELECTRIC COMPANY | ON OCTOBER 10TH AT APPROXIMATELY 7:45 AM, A CONTRACTOR WORKING TO MAKE PROACTIVE REPAIRS TO OUT 16" NATURAL GAS MAIN PUNCTURED THE TOP OF THE MAIN WITH A HIGHHOE. THE STRIKE PRODUCED A HOLE APPROXIMATELY 9" BY 5" AND ALSO CAUSED THE MAIN TO CRACK ABOUT 3 | 0
249 | 2005-10-04 | MN | natural disasters | UNKNOWN (WASHINGTON COUNTY ) | NORTHERN STATES POWER COMPANY D/B/A XCEL ENERGY | ROCKING IMPINGING ON A 1-1/2" CENTURY PLASTIC MAIN CAUSED A BRITTLE CRACK FAILURE OF THE PIPE WALL. GAS LEAKED FROM THE FAILURE, MIGRATED TO THE BUILDING, AND WAS IGNITED BY AN UNKNOWN SOURCE OF IGNITION. | 0
250 | 2005-10-20 | TX | sabotage | UNKNOWN (WARD COUNTY ) | TEXAS GAS SERVICE COMPANY | 5" GAS MAIN HIT AND DAMAGED BY GRADER, REPLACED 27 FT. OF GAS MAIN. NO LINE LOCATES REQUESTED. | 56798
251 | 2005-08-30 | LA | sabotage | UNKNOWN (LAFOURCHE COUNTY ) | SOUTH COAST GAS CO |  | 375
252 | 2005-09-05 | LA | sabotage | UNKNOWN (LAFOURCHE COUNTY ) | SOUTH COAST GAS CO |  | 760
253 | 2005-09-05 | LA | sabotage | UNKNOWN (LAFOURCHE COUNTY ) | SOUTH COAST GAS CO |  | 1106
254 | 2005-07-21 | LA | sabotage | UNKNOWN (LAFOURCHE COUNTY ) | SOUTH COAST GAS CO |  | 446
255 | 2005-09-03 | LA | sabotage | UNKNOWN (LAFOURCHE COUNTY ) | SOUTH COAST GAS CO |  | 491
256 | 2005-09-02 | LA | sabotage | UNKNOWN (LAFOURCHE COUNTY ) | SOUTH COAST GAS CO |  | 1183
257 | 2005-07-05 | LA | sabotage | UNKNOWN (THREBORNE COUNTY ) | SOUTH COAST GAS CO |  | 743
258 | 2005-07-20 | LA | sabotage | UNKNOWN (LAFOURCHE COUNTY ) | SOUTH COAST GAS CO |  | 347
259 | 2005-10-25 | CO | technical failure | UNKNOWN (ADAMS COUNTY ) | PUBLIC SERVICE COMPANY OF COLORADO | CREW WAS GOING TO CONNECT A 1 1/4" PIECE OF POLYETHYLENE INTO A PVC TAPPING TEE WITH GAS BLOWING. WHEN THE CREW WENT TO REMOVE THE CAP ON THE BRANCH OF THE PVC TAPPING TEE, A STATIC CHARGE JUMPED FROM THE CAP TO THE BODY OF THE TEE CAUSING THE ESCAPING GA | 50
260 | 2005-10-24 | NC | sabotage | UNKNOWN (ROWAN COUNTY COUNTY ) | PUBLIC SERVICE OF NORTH CAROLINA, INCORPORATED (DBA PSNC ENERGY) | GAS SERVICE WAS DAMAGED BY CONTRACTOR RECLAIMING THE ROAD. SEE ATTACHED REPORT. 11/09/2005 FINAL REPORT: NORTH FRANKLIN STREET, CHINA GROVE NORTH CAROLINA TIME LINE OF EVENTS MONDAY, OCTOBER 24,2005 1:26 P.M. PROPST CONSTRUCTION COMPANY | 442
261 | 2006-01-03 | AK | other | UNKNOWN (KENAI PENINSULA COUNTY ) | ENSTAR NATURAL GAS COMPANY | ENSTAR WAS NOTIFEID OF A MOBILE HOME FIRE AT 3:45AM ON 1/3/06 AT TRACT 12A ECHO LAKE SUBDIVISION, LAKESIDE AVENUE, NEAR SOLDOTNA ALASKA. A SERVICE MAN WAS DISPATCHED TO FIND THE GAS METER AT THIS LOCATION SHUT OFF UPON ARRIVAL. A FIRE AT THE MOBILE HOME | 10
262 | 2005-10-23 | CA | maintenance | UNKNOWN (SANTA CLARA COUNTY ) | PACIFIC GAS & ELECTRIC COMPANY | REGULATOR MALFUNCTION AND IRV DID NOT APPEAR TO PERFORM AS REQUIRED AND CAUSE PRESSURE TO BUILD UP DOWNSTREAM AND EVENTUALLY CAUSE THE TOP OF THE METER TO RUPTURE, RELEASING GAS TO ATMOSPHERE AND THE SUBSEQUENT FIRE. | 0
263 | 2005-11-10 | LA | sabotage | UNKNOWN (LAFOURCHE COUNTY ) | SOUTH COAST GAS CO INC |  | 587
264 | 2005-11-10 | LA | sabotage | UNKNOWN (LAFOURCHE COUNTY ) | SOUTH COAST GAS CO INC |  | 361
265 | 2005-12-05 | IL | other | UNKNOWN (WILL COUNTY ) | NICOR GAS | STRUCTURE FIRE ORIGINATED INSIDE THE GARAGE. THE METER SET, WHICH WAS ATTACHED TO THE OUTSIDE GARAGE WALL, WAS MELTED AS A RESULT OF THE FIRE. | 500
266 | 2005-12-14 | LA | sabotage | UNKNOWN (TERREBONNE COUNTY ) | SOUTH COAST GAS CO. |  | 926
267 | 2005-11-03 | TX | sabotage | UNKNOWN (NACOGDOCHES COUNTY ) | CHIRENO NATURAL GAS | TEXAS DEPARTMENT OF TRANSPORATION DID NOT CALL IN A LOCATE NOR DID WE RECIEVE ANY NOTIFICATION OF THEIR ACTIVITIES ON LOOP 34. | 2912
268 | 2005-11-11 | MD | other | UNKNOWN (nan COUNTY ) | BALTIMORE GAS & ELECTRIC COMPANY | BALTIMORE CITY FIRE DEPT. (BCFD) REQUESTED OUR ASSISTANCE TO TURN OFF NATURAL GAS SERVICE TO 3852 QUARRY ST. A GAS MECHANIC WAS DISPATCHED AT 13:34 AND ARRIVEDAT 13:58. THE 1" INSULOCK LEAADING TOTHE INLET SIDE OF THE METER HAD BEEN DAMAGED BY THE HEAT | 0
269 | 2005-11-11 | TX | sabotage | UNKNOWN (HARRIS COUNTY ) | CENTERPOINT ENERGY | THIRD PARTY DAMAGED A 4" I.P. STEEL SERVICE RISER, WHILE CLEARING A LOT WITH A BULLDOZER. THE HOUSTON FIRE DEPARTMETN BLOCKED LIBERTY ROAD FROM LOCKWWOD DRIVE TO KASHMERE STREET. *ORGINALLY REPORTED AS LOCKWOOD AT LIBERTY, BUT LATER CORRECTED TO 520 | 241606
270 | 2005-11-09 | MA | other | UNKNOWN (nan COUNTY ) | BOSTON GAS COMPANY D/B/A KEYSPAN ENERGY DELIVERY NEW ENGLAND |  | 0
271 | 2005-12-11 | TX | other | UNKNOWN (HARRIS COUNTY ) | CENTERPOINT ENERGY | RADIANT HEAT FROM A VEHICLE FIRE MELTED METER SET ASSEMBLY AND THE ESCAPING GAS WAS IGNITED. DRIVER OF VEHICLE WAS KILLED WHILE STILL INSIDE VEHICLE. *ORIGINALLY REPORTED AS 530 E. CANINO, BUT WAS LATER CORRECTED TO 613 E. CANINO. | 0
272 | 2005-12-13 | NJ | sabotage | UNKNOWN (BERGEN COUNTY ) | PUBLIC SERVICE ELECTRIC & GAS COMPANY | ON TUESDAY, DECEMBER 13, 2005, WORKERS FROM THE AMERICAN TANK COMPANY WERE IN THE PROCESS OF REMOVING AN UNDERGROUND OIL TANK THAT SERVED A THREE STORY 24 UNIT APARTMENT BUILDING WHEN THE GROUND SURROUNDING A 1-1/4 INCH 15 PSI DESIGN PRESSURE STEEL GAS SE | 5000
273 | 2005-09-25 | PA | other | UNKNOWN (PHILADELPHIA COUNTY ) | PHILADELPHIA GAS WORKS | PGW WAS CALLED TO THE SCENE OF A FIRE/EXPLOSION BY THE PHILADELPHIA FIRE DEPARTMENT. UPON ARRIVAL WE FOUND A FIRE WITH EXTENSIVE STRUCTURAL DAMAGE TO 3304 AND 3306 N. HOPE STREET, ALSO DAMAGED WERE 3302 AND 3308. THERE WAS A GAS FIRE APPROXIMATELY 12 FE | 0
274 | 2005-11-01 | VA | sabotage | UNKNOWN (nan COUNTY ) | WASHINGTON GAS | NATELCO ELECTRICAL CONTRACTOR TRENCHING FOR VERIZON TO INSTALL PHONE CONDUIT STRUCK A 2" PLASTIC GAS MAIN IN THE ECONOMY PARKING LOT AT REAGAN NATIONAL AIRPORT. THE ESCAPING GAS IGNITED AND DESTROYED THE CONTRACTOR'S RENTAL TRENCHER AND CAUSED MINOR DAMA | 126
275 | 2005-12-12 | AR | natural disasters | UNKNOWN (PULASKI COUNTY ) | CENTERPOINT ENERGY | A STRESS FRACTURE CAUSED A 2" CAST IRON MAIN TO RUPTURE THAT WAS LOCATED BETWEEN 2008 AND 2016 DURWOOD, LITTLE ROCK,AR APPROXIMATELY 11' FROM THE REAR (NORTHWEST CORNER) OF 2016. AT APPROXIMATELY 1:00 AM ON 12/12/05, THERE WAS A REPORTED SMALL EXPLOSION I | 1800
276 | 2005-12-10 | TX | leaks and spills | UNKNOWN (HARRIS COUNTY ) | CENTERPOINT ENERGY | THIRD PARTY DAMAGED A 2" I.P. STEEL SERVICE LINE WITH A BORING TOOL WHILE INSTALLING FIBER OPTIC CABLES. HOUSTON FIRE DEPARTMENT BLOCKED THE EAST BOUND TRAFFIC LANES OF WESTHEIMER. | 59527
277 | 2005-11-17 | LA | sabotage | UNKNOWN (TERREBONNE COUNTY ) | SOUTH COAST GAS CO. |  | 408
278 | 2005-12-11 | KS | natural disasters | UNKNOWN (JOHNSON COUNTY ) | KANSAS GAS SERVICE | ON DECEMBER 11, 2005 AT 0810 HRS KANSAS GAS SERVICE WAS NOTIFIED BY THE SHAWNEE, KANSAS FIRE DEPARTMENT OF AN EXPLOSION AND FIRE AT 6513 HALSEY, SHAWNEE, JOHNSON COUNTY, KANSAS. COMPANY PERSONNEL WERE DISPATCHED TO THE SITE AND THE FIRST RESPONDER ARR | 0
279 | 2005-11-09 | AL | sabotage | UNKNOWN (TALLAPOOSA COUNTY ) | DADEVILLE WATER SUPPLY AND GAS BOARD | TRACKHOE OPERATOR HIT 4" HP MAIN.LINE LOCATION WAS NOT CALLED IN. THE OPERATOR WHO HIT THE LINE IS HEATH MCADAMS. EMPLOYER IS RACON, FROM TUSCALOOSA,ALABAMA. REPAIRS MAID, LINE IS BACK IN OPERATION. COST - $12,818.99 GAS LOST - $1,783.22 | 1780
280 | 2005-11-04 | LA | sabotage | UNKNOWN (LAFOURCHE COUNTY ) | SOUTH COAST GAS CO. |  | 196
281 | 2005-10-10 | MO | technical failure | UNKNOWN (COOPER COUNTY ) | UNION ELECTRIC COMPANY D/B/A AS AMERENUE | PRE-INCIDENT INFORMATION: A CAST IRON REPLACEMENT PROJECT WAS UNDERWAY WHICH INVOLVED REPLACING VARIOUS SIZES OF LOW PRESSURE (INCHES OF WATER COLUMN) CAST IRON MAINS AND STEEL SERVICES, AND CONVERTING ALL OF THESE NEW FACILITIES AND SOME EXISTING LOW PRE | 0
282 | 2005-12-06 | LA | sabotage | UNKNOWN (LAFOURCHE COUNTY ) | SOUTH COAST GAS CO. |  | 2680
283 | 2005-12-20 | LA | sabotage | UNKNOWN (LAFOURCHE COUNTY ) | SOUTH COAST GAS CO. |  | 0
284 | 2005-12-10 | NY | sabotage | UNKNOWN (nan COUNTY ) | NEW YORK STATE ELECTRIC & GAS | THE INVESTIGATION OF THE ORIGIN AND CAUSE OF THE INCIDENT IS CURRENTLY UNDER INVESTIGATION. AT THIS TIME, WE DO NOT KNOW WHAT CAUSED THE INCIDENT OR WHY IT OCCURRED. A PARTIALLY CIRCUMFRENTIAL CRACK WAS FOUND ON THE UPPER SIDE OF THE THREAD ROOT OF A SERV | 3000
285 | 2005-11-22 | LA | sabotage | UNKNOWN (LAFOURCHE COUNTY ) | SOUTH COAST GAS CO. |  | 1004
286 | 2005-12-20 | MI | sabotage | UNKNOWN (WAYNE COUNTY ) | MICHIGAN CONSOLIDATED GAS COMPANY / DTE ENERGY |  | 0
287 | 2005-12-08 | TX | other | UNKNOWN (WILLIAMSON COUNTY ) | ATMOS ENERGY CORPORATION | A RELIEF VALVE OPERATED PROPERLY. | 112000
288 | 2005-12-10 | TX | other | UNKNOWN (WILLIAMSON COUNTY ) | ATMOS ENERGY CORPORATION., MID TEX DIVISION | A RELIEF VALVE OPERATED PROPERLY. | 53000
289 | 2006-01-06 | IL | other | UNKNOWN (nan COUNTY ) | NICOR GAS | STRUCTURE FIRE ORIGINATING IN A BEDROOM SPREAD TO THE EXTERIOR WALL DAMAGING THE METER SET, THUS CAUSING A RELASE OF NATURAL GAS. | 250
290 | 2006-01-05 | SC | sabotage | UNKNOWN (SPARTANBURG COUNTY ) | PIEDMONT NATURAL GAS | HIGHWAY CONTRACTOR INSTALLING DRAINAGE FACILITIES FOR ROAD WIDENING PROJECT STRUCK GAS MAIN. LINE WAS MARKED BUT CONTRACTOR ASSUMED LINE WAS ABANDONED BECAUSE OF PREVIOUS EXPERIENCE WITH ABANDONED MAIN IN ADJACENT AREAS. | 57325
291 | 2005-12-14 | TX | other | UNKNOWN (HARRIS COUNTY ) | CENTERPOINT ENERGY | A LEAK OCCURRED ON A 6' NATURAL GAS DISTRIBUTION LINE, WITH THE BANKS OF GREENS BAYOU. THE LEAKING NATURAL GAS CAUSED THE COAST GUARD TO TAKE PRECAUTIONARY MEASURES AND TEMPORARILY RESTRICT BOAT TRAFFIC IN THE AREA. THE LINE WAS SHUT DOWN AND TAKEN OUT | 0
292 | 2005-12-30 | WI | technical failure | UNKNOWN (MILWAUKEE COUNTY ) | WISCONSIN GAS COMPANY, D/B/A WE-ENERGIES | ON DECEMBER 30TH, 2005 A CONTRACT EMPLOYEE FROM SOUTHERN CROSS CORPORATION, PERFORMED A GAS SERVICE SURVEY INVOLVING AN INSIDE METER SET AT 3491 N. BARLETT AVENUE, MILWAUKEE, WISCONSIN. WHILE COMPLETING THE LEAK SURVEY ON THE INSIDE METER SET, HE FOUND A | 338
293 | 2006-01-23 | CA | other | UNKNOWN (LOS ANGELES COUNTY ) | SOUTHERN CALIFORNIA GAS COMPANY | ON JANUARY 23, 2006 A DAMAGED METER SET CAUGHT FIRE AND GAS IGNITED AT THE LOCATION OF 17325 HALSTED STREET, NORTHRIDGE. THE INCIDENT WAS REPORTED TO THE DOT AND CPUC BRANCH DUE TO TOTAL FIRE DAMAGE EXPECTED TO EXCEED $50,000. INVESTIGATIONS BY BOTH T | 0
294 | 2006-01-25 | MN | other | UNKNOWN (RAMSEY COUNTY ) | NORTHERN STATES POWER COMPANY DBA XCEL ENERGY | VEHICLE STRUCK DUAL METER SET, SHEARING OFF ANODELESS RISERS AT GRADE LEVEL AND ALLOWING GAS TO ESCAPE IN TO RESIDENCE. ESCAPING GAS IGNITED CAUSING FIRE AND SECONDARY EXPLOSION. | 0
295 | 2006-01-31 | MI | other | UNKNOWN (MACOMB COUNTY COUNTY ) | SEMCO ENERGY GAS COMPANY |  | 50
296 | 2005-04-11 | CA | other | UNKNOWN (ORANGE COUNTY COUNTY ) | SOUTHERN CALIFORNIA GAS COMPANY | ON APRIL 11, 2005 A METER SET ASSEMBLY WAS DAMAGED WHEN A DRIVER LOST CONTROL OF HIS VEHICLE ON THE ROADWAY, COMING TO REST ON A METER SET ASSEMBLY. THIS METER SET ASSEMBLY IS LOCATED 45¿ OFF THE ROADWAY. ESCAPING GAS FROM THE DAMAGED METER SET ASSEMBL | 0
297 | 2003-04-26 | CA | other | UNKNOWN (FRESNO COUNTY COUNTY ) | SOUTHERN CALIFORNIA GAS COMPANY | ¿ ON APRIL 26, 2003, A VEHICLE ACCIDENT OCCURRED AT THE INTERSECTION OF NEBRASKA AVE. AND ACADEMY AVE. IN THE CITY OF SELMA. THE COLLISION CAUSED ONE VEHICLE TO CAREEN OFF THE ROAD AND STRIKE A BARRICADED METER SET ASSEMBLY, BREAKING PIPING ABOVE THE LOW | 0
298 | 2006-01-26 | OH | sabotage | UNKNOWN (FRANKLIN COUNTY ) | COLUMBIA GAS OF OHIO INC. | A THIRD PARTY EXCAVATOR INSTALLING CONDUIT, DIRECTIONAL BORED INTO A COLUMBIA GAS OF OHIO,INC. 4-INCH PLASTIC GAS MAIN. THE EXTENT OF THE DAMAGE REQUIRED COLUMBIA GAS OF OHIO,INC. TO SHUT DOWN AND ISOLATE THE DAMAGED PORTION OF THE MAIN TO SAFELY MAKE THE | 10745
299 | 2005-11-15 | IN | other | UNKNOWN (MONROE COUNTY ) | COMMUNITY NATURAL GAS CO. INC. | FIRE STAARTED NEAR ELECTRICAL SERVICE BOX IN GARAGE AT APPROX. 1:10AM. RESIDENCE WAS APPROX. 40 YRS OLD AND UNOCUPIED AT TIME OF FIRE. ROOF COLLAPSE CAUSED DAMAGE TO 1" BLACK STEEL PIPE CAUSING SOME GAS TO ESCAPE. FIRE WAS PUT OUT IN APPROX. 1HR. METER | 50
300 | 2004-12-01 | NY | maintenance | UNKNOWN (SUFFOLK COUNTY ) | KEYSPAN ENERGY DELIVERY LONG ISLAND | WORKING FIRE REPORTED BY SUFFOLK COUNTY CENTRAL FIRE DISPATCH #6. UPON KEYSPAN ENERGY ARRIVAL GAS READINGS WERE OBTAINED AT THE FOUNDATION AND MIDPOINT OF THE SERVICE. IN ADDITION, SEVERE DAMAGE WAS DISCOVERED AT THE REAR OF THE BUILDING. THERE WERE 16 IN | 0
301 | 2004-10-12 | NY | leaks and spills | UNKNOWN (SUFFOLK COUNTY ) | KEYSPAN ENERGY DELIVERY LONG ISLAND (KEYSPAN GAS EAST CORP, DBA) | ONE 1 BUILDING AND NUMEROUS AUTOMOBILES SUSTAINED DAMAGE FROM A DISTURBANCE AND ENSUING FIRE. THERE WERE 9 NINE INDIVIDUALS IN THE BUILDING AT THE TIME OF THE INCIDENT,WITH ONE REPORTED INJURY. GAS TECHNOLOGY INST. CONDUCTED THE EVALUATION OF THE PIP | 0
302 | 2004-12-03 | NY | sabotage | UNKNOWN (SUFFOLK COUNTY ) | KEYSPAN ENERGY DELIVERY LONG ISLAND | LAURELWOOD LANDSCAPING CONSTRUCTION INC. ( SUBCONTRACTOR TO NEWBORN CONSTRUCTION ) DAMAGED AN 8¿ HIGH PRESSURE PLASTIC GAS MAIN ON ROUTE 25 IN CUTCHOGUE. AS A RESULT OF THIS DAMAGE, GAS SERVICE WAS INTERRUPTED TO OVER 1,800 CUSTOMERS. THE OPERATOR DAMAGE | 2720
303 | 2006-01-21 | TX | sabotage | UNKNOWN (HARRIS COUNTY ) | CENTERPOINT ENERGY | THIRD PARTY DAMAGED A 4" I.P. POLY GAS MAIN WITH A BORING TOOL WHILE INSTALLING CONDUIT FOR WATER LINE. HOUSTON FIRE DEPARTMENT AND POLICE DEPARTMENT BLOCKED HOUSTON CENTER BLVD. FROM RICHMOND AVE. SOUTH TO WEST PARK DR. *ORIGINALLY TELEPHONICALLY R | 83237
304 | 2006-01-18 | TX | leaks and spills | UNKNOWN (DALLAS COUNTY ) | ATMOS ENERGY CORPORATION., MID TEX DIVISION | A CUSTOMER SERVICE TECHNICIAN INVESTIGATING A REPORTED LEAK WAS BAR TESTING NEAR A METER. THE BAR TEST HOLE PROVIDED AN ENHANCED AVENUE FOR THE GAS ESCAPING FROM THE EXISTING LEAK TO VENT THE ATMOSPHERE. THE ESCAPING GAS WAS IGNITED BY A SPARK FROM AN OVE | 0
305 | 2006-02-14 | NV | sabotage | UNKNOWN (CLARK COUNTY ) | SOUTHWEST GAS CORP. | WHILE DIGGING WITH A BACKHOE TO INSTALL POWER CONDUIT, AN OPERATOR FOR ACME ELECTRIC HIT AND DAMAGED A 2" PE DISTRIBUTION MAIN WITH TWO-WAY FEED. SEVERAL SOURCES OF IGNITION WHERE PRESENT AND IGNITION OCCURRED PRIOR TO SWG CREWS ARRIVING ON THE SCENE. AVA | 2725
306 | 2006-02-20 | CA | leaks and spills | UNKNOWN (IMPERIAL COUNTY ) | SOUTHERN CALIFORNIA GAS COMPANY | ON FEBRUARY 20, 2006, GAS FROM A LEAKING 2¿ PLASTIC MEDIUM PRESSURE MAIN AT THE INTERSECTION OF CROSS ROAD AND ATEN, CITY OF IMPERIAL WAS IGNITED BY A CATERING TRUCK PASSING OVER THE LOCATION. THE RESULTING FIRE DESTROYED THE CATERING TRUCK AND CONTENTS. | 0
307 | 2006-03-01 | LA | sabotage | UNKNOWN (LAFOURCHE COUNTY ) | SOUTH COAST GAS CO. |  | 2926
308 | 2006-02-22 | LA | sabotage | UNKNOWN (LAFOURCHE COUNTY ) | SOUTH COAST GAS CO. |  | 567
309 | 2006-02-27 | LA | sabotage | UNKNOWN (LAFOURCHE COUNTY ) | SOUTH COAST GAS CO. |  | 222
310 | 2005-12-19 | KS | sabotage | UNKNOWN (NEOSHO COUNTY ) | KANSAS GAS SERVICE | ALLEN CONSTRUCTION WAS IN THE PROCESS OF INSTALLING PIPE USING A LARGE TRACK ROCK TRENCHER FOR THE EXCAVATION WHEN THEY HIT OUR GAS LINE. ACCORDING TO THE KANSAS ONE CALL LOCATE TICKET #5458642 AND OUR GPLS LOCATOR THE REQUEST WAS FROM HWY 59 AND HWY 39, | 2672
311 | 2006-03-05 | NY | sabotage | UNKNOWN (ULSTER COUNTY ) | CENTRAL HUDSON GAS & ELECTRIC CORPORATION | THE PORT EWEN WATER DEPARTMENT WAS EXCAVATING TO REPAIR A WATER MAIN LEAK IN FRONT OF 150 WEST MAIN STREET IN PORT EWEN ON MARCH 5, 2006. THE WATER DEPARTMENT, UTILIZING AN EXCAVATOR, STRUCK THE 3/4" STEEL NATURAL GAS SERVICE LINE OPERATING AT 30 PSIG. | 186
312 | 2006-02-21 | FL | maintenance | UNKNOWN (BREVARD COUNTY ) | FLORIDA CITY GAS | FCG WAS NOTIFIED OF A LEAK ON A 6'' STEEL LINE OPERATING AT APPROX 57 PSI CROSSING UNDER INDIAN RIVER. THE LEAK WAS FOUND TO BE LOCATED APPROX 500'SOUTH OF THE SR 520 BRIDGE AND APPROX 2000' FROM EITHER SHORE. A COURTESY CALL WAS MADE TO THE NATIONAL RESP | 0
313 | 2006-04-02 | AK | other | UNKNOWN (MATANUSKA SUSITNA BOROUGH COUNTY ) | ENSTAR NATURAL GAS COMPANY | ENSTAR NATURAL GAS COMPANY WAS NOTIFIED OF A RESIDENTIAL STRUCTURE FIRE AT 2850 S. TEELAND STREET, WASILLA AK AT 10:07PM AST ON 4/2/06. THE FIRE CAUSED ENSTAR'S HDPE SERVICE LINE TO MELT INSIDE THE STEEL RISER, RELEASING NATURAL GAS. THE SERVICE LINE WA | 50
314 | 2006-03-21 | OK | other | UNKNOWN (KAY COUNTY ) | CENTERPOINT ENERGY | AT APPROX 2:41AM ON MARCH 21ST 2006, CENTERPOINT ENERGY WAS NOTIFIED OF ZERO GAS PRESSURE AT THE BLACKWELL AND TONKAWA OKLAHOMA TOWN BORDER STATIONS. CENTERPOINT ENERGY PIPELINE SERVICES, THE SUPPLIER FOR CENTERPOINT ENERGY, OK ADVISED THAT A METERING STA | 0
315 | 2006-04-07 | AK | other | UNKNOWN (MATANUSKA SUSITNA BOROUGH COUNTY ) | ENSTAR NATURAL GAS COMPANY | ON FRIDAY, APRIL 7, 2006 AT 1:01 PM ADT, ENSTAR NATURAL GS COMPANY WAS NOTIFIED OF A RESIDENTIAL STRUCTURE FIRE AT LOT 7, BLOCK 5 EAGLE ESTATES IN PALMER, ALASKA. HEAT FROM THE FIRE CAUSED ENSTAR'S HDPE SERVICE LINE RISER TO MELT, RELEASING NATURAL GAS. | 50
316 | 2006-03-10 | IL | other | UNKNOWN (COOK COUNTY ) | PEOPLES GAS LIGHT & COKE CO | DATA COLLECTION TEAM - 06/30/2014 THE PEOPLES GAS LIGHT AND COKE COMPANY HAS COMPLETED ITS INVESTIGATION OF THE INCIDENT AT 3211 SOUTH WOOD STREET, CHICAGO, IL. AT APPROX. 1:10P.M. ON MARCH 10,2006, AN EXPLOSION OCCURRED AT 3211 S.WOOD IN CHICA | 0
317 | 2006-03-13 | OH | sabotage | UNKNOWN (BUTLER COUNTY ) | DUKE ENERGY,OHIO | A PLUMBING CONTRACTOR AUGERING A SEWER LATERAL STRUCK A GAS SERVICE CAUSING GAS TO MIGRATE INTO THE HOME, RESULTING IN AN EXPLOSION. | 0
318 | 2006-03-09 | IN | natural disasters | UNKNOWN (JACKSON COUNTY ) | INDIANA GAS CO INC | A VECTREN SIX INCH STEEL DISTRIBUTION LINE THAT CROSSES UNDER THE WHITE RIVER NORTH OF SEYMOUR, INDIANA DEVELPOED A LEAK AND RELEASED GAS THROUGH THE WATER INTO THE ATMOSPHERE REQUIRING IT TO BE SHUT DOWN. WHEN HIGH WATERS RECEDED ENOUGH TO SAFELY ALLOW F | 25346
319 | 2006-03-08 | TX | sabotage | UNKNOWN (HARRIS COUNTY ) | CENTERPOINT ENERGY | THIRD PARTY DAMAGE TO 16" HP STEEL MAIN WITH TRACKHOE PACE SERVICE LP 281 256-2201. | 146435
320 | 2005-08-29 | LA | natural disasters | UNKNOWN (ORLEANS COUNTY ) | ENTERGY NEW ORLEANS, INC - GAS DISTRIBUTION BUSINESS | EXPLANATION OF 5.C ABOVE RESTORATION (COST TO GET CURRENT SYSTEM OPERATIONAL) $107,263,900 LOSS PRODUCT (NATURAL GAS) $4,000,000 REPLACEMENT OF PIPE/INFRASTRUCTURE $355,254,217 GAS SERVICE HAS BEEN RESTORED AND IS AVAILABLE TO ALL FLOODED AREAS WITHIN | 4000000
321 | 2005-11-22 | GA | natural disasters | UNKNOWN (FULTON COUNTY ) | ATLANTA GAS LIGHT COMPANY | A POWER LINE FELL IN WINDY CONDITIONS AND ENERGIZED A WATER DEPARTMENT VAULT WHICH IN TURN CAUSED ARCING BETWEEN THE WATER LINE AND A 2" STEEL GAS LINE SERVING THE GREENBRIAR COMMONS APARTMENT COMPLEX. THE ARCING BURNED 3 HOLES IN THE GAS SERVICE AT A PO | 893
322 | 2004-09-17 | PA | natural disasters | UNKNOWN (ALLEGHENY COUNTY ) | EQUITABLE GAS CO | AN 10 INCH STEEL GAS MAIN FAILED AS A RESULT OF HEAVY RAINS. PIPELINE SECTION IS PHYSICALLY SEPARATED AND ABANDONED. | 0
323 | 2004-09-17 | PA | natural disasters | UNKNOWN (ALLEGHENY COUNTY ) | EQUITABLE GAS CO | AN 8 INCH STEEL GAS MAIN FAILED AS A RESULT OF HEAVY RAINS. PIPELINE SECTION IS PHYSICALLY SEPARATED AND ABANDONED. | 0
324 | 2006-03-24 | UT | natural disasters | UNKNOWN (SUMMIT COUNTY ) | QUESTAR GAS COMPANY | A 3/4¿ NIPPLE FITTING (LOCATED BENEATH THE SERVICE REGULATOR) ON A METER SET CRACKED ON THE THREADS DUE TO HEAVY SNOW ACCUMULATION ON QUESTAR GAS COMPANY¿S NATURAL GAS METER AT 6871 SADDLE CT, PARK CITY, UTAH. THE ESCAPING GAS FROM THE CRACKED NIPPLE F | 10
325 | 2006-04-21 | FL | natural disasters | UNKNOWN (ALACHUA COUNTY ) | GAINESVILLE REGIONAL UTILITIES - GAS | AT 1752, ON 04/21/06, GRU SYSTEM CONTROL DISPATCHED THE ON CALL GAS WORKER TO A REPORTED LEAK AT 3455 NW 50TH AVE. IN GAINESVILLE FLORIDA. THE GAINESVILLE FIRE DEPARTMENT WAS ON THE SCENE AND HAD EXTINGUISHED A SMALL FIRE AT THE BASE OF A TREE THAT HAD B | 0
326 | 2006-04-04 | TX | other | UNKNOWN (BOWIE COUNTY ) | CENTERPOINT ENERGY | THE HOME LOCATED AT 23 SARAH LANE,RED LICK, TEXAS, CAUGHT FIRE AND WAS BELIEVED TO BE A COMPLETE LOSS. THE INCIDENT WAS REPORTED BASED ON THE ESTIMATED PROPERTY DAMAGE OF APPROXIMATELY $100,000. GAS SERVICE TO THE RESIDENCE WAS ACTIVE AT THE TIME OF THE I | 0
327 | 2006-04-11 | PA | other | UNKNOWN (nan COUNTY ) | PECO ENERGY CO | A VEHICLE WAS TRAVELING NORTH ON ROUTE 152 (LIMEKILN PIKE ) FAILED TO TURN LEFT AT THE TRAFFIC SIGNAL AT ROUTE 202 (BUTLER AVE.) AND PROCEEDED INTO THE EXIT AREA OF THE PROPERTY IMPACTING THE SOUTH SIDE OF THE BUILDING, BALLARD AND GAS ROTARY METER SET. G | 0
328 | 2006-03-21 | NY | sabotage | UNKNOWN (nan COUNTY ) | ROCHESTER GAS & ELECTRIC | ON 3-21-2006 AT 11:38 AM A CALL WAS RECEIVED BY RG&E FROM THE ROCHESTER FIRE DEPT INDICATING AN INCIDENT HAD OCCURRED AT 68 AKRON ST IN THE CITY OF ROCHESTER. THE CONTRACTOR (R.P. MYERS) WAS DIGGING ADJACENT TO THE MAIN AS PART OF THE CAST IRON MAIN REPLA | 750
329 | 2006-05-02 | TN | natural disasters | UNKNOWN (DICKSON COUNTY ) | GREATER DICKSON GAS AUTHORITY | LIGHTING HIT GAS METER CAUSING THE GAS TO IGNITE WHICH SET HOUSE ON FIRE. | 400
330 | 2006-04-06 | CA | other | UNKNOWN (MERCED COUNTY ) | PACIFIC GAS & ELECTRIC CO | OUT OF CONTROL VEHICLE RAN THROUGH A FENCE AND STRUCK A RESIDENTIAL GAS METER AT 1181 W. CHILDS AVE., MERCED, CA, SHEARING THE METER OFF AT THE RISER. ESCAPING GAS WAS IGNITED, CAUSING A FIRE WHICH CAUSED DAMAGE IN EXCESS OF $50,000. | 0
331 | 2006-04-11 | IL | other | UNKNOWN (COOK COUNTY ) | NICOR GAS | GARAGE FIRE AT THIS ADDRESS. HEAT FROM DIRECT FLAME CAUSED DAMAGE TO THE METER SET CAUSING A RELEASE OF NATURAL GAS. CAUSE OF THE FIRE IN UNKNOWN. NOTE: THIS WAS ORIGINALLY REPORTED AS A A VEHICLE HITTING THE METER SET. AFTER FURTHER INVESTIGATION | 250
332 | 2006-04-11 | TX | other | UNKNOWN (POLK COUNTY ) | CENTERPOINT ENERGY | A HOUSE FIRE AT 314 MORRISON, LIVINGSTON, POLK COUNTY, TEXAS RESULTED IN ONE (1) DEATH AND ONE (1) INJURY REQUIRING HOSPITALIZATION FOR WHAT WAS REPORTED AS 3RD DEGREE BURNES. THE HOME WAS OCCUPIED BY AN ELDERLY COUPLE. THE WOMAN IS REPORTED TO HAVE SMO | 0
333 | 2006-04-17 | WV | natural disasters | UNKNOWN (TUCKER COUNTY ) | CANAAN VALLEY GAS COMPANY | ON FRIDAY, APRIL 14, 2006 AT APPROXIMATELY 9:00 P.M., A SEVERE THUNDERSTORM PASSED THROUGH THE AREA. LIGHTNING APPARENTLY HIT IN THE VICINITY OF OUR PIPELINE. THE LIGHTNING IS BELIEVED TO HAVE TRAVELED THE TRACER WIRE TO A 1" TAP ON A 4" MAIN, CAUSING T | 0
334 | 2006-04-16 | OH | other | UNKNOWN (FRANKLIN COUNTY ) | COLUMBIA GAS OF OHIO, INC. | ON APRIL 16,2006 COLUMBIA GAS OF OHIO CONTACTED DOT AND REPORTED THE INCIDENT REFERENCED ABOVE. AT THE TIME OF THE OCCURRENCE THE CITY OF COLUMBUS FIRE DEPARTMENT REPORTED THAT THE CAUSE OF THE EXPLOSION WAS LIKELY A RELEASE OF NATURAL GAS. SINCE THE | 0
335 | 2006-05-08 | VA | other | UNKNOWN (nan COUNTY ) | CITY OF RICHMOND DEPARTMENT OF PUBLIC UTILITIES | ON MAY 8, 2006 AT APPROXIMATELY 3:40 P.M., A VEHICLE BACKED INTO AND DAMAGED THE NATURAL GAS METER AT THE OUTBACK RESTAURANT (7917 WEST BROAD STREET, RICHMOND, VIRGINIA 23226). THE METER IS A 10,000 ROCKEWELL SERIES METER AND WAS LOCATED THIRTY-SIX (36) | 0
336 | 2006-04-25 | IL | other | UNKNOWN (KANE COUNTY ) | NICOR GAS | REVISED REPORT WITH UPDATES PROPERTY DAMAGE AMOUNT. ___________________________________________________________________________ HIGH WINDS KNOCKED CHARCOAL FROM GRILL AND STARTED FIRE ON THE BALCONY. DEBRIS FROM THE BALCONY FELL ONTO THE METER SET, C | 500
337 | 2006-04-24 | LA | sabotage | UNKNOWN (HARRIS COUNTY ) | CENTERPOINT ENERGY | THIRD PARTY DAMAGED 8" STEEL MAIN WHILE DRIVING PILINGS IN CANAL. (NON-REPORTABLE) | 15377
338 | 2006-04-23 | NM | other | UNKNOWN (TORRANCE COUNTY ) | E. M. W. GAS ASSOCIATION | THE GAS SERVICE TO THIS ADDRESS WAS INSTALLED AS PART OF THE ORIGINAL SYSTEM IN 1964.AND AT SOME POINT THROUGH THE YEARS THE HOMEOWNER BUILT A ROOM OVER THE RISER.NOBODY FROM E.M.W. KNEW THE RISER WAS THEIR.ON APRIL 23, 2006 THE HOMEOWNER WAS ATTEMPTING T | 101
339 | 2006-03-30 | MO | other | UNKNOWN (ST.CHARLES COUNTY ) | LACLEDE GAS COMPANY | THE INCIDENT RESULTED FROM A HOUSE FIRE WHICH ORIGINATED OUTSIDE THE HOUSE IN A WOOD MULCH BED NEAR THE NATURAL GAS METER SET SERVING THE RESIDENCE. VISUAL OBSERVATION AT THE SCENE INDICATED THAT THE MULCH IGNITED AND EVENTUALLY ENGULFED THE SERVICE LINE | 0
340 | 2006-04-19 | KY | sabotage | UNKNOWN (HENRY COUNTY ) | LOUISVILLE GAS AND ELECTRIC COMPANY | ON APRIL 19, 2006, MR. BILLY GRIGSBY WAS ATTEMPTING TO REPAIR A WATERLINE LEAK AT 8016 MAIN STREET IN CAMPBELLSBURG, KENTUCKY. MR. GRIGSBY INDICATED HE WAS DIGGING BY HAND AND COULD NOT GET A DEEP ENOUGH HOLE TO FIND THE WATERLINE. MR. GRIGSBY SAW A BAC | 371
341 | 2006-05-07 | KS | other | UNKNOWN (nan COUNTY ) | KANSAS GAS SERVICE | AT APPROXIMATELY 0730HRS ON MAY 7, 2006 A CAR TRAVELING THROUGH THE INTERSECTION AT 7TH AND KANSAS AVE, KANSAS CITY, KANSAS HIT A CAR IN THAT INTERSECTION AND THEN VERED OFF THE ROAD AND HIT THE REGULATOR STATION LOCATED ON THE NE CORNER OF THE INTERSECTI | 4925
342 | 2006-04-19 | FL | sabotage | UNKNOWN (ESCAMBIA COUNTY ) | CITY OF PENSACOLA - ENERGY SERVICE OF PENSACOLA (ESP) | PRELIMINARY INVESTIGATION REVEALED FRACTURES ON SERICE LINE COMPONENTS APPARENTLY DUE TO ACTIVITY OF EXCAVATOR CONTRACTOR. THE VALVE CONNECTION OF THE SERVICE LINE FRACTURED, APPARENTLY DUE TO IMPROPER SUPPORT AND BACKFILL BY THE EXCAVATOR AND TO EXCESSI | 276
343 | 2006-04-02 | MO | natural disasters | UNKNOWN (PEMISCOT COUNTY ) | ATMOS ENERGY | TORNADO DAMAGE IN TOWN ONE STATION HAD TO BE TURNED OFF. A BLOW DOWN VALVE WAS SHEARED OFF AT GROUND LEVEL BY FLYING DEBRIS AND APPROX. 425 CUSTOMERS HAD TO BE TURNED OFF. AT THIS TIME THE NUMBER OF RETURNING CUSTOMERS IS UNDETERMINED. | 19689
344 | 2006-05-18 | LA | sabotage | UNKNOWN (LA FOURCHE COUNTY ) | SOUTH COAST GAS CO |  | 331
345 | 2006-05-09 | LA | sabotage | UNKNOWN (LA FOURCHE COUNTY ) | SOUTH COAST GAS CO |  | 357
346 | 2006-05-10 | IL | other | UNKNOWN (WINNEBAGO COUNTY ) | NICOR GAS | VOLUNTEER FIREFIGHTER AND FORMER EMPLOYEE OF THE BUSINESS AT 2758 ALWORTH WAS ACCUSED OF SETTING THE FIRE THAT DESTROYED THE STRUCTURE AND DAMAGED THE METER SET WHICH WAS ATTACHED TO THE STRUCTURE. | 500
347 | 2006-05-12 | IL | other | UNKNOWN (KENDALL COUNTY ) | NICOR GAS | FIRE AND/OR EXPLOSION IN UTILITY/BOILER ROOM OF SINGLE FAMILY HOME. CAUSE OF THE FIRE/EXPLOSION IS UNKNOWN AFTER INVESTIGATIONS. | 1
348 | 2006-05-15 | UT | other | UNKNOWN (SALT LAKE COUNTY ) | QUESTAR GAS COMPANY | THE FIRE ORIGINATED INSIDE THE RESIDENCE AND WAS NOT RELATED TO NATURAL GAS. THE FIRE MOVED OUT OF A WINDOW AND THE HEAT OF THE FIRE CAUSED THE REGULATOR TO MELT AND A RELEASE OF NATURAL GAS. THE PUBLIC/PRIVATE PROPERTY DAMAGES OF $100,000.00 IS A DI | 230
349 | 2005-11-08 | CA | leaks and spills | UNKNOWN (RIVERSIDE COUNTY ) | SOUTHERN CALIFORNIA GAS COMPANY | ON NOVEMBER 8, 2005 AN EXPLOSION AND FIRE OCCURRED AT THE ADDRESS OF 5760 LUCRETIA, MIRA LOMA. UNDERGROUND NATURAL GAS WAS DISCOVERED AT THE FOUNDATION OF THE DAMAGED BUILDING. THE INCIDENT WAS REPORTED TO THE CPUC AS A RESULT OF MAJOR MEDIA BEING PRESEN | 0
350 | 2006-06-02 | VA | other | UNKNOWN (nan COUNTY ) | CITY OF RICHMOND PUBLIC UTILITIES | ON JUNE 2, 2006 AT APPROXIMATELY 3:52 P.M., OPERATOR RESPONDED TO A HOUSE FIRE AT 3701 GRANDEL DRIVE. THE ENSUING FIRE EVENTUALLY CONSUMED THE METER AND REGULATOR SET CAUSING GAS RELEASE. THE FIRE, THEN BEING GAS FED, ESCALATED IN INTENSITY UNTIL EXTING | 0
351 | 2006-05-27 | LA | sabotage | UNKNOWN (TERREBONNE COUNTY ) | SOUTH COAST GAS CO |  | 181
352 | 2006-05-06 | TX | natural disasters | UNKNOWN (HARRIS COUNTY ) | CENTERPOINT ENERGY | LIGHTNING STRIKE TO LIGHTPOLE, WHICH HIT FENCE CAUSING ARC TO 2" STEEL MAIN AND ESCAPING GAS IGNITED. | 1369
353 | 2006-05-19 | IL | other | UNKNOWN (MCHENRY COUNTY ) | NICOR GAS | FULLY INVOLVED STRUCTURE FIRE. WALL COLLAPSED ONTO THE METER SET CAUSING A RELEASE OF GAS. | 500
354 | 2006-03-30 | CO | other | UNKNOWN (nan COUNTY ) | PUBLIC SERVICE CO OF COLORADO | HEAVY SNOW IN THE REGION THIS YEAR CAUSED SNOW TO BE PILED IN ABNORMAL LOCATIONS. WHEN THE SNOW WAS CLEARED FROM THE PAVED ACCESS ROAD RUNNING THROUGH THE ANTLERS COMPLEX, IT WAS PUSHED OFF AN EMBANKMENT TO AN AREA WHERE XCEL ENERGY'S METERS WERE LOCATED | 1500
355 | 2006-06-05 | CA | sabotage | UNKNOWN (ORANGE COUNTY COUNTY ) | SOUTHERN CALIFORNIA GAS COMPANY | ON JUNE 5 2006 A 3¿ NATURAL GAS DISTRIBUTION PIPELINE OPERATING AT APPROXIMATELY 45 POUNDS WAS DAMAGED BY A CONTRACTOR INSTALLING NATURAL GAS PIPELINES FOR THE OPERATOR (SOUTHERN CALIFORNIA GAS COMPANY). NO INJURIES OR PUBLIC PROPERTY DAMAGE RESULTED FRO | 500
356 | 2006-05-30 | CA | other | UNKNOWN (STANISLAUS COUNTY ) | PACIFIC GAS AND ELECTRIC COMPANY | AT 1312 HOURS THE DUPLEX AT 106/108 OAK STREET EXPLODED AND BURNED. NATURAL GAS WAS SUSPECTED TO HAVE BEEN INVOLVED. AT 1730 HOURS WE WERE INFORMED THAT A PASSERBY HAD BEEN INJURED IN THE EXPLOSION AND HAD BEEN TAKEN TO THE UC DAVIS MEDICAL CENTER IN SA | 0
357 | 2006-06-19 | NC | sabotage | UNKNOWN (nan COUNTY ) | PIEDMONT NATUAL GAS CO. | A 3RD PARTY CONTRACTOR, PIKE ELECTRIC, WAS DIGGING UNDERGROUND IN THE PROCESS OF INSTALLING LIGHTING IN THE RUNAWAY BAY APARTMENTS IN CHARLOTTE, NC. AT AROUND 10:30 AM (6.19.06)THE PIKE CREW CUT A 1 1/4 PLASTIC GAS LINE COSE TO ONE OF THE APARMENT BUILDIN | 472
358 | 2006-06-03 | PA | other | UNKNOWN (CRAWFORD COUNTY COUNTY ) | NATIONAL FUEL GAS DISTRIBUTION CORPORATION | A PASSENGER VEHICLE TRAVELLING WEST BOUND ON PA SR 408 LEFT THE ROADWAY, TRAVELLING THROUGH LIVESTOCK FENCE, AND APPROXIMATELY 350' BEFORE CRASHING THROUGH STATION CHAIN LINK SECURITY FENCE. THE VEHICLE STRUCK PRESSURE RELIEF AND REGULATION FACILITIES, S | 10000
359 | 2006-07-02 | AK | other | UNKNOWN (KENAI PENINSULA BOROUGH COUNTY ) | ENSTAR NATURAL GAS COMPANY |  | 50
360 | 2006-06-16 | MN | natural disasters | UNKNOWN (HENNEPIN COUNTY ) | CENETERPOINT ENERGY RESOURCES GROUP D/B/A CENTERPOINT ENERGY MINNESOTA GAS | METER SET AND OR HOUSE WAS STRUCK BY LIGHTING CAUSING A FIRE. | 0
361 | 2006-05-31 | MN | technical failure | UNKNOWN (HENNEPIN COUNTY ) | CENTERPOINT ENERGY RESOURCES GROUP D/B/A CENTERPOINT ENERGY MINNESOTA GAS | CONTRACT EMPLOYEE USED A SAZALL TO CUT THROUGH A SERVICE LINE. A GASOUS ATMOSPHERE WAS CREATED AND A FLASH FIRE FOLLOWED. | 1000
362 | 2006-04-28 | MA | technical failure | UNKNOWN (MIDDLESEX COUNTY ) | NSTAR GAS COMPANY | THE INJURED EMPLOYEE WAS TAPPING THE 2 INCH HIGH VOLUME TAPPING TEE INSTALLED ON AN EXISTING 2INCH INTERMEDIATE PRESSURE PLASTIC MAIN. THE ELECTROFUSION TAPPING TEE WAS ONE OF FOUR TAPS PLANNED ON A DOUBLE BYPASS TO FACILITATE A MAIN CUTOUT IN CONJUNCTIO | 3000
363 | 2006-05-02 | TX | sabotage | UNKNOWN (BRAZORIA COUNTY ) | CENTERPOINT ENERGY | THIRD PARTY DAMAGE TO 3/4" POLY SERVICE LINE WHILE HEAT SHRINKING PHONE CABLE AN ESCAPING GAS IGNITED. | 600
364 | 2006-05-14 | TX | other | UNKNOWN (HARRIS COUNTY ) | CENTERPOINT ENERGY | STOLEN VEHICLE HIT METER SET ASSEMBLY AND ESCAPING GAS IGNITED. | 1405
365 | 2005-12-17 | AL | other | UNKNOWN (JEFFERSON COUNTY ) | ALABAMA GAS CORPORATION | COMPANY RESPONDED TO RESIDENCE FIRE AT REQUEST OF MIDFIELD FIRE DEPARTMENT. CAUSE OF FIRE WAS NOT DETERMINED DURING THE INVESTIGATION ASSOCIATED WITH THIS INCIDENT. THE HOMEOWNER ALLEGED IN LITIGATION THAT THERE WAS AN EXPLOSION AT THE RESIDENCE PRECEDIN | 0
366 | 2006-05-31 | CA | other | UNKNOWN (SHASTA COUNTY ) | PACIFIC GAS AND ELECTRIC COMPANY | LINSEED OIL SOAKED RAGS IN THE GARAGE SPONTANEOUSLY COMBUSTED AND CAUSED THE STRUCTURE FIRE TO SPREAD TO THE GAS METER SET. THE DAMAGE TO THE GAS METER SET CAUSED NATURAL GAS TO ESCAPE AND IGNITE. THE FIRE DEPARTMENT SHUT THE GAS SERVICE VALVE PRIOR TO | 0
367 | 2006-06-18 | IL | other | UNKNOWN (COOK COUNTY ) | NICOR GAS | SUSPICIOUS FIRE SPREAD THROUGHOUT THE VACANT STRUCTURE WHICH THEN DAMAGED THE METER SET AND CAUSED A RELEASE OF GAS. | 500
368 | 2006-04-16 | VA | other | UNKNOWN (FAIRFAX COUNTY ) | COLUMBIA GAS OF VIRGINIA | VEHICLE JUMPED PARKING LOT CURBING TRAVELING APPROXIMATELY 25¿ ACROSS GRASS AREA AND SIDEWALK STRIKING FOUR METER MANIFOLD SETTING. THE FAIRFAX COUNTY FIRE DEPT. TURNED OFF THE METER SETTING EXTINGUISHING THE FIRE. VEHICLE WAS APPARENT IGNITION SOURCE. | 0
369 | 2006-06-19 | CA | sabotage | UNKNOWN (CONTRA COSTA COUNTY ) | PACIFIC GAS & ELECTRIC COMPANY | ON MONDAY, JUNE 19, 2006, AT APPROXIMATELY 1245 HOURS, A CONSTRUCTION CREW FROM PERFORMANCE MECHANICAL INC. (PMI) DUG INTO A 4-INCH PLASTIC MAIN AT STONEMAN AVENUE AND BRIAR CLIFF DRIVE IN PITTSBURG CAUSING GAS TO ESCAPE WHILE EXCAVATING TO EXPOSE A WATE | 0
370 | 2006-06-28 | NY | natural disasters | UNKNOWN (BROOME COUNTY ) | NEW YORK STATE ELECTRIC & GAS CORPORATION | ON JUNE 27TH 2006 FLOOD WATERS IN BROOME COUNTY NEW YORK REACHED RECORD LEVELS ESPECIALLY IN THE CONKLIN NEW YORK AREA. DURING AN INVESTIGATION OF 14 VICTORY STREET IT WAS MOTED THAT THE GAS DRYER IN THE BASEMENT WAS MOVED AWAY FROM THE WALL PULLING ON T | 0
371 | 2006-06-16 | CA | other | UNKNOWN (nan COUNTY ) | PACIFIC GAS & ELECTRIC COMPANY | ON JUNE 16, 2005 A SUSPECT FLEEING FROM POLICE CRASHED INTO AN APPLIANCE STORE AND DAMAGED THE GAS METER AT 1048 W 8TH STREET IN CHICO, CALIFORNIA. FIREFIGHTERS EXTINGUISHED THE RESULTING STRUCTURAL FIRE AND VALVED OFF THE GAS RISER FOR SAFETY. THERE | 0
372 | 2006-06-24 | VA | other | UNKNOWN (PRINCE WILLIAM COUNTY ) | WASHINGTON GAS | THE FIRE/DAMAGE LOCATION, A HOUSE AT 3217 BERKLEY LANE - DALE CITY, VIRGINIA WAS THE RESULT OF A VEHICLE STRIKING THE SIDE OF THE HOUSE AND METER BUILD UP (DRIVER FLED SCENE) CAUSING IT TO RUPTURE AND A FIRE ENSUED THERBY DAMAGING THE STRUCTURE AND DISPLA | 57
373 | 2006-06-19 | OH | sabotage | UNKNOWN (SUMMIT COUNTY ) | DOMINION EAST OHIO GAS | ON JUNE 19,2006 AT APPOROXIMATELY 1:28 PM DOMINION EAST OHIO GAS CALL CENTER RECEIVED A REPORT FROM CABLING PROFESSIONALS THAT A PIPELINE WAS HIT AND DAMAGED BY A CONTRACTOR DIRECTIONAL BORING THE ROAD AT ILLINOIS PLAXE AND IOWA PLACE, BARBERTON, SUMMIT C | 1300
374 | 2006-07-15 | WY | other | UNKNOWN (PARK COUNTY ) | MONTANA-DAKOTA UTILITIES CO. | HOME OWNER WAS SIPHONING GASOLINE NEAR HOME. GASOLINE CAUGHT FIRE, MIGRATEED TO HOME AND IGNITED STRUCTURE. TOP OF NATURAL GAS METER WAS DESTROYED BY FIRE, RESULTING IN THE RELEASE OF NATURAL GAS. ONCE FIRE WAS EXTINGUISHED, SERVICEMAN WAS ABLE TO CLOSE | 20
375 | 2006-06-20 | KY | sabotage | UNKNOWN (HAZARD COUNTY ) | CITY OF HAZARD KENTUCKY/ HAZARD GAS COMPANY |  | 0
376 | 2006-07-14 | CA | sabotage | UNKNOWN (LOS ANGELES COUNTY ) | SOUTHERN CALIFORNIA GAS COMPANY | ON JULY 14, 2006, A 16¿ STEEL MEDIUM PRESSURE MAIN WAS DAMAGED BY A CONTRACTOR USING POWER AUGERING EQUIPMENT DURING A ROAD WIDENING PROJECT. THERE WAS A USA REQUEST FOR THIS AREA, AND FACILITIES WERE PROPERLY MARKED. NO FIRE OR INJURIES RESULTED FRO | 7000
377 | 2006-07-26 | MN | other | UNKNOWN (ANOKA COUNTY ) | CENTERPOINT ENERGY RESOURCES GROUP D/B/A CENTERPOINT ENERGY MINNESOTA GAS | A CAR BAUSING A FIRE STRUCK THE RESIDENTIAL HOME AND OUR METER SET. | 0
378 | 2006-06-28 | NY | natural disasters | UNKNOWN (BROOME COUNTY ) | NEW YORK STATE ELECTRIC & GAS CORPORATION | ON JUNE 27TH FLOOD WATERS IN BROOME COUNTY NEW YORK REACHED RECORD LEVELS ESPECIALLY IN THE CONKLIN NEW YORK AREA. DURING AN INVESTIGATION OF 21 MORRIS BLVD, IT WAS NOTED THAT THE BACK WALL OF THE STRUCTURE FACING THE RIVER HAD CAVED IN, NEGATIVELY AFFEC | 0
379 | 2006-07-20 | CA | sabotage | UNKNOWN (LOS ANGELES COUNTY ) | SOUTHERN CALIFORNIA GAS COMPANY | ON JULY 20, 2006, A 6¿ PLASTIC MEDIUM PRESSURE MAIN WAS PUNCTURED BY A CONTRACTOR WORKING FOR SOUTHERN CALIFORNIA GAS COMPANY¿S TRANSMISSION DEPARTMENT. THE CONTRACTOR WAS PERFORMING PIPELINE INTEGRITY WORK, USING A BACKHOE WHEN HE STRUCK THE DISTRIBUTIO | 1000
380 | 2006-07-13 | MD | other | UNKNOWN (PRINCE GEORGES COUNTY ) | WASHINGTON GAS | THE SERVICE RISER THAT FEEDS THIS LOCATION WAS ALTERED BY AN UNKNOWN INDIVIDUAL WITHOUT APPROVAL FROM WASHINGTON GAS. THE ALTERED LINE APPEARED TO BE BENT AND SUBSEQUENTLY DAMAGED CONTRIBUTING TO THE HOUSE EXPLOSION. UPDATED BY PHMSA ON 1/25/2016 PER | 0
381 | 2006-07-06 | WI | sabotage | UNKNOWN (WAUKESHA COUNTY ) | WISCONSIN GAS COMPANY, D/BA WE-ENERGIES | ON JULY 6, 2006, AT APPROXIMATELY 1:56PM, HOFFMAN CONSTRUCTION COMPANY OF BLACK RIVER FALLS, WI., WAS EXCAVATING SOIL AS PART OF A ROAD RECONSTRUCTION PROJECT WITH A TRACK MOUNTED BACKHOE IN THE VICINITY OF WISCONSIN GAS COMPANY¿S 3¿ ¿ 35# DISTRIBUTION MA | 17027
382 | 2006-07-16 | TX | other | UNKNOWN (PECOS COUNTY ) | CITY OF FORT STOCKTON | AN 11 YEAR OLD GIRL GOT IN A VEHICLE AND BACKED UP IN HER YARD HITTING THE GAS METER. THE VEHICLE BECAME HIGH CENTERED ON TOP OF THE GAS METER SET AND COULD NOT BE MOVED. | 316
383 | 2006-07-20 | IL | other | UNKNOWN (COOK COUNTY ) | NICOR GAS | INVESTIGATION FOUND THAT A BOX OF CLOTHES WAS STORED ON THE FLOOR IN FRONT OF ONE OF TWO WATER HEATERS IN THE UTILITY ROOM. THE BOX WAS STORED TOO CLOSE TO THE WATER HEATER AND WAS IGNITED FROM THE WATER HEATER BURNER. THERE WERE TWO GAS METERS LOCATED | 0
384 | 2006-07-18 | TX | sabotage | UNKNOWN (HARRIS COUNTY ) | CENTERPOINT ENERGY | THIRD PARTY COLT UTILITIES DAMAGED 4" PLASTIC MAIN WHILE INSTALLING STORM SEWER WITH A TRACKHOE. | 73224
385 | 2006-07-18 | MS | maintenance | UNKNOWN (LAUDERDALE COUNTY ) | ATMOS ENERGY CORPORATION | <P>RECORDS REFLECT THAT THE INITIAL SERVICE TAP TO THE MAIN WAS INSTALLED IN 1962, AFTER WHICH THE STEEL SERVICE LINE IN QUESTION WAS INSTALLED. THE INVESTIGATION REVEALED A HOLE IN A SERVICE LINE APPARENTLY DUE TO LOCALIZED CORROSION. THE CAUSE OF THE LO | 0
386 | 2006-08-02 | LA | sabotage | UNKNOWN (LAFOURCHE COUNTY ) | SOUTH COAST GAS CO. |  | 315
387 | 2006-02-27 | TX | other | UNKNOWN (LUBBOCK COUNTY COUNTY ) | ATMOS ENERGY CORPORATION | AT APPROXIMATELY 4:30 P.M. A PROPANE TANK AT WYLIE LP GAS INC. IGNITED, RESULTING IN A LARGE FIRE AT 8205 AVENUE F. THE LUBBOCK FIRE AND POLICE DEPARTMENT RESPONDED TO THE AREA AND SET UP A 1/2 MILE RADIUS PERIMETER AROUND THE PROPANE FIRE. BUSINESSES A | 1193
388 | 2006-08-02 | IL | other | UNKNOWN (COOK COUNTY ) | NICOR GAS | FIRE DEPARTMENT INVESTIGATION REVEALED THIS WAS AN ARSON FIRE WHICH DAMAGED THE GAS METER WHICH WAS LOCATED INSIDE THE GARAGE. DAMAGE FROM THE FIRE CAUSED THE RELEASE OF GAS FROM THE METER. REGULATOR WAS LOCATED OUTSIDE AND SUSTAINED NO DAMAGE. NOTE: | 0
389 | 2006-08-07 | SC | other | UNKNOWN (SOUTH CAROLINA COUNTY ) | SOUTH CAROLINA ELECTRIC & GAS COMPANY |  | 21
390 | 2006-08-21 | LA | sabotage | UNKNOWN (TERREBONNE COUNTY ) | SOUTH COAST GAS CO. |  | 400
391 | 2005-09-08 | LA | natural disasters | UNKNOWN (ST. BERNARD PARISH COUNTY ) | ATMOS ENERGY - LOUISIANA DIVISION | THIS INCIDENT OCCURRED AS A RESULT OF THE AFTERMATH OF HURRICANE KATRINA WHICH INCLUDED RECEIVING FLOOD WATERS WITH THE RESULTS OF MOST OF OUR SYSTEM BEING SUBMERGED. THE RESULTING RELEASE OF NATURAL GAS WS DUE MAINLY FROM HOUSES AND DEBRIS BEING PUSHED | 1000000
392 | 2006-08-02 | MO | sabotage | UNKNOWN (WARREN COUNTY ) | UNION ELECTRIC COMPANY D/B/A AS AMERENUE | RALPH JONES GRADING AND CONTRACTING WAS PERFORMING EXCAVATION FOR THE INSTALLATION OF A NEW ROAD FOR A RESIDENTIAL SUBDIVISION NEAR THE INTERSECTION OF STUERMANN ROAD AND HIGHWAY H NEAR WRIGHT CITY, MO. THE CONTRACTOR WAS OPERATING EXCAVATING EQUIPMENT A | 62021
393 | 2006-08-13 | CA | other | UNKNOWN (ALAMEDA COUNTY ) | PACIFIC GAS AND ELECTRIC COMPANY | ON 8/13/2006 AT 1602 HOUR, A STRUCTURAL FIRE OCCURED AT 2126 35TH AVENUE IN OAKLAND, CALIFORNIA TO A 4-UNIT APARTMENT BUILDING CAUSING DAMAGE TO 1 UNIT AND THE BASEMENT. GAS METER WAS MELTED DOWN DUE TO FIRE, BURNING GAS THROUGH SERVICE RISER WAS A RESUL | 0
394 | 2006-08-24 | OH | other | UNKNOWN (GUERNSEY COUNTY ) | COLUMBIA GAS OF OHIO | PROPERTY OWNER AT 1439 ELM STREET, CAMBRIDGE, OH WAS USING AN AUGER DEVICE TO CLEAN OUT THE SEWER LATERAL FROM HIS PROPERTY WHEN THE DEVICE PUCTURED A PLASTIC MEDIUM PRESSURE MAIN GAS LINE RESULTING IN A LEAK. WITHIN A SHORT TIME THE LEAK CAUSED AN EXPLO | 719
395 | 2006-08-24 | IA | sabotage | UNKNOWN (POLK COUNTY ) | MIDAMERICAN ENERGY COMPANY | PROPERTY MANAGEMENT COMPANY EMPLOYEES HIT A 2" 60 PSIG GAS MAIN AT 6944 HEMINGWAY ST. WHILE ADDRESSING A PROBLEM WITH SURFACE WATER DRAINAGE. THE PROPERTY MANAGEMENT COMPANY HAD NOT REQUESTED LOCATES. | 1500
396 | 2006-08-30 | OR | sabotage | UNKNOWN (JACKSON COUNTY COUNTY ) | AVISTA UTILITIES | A THIRD PARTY CONTRACTOR WAS GRADING AND CLEARING A RESIDENTIAL BUILDING LOT WITH A TRACKHOE TO PREPARE IT FOR BUILDING CONSTRUCTION AT 173 EVENBROOK. HE STRUCK BOTH THE 2" PE GAS MAIN AND THE POWERLINE THAT WERE INSTALLED IN A JOINT DITCH IN THE PUBLIC | 700
397 | 2006-09-09 | CA | sabotage | UNKNOWN (LOS ANGELES COUNTY ) | SOUTHERN CALIFORNIA GAS COMPANY | HOMEOWNER REMOVING STREE STUMP WITH POWERED EXCAVATING EQUIPMENT PULLED SERVICE, EXERTING PRESSURE ON METER SET ASSEMBLY THAT ULTIMATELY BROKE, RELEASING NATURAL GAS AT HOUSELINE PRESSURE (1/3 PSI.) ESCAPING GAS WAS INGINITED BY NEARBY WATER HEATER, CA | 20
398 | 2006-09-18 | CA | sabotage | UNKNOWN (LOS ANGELES COUNTY ) | SOUTHERN CALIFORNIA GAS COMPANY | CONTRACTOR WAS AUGERING HOLES 10' TO 15' WHEN HE STRUCK 8" STEEL MAIN. AUGER BECAME STUCK IN MAIN, AND LARGE SHORED EXCAVATION HAD TO BE DUG TO RETRIEVE EQUIPMENT. ADJACENT FREEWAY WAS CLOSED AS A RESULT. BECAME REPORTABLE WHEN IT WAS EVIDENT THAT CO | 5000
399 | 2006-09-03 | MD | sabotage | UNKNOWN (WORCESTER COUNTY ) | EASTERN SHORE GAS COMPANY |  | 0
400 | 2006-09-01 | TX | other | UNKNOWN (WILLIAMSON COUNTY ) | ATMOS ENERGY CORPORATION - MID TEXAS DIVISION | A VEHICLE STRUCK A TWO METER MANIFOLD CAUSING A GAS LEAK AND THE ESCAPING GAS IGNITED. | 200
401 | 2006-09-02 | PA | leaks and spills | UNKNOWN (LANCASTER COUNTY ) | UGI UTILITIES, INC. | 04/28/2015: AN INVESTIGATION INTO THE FAILURE INDICATED THAT TWO OF THE FOUR NYLON BOLTS USED TO ATTACH THE TEE TO THE MAIN CRACKED AND ALLOWED GAS TO LEAK. A REMEDIATION PROGRAM WAS LAUNCHED TO INVESTIGATE AND REPAIR SIMILIAR TEES. THIS FINAL REPOR | 0
402 | 2006-07-22 | MS | other | UNKNOWN (WARREN COUNTY ) | MISSISSIPPI RIVER GAS | RAINING ALL DAY, VERY WET CONDITION, CAR LOST CONTROL HIT GAS REGULATOR. | 5259
403 | 2006-10-07 | OH | other | UNKNOWN (WOOD COUNTY COUNTY ) | COLUMBIA GAS OF OHIO | THE CAUSE OF THIS FIRE IS UNDETERMINABLE AND THIS REPORT SHOULD BE CONSIDERED FINAL. THE FIRE WAS INVESTIGATED BY COLUMBIA INVESTIGATORS WHO WERE NOT ABLE TO ASCERTAIN, WITH REASONABLE CERTAINTY, THE CAUSE OR ORIGIN. A NON-JUISDICTIONAL POOL HEATER WI | 55
404 | 2006-09-12 | MO | sabotage | UNKNOWN (SAINT LOUIS COUNTY ) | LACLEDE GAS COMPANY | ADB UTILITY CONTRACTING, A SUBCONTRACTOR FOR AMEREN UE IN PREPARATION FOR INSTALLING AN ELECRIC LINE, WAS BORING FROM 1387 PREMIO DRIVE UNDERNEATH AND ACROSS PREMIO DRIVE TO A PEDESTAL LOCATION IN FRONT OF 1394 PREMIO DRIVE. DURING THE BORING OPERATION, | 0
405 | 2006-09-28 | CA | sabotage | UNKNOWN (SACRAMENTO COUNTY ) | PACIFIC GAS & ELECTRIC COMPANY | AT 0734 HOURS TEICHERT CONSTRUCTION WAS USING AN EARTHMOVER IN ITS QUARRY WHEN IT STRUCK A 12 INCH GAS DISTRIBUTION MAIN CAUSING GAS TO ESCAPE THROUGH A 3 INCH BY 36 INCH RIP. THE DECREASE IN LINE PRESSURE CAUSED LOSS OF SERVICE TO TWO CUSTOMERS, ONE OF | 14563
406 | 2006-10-09 | GA | maintenance | UNKNOWN (PEACH COUNTY ) | FORT VALLEY UTILITY COMMISSION | IN ORDER TO INSTALL A REPAIR CLAMP ON A LEAKING MAIN, TWO EMPLOYEES ENTERED AN EXCAVATED AREA AT THE LEAK SITE AND WORKED THROUGH BLOWING GAS AND DIRT WHILE TWO MORE EMPLOYEES STOOD BY. AFTER COMPLETION OF THE REPAIR, BOTH EMPLOYEES THAT HAD ENTERED THE | 200
407 | 2006-11-13 | AK | other | UNKNOWN (nan COUNTY ) | ENSTAR NATURAL GAS COMPANY | ON NOVEMBER 13, 2006, AT 2314 AST, ENSTAR NATURAL GAS COMPANY WAS NOTIFIED OF A HOUSE FIRE AT LOT 11, LAKE ESTATES, ROSS DRIVE, IN SOLDOTNA ALASKA. THE ORIGIN OF THE FIRE IS UNKNOWN, BUT NATURAL GAS IS NOT BELIEVED TO HAVE CAUSED OR CONTRIBUTED TO THE FI | 50
408 | 2006-10-22 | IL | other | UNKNOWN (nan COUNTY ) | NICOR GAS | STRUCTURE FIRE TRAVELED THROUGH THE HOUSE AND REACHED THE ATTACHED OUTSIDE METER SET CAUSING DAMAGE WHICH RESULTED IN A RELEASE OF GAS. | 100
409 | 2006-10-14 | SD | natural disasters | UNKNOWN (MINNEHAHA COUNTY COUNTY ) | MIDAMERICAN ENERGY COMPANY | MIDAMERICAN ENERGY COMPANY CONSIDERS THIS INCIDENT TO BE A SIGNIFICANT EVENT. A GAS LEAK WAS IGNITED BY A MOTOR VEHICLE STOPPED AT A TRAFFIC SIGNAL RED LIGHT. THE INVESTIGATION DISCOVERED THAT THE 4" CAST IRON MAIN INSTALLED IN 1950 CRACKED CIRCUMFE | 300
410 | 2006-10-27 | MO | maintenance | UNKNOWN (ATCHISON COUNTY ) | EMPIRE DISTRICT GAS CO | COMPANY EMPLOYEE WAS SHUTTING OFF GAS METER FOR CUSTOMER EQUIPMENT MAINTENANCE. THE SHUT OFF VALVE CORE BROKE CAUSING GAS TO ESCAPE. ESCAPING GAS IGNITED CAUSING THE BUILDING TO CATCH ON FIRE AND BURN. | 0
411 | 2006-10-23 | OR | sabotage | UNKNOWN (WASHINGTON COUNTY ) | NW NATURAL GAS COMPANY | A PAINTING CONTRACTOR HIRED BY THE HOMEOWNER AT 16229 S.W. STAHL DRIVE, TIGARD OREGON, BELIEVED THE HOUSE WAS NOT ELECTRICALLY GROUNDED. THE PAINTING CONTRACTOR CONTACTED AN ELECTRICIAN TO INSTALL A GROUNDING ROD. THE ELECTRICIAN DROVE A 3/4 INCH DIAMET | 0
412 | 2006-10-20 | MD | other | UNKNOWN (PRINCE GEORGES COUNTY ) | WASHINGTON GAS | WASHINGTON GAS WAS RESPONDED TO A HOUSE FIRE IN PROGRESS AT 6401 GREENVALE PARKWAY IN RIVERDALE, MARYLAND. UPON ARRIVAL, THE E WAS ENGULFED IN FLAMES. ACCESS TO THE METER, WHICH WAS LOCATED IN THE BASEMENT, COULD NOT BE GAINED WHICH MADE THE RETRIEVAL OR | 0
413 | 2006-10-26 | NY | other | UNKNOWN (MONROE COUNTY ) | ROCHESTER GAS AND ELECTRIC | A RG&E EMPLOYEE WAS INJURED WHILE REMOVING A CAP FROM A 1 1/2" SAV-A-VALVE NIPPLE ON A 2" STEEL MAIN OPERATING AT 60PSI. THE INSERT TO THE SAV-A-VALVE HAD NOT BEEN REPLACED AT A TIME PRIOR TO THIS INCIDENT. FITTINGS IN THE CONDITION ARE TYPICALLY STRAPPE | 0
414 | 2006-11-28 | NM | maintenance | UNKNOWN (LOS ALAMOS COUNTY ) | KSL | ISOLATION VALVE FROM LOCAL TRANSPORTATION COMPANY (PNM) LEAKED BY DURING TIC INS FOR A NEW SERVICES. NO SIGNIFICANT SAFETY ISSUES OCCURED. | 0
415 | 2006-10-10 | CA | sabotage | UNKNOWN (NAPA COUNTY ) | PACIFIC GAS & ELECTRIC COMPANY | A CONTRACTOR WORKING FOR CALTRANS STRUCK A 2" STUB OFF A 6" DFM TRANSMISSION LINE CAUSING THE STUB TO COME AWAY FROM THE WELD CREATING A LEAK. A PG&E STAND-BY PERSON WAS PRESENT. MEDIA WAS PRESENT ON SITE @ 0720 AND CPUC WAS NOTIFIED. COST OF INCIDENT | 10000
416 | 2006-10-26 | TX | other | UNKNOWN (HARRIS COUNTY ) | CENTERPOINT ENERGY | OUTSIDE FORCE DAMAGE TO 3/4'" POLY PIPE BY UNKNOWN PARTY ON UNKNOWN DATE AT 3714 QUITMAN WHERE A FIRE AND EXPLOSION OCCURRED. | 122
417 | 2006-11-11 | NY | sabotage | UNKNOWN (nan COUNTY ) | KEYSPAN ENERGY DELIVERY LONG ISLAND (KEYSPAN GAS EAST CORP, DBA) | ON SATURDAY, NOVEMBER 11, 2006, THE HOUSE AT 21 CARLEY AVE. IN HUNTINGTON SUSTAINED EXTENSIVE DAMAGE FROM A FIRE/EXPLOSION. THE INCIDENT WAS CAUSED BY A CONTRACTOR WHO WAS EXCAVATING WITH A BACKHOE ON THE PROPERTY DURING HOME RENOVATION WORK. THE BACKHO | 0
418 | 2006-10-16 | TX | sabotage | UNKNOWN (COLLIN COUNTY ) | ATMOS ENERGY CORP, MID-TEX DIVISION | THE INVESTIGATION BY GEO-TECHNICAL, MATERIALS, AND MECHANICAL ENGINEERS HAS DETERMINED THAT THE SERVICE LINE NEARLY COMPLETELY PULLED OUT OF THE COMPRESSION COUPLING DUE TO FORCES FROM THE OPERATION OF HEAVY VIBRATORY COMPACTING EQUIPMENT BY A THIRD PARTY | 0
419 | 2006-11-03 | IL | other | UNKNOWN (nan COUNTY ) | THE PEOPLES GAS LIGHT AND COKE COMPANY | ON NOVEMBER 3, 2006 AT 5:39 P.M., THE CHICAGO FIRE DEPARTMENT REPORTED AN EXPLOSION AT 5404 S. AVERS ("PREMISES") TO PEOPLES GAS. IT APPEARS TO HAVE BEEN A NATURAL GAS EXPLOSION. THE INVESTIGATION IN TO THE CAUSE IS COMPLETE. NO GAS LEAKS WERE FOUND OU | 0
420 | 2006-11-20 | IN | sabotage | UNKNOWN (HUNTINGTON COUNTY ) | INDIANA GAS COMPANY, INC. | THIRD PARTY DAMEGED VECTREN 1-INCH PE SERVICE TO 1117 N. JEFFERSON ST., HUNTINGTON, IN BY PIERCING THE SERVICE WITH WHAT APPEARS TO BE A 5/8" ROD THAT WAS TO BE USED FOR GROUNDING PURPOSES. WITHIN APPROXIMATELY 2 MINUTES OF ARRIVAL OF THE VECTREN FIRST R | 0
421 | 2006-12-08 | AL | leaks and spills | UNKNOWN (LAMAR COUNTY ) | NORTHWEST ALABAMA GAS DISTRICT |  | 160
422 | 2006-11-27 | VA | sabotage | UNKNOWN (nan COUNTY ) | VIRGINIA NATURAL GAS | A VIRGINIA NATURAL GAS FIELD SERVICE REPRESENTATIVE (FSR) WAS OVERCOME BY NATURAL GAS WHEN REPAIRING A LEAK CAUSES BY A THIRD PARTY EXCAVATOR DAMAGE. THE FSR REQUIRED OVERNIGHT HOSPITALIZATION. A DESCRIPTION OF THE INCIDENT IS ATTACHED. | 3347
423 | 2006-11-14 | MI | other | UNKNOWN (ISABELLA COUNTY ) | MICHIGAN CONSOLIDATED GAS COMPANY/DTE ENERGY | ON NOVEMBER 14, 2006 AT APPROXIMATELY 2:00 PM A DRIVER LEAVING 204 NORTH ADAMS PREPARED TO BACK A PASSENGER CAR FROM THE DRIVEWAY AT THAT ADDRESS. THE DRIVER REPORTED THAT AFTER SELECTING REVERSE GEAR THE VEHICLE SUDDENLY SPED UNCONTROLLED BACKWARDS ACRO | 50
424 | 2006-11-13 | TX | sabotage | UNKNOWN (FT. BEND COUNTY ) | CENTERPOINT ENERGY | THIRD PARTY DAMAGE TO 4" PLUG VALVE WHILE BACKFILLING WITH TRACKHOE. | 10973
425 | 2006-12-09 | PA | technical failure | UNKNOWN (LEIGH COUNTY COUNTY ) | UGI UTILITIES, INC. | A SUBCONTRACTOR FAILED TO FOLLOW PROCEDURE AND MISTAKENLY REMOVED A PLUG AT THE HEAD OF A MEDIUM PRESSURE SERVICE RELEASING GAS INTO THE RESIDENCE AT 789 MOHAWK STREET ALLENTOWN, PA. THE GAS IGNITED CAUSING AN EXPLOSION, WHICH COLLAPSED THE BUILDING AND | 224
426 | 2006-12-09 | DC | other | UNKNOWN (nan COUNTY ) | WASHINGTON GAS LIGHT COMPANY | UPON ARRIVAL IT WAS DETERMINED THAT AN ILLEGAL CONNECTION HAD BEEN INSTALLED FROM THE OUTLET OF THE RISER TO A METER THAT HAD BEEN STOLEN FROM ANOTHER LOCATION. THE SET WAS THEN PLACED IN TO SERVICE WITHOUT A SERVICE REGULATOR BY AN UNAUTHORIZED INDIVIDU | 1500
427 | 2006-12-03 | CO | sabotage | UNKNOWN (LARIMER COUNTY COUNTY ) | PUBLIC SERVICE COMPANY OF COLORADO | THE LANDOWNER OF THIS COMMERCIAL PROPERTY SET A MODULAR TRAILER OVER THE GAS SERVICE THAT SERVED A RESIDENTIAL HOUSE TOWARDS THE BACK OF HIS PROPERTY. THE ELECTRIC CONTRACTOR HIRED BY THE PROPERTY OWNER DAMAGED THE GAS LINE WHILE TRENCHING IN A NEW ELECT | 250
428 | 2006-12-06 | MD | other | UNKNOWN (MONTGOMERY COUNTY ) | WASHINGTON GAS LIGHT COMPANY | A FIRE IN THE STRUCTURE CAUSED THE COPPER HOUSE LINE TO MELT. THE METER THAT IS LOCATED AT THE RESIDENCE WAS DAMAGED FROM THE FIRE. | 2000
429 | 2007-01-02 | CO | other | UNKNOWN (JEFFERSON COUNTY COUNTY ) | COLORADO NATURAL GAS, INC. | SNOW/ICE SLID OFF OF RESIDENTIAL BUILDING ROOF CAUSING DAMAGE TO METER ASSEMBLY RESULTING IN A NATURAL GAS LEAK. GAS TRAVELED APPROX. 15 FEET TO DIRECT VENT ASSEMBLY FOR FIREPLACE, CAUSING IGNITION AND FLASHBACK TO ORIGIN OF LEAK. INSUING FLAME MELTED M | 40
430 | 2006-12-21 | IL | other | UNKNOWN (COOK COUNTY ) | NICOR GAS | CONTRACTOR, HIRED BY THE HOMEOWNER TO BUILD AN ADDITION ON THE HOUSE, HIT THE SERVICE LINE RISER AND BROKE OFF THE REGULATOR ADJUSTMENT SCREW WHILE BACKING UP A PICK UP TRUCK. GAS MIGRATED INTO THE HOME AND IGNITED. | 100
431 | 2006-12-06 | GA | maintenance | UNKNOWN (DEKALB COUNTY ) | ATLANTA GAS LIGHT COMPANY | A LEAK WAS DETECTED ON PIPE INSTALLED ON THE ON THE ROADWAY BRIDGE ABOVE INTERSTATE 285. A TEMPORARY BYPASS WAS CONSTRUCTED AND THE LEAKING SECTION WAS REMOVED FROM SERVICE. COMPLETION OF A NEW TIE-IN NEARBY WILL ALLOW THE TEMPORARY PIPING TO BE REMOVED | 0
432 | 2006-11-16 | TX | sabotage | UNKNOWN (BOSQUE COUNTY ) | ATMOS ENERGY CORP, MID-TEX DIVISION | AN EXCAVATOR STRUCK A GAS MAIN. | 0
433 | 2006-12-12 | MI | other | UNKNOWN (OAKLAND COUNTY ) | MICHIGAN CONSOLIDATED GAS COMPANY/DTE ENERGY | AT 7:52 AM ON 12-12-06 THERE WAS AN EXPLOSION AND AN ENSUING FIRE THAT COMPLETELY DESTROYED A SINGLE FAMILY DWELLING AT 622 ELIZABETH. AT 16:19, THE CAST IRON MAIN IN FRONT OF 622 ELIZABETH WAS FOUND BROKEN AND WAS REPAIRED WITH A 4”X 12” REPAIR CLAMP. T | 0
434 | 2006-12-26 | IL | technical failure | UNKNOWN (nan COUNTY ) | THE PEOPLES GAS LIGHT AND COKE COMPANY | ON DECEMBER 26, 2006, WHILE PEOPLES GAS WAS REPAIRING A SERVICE LINE INSIDE THE PREMISES OF 3240 N. SACRAMENTO, NATURAL GAS FROM THE SERVICE LINE IGNITED. INVESTIGATION INTO THE SOURCE OF THE IGNITION REVEALED SERVICE PERSONNEL FAILED TO MAKE THE SERVICE | 0
435 | 2007-01-24 | AK | other | UNKNOWN (ANCHORAGE COUNTY ) | ENSTAR NATURAL GAS COMPANY |  | 100
436 | 2006-04-20 | MN | other | UNKNOWN (MILLS COUNTY ) | NEW YORK MILLS MUNICIPAL GAS | GOPHER CHEW ON 1/2" CTS PE SERVICE LINE | 0
437 | 2006-12-13 | TX | sabotage | UNKNOWN (DALLAS COUNTY ) | ATMOS ENERGY CORP, MID-TEX DIVISION | AN EXCAVATOR STRUCK A GAS MAIN. THE LOCATE REQUEST INDICATED TO MARK BOTH SIDES OF THE STREET AND THAT THE AREA TO BE MARKED WAS WHITE LINED. THE WHITE LINE WAS ONLY ON THE OTHER SIDE OF THE STREET AND THAT WAS THE AREA MARKED. THE DAMAGE OCCURERD ON THE | 0
438 | 2007-01-02 | OK | other | UNKNOWN (MARSHALL COUNTY ) | OKLAHOMA NATURAL GAS COMPANY | CITY OF MADILL PUBLIC WORKS EMPLOYEES WERE USING A ROOT CUTTING DEVICE TO CLEAR AN OBSTRUCTION IN THE SEWER LINE NEAR THE INTERSECTION OF S.2ND AVE. AND MCARTHUR ST. THE OBSTRUCTION WAS ONG'S 2" POLY GAS MAIN. THE ROOT CUTTING DEVICE PUNCTURED THE MAIN, | 335
439 | 2007-01-16 | CA | leaks and spills | UNKNOWN (LOS ANGELES COUNTY ) | SOUTHERN CALIFORNIA GAS COMPANY | ON JANUARY 16, 2007, AN EXPLOSION OCCURRED 3552 OPAL, IN THE CITY OF LOS ANGELES AT APPROXIMATELY 0300. THE EXPLOSION DESTROYED THE HOME AT THIS ADDRESS AND CAUSED MINOR DAMAGE TO TWO ADJACENT HOMES. THE DESTROYED HOME WAS UNOCCUPIED, AND NO INJURIES RE | 100
440 | 2007-01-11 | CA | sabotage | UNKNOWN (SONOMA COUNTY ) | PACIFIC GAS & ELECTRIC CO. | WHILE INSTALLING A SEWER LINE AT THE INTERSECTION OF SNYDER LANE AND EAST COTATI AVE IN ROHNERT PARK, THE CONTRATCOR DUG INTO PG&E'8-INCH STEEL DISTRIBUTION LINE. THE TRAFFIC WAS RE-ROUTED AND AREA WAS CORDONED OFF BY THE POLICE. THE AREA WAS MADE SAFE | 0
441 | 2007-02-02 | CO | leaks and spills | UNKNOWN (GILPIN COUNTY ) | COLORADO NATURAL GAS INC. | EXCESSIVE SNOWS FROM 2 LOCAL BLIZZARDS IN DECEMBER 2006 AND 1 IN JANUARY 2007. ALSO CONTRIBUTING TO THE INCIDENT WAS RECENT HIGH WINDS AND BLOWING SNOW RESULTED IN ACCUMULATING 6 + FEET OF HEAVY SNOW ON THE NATURAL GAS METER ADJACENT TO THE REAR OF HOME. | 82
442 | 2007-01-01 | TX | sabotage | UNKNOWN (TARRANT COUNTY ) | ATMOS ENERGY CORP, MID-TEX DIVISION | 2 INCH STEEL MAIN WAS DAMAGED BY A THIRD-PARTY CONTRACTOR. THIRD-PARTY CONTRACTOR FAILED TO NOTIFY THE OPERATOR OF THE DAMAGE, RESULTING IN THE INCIDENT. | 0
443 | 2007-01-20 | CO | leaks and spills | UNKNOWN (DENVER COUNTY ) | PUBLIC SERVICE COMPANY OF COLORADO | FOUND 3/4" CAB SERVICE PULLED OUT OF 3/4 X 3/4" COMPRESSION COUPLING. CREW EXCAVATED AND CUT OFF CAB SERVICE BEHIND CURB IN EFFORTS TO SHUT OFF GAS FOR LOCAL FIRE DEPARTMENT. THE SEPARATION OF THE CAB FROM THE COMPRESSION COUPLING MAY HAVE OCCURRED POST | 550
444 | 2007-01-04 | MO | other | UNKNOWN (SAINT LOUIS COUNTY ) | LACLEDE GAS COMPANY | AN AUTO ACCIDENT CAUSED ENERGIZED POWER LINES TO CONTACT A METALLIC STREET SIGHN WHICH WAS INSTALLED IN POXIMITY TO AN UNDERGROUND FOUR-INCH NATURAL GAS MAIN. AS A RESULT OF THE POWER LINE CONTACT, ELECTRICAL ARCING BETWEEN THE SIGN POST AND THE GAS MAIN | 0
445 | 2007-01-09 | TX | sabotage | UNKNOWN (BASTROP COUNTY ) | CENTERPOINT ENERGY | CITY OF SMITHVILLE WATER & SEWER DEPARTMENT DAMAGED A 1" STEEL SERVICE WITH A BACKHOE. THE ESCAPING GAS IGNITED AND THE HOUSE CAUGHT FIRE. | 42
446 | 2007-01-23 | OK | maintenance | UNKNOWN (TULSA COUNTY ) | OKLAHOMA NATURAL GAS COMPANY | 1" STEEL THREADS ON SERVICE RISER LEAKING IN COLLAR BELOW GROUND. SERVICE RISER WAS PUSHED OVER AND BURIED FOR UNKNOWN YEARS. OPERATIONS PERSONNEL DID NOT KNOW THE SERVICE WAS IN PLACE BECAUSE THE SERVICES OF THAT VINTAGE WERE NOT MAPPED. POSSIBLE PRE- | 0
447 | 2007-02-01 | IL | other | UNKNOWN (nan COUNTY ) | NICOR GAS | PERSON WORKING IN THE BASEMENT OF THE STRUCTURE ACCIDENTALLY STARTED THE FIRE. INTENSITY OF THE FIRE CAUSED THE STRUCTURE TO EVENTUALLY COLLAPSE. THE STRUCTURE FIRE REACHED THE METER SET AND CAUSED IT TO MELT, THUS CAUSING A RELEASE OF NATURAL GAS. | 50
448 | 2007-02-10 | MI | maintenance | UNKNOWN (GENESEE COUNTY ) | CONSUMERS ENERGY | THE FINAL INVESTIGATION DETERMINED THAT THE CAUSE OF THE INCIDENT WAS A CUSOTMER OWNED FUEL LINE FAILURE ON NONJURISDICTIONAL PIPING. THIS REPORT CAN BE ELIMINEATED FROM THE DOT DATABASE. . | 100
449 | 2007-02-05 | IL | other | UNKNOWN (COOK COUNTY ) | NICOR GAS | GREASE FIRE IN KITCHEN MIGRATED THROUGH THE STRUCTURE AND REACHED THE METER SET, CAUSING DAMAGE WHICH LED TO THE RELEASE OF GAS. | 100
450 | 2007-02-04 | CA | sabotage | UNKNOWN (SANTA CLARA COUNTY ) | PACIFIC GAS AND ELECTRIC COMPANY | HOMEOWNER DUG INTO A GAS SERVICE WITH A DIGGING BAR AND PUNCTURED THE GAS SERVICE. GAS IGNITED AND A HOUSE FIRE TO THE HOMEOWNERS HOME AND THE ADJACENT HOME RESULTED. GAS FLOW WAS STOPPED AT THE MAIN. GAS SERVICE TO BOTH HOUSES IS DISCONTINUED UNTIL REPAI | 50
451 | 2007-02-28 | NY | leaks and spills | UNKNOWN (STEUBEN COUNTY ) | CORNING NATURAL GAS CORPORATION | TWO INCH STEEL MAIN WAS ASSEMBLED IN 1948 WITH THREADED COUPLINGS. FROST HEAVE CAUSED THE MAIN TO CRACK AT THE POINT WHERE THE MAIN SCREWED INTO THE COUPLING. | 0
452 | 2007-01-25 | MI | sabotage | UNKNOWN (WAYNE COUNTY ) | MICHIGAN CONSOLIDATED GAS COMPANY/DTE ENERGY | AN EXCAVATOR INSTALLING WATER MAIN FAILED TO CONFIRM THE LOCATION OF A 12" CAST IRON MAIN PRIOR TO DIGGING. THE 12" MAIN WAS BROKEN BY THE EXCAVATOR'S BACKHOE. | 38287
453 | 2007-01-25 | TX | sabotage | UNKNOWN (FT. BEND COUNTY ) | CENTERPOINT ENERGY | RAIN CAUSED A DIFFEREENTIAL SETTLEMENT OF CONSTRUCTION MATERIALS, CAUSING DRESSER STYLE COUPLING TO PARTIALLY SEPARATE. NATURAL GAS MIGRATED FROM THE SEPARATION TO THE HOUSE AND FOUND IGNITION SOURCE RESULTING IN EXPLOSION AND FIRE. | 1000
454 | 2007-01-13 | IL | other | UNKNOWN (MADISON COUNTY ) | AMERENCIPS | AMERENCIPS WAS MOTIFIED OF A HOUSE FIRE ON JANUARY 13, 2007 AT 0926 ARRIVED AT THE SCENE AT 0936. THE FIRE DEPARTMENT SUSPECTED THAT GAS IGNITIONWAS THE CAUSE OF THE FIRE THAT FAILED CONTROL VALVE ON THE WATER HEATER. GAS SERVICE TO THE STRUCTURE WAS DI | 0
455 | 2007-01-09 | TX | sabotage | UNKNOWN (DALLAS COUNTY ) | ATMOST ENERGY CORP, MID-TEX DIVISION | DURING A THIRD-PARTY DAMAGE EVENT, OUR 1 _ INCH STEEL SERVICE LINE WAS PULLED FROM A COMPRESSION COUPLING IN THE ALLEY BEHIND 715 E. CELESTE, GARLAND, TEXAS. THE OCCUPANTS OF 715 E. CELESTE WERE EVACUATED, AND A STRUCTURE FIRE RESULTED DUE TO THE THIRD-PA | 0
456 | 2007-01-11 | TX | natural disasters | UNKNOWN (TRAVIS COUNTY ) | TEXAS GAS SERVICE COMPANY | INVESTIGATION DETERMINED THE LEAKAGE WAS CAUSED BY A 30" LONG BY .125" WIDE FAILURE OF A WELD. INSTALLED A WELD SLEEVE OVER THE ENTIRE WELD TO MAKE A PERMANET REPAIR. | 31195
457 | 2007-02-17 | WI | other | UNKNOWN (PIERCE COUNTY ) | ST. CROIX VALLEY NATURAL GAS CO. | A NORTH-BOUND 1991 GMC SIERRA PICKUP TRUCK TRAVELING AT AN UNKNOW RATE OF SPEED LEFT THE ROAD AND TRAVELED ACROSS A HOMEOWNER'S YARD TO IMPACT THE SIDE OF THE HOUSE. THE POSTED SPEED IS 25 MILES PER HOUR. THE HOUSE SITS APPROXIMATELY 45 FEET OFF THE ROA | 225
458 | 2007-01-22 | OH | sabotage | UNKNOWN (MEDINA COUNTY ) | COLUMBIA GAS OF OHIO, INC. | THIRD PARTY CONTRACTOR, INSTALLING UTILITY POLES FOR A TRAFFIC SIGNALIZATION PROJECT, AUGURED INTO OPERATOR'S 6" PLASTIC GAS MAIN CAUSING A RELEASE AND IGNITION OF NATURAL GAS. THE THIRD PARTY CONTRACTOR FAILED TO PLACE A CALL TO THE OHIO UTILITIES PROTE | 573
459 | 2007-02-01 | AL | other | UNKNOWN (JEFFERSON COUNTY ) | ALABAMA GAS CORPORATION | THE LOCAL FIRE DEPARTMENT HAS REPORTED THAT THE INCIDENT RESULTED FROM PIPE RUPTURE AT A LOCATION ALONG THE SERVICE LINE WHERE AN IMPROPER REPAIR WITH NON-STANDARD FITTINGS HAS BEEN MADE BY A THIRD PARTY NOT AUTHORIZED BY ALABAMA GAS CORPORATION. | 0
460 | 2007-02-06 | UT | sabotage | UNKNOWN (UTAH COUNTY ) | QUESTAR GAS COMPANY | AT SOME POINT PRIOR TO 13:00 HOURS ON FEBRUARY 6, 2007 (AND FOR THE SECOND TIME IN TWO DAYS) S&E CABLE FAILED TO EXCAVATE WITH HAND TOOLS A PROPERLY MARKED NATURAL GAS LINE IN VIOLATION OF UTAH CODE ANNOTATED §54-8A-2 ET. SEQ. AS A RESULT, S&E CABLE STRU | 46
461 | 2007-02-06 | MD | other | UNKNOWN (MONTGOMERY COUNTY ) | WASHINGTON GAS | A TWO-INCH ROCKWELL 461-57S DISTRIBUTION REGULATOR WAS UNABLE TO SUPPLY THE GAS DEMANDED ON AN EXTREMELY COLD DAY, DUE TO A 40-FOOT TEMPORARY DISCONNECT OF 4" PLASTIC PIPE. THE 40-FOOT SECTION OF PIPE PROVIDED AN ADDITIONAL FEED, WAS TEMPORARILY DISCONNE | 0
462 | 2007-02-06 | OH | other | UNKNOWN (LORAIN COUNTY COUNTY ) | COUMBIA GAS OF OHIO | ORIGIN OF FIRE STILL UNDER INVESTIGATION. WILL PROVIDE AN UPDATE ON SUPPLEMENTAL REPORT. | 112
463 | 2007-02-19 | PA | other | UNKNOWN (ALLEGHENY COUNTY ) | COLUMBIA GAS OF PENNSYLVANIA INC. | IN PITTSBURGH, ALLEGHENY COUNTY, PENNSYLVANIA, WHILE CONTRACTOR EMPLOYEE WAS ATTEMPTING TO COMPLETE AN ABANDONMENT OF A 1 1/4 INCH SERVICE LINE AT 342 CLIMAX STREET, WA OVER COME BY NATURAL GAS. EMPLOYEE SPENT ONE NIGHT IN THE HOSPITAL FOR OBSERVATION. | 0
464 | 2007-03-23 | AK | other | UNKNOWN (KENAI PENINSULA BOROUGH COUNTY ) | ENSTAR NATURAL GAS COMPANY | ENSTAR WAS NOTIFIED OF A STRUCTURE FIRE AT LOT 9, RAYMOND BURTON SUBDIVISION, KASILOF, ALASKA, AT 0017 ON 3/23/07. A SERVICE TECH WAS DISPATCHED. ENSTAR'S METER AND RISER WERE ON FIRE. A DISTRIBUTION CREW WAS DISPATCHED TO DIG UP AND PINCH OFF THE LINE | 100
465 | 2007-03-15 | AZ | sabotage | UNKNOWN (MOHAVE COUNTY ) | UNISOURCE ENERGY SERVICES INC. | ON MARCH 15, 2007 A GRADER OWNED BY D&R EXCAVATION WAS CREATING DEEP BAR BAR DITCHS ON A DIRT ROAD LEADING TO THEIR GRAVEL PIT EAST OF KINGMAN ARIZONA. THE GRADER WAS BEING OPERATED BY D&R EXCAVATION EMPLOYEE GENE WEISS WITHOUT CALLING IN THE STATE'S ONE | 16656
466 | 2007-02-17 | PA | natural disasters | UNKNOWN (LEHIGH COUNTY COUNTY ) | UGI UTILITIES, INC. | A LEAKING COPPER WATER SERVICE TO 1536 HOTTLE AVENUE, BETHLEHM, PA, UNDERMINED THE GAS IN FRONT OF 1534 HOTTLE AVE. THE SOIL BENEATH THE MAIN SUBSIDED, RESULTING IN A CIRCUMFERENTIAL SEPARATION/FRACTURE IN THE 4" CAST IRON MAIN. GAS MIGRATED INTO 1534 HO | 0
467 | 2007-02-28 | PA | leaks and spills | UNKNOWN (YORK COUNTY ) | COLUMBIA GAS OF PENNSYLVANIA INC. | IN SPRY, YORK COUNTY, PENNSYLVANIA, AN EXPLOSION OCCURRED AT 2433 S. QUEEN STREET. LEAKAGE WAS DETECTED IN THE AREA OF MEMORY LANE AND S. QUEEN STREET, YORK PA. CRITICAL VALVE CY-1918 WAS SHUT OFF AT 12:56 PM. THE 2 INCH BARE STEEL MAIN WAS EXPOSED AT THE | 0
468 | 2007-03-14 | AZ | sabotage | UNKNOWN (PINAL COUNTY ) | CITY OF MESA COM | ON MARCH 14, 2007, SUNDT CONSTRUCTION HIT AND DAMAGED MESA¿S 4¿ STEEL HIGH PRESSURE GAS LINE AT NORTH IRONWOOD DRIVE AND EAST WESTBROOK ROAD. ON MARCH 13, 2007, CITY OF MESA PERSONNEL MET WITH, SUNDT CONSTRUCTION STAFF, TO DISCUSS PENDING EXCAVATION. SU | 743
469 | 2007-03-14 | MD | other | UNKNOWN (BALTIMORE COUNTY ) | BALTIMORE GAS & ELECTRIC COMPANY | ACCORDING TO FIRE INVESTIGATION BUREAU #2 CHIEF MARTIN FOR THE BALTIMORE CITY FIRE DEPARTMENT THAT THE POINT OF FIRE ORIGINATION IS UNKNOWN DUE TO THE EXTENT OF THE DAMAGE TO THE HOUSE. THE F.I.B. REPORTS THAT THE FIRE IMPINGED ON THE METER INSTALLATION | 0
470 | 2007-03-16 | MD | maintenance | UNKNOWN (PRINCE GEORGES COUNTY ) | BALTIMORE GAS & ELECTRIC COMPANY | FOUND 9155 HITCHING-POST LA UNIT C DAMAGED BY EXPLOSION AND FIRE. DURING THE INVESTIGATION, ICE WAS FOUND ON THE REGULATOR BODY SUPPLING 9155 HITCHING-POST LA UNIT C AND IT WAS FOUND THAT THE REGULATOR VENT WAS PAINTED OVER. ELEVATED PRESSURE WAS SUPPLE | 0
471 | 2007-03-06 | NM | sabotage | UNKNOWN (BERNALILLO COUNTY ) | PUBLIC SERVICE COMPANY OF NEW MEXICO | CONTRACTOR HIT GAS LINE WHILE CLEANING ARROYO BEHIND CONTRACTOR'S BUILDING. | 57544
472 | 2007-03-08 | SD | sabotage | UNKNOWN (DAVISION COUNTY ) | NORTHWESTERN ENERGY | AT 11:31 AM ON MARCH 8, 2007 A HOME AT 1612 BRIDLE DRIVE IN MITCHELL, SD EXPLODED. IN ADDITION TO 1612 BRIDLE DRIVE RESIDENCE THE EXPLOSION ALSO DAMAGED THE RESIDENCES AT 1608 AND 1616 BRIDLE DRIVE. A NORTHWESTERN EMPLOYEE READING METERS IN THE AREA HEARD | 362
473 | 2007-04-11 | AK | other | UNKNOWN (MATANUSKA SUSITNA BOROUGH COUNTY ) | ENSTAR NATURAL GAS COMPANY | ENSTAR WAS NOTIFIED OF A STRUCTURE FIRE AT 9120 N. SUN VALLEY DR, PALMER, ALASKA AT 0220 ON 4/11/2007. THE FIRE SEVERELY DAMAGED THE STRUCTURE AND BURNED ENSTAR'S REGULATOR AND METER CAUSING A RELEASE OF NATURAL GAS. FIRE DEPARTMENT PERSONNEL SHUT OFF T | 100
474 | 2007-03-17 | TX | natural disasters | UNKNOWN (nan COUNTY ) | CPS ENERGY | GAS IGNITION OCCURED WHEN THE CUSTOMER AT 5618 LAKEBEND WEST FLIPPED A SWITCH IN THE BATHROOM. AFTER INVESTIGATION, IT IS BELIEVED THAT THE SOURCE OF GAS ORIGINATED FROM A FAILURE AT THE THREADED END OF THE 1" STEEL SERVICE OF 5618 LAKEBEND WEST, WHERE I | 0
475 | 2007-03-06 | TX | sabotage | UNKNOWN (EL PASO COUNTY ) | TEXAS GAS SERVICE COMPANY | 2" POLYETHYLENE SERVICE LINE DAMAGED BY A TRENCHER. NO LINE LOCATES WERE REQUESTED. MEDIA WAS ON SITE. 350 PEOPLE WERE EVACUATED. | 2315
476 | 2007-02-21 | TX | sabotage | UNKNOWN (DALLAS COUNTY ) | ATMOS ENERGY CORP. MID-TEX DIVISION | AN EXCAVATOR STRUCK A SERVICE LINE CAUSING A LEAK. | 0
477 | 2007-02-26 | TX | sabotage | UNKNOWN (DALLAS COUNTY ) | ATMOS ENERGY CORP. MID-TEX DIVISION | AN EXCAVATOR STRUCK A MAIN, CAUSING A LEAK. | 0
478 | 2007-04-09 | MS | sabotage | UNKNOWN (MADISON COUNTY ) | ATMOS ENERGY CORPORATION - MISSISSIPPI DIVISION | A FOUNDATION REPAIR CONTRACTOR FOR THE HOMEOWNER DUG A HOLE WITH A TILE SPADE ADJACENT TO THE CONCRETE SLAB AND NEAR THE METER SET. THE SPADE DAMAGED THE SERVICE LINE CAUSING NATURAL GAS TO LEAK. IT IS REPORTED THAT DUE TO THE NOISE OF THE BLOWING GAS, TH | 500
479 | 2007-04-08 | MT | natural disasters | UNKNOWN (SILVER BOW COUNTY ) | NORTHWESTERN ENERGY | CHANGES IN EXTERNAL ENVIRONMENT AND APPLICATION OF UNKNOWN ADDITIONAL LOADING. 01/27/2014 - THIS IS NORTHWESTERN ENERGY'S FINAL REPORT FOR THIS INCIDENT. SINCE THE LAST UPDATE METALLURGY TESTING HAS BEEN COMPLETED. THE REPORT HAS BEEN SUBMITTED TO TH | 0
480 | 2007-04-01 | TX | leaks and spills | UNKNOWN (nan COUNTY ) | CENTERPOINT ENERGY | 1 1/4" X 1/2" PLASTIC SERVICE TEE PARTIALLY SEPARATED FROM 1 1/4" POLY MAIN LINE IN REAR EASEMENT OF 10735 LAKEWOOD OAKS DR, ESCAPING GAS MIGRATED TO 10727 LAKEWOOD OAKS DR. WHERE A FIRE/EXPLOSION OCCURED. | 100
481 | 2007-04-06 | ME | maintenance | UNKNOWN (YORK COUNTY ) | NORTHERN UTILITIES | AT APPROXIMATELY 2:47 A.M. ON 4/6/07 BLOWING GAS WAS REPORTED BY THE RACO FIRE DEPARTMENT AT AN APARTMENT COMPLEX IN THE VICINITY OF THE MOODY ROAD POINT OF DELIVERY OFF OF THE GRANITE STATE TRANSMISSION PIPELINE. EVACUATIONS OCCURED AT 34 OCEAN PARK AND | 5000
482 | 2007-04-12 | OR | sabotage | UNKNOWN (MARION COUNTY ) | NW NATURAL GAS COMPANY | A CONTRACTOR WAS OPERATING AN INDUSTRIAL TILLER TO LOOSEN SOIL IN ORDER TO LOWER THE GRADE. THE CONTRACTOR STRUCK NW NATURAL'S 6-INCH DIAMETER PE 2406/SD11.5 POLYETHYLENE MAIN RESULTING IN THE RELEASE AND IGNITION OF NATURAL GAS. THE TILLER WAS INVOLVED | 460
483 | 2004-08-22 | NE | other | UNKNOWN (DOUGLAS COUNTY ) | METROPOLITAN UTILITIES DISTRICT | THROUGH OUR INVESTIGATION IT WAS DISCOVERED THAT THE ORIGIN OF THE FIRE CAME FROM A TRASH CAS LOCATED AT 7515 NORTH 155TH TERRACE WHICH WAS IS THE DWELLING NORTH OF 7509 NORTH 155TH TERRACE. THE FIRE IN THE TRASH CAN THEN SPREAD TO THE NEIGHBORING HOME AN | 0
484 | 2007-04-19 | OR | sabotage | UNKNOWN (CLACKAMAS COUNTY ) | NW NATURAL GAS COMPANY | INVESTIGATION COMPLETE A CONTRACTOR WAS DIRECTIONAL DRILLING TO INSTALL FIBER OPTIC TELEPHONE CABLE AND STRUCK NW NATURAL'S 2-INCH DIAMETER PE 2406 POLYETHYLENE MAIN. LOCATES WERE PRESENT AND ACCURATE. AN UNDERGROUND RELEASE OF NATURAL GAS OCCURRED. T | 180
485 | 2007-04-26 | PA | other | UNKNOWN (ALLEGHENY COUNTY ) | DOMINIONPEOPLES | A 2" BRANCH PIPE NIPPLE SNAPPED OFF AN 8" STEEL MAINLINE CAUSING A LEAK. AN ELECTRICAL SHORT IN OVERHEAD LINES IGNITED THE ESCAPING GAS, RESULTING IN A FIRE. DOMINION-PEOPLES GAS COMPANY WAS CONDUCTING A ROUTINE LEAK REPAIR ON AN 8" MAINLINE. THE EL | 500
486 | 2004-06-29 | NE | other | UNKNOWN (DOUGLAS COUNTY ) | METROPOLITAN UTILITIES DISTRICT |  | 3500
487 | 2007-04-23 | VA | other | UNKNOWN (FAIRFAX COUNTY ) | WASHINGTON GAS LIGHT COMPANY | ACCORDING TO FAIRFAX FIRE MARSHAL'S REPORT 20071132600, THIS WAS AN ACCIDENTAL FIRE RESULTING FROM AN UNDETERMINED EVENT THAT CAUSED A PROPANE GRILL LOCATED ON THE REAR DECK OF 6400 DAKINE CIRCLE TO IGNITE THE COMBUSTIBLE VINYL SIDING AND SPREAD TO ADJACE | 100
488 | 2007-04-24 | VA | other | UNKNOWN (LOUDOUN COUNTY ) | WASHINGTON GAS LIGHT COMPANY | UPDATED BY PHMSA ON 1/13/2016 PER OPERATOR'S MARK UP (PART F - APPARENT CAUSE; AND PART I NARRATIVE). WASHINGTON GAS PERSONNEL RESPONDED TO A REPORT OF GAS INVOLVED FIRE ON 4/24/2007 AT 43655 PIERPOINT TERRACE, LEESBURG, VA. THE THREE STORY WOOD FRA | 100
489 | 2007-05-03 | TX | sabotage | UNKNOWN (TRAVIS COUNTY ) | TEXAS COMMUNITY PROPANE, LTD. | PLUMBING COMPANY USING ROCKSAW INSTALL WATER LINES HIT SERVICE LINE AND CAUSED DAMAGE. | 144
490 | 2007-05-18 | MN | other | UNKNOWN (OLMSTED COUNTY ) | MINNESOTA ENERGY RESOURCE CORPORATION | AT APPROXIMATELY 0430 ON THE 18TH OF MAY, 2007 A DRIVER LOST CONTROL OF HER CAR. THE VEHICLE TOPPLED A UTILITY POLE, HIT A 3¿ X 4¿ ELECTRICAL TRANSFORMER AND THEN THE GAS SERVICE AND METER. THE VEHICLE CLIPPED THE SERVICE LINE AT THE BUILDING, IGNITING TH | 107
491 | 2007-05-01 | TX | sabotage | UNKNOWN (EL PASO COUNTY ) | TEXAS GAS SERVICE COMPANY | EXCAVATOR INSTALLING A IRRIGATION SYSTEM HIT 1" POLY SERVICE LINE. REPAIRS WERE MADE BY REPLACING A TWO FOOT SECTION OF POLY PIPE. 600 PEOPLE WERE EVACUATED AND MEDIA WAS ON SITE. | 261
492 | 2007-04-04 | MD | other | UNKNOWN (WORCESTER COUNTY ) | EASTERN SHORE GAS COMPANY |  | 0
493 | 2007-05-14 | IL | other | UNKNOWN (COOK COUNTY ) | NORTHERN ILLINOIS GAS D/B/A NICOR GAS | A CIGARETTE IGNITED LANDSCAPING WOOD CHIPS NEAR THE LOCATION OF THE METER SET. THE FIRE DAMAGED THE METER SET, THUS CAUSING A RELEASE OF NATURAL GAS INTO THE ATMOSPHERE. | 100
494 | 2007-05-15 | VA | other | UNKNOWN (PRINCE WILLIAM COUNTY ) | WASHINGTON GAS LIGHT COMPANY | WASHINGTON GAS (WGL) RESPONDED TO A WORKING HOUSE FIRE AT THE REQUEST OF THE PRINCE WILLIAM COUNTY FIRE DEPARTMENT TO TURN THE GAS OFF. WGL INTERVIEWED THE HOMEOWNER, LARRY STROUD, AND FOUND THAT THE FIRE WAS FIRST NOTICED ON THE FRONT PORCH AND LATER CO | 100
495 | 2007-05-03 | TX | sabotage | UNKNOWN (DALLAS COUNTY ) | ATMOS ENERGY CORP., MID-TEX DIVISION | AN EXCAVATOR STRUCK A SERVICE LINE, CAUSING A LEAK. | 0
496 | 2007-05-02 | TX | sabotage | UNKNOWN (TARRANT COUNTY ) | ATMOS ENERGY CORP., MID-TEX DIVISION | AN EXCAVATOR STRUCK A MAIN, CAUSING A LEAK. | 0
497 | 2007-05-16 | CA | other | UNKNOWN (KERN COUNTY ) | SOUTHERN CALIFORNIA GAS COMPANY | ON MAY 16, 2007 A PIPELINE CONTRACTOR WORKING FOR SOUTHERN CALIFORNIA GAS COMPANY INSTALLED A 1¿ PE BYPASS SYSTEM ON A 3¿ PE MAIN, USING MECHANICAL TAPPING TEE FITTINGS. AFTER COMPLETION OF STAND-UP TEST, AND TAPPING OF TEES, 1¿ PIPE PULLED OUT OF TEE TH | 1000
498 | 2007-05-17 | TN | other | UNKNOWN (DAVIDSON COUNTY ) | PIEDMONT NATURAL GAS | 02/10/2010: AFTER THE FIRE ON MAY 17, 2007, PIEDMONT HIRED OUTSIDE EXPERTS TO INVESTIGATE THE CAUSE OF THE FIRE. PRIOR TO CONCLUSION OF THE EXPERT'S INVESTIGATION, PIEDMONT SETTLED SEVERAL PERSONAL INJURY AND PROPERTY DAMAGE CLAIMS WITHOUT ADMISSION OF | 0
499 | 2007-05-18 | VA | other | UNKNOWN (FAIRFAX COUNTY ) | WASHINGTON GAS LIGHT COMPANY | ACCORDING TO FAIRFAX FIRE MARSHAL'S REPORT 20071380315, THIS WAS AN ACCIDENTAL FIRE WHICH STARTED ON THE REAR DECK OF THE HOUSE AND LATER ENTERED THE HOUSE THROUGH THE WINDOWS, SOFFIT AND ROOF LINE. WASHINGTON GAS FACILITIES WERE CONSUMED BY THE FIRE AND | 100
500 | 2007-05-17 | MA | other | UNKNOWN (NORFOLK COUNTY ) | BAY STATE GAS COMPANY | DISTRIBUTION CREW WAS WORKING ON A MAIN TIE-IN. FIRE OCCURED IN THE OPEN DITCH. ONE EMPLOYEE RECEIVED BURNS WHICH REQUIRED INPATIENT HOSPITALIZATION. | 8064
501 | 2007-05-10 | TX | sabotage | UNKNOWN (DENTON COUNTY ) | ATMOS ENERGY CORP., MID-TEX DIVISION | AN EXCAVATOR STRUCK A MAIN, CAUSING A LEAK. | 0
502 | 2007-05-24 | IL | other | UNKNOWN (COOK COUNTY ) | NICOR GAS | ARSON FIRE ENGULFED STRUCTURE. FIRE THEN PROGRESSED TO THE METER SET THUS CAUSING THE DAMAGE TO THE METER SET AND THE SUBSEQUENT RELEASE OF GAS. NOTE: THIS INCIDENT WAS ORIGINALLY REPORTED UNDER 15549 LATROP, HARVEY. | 500
503 | 2007-06-07 | MD | other | UNKNOWN (PRINCE GEORGE'S COUNTY ) | WASHINGTON GAS LIGHT COMPANY | WASHINGTON GAS RESPONDED TO A HOUSE FIRE AT THE REQUEST OF THE PRINCE GEORGE'S FIRE BOARD. THE GAS WAS OFF UPON THE ARRIVAL OF THE WGL SERVICE MAN, HOWEVER, DEBRIS AND ASHES FROM THE FIRE ACCUMULATED AROUND THE SERVICE RISER CAUSING A RELEASE. THE SERVI | 100
504 | 2007-05-29 | TX | other | UNKNOWN (JOHNSON COUNTY ) | ATMOS ENERGY CORP., MID-TEX DIVISION | THE CAUSE OF THIS EVENT APPEARS TO BE THE RESULT OF A COMBINATION OF FACTORS THAT WAS NOT READILY FORESEEABLE. DURING ATMOS ENERGY CORPORATION INVESTIGATION SUBSEQUENT TO THE INCIDENT, THREE LEAKS WERE FOUND AND REPAIRED ON WOODARD AVENUE. HOWEVER, THERE | 0
505 | 2007-06-01 | GA | sabotage | UNKNOWN (DOUGLAS COUNTY ) | ATLANTA GAS LIGHT | AN EXTERMINATING COMPANY EMPLOYEE DRILLED INTO A PLASTIC SERVICE WITH A GASOLINE ENGINE DRIVEN AUGER WHILE MAKING HOLES IN THE GROUND FOR INSTALLATION OF TERMITE BAITS. THE ESCAPING GAS IGNITED AND THE EXTERMINATING EMPLOYEE'S FACE WAS BURNED. HE WAS SU | 0
506 | 2007-07-11 | TX | sabotage | UNKNOWN (DENTON COUNTY ) | COSERV GAS LTD | EXCAVATOR DAMAGED A 2" POLY MAIN WHILE MAKING AN ELECTRICAL CONNECTION TO A NEW STRUCTURE. EXCAVATOR STATED THAT THEY KNEW WHERE THE LINES WERE AND DIDN'T CALL FOR LOCATES. | 535
507 | 2007-06-23 | VA | other | UNKNOWN (FAIRFAX COUNTY ) | WASHINGTON GAS LIGHT COMPANY | WASHINGTON GAS RESPONDED TO A FIRE AT THE REQUEST OF THE FAIRFAX COUNTY FIRE DEPARTMENT TO TURN THE GAS OFF. ACCORDING TO A PRESS RELEASE FROM THE FAIRFAX COUNTY FIRE AND RESCUE DEPARTMENT, ¿MOLOTOV COCKTAILS WERE THROWN AND EXPLODED IN THE REAR OF THE S | 100
508 | 2007-06-29 | CA | sabotage | UNKNOWN (SACRAMENTO COUNTY ) | PACIFIC GAS & ELECTRIC | WHILE TILLING IN LIME INTO THE SOIL TO CREATE A STRUCTURAL ROAD BASE MATERIAL, A PRIVATE SOIL STABILIZATION COMPANY HIT PACIFIC GAS & ELECTRIC'S 4-INCH DIAMETER HIGH PRESSURE PLASTIC DISTRIBUTION MAIN. A SUBSEQUENT FIRE WHICH DESTROYED THE CONTRACTOR'S C | 1000
509 | 2007-06-19 | IL | sabotage | UNKNOWN (PEORIA COUNTY ) | AMERENCILCO | The homeowner and person who was injured had just purchased a gasoline powered auger. the were augering a hole within 2 to 3 feet of the gas meter and had not called JULIE (1-call) to request a locate. They augered through a 1/2" PE service installed in | 300
510 | 2007-06-24 | CA | other | UNKNOWN (EL DORADE COUNTY COUNTY ) | SOUTHWEST GAS CORPORATION | A FOREST FIRE, LATER NAMED THE ANGORA FIRE, BEGAN AROUND 14:00 ON JUNE 24TH IN THE AREA WEST OF THE TAHOE PARADISE SUBDIVISION NEAR SOUTH LAKE TAHOE. SOUTHWEST GAS WAS CONTACTED BY THE LAKE VALLEY FIRE DEPARTMENT AT APPROXIMATELY 16:00 TO ASSIST BY SHUTT | 105
511 | 2007-06-23 | LA | sabotage | UNKNOWN (ORLEANS COUNTY ) | ENTERGY NEW ORLEANS, INC - GAS DISTRIBUTION BUSINESS | ENTERGY GAS OPERATION WAS CONTACTED AT ABOUT 1300 HOURS BY OWNER OF 6024 ARGONNE BLVD INDICATING THERE HAD BEEN AN EXPLOSION AT HIS RESIDENCE AT 0630 HRS. HOMEOWNER CONTACTED PLUMBER PRIOR TO CONTACTING ENTERGY BECAUSE HE INITIALLY THOUGHT IT WAS A PROBL | 250
512 | 2007-07-05 | VA | other | UNKNOWN (FAIRFAX COUNTY ) | WASHINGTON GAS LIGHT COMPANY | WASHINGTON GAS RESPONDED TO A FIRE AT THE REQUEST OF THE FAIRFAX FIRE DEPARTMENT TO TURN THE GAS OFF. WGL CONDUCTED A LEAK SURVEY, ODORANT TEST, AND SEVERAL LEAK SURVEYS TO VERIFY THE INTEGRITY OF THE SYSTEM AND NO ISSUES WERE FOUND. THE CAUSE OF THE FI | 100
513 | 2007-07-12 | CA | sabotage | UNKNOWN (SONOMA COUNTY ) | PACIFIC GAS & ELECTRIC | WHILE EXCAVATING THE SOIL FOR A PROJECT TO INSTALL CURB AND GUTTERS A CONTRACTOR HIT A PACIFIC GAS & ELECTRIC 8-INCH DIAMETER STEEL HIGH-PRESSURE GAS DISTRIBUTION MAIN. THE SUBSEQUENT RELEASE OF GAS RESULTED IN THE EVACUATION OF LOCAL BUSINESS AND CAUSED | 12000
514 | 2007-07-14 | MD | other | UNKNOWN (FREDERICK COUNTY ) | WASHINGTON GAS LIGHT COMPANY | A WASHINGTON GAS REGULATOR STATION LOCATED APPROXIMATELY 25 FEET BEHIND THE CURB WAS DAMAGED AS A RESULT OF VEHICULAR TRAFFIC. THE STATION HAD BARRICADE PROTECTION, HOWEVER, THE CAR DID STRIKE THE ABOVE GROUND PIPING AND BROKE A ONE-INCH NIPPLE AT THE TH | 700
515 | 2007-07-21 | CA | other | UNKNOWN (RIVERSIDE COUNTY ) | SOUTHERN CALIFORNIA GAS COMPANY | ON JULY 21, 2007 A METER SET ASSEMBLY WAS DAMAGED FROM BEING STRUCK BY A MOTORIZED PALLET JACK, CRACKING A 1¿ BYPASS FITTING. ESCAPING GAS FROM THE DAMAGED METER SET ASSEMBLY IGNITED, CAUSING APPROXIMATELY $100K DAMAGE TO THE STRUCTURE. NO INJURIES WERE | 100
516 | 2007-07-10 | KY | sabotage | UNKNOWN (JEFFERSON COUNTY ) | LOUISVILLE GAS AND ELECTRIC COMPANY | ATTACHED LG&E REPORT TO THE KPSC REPORT SUBMITTED SIMULTANEOUSLY. | 16706
517 | 2007-07-23 | CA | other | UNKNOWN (KINGS COUNTY ) | SOUTHERN CALIFORNIA GAS COMPANY | ON JULY 23, 2007 A GAS SERVICE RISER WAS DAMAGED FROM A VEHICLE WHOSE DRIVER LOST CONTROL, LEAVING THE TRAVELED ROADWAY. ESCAPING GAS FROM THE DAMAGED METER SET ASSEMBLY IGNITED, CAUSING APPROXIMATELY $150K DAMAGE TO THE STRUCTURE. ALTHOUGH THE DRIVER W | 500
518 | 2007-08-22 | TX | sabotage | UNKNOWN (COLLIN COUNTY ) | COSERV GAS LTD | CITY OF FAIRVIEW WAS EXCAVATING TO INSTALL A TAP ON A WATER LINE AND DAMAGE A 6" POLY MAIN | 1200
519 | 2007-07-03 | NY | other | UNKNOWN (CHEMUNG COUNTY ) | NEW YORK STATE ELECTRIC & GAS | THIS REPORT IS BEING SUBMITTED IN AN ABUNDANCE OF CAUTION EVEN THOUGH THE INVESTIGATION DONE TO DATE INDICATES THAT NO MISFEANCE OCCURED ON THE PART OF NEW YORK STATE GAS AND ELECTRIC. THIS REPORT IS BEING FILED SINCE THE COMPANY MADE A TELEPHONE REPORT | 0
520 | 2007-07-17 | NC | sabotage | UNKNOWN (MECKLENBURG COUNTY ) | PUBLIC SERVICE OF NORTH CAROLINA, INC | A CONTRACTOR USING A SKID STEER FRONT-END LOADER WAS EXCAVATING NEAR THE METER AT 525 DELBURG STREET, DAVIDSON, NC, AND DAMAGED THE 3/4" PLASTIC SERVICE. LEAKING GAS IGNITED CAUSING THE HOUSE TO BE DAMAGED BY FIRE BEFORE GAS COULD BE SHUT OFF AND THE FI | 0
521 | 2007-07-03 | NM | other | UNKNOWN (BERNALILLO COUNTY ) | PUBLIC SERVICE COMPANY OF NEW MEXICO | AT APPROXIMATELY 13:50 ON JULY 3RD, 2007, A TRUCK WAS INTENTIONALLY DRIVEN INTO A METER SET WHICH SERVED A SUX UNIT APARTMENT BUILDING AT 246 TEXAS SE, ALBUQUERQUE, NEW MEXICO 87108. THE TRUCK STRUCK THE METERS AND THEN PUNCTURED THE BUILDING WALL THE T | 282
522 | 2007-07-25 | TX | sabotage | UNKNOWN (DENTON COUNTY ) | ATMOS ENERGY CORP. MID-TEX DIVISION | AN EXCAVATOR STRUCK A MAIN, CAUSING A LEAK. | 1000
523 | 2007-08-13 | CO | sabotage | UNKNOWN (LARIMER COUNTY COUNTY ) | PUBLIC SERVICE CO. OF COLORADO | THE SUBCONTRACTOR FOR THE CITY OF FORT COLLINS WAS WORKING ON A ROAD IMPROVEMENT PROJECT. THE SUBCONTRACTOR HAD CALLED THE ONE CALL SYSTEM FOR LOCATES ON 8/10/07 (FRIDAY) AND THE GAS LINE WAS SCHEDULED TO BE LOCATED IN THE FIELD ON 8-14-07 (TUESDAY). TH | 4000
524 | 2007-07-26 | CT | sabotage | UNKNOWN (nan COUNTY ) | YANKEE GAS SERVICES COMPANY | A CONTRACTOR WHILE USING A RECLAIMING MACHINE WORKING FOR THE TOWN OF BETHEL, HIT AND BROKE A DRIP STEM LOCATED APPROXIMATELY TWO INCHES UNDER THE ASPHALT ON A SIX INCH, 35 LB STEEL NATURAL GAS DISTRIBUTION SYSTEM. AN IMMEDIATE IGNITION OF THE GAS CAUSED | 1400
525 | 2007-08-23 | CA | other | UNKNOWN (SAN MATEO COUNTY ) | PACIFIC GAS AND ELECTRIC COMPANY | A CONTRACT EMPLOYEE JUST COMPLETED A WELD ON A STEEL-TO-PLASTIC COMPRESSION CONNECTION TO REPLACE A COPPER SERVICE. IN THE SAME BELL HOLE WAS A SECOND COPPER SERVICE WHICH WAS STILL PRESSURIZED. WHILE POSITIONING HIMSELF, THE WORKER BUMPED THE PRESSURIZED | 0
526 | 2007-08-07 | NM | other | UNKNOWN (nan COUNTY ) | PNM GAS SERVICES | CAR TURNED ON TO BERRYHILL AT HIGH RATE OF SPEED LOST CONTROL SIDING DOWN THE ROAD OVER CORRECTED AND RAN IN METER LOCATED AT PROPERTY LINE IN FRONT OF HOUSE. DESTROYING THE METER AND BREAKING THE SERVICE LINE AT THE STOP. DRIVER DIED AT THE SCENE DUE T | 180
527 | 2007-09-14 | GA | natural disasters | UNKNOWN (MONROE COUNTY ) | FORT VALLEY UTILITIES | LIGHTNING STRIKE TO EL PASO(SOUTHERN NATURAL GAS) GATE STATION TO FORT VALLEY UTILITIES. LIGHTNING CAUSED DAMAGE AND FIRE AT EL PASO FACILITY. DUE TO CLOSE PROXIMITY OF FORT VALLEY UTILITIES METER STATION HEAT DAMAGE OCCURED TO METER COMPONENTS AND ODERAZ | 5000
528 | 2007-09-18 | TX | other | UNKNOWN (COLLIN COUNTY ) | COSERV GAS LTD | THIRD PARTY REPAIRING A PHONE LINE UTILIZING A BLOW TORCH ADCCIDENTALLY CAME IN CONTACT WITH A BLANKET WHICH WAS LAYING OVER GAS LINE. THE BLANKET CAUGHT ON FIRE AND MELTED A SMALL PIN HOLE IN GAS PIPE. A SMALL FLASH FIRE OCCURRED AND WAS EXTINGUISHED IMM | 0
529 | 2007-08-19 | MN | natural disasters | UNKNOWN (DAKOTA COUNTY ) | CENTERPOINT ENERGY RESOURCES GROUP DBA CENTERPOINT ENERGY MINNESOTA GAS | METER SET AND OR HOUSE WAS STRUCK BY LIGHTNING CAUSING A FIRE. | 0
530 | 2007-09-09 | NM | other | UNKNOWN (SANTA FE COUNTY ) | PUBLIC SERVICE COMPANY OF NEW MEXICO - GAS SVCS | A FIRE STARTED IN THE SHED AT #22 LOIS, SANTA FE, NM AND MIGRATED ITS WAY ACROSS GRASS AND WEEDS TO A MOBILE HOME. THE SANTA FE FIRE DEPT ESCORTED OUR SERVICE TECH TO THE GAS METER SET WHERE HE FOUND THE STOPCOCK ALREADY TURNED OFF BY SFFD. THE TECH REM | 0
531 | 2007-08-30 | SC | natural disasters | UNKNOWN (RICHLAND COUNTY ) | SOUTH CAROLINA ELECTRIC AND GAS | A LIGHTNING STRIKE APPEARS TO HAVE HIT AN ELECTRIC METER PEDESTAL AT TRAILER NUMBER 134 AT 2928 ALPINE ROAD. THE SURGE OF ENERGY ARCHED FROM THE ELECTRIC METER PEDESTAL ONTO THE REGULATOR ON OUR GAS METER SET. THE REGULATOR (SINGER 1813B) BODY SEPARATED | 719
532 | 2007-08-22 | PA | sabotage | UNKNOWN (BEAVER COUNTY ) | COLUMBIA GAS OF PENNSYLVANIA INC | CONSTRUCTION CREW INSTALLING GUIDE RAIL ON RT 989 (NEAR SOLAR COURT) IN BEAVER COUNTY, POUNDED GUIDE RAIL INTO 4 INCH STEEL MAIN. CONSTRUCTION CREW STARTED INSTALLATION OF GUIDE RAIL PRIOR TO GAS LINE BEING LOCATED. LOCATOR FOR OPERATOR WAS COMMUNICATIN | 5000
533 | 2007-08-28 | PA | sabotage | UNKNOWN (LEBANON COUNTY ) | UGI UTILITIES, INC. | EXCAVATOR INSTALLING A SEWER MAIN STRUCK A 3/4" MEDIUM PRESSURE GAS SERVICE THAT WAS NOT MARKED. GAS ESCAPED AND RESULTED IN A FIRE THAT DESTROYED A TRAILER HOME. NO INJURIES WERE INCURRED. | 200
534 | 2007-08-24 | SD | other | UNKNOWN (BROWN COUNTY ) | NORTHWESTERN ENERGY | A FIRE UNRELATED TO NATURAL GAS OCCURRED AT 119 RAILROAD AVE IN ABERDEEN, SD. FIRE OFFICIALS WERE NOTIFIED OF THE FIRE AT 4;45 AM WHO IN TURN NOTIFIED NORTH WESTERN AT 5:00 AM. THE FIRE WAS ALREADY TOO SEVERE ONCE THE FIREFIGHTERS ARRIVED ON SCENE (FIRE | 268
535 | 2007-09-10 | CA | other | UNKNOWN (SAN BERNARDINO COUNTY ) | SOUTHERN CALIFORNIA GAS COMPANY | ON SEPTEMBER 10, 2007 A METER SET ASSEMBLY WAS DAMAGED BY AN ADJACENT BURNING BUILDING. THE FIRE THAT STARTED AT THE BUILDING WAS NOT RELATED TO NATURAL GAS. NO OR INJURIES OR THIRD PARTY DAMAGE WERE ATTRIBUTED TO ESCAPING GAS. REPAIRS WERE COMPLETE | 0
536 | 2007-09-02 | TX | natural disasters | UNKNOWN (JEFFERSON COUNTY ) | TEXAS GAS SERVICE COMPANY | A HOUSE FIRE OCCURRED THAT WAS FUELED BY NATURAL GAS FROM UNDER THE HOUSE SLAB. AN ADDITION HAD BEEN ADDED ONTO THE HOME AND THE CONSTRUCTION WAS OVER THE NATURAL GAS SERVICE LINE. A LEAK OCCURRED UNDER THIS SLAB. THE ACTUAL PIECE OF THE SERVICE LINE T | 0
537 | 2007-08-22 | OH | sabotage | UNKNOWN (CUYAHOGA COUNTY COUNTY ) | COLUMBIA GAS OF OHIO | THIRD PARTY CONTRACTOR, INSTALLING CABLE, BORED INTO COLUMBIA GAS OF OHIO INC'S 2" PLASTIC GAS MAIN CAUSING A RELEASE OF NATURAL GAS AND ULTIMATE EXPLOSION AT 20788/20806 SPEINGFIELD CIRCLE, STONGSVILLE, OHIO. THE GAS MAIN HAD BEEN CORRECTLY MARKED PER O | 143
538 | 2007-08-29 | TX | sabotage | UNKNOWN (TAYLOR COUNTY ) | ATMOS ENERGY CORP., MID-TEX DIVISION | AN EXCAVATOR STRUCK A SERVICE LINE, CAUSING A LEAK. | 0
539 | 2007-09-14 | UT | sabotage | UNKNOWN (TOOELE COUNTY ) | QUESTAR GAS COMPANY | KRYPTONITE CONSTRUCTION WAS WORKING ON A SEWER LINE NEAR AN EXPOSED 2" PLASTIC DISTRIBUTION MAIN. A BACK-HOE OWNED AND OPERATED BY KRYPTONITE CONSTRUCTION FELL INTO THE TRENCH AND STRUCK THE EXPOSED GAS LINE. THE GAS LINE RUPTURED AND IGNITED. THE BACK | 1447
540 | 2007-09-20 | WI | other | UNKNOWN (FOND DU LAC COUNTY ) | ALLIANT ENERGY - WISCONSIN POWER AND LIGHT COMPANY | CONTRACTOR CREW FOR THE OPERATOR WAS IN THE PROCESS OF RETIRING AN 8-INCH STEEL MAIN. THE SECOND CUT ON THE 8-INCH STEEL PIPE WAS BEING MADE WITH A BEVELING TORCH. DURING THE CUTTING PROCESS NATURAL GAS IGNITED. THE BEVELING TORCH IS THE KNOWN SOURCE O | 480
541 | 2007-09-17 | WI | leaks and spills | UNKNOWN (nan COUNTY ) | WISCONSIN GAS COMPANY, D/B/A WE-ENERGIES | A GAS COMPANY CONTRACTOR CREW WAS IN THE PROCESS OF REPLACING TWO 8" VALVES IN AN ASSEMBLY TAPPED OFF A NEARBY 20" - 100# LINE (ONE 8" VALVE WHICH WAS IN-OPERABLE AND NECESSITATED THE WORK) WHICH WERE REQUIRED TO BE ABLE TO SHUT DOWN A DOWNSTREAM OPERATOR | 40280
542 | 2007-09-10 | MA | sabotage | UNKNOWN (PLYMOUTH COUNTY ) | BAY STATE GAS COMPANY | COMPANY WAS WORKING ON A MAIN REPLACEMENT. THE INCIDENT LOCATION WAS SCHEDULED FOR A SERVICE REPLACEMENT. THE OLD SERVICE WAS SCHEDULED FOR REPLACEMENT ON THE DAY OF THE INCIDENT. UPDATED BY PHMSA PER OPERATOR ON 11/20/2015: EXCAVATION DAMAGE TO CUST | 737
543 | 2007-09-17 | TX | sabotage | UNKNOWN (MONTGOMERY COUNTY ) | CENTERPOINT ENERGY ENTEX | 3RD PARTY DAMAGED A 2" PLASTIC MAIN WITH A BACKHOE WHILE BUILDING A NEW ADDITION. | 553
544 | 2007-09-25 | WV | sabotage | UNKNOWN (LEWIS COUNTY ) | HOPE GAS INC DBA DOMINION HOPE | ON 9/25/2007, JON J. SHIMKO WAS OPERATING A DITCH WITCH TO INSTALL A WATER SERVICE LINE AT THE PROPERTY OF JOEL BRUFFEY IN WALKERSVILLE, WEST VIRGINIA. MR. SHIMKO HIT A TWO INCH PLASTIC GAS LINE WITH 34 LBS. OF PRESSURE. THE GAS LEAK IGNITED, BURNING | 181
545 | 2007-09-28 | IL | technical failure | UNKNOWN (COOK COUNTY ) | PEOPLES GAS LIGHT AND COKE COMPANY | AT 4:15 P.M. ON SEPTEMBER 28, 2007, THE PEOPLES GAS LIGHT AND COKE COMPANY (PEOPLES GAS) WAS NOTIFIED BY THE CHICAGO FIRE DEPARTMENT OF AN EXPLOSION AT 410 E. 107TH STREET CHICAGO, IL. A PEOPLES GAS EMPLOYEE WAS IMMEDIATELY DISPATCHED TO THE SCENE. WHIL | 0
546 | 2007-09-17 | GA | sabotage | UNKNOWN (FORSYTH COUNTY ) | ATLANTA GAS LIGHT | A 3RD-PARTY EXCAVATOR GRADING FOR ROAD WIDENING HIT A CORRECLT-LOCATED 2" LATERAL OFF OF A 12" MAIN CAUSING PARTIAL SEPARATION BETWEEN THE TWO. STATE HIGHWAY 9 WAS SHUT DOWN AND A NEARBY ELEMENTARY SCHOOL WAS EVACUATED BY EMERGENCY OFFICIALS AS A PRECAUTI | 60475
547 | 2007-10-07 | NE | other | UNKNOWN (nan COUNTY ) | SOURCEGAS LLC | VEHICLE DRIVEN BY ANTHONY MATTISON OF 518 N. CLAY AVE CLAY CENTER NE,68933 DRIVERS LICENSE # H 13076143 DATE OF BIRTH 12/30/88 WAS DRIVING 1983 GMC S1500 JIMMY LEFT ROADWAY CROSSED DITCH TAKING OUT FENCE AND RUNNING INTO AND DESTROYING METER GUARD AND 2 | 716
548 | 2007-09-30 | IL | other | UNKNOWN (LA SALLE COUNTY ) | NICOR GAS | STRUCTURE FIRE DUE TO ARSON SPREAD THROUGH THE HOUSE AND MELTED THE METER SET, THUS CAUSING A RELEASE OF NATURAL GAS. | 100
549 | 2007-09-15 | MS | sabotage | UNKNOWN (nan COUNTY ) | CENTERPOINT ENERGY | ON SEPTEMBER 15, 2007 AT APPROX. 8:30 A.M., CNP RECEIVED A CALLFROM THE PHILADELPHIA, MS POLICE DEPT REPORTING A NATURAL GAS LEAK AT 566 HOLLAND AVE. A CENTERPOINT ENERGY EMPLOYEE ARRIVED ON SITE AND STARTED SOME ROUTINE CHECKS IN THE AREA. WHILE ATTEMP | 2388
550 | 2007-10-08 | CO | sabotage | UNKNOWN (JEFFERSON COUNTY ) | PUBLIC SERVICE CO. OF COLORADO | GREEN TREE LANDSCAPING WAS REMOVING TREE ROOTS WITH A BACKHOE, AND ENDED UP SEVERING THE SERVICE LINE FROM THE METER. THE CONTRACTOR PLACED HIS COAT OVER THE BLOWING SERVICE, AND A FEW MOMENTS LATER THE GAS IGNITED IN THE HOUSE. LOCATES WERE NOT CALLED I | 1250
551 | 2007-10-03 | CA | natural disasters | UNKNOWN (SAN DIEGO COUNTY ) | SAN DIEGO GAS AND ELECTRIC | ON OCTOBER 3, 2007, THE LOCATIONS OF MAIN, SERVICES, AND METER SET ASSEMBLIES WERE COMPROMISED WHEN A LANDSLIDE OCCURRED IN THE COMMUNITY OF LA JOLLA. A TOTAL OF 7 HOMES WERE DETERMINED TO BE UNINHABITABLE, AND A 390¿ SECTION OF 3¿ PE MAIN ABANDONED. | 0
552 | 2007-10-09 | UT | sabotage | UNKNOWN (SALT LAKE COUNTY ) | QUESTAR GAS COMPANY | QUESTAR GAS RESPONDED TO A CUSTOMER GAS LEAK CALL. A QUESTAR GAS EMPLOYEE BARRED THE LINE AS PART OF QUESTAR'S STANDARD LEAK LOCATING PROCEDURE. IN BARRING THE LINE, THE BAR WAS PUNCHED THROUGH THE PLASTIC LINE MAKING A 3/8" HOLE AND RESULTED IN A RELEASE | 30
553 | 2007-10-12 | CA | other | UNKNOWN (ORANGE COUNTY ) | SOUTHERN CALIFORNIA GAS COMPANY | ON OCTOBER 12, 2007, EMPLOYEE WAS ATTEMPTING TO REPLACE A SERVICE STOPCOCK DUE TO BROKEN OPERATING TANG. WHILE ATTEMPTING TO PERFORM REPLACEMENT, CORE SEPARATED FROM STOPCOCK, RELEASING GAS TO ATMOSPHERE WHICH WAS LIKELY IGNITED BY A NEARBY WATER HEATER. | 0
554 | 2007-10-10 | NC | sabotage | UNKNOWN (WAKE COUNTY ) | PUBLIC SERVICE CO OF NORTH CAROLINA | EXCAVATION STARTED AT THIS SITE PRIOR TO THE LOCATE REQUEST BECOMING VALID WHICH REQUIRE A MINIMUM 48 HOUR NOTIFICATION. HOWEVER, PRIOR LOCATE MARKS AT THIS SITE WERE STILL ACCURATE AND VISIBLE AT THE TIME THIS EXCAVATION AND DAMAGE WAS DONE. | 20201
555 | 2007-10-14 | MI | other | UNKNOWN (KENT COUNTY ) | MICHIGAN CONSOLIDATED GAS CO (MICHCON) | ON SUNDAY, OCTOBER 14, 2007 AT APPROXIMATELY 1:49 AM A NORTHBOUND VEHICLE FAILED TO NEGOTIATE A CURVE ON PETTIS AVENUE, LEFT THE ROADWAY, AND STRUCK A HOUSE AT 600 PETTIS AVENUE. THE DRIVER FLED THE SCENE IN THE VEHICLE. AT APPROXIMATELY 1:58 AM MICHCO | 76
556 | 2007-10-05 | FL | sabotage | UNKNOWN (BROWARD COUNTY ) | FLORIDA CITY GAS | DUE TO A BROKEN TRACER WIRE, THE LOCATING EQUIPMENT SIGNAL BLED FROM THE GAS MAIN ONTO ANOTHER FACILITY PARALLELING THE GAS MAIN. THE GAS MAIN WAS MARKED INCORRECTLY AND WAS SUBSEQUENTLY DAMAGED BY AN EXCAVATOR. GAS SERVICE TO APPROXIMATELY 1625 CUSTOMERS | 0
557 | 2007-10-01 | ME | sabotage | UNKNOWN (CUMBERLAND COUNTY ) | NORTHERN UTILITIES INC (ME) | ON 10/01/2007, AT APPROXIMATELY 8:25AM, NORTHERN UTILITIES RECEIVED A CALL REGARDING A LEAK DUE TO A THIRD PARTY DAMAGE ON A SERVICE LINE T0 #47 D STREET, SOUTH PORTLAND, MAINE. AT APPROXIMATELY 8:25AM, NORTHERN UTILITIES' PERSONNEL WERE DISPATCHED TO THE | 0
558 | 2007-11-11 | AK | other | UNKNOWN (MATANUSKA SUSITNA BOROUGH COUNTY ) | ENSTAR NATURAL GAS CO |  | 50
559 | 2007-10-22 | CA | other | UNKNOWN (SAN DIEGO COUNTY ) | SAN DIEGO GAS & ELECTRIC CO | ON OCTOBER 21, 2007 NUMEROUS FIRES BROKE OUT ACROSS SAN DIEGO GAS AND ELECTRIC¿S (SDG&E) SERVICE TERRITORY, DAMAGING SERVICES, RISERS AND METER SET ASSEMBLIES. DAMAGE TO SDG&E GAS FACILITIES WAS LIMITED TO THESE COMPONENTS AND ONE SMALL ONE-WAY FEED PE D | 0
560 | 2007-10-21 | CA | other | UNKNOWN (LOS ANGELES COUNTY ) | SOUTHERN CALIFORNIA GAS CO | ON OCTOBER 21, 2007 NUMEROUS FIRES BROKE OUT ACROSS SOUTHERN CALIFORNIA GAS COMPANY (SOCALGAS) SERVICE TERRITORY, DAMAGING SERVICES, RISERS AND METER SET ASSEMBLIES. DAMAGE TO SOCALGAS GAS FACILITIES WAS LIMITED TO THESE COMPONENTS. NO DAMAGE TO DISTRIB | 0
561 | 2007-10-27 | IL | other | UNKNOWN (KENDALL COUNTY ) | NORTHERN ILLINOIS GAS CO | STRUCTURE FIRE OF UNKNOWN CAUSE DAMAGED THE METER SET THUS CAUSING A RELEASE OF NATURAL GAS INTO THE ATMOSPHERE. | 100
562 | 2007-11-03 | LA | other | UNKNOWN (IBERVILLE COUNTY ) | IBERVILLE PARISH NATURAL GAS SYSTEM | RESIDENT WAS CUTTING THE REMAINS OF A TRAILER FLOOR WITH A WELDING TORCH AND WAS NOT AWARE THAT A GAS SERVICE LINE WAS BENEATH THE PILE OF MATERIALS. THE GAS SERVICE LINE WAS A 0.75 POLYETHYLENE PIPE WITH AND ANODELESS RISER, VALVE AND PLUG. WHILE THE RES | 0
563 | 2007-11-14 | TX | sabotage | UNKNOWN (HARRIS COUNTY ) | ENTEX, A NORAM ENERGY COMPANY (FORM. DIV OF ARKLA | 3RD PARTY DAMAGED A 4" POLY MAIN WHILE DIRECTIONAL BORING INSTALLING WATER LINES FOR CITY OF HUMBLE. | 2096
564 | 2007-11-08 | DC | sabotage | UNKNOWN (DC COUNTY ) | WASHINGTON GAS LIGHT CO | FLIPPO CONSTRUCTION COMPANY, INC. DAMAGED A FOUR-INCH PLASTIC GAS SERVICE WITH MINI-EXCAVATOR WHILE EXCAVATING TO INSTALL A 12-WAY ELECTRIC DUCT BANK. | 500
565 | 2007-11-20 | CA | sabotage | UNKNOWN (FRESNO COUNTY ) | PACIFIC GAS & ELECTRIC CO | PG&E ELECTRIC DEPARTMENT WAS HAND-DIGGING TO FIND AN ELECTRIC FAULT ON A RESIDENTIAL SERVICE IN A JOINT TRENCH AND HIT A 1/2-INCH PLASTIC GAS SERVICE. A GAS CREW WAS DISPATCHED AND ATTEMPTED TO USE A BATTERY-OPERATED RECIPROCATING SAW TO CLEAR TREE ROOTS | 50
566 | 2007-11-29 | IL | other | UNKNOWN (LAKE COUNTY ) | NORTHERN ILLINOIS GAS CO | HOMEOWNER BACKED A TRAILER AND STRUCK THE METER SET, CAUSING A RELEASE OF GAS AND IGNITION. NOTE: THIS INCIDENT WAS OGINALLY REPORTED AS "FIRE FIRST". FURTHER INVESTIGATION REVEALED ACTUAL CAUSE OF THE FIRE WAS OTHER OUTSIDE FORCE DAMAGE. | 100
567 | 2007-11-25 | VA | other | UNKNOWN (FAIRFAX COUNTY ) | WASHINGTON GAS LIGHT CO | WASHINGTON GAS RESPONDED TO A HOUSE FIRE AT 5103 & 5105 MYRTLE LEAF DRIVE IN FAIRFAX COUNTY VIRGINIA AT THE REQUEST OF THE FAIRFAX COUNTY FIRE DEPARTMENT. UPON ARRIVAL OF THE EMERGENCY RESPONDER, GAS WAS FOUND OFF TO BOTH ADDRESSES AND THE FIRE WAS EXTIN | 100
568 | 2007-11-09 | TX | natural disasters | UNKNOWN (MCLENNAN COUNTY ) | ATMOS ENERGY CORP., MID-TEX DIVISION | WHILE PERFORMING A LEAK SURVEY, A LEAK WAS DETECTED. WHILE PERFORMING THE LEAK INVESTIGATION, THE DETERMINATION WAS MADE TO EVACUATE A BUILDING. | 0
569 | 2007-12-02 | TX | other | UNKNOWN (EL PASO COUNTY ) | TEXAS GAS SERVICE COMPANY | 1" STEEL RISER TO METER SETTING WAS DAMAGED AFTER A TWO CAR COLLISION SENT ONE OF THE VEHICLES INTO THE METER SETTING. REPAIRS WERE MADE BY REPLACING THE GAS METER. THERE WERE TWO FATALITIES AND ONE INJURY DUE TO THE NATURE OF THE COLLISION. | 7
570 | 2007-11-21 | NY | leaks and spills | UNKNOWN (QUEENS COUNTY ) | CONSOLIDATED EDISON CO OF NEW YORK | ON NOVEMBER 21, 2007, AT 3:33 P.M., THE FIRE DEPARTMENT OF NEW YORK (FDNY) CONTACTED CON EDISON'S GAS EMERGENCY RESPONSE CENTER (GERC) TO REPORT AN ODOR OF GAS IN FRONT OF 48-15 41ST STREET IN SUNNYSIDE, QUEENS. AT 4:04 P.M., A CON EDISON CREW, CONSISTING | 100
571 | 2007-09-18 | CA | other | UNKNOWN (ORANGE COUNTY ) | SOUTHERN CALIFORNIA GAS CO | ON SEPTEMBER 18, 2007, A LEAK WAS DISCOVERED ON A 10¿ HIGH PRESSURE DISTRIBUTION MAIN. LEAK WAS DISCOVERED BY CITY WATER CREW PERFORMING EMERGENCY WATER LEAK REPAIR. AFTER EXCAVATING, IT WAS DETERMINED THAT LEAK ON GAS MAIN WAS LIKELY THE RESULT OF HI | 0
572 | 2007-10-21 | CT | other | UNKNOWN (HARTFORD COUNTY ) | CONNECTICUT NATURAL GAS CORP | THE BUILDING AT 75 1/2 BIRCH ST. MANCHESTER CAUGHT FIRE AND BURNED TO THE POINT WHICH THE BUILDING COLLAPSED ONTO THE GAS METER SET LOCATED OUTSIDE AND ADJACENT TO THT BUILDING. THIS CAUSED THE METER TO BECOME DAMAGED AND RELEASED GAS THUS FURTHER FUELING | 20
573 | 2007-12-11 | MA | other | UNKNOWN (nan COUNTY ) | BOSTON GAS CO |  | 0
574 | 2007-12-17 | MD | other | UNKNOWN (BALTIMORE COUNTY ) | BALTIMORE GAS & ELECTRIC CO | ACCORDING TO BALTIMORE COUNTY FIRE DEPARTMENT, THE POINT OF ORIGINATION IS UNKNOWN DUE TO THE EXTENT OF DAMAGE. BALTIMORE COUNTY FIRE DEPARTMENT'S REPORT STATED THAT THE DWELLING WAS HEAVILY ENGULFED UPON ARRIVAL. FIRE INVESTIGATION DEPARTMENT WAS REQUEST | 0
575 | 2007-12-01 | OH | other | UNKNOWN (LUCAS COUNTY ) | COLUMBIA GAS OF OHIO INC | A STRUCTURE FIRE AT A COMMERCIAL BUILDING CAUSED A ROOF COLLAPSE, WHICH FRACTURED A FITTING ON THE SERVICE LINE SERVING THE BUILDING. THERE IS NO INDICATION THAT THE FIRE WAS CAUSED BY A RELEASE OF GAS FROM A JURISDICTIONAL PIPELINE FACILITY, BUT AS A RES | 100
576 | 2007-12-28 | NM | leaks and spills | UNKNOWN (BERNALILLO COUNTY ) | PUBLIC SERVICE COMPANY OF NEW MEXICO - GAS SVCS | PIPE SEGMENT SENT TO LAB FOR FAILURE ANALYSIS. THERE WAS NO EVIDENCE OF PROGRESSIVE OR FATIGUE CRACKING AT THE ORIGIN NOR AT ANY POINT ON THE FRACTURE SURFACE. THE CRACK HAS THE APPEARANCE OF A TOUGH, DUCTILE MATERIAL. | 0
577 | 2007-12-24 | MN | natural disasters | UNKNOWN (CLAY COUNTY ) | NORTHERN STATES POWER CO. OF MINNESOTA | WATER DRIPPING FROM A LARGE ICE DAM ON THE ROOF FROZE OVER THE SERVICE REGULATOR VENT, CAUSING AN OVER PRESSURE CONDITION ON THE CUSTOMERS HOUSE PIPING. CUSTOMER EQUIPMENT FAILED, CAUSING A FIRE THAT DAMAGED THE LOWER LEVEL OF THE HOUSE. | 0
578 | 2007-12-27 | NV | sabotage | UNKNOWN (CLARK COUNTY ) | SOUTHWEST GAS CORP | WHILE EXCAVATING AROUND NATURAL GAS PIPELINE FACILITIES LOCATED AT NORTH 5TH STREET AND COLDWELL STATION AVENUE, AN OPERATOR FOR TEJAS UNDERGROUND, PERFORMING WORK FOR SOUTHWEST GAS CORPORATION, DAMAGED A 1-INCH PE PURGE ASSEMBLY ON A ONE WAY FED 4-INCH P | 208
579 | 2008-01-04 | NY | maintenance | UNKNOWN (SUFFOLK COUNTY ) | KEYSPAN ENERGY DELIVERY - LONG ISLAND | AT 0444, NATIONAL GRID LI RECEIVED A CALL REPORTING A DISTURBANCE AT 96 CARLETON AVENUE, CENTRAL ISLIP. UPON ARRIVAL, NATIONAL GRID PERSONNEL FOUND THAT THE LOCATION HAD SUSTAINED DAMAGE TO WINDOWS, DOORS, AND THE BUILDING INTERIOR DUE TO AN APPARENT DIST | 0
580 | 2008-01-05 | PA | other | UNKNOWN (YORK COUNTY ) | COLUMBIA GAS OF PENNSYLVANIA | ON JANUARY 5, 2008 AT APPROXIMATELY 02:37 COLUMBIA GAS RECEIVED A CALL FROM 911. A VEHICLE CRASHED INTO A METER SET ADJACENT TO A RESIDENTIAL HOME LOCATED AT 3445 EAST PROSPECT RD. IN YORK, PA. ACCORDING TO THE RESPONDING FIRE AND POLICE, THE OCCUPANTS | 250
581 | 2008-01-12 | CA | other | UNKNOWN (ELDORADO COUNTY ) | SOUTHWEST GAS CORP | ON JANUARY 9, 2008, A ROOFING CONTRACTOR SHOVELED WET SNOW OFF OF THE ROOF AND PILED IT ON TOP OF THE GAS METER. THE WET SNOW AND ICE THAT WAS PILED BETWEEN THE STRUCTURE AND THE GAS FACILITIES EXPANDED DUE TO ITS PARTIAL MELTING AND SUBSEQUENT FREEZING | 1328
582 | 2008-01-09 | IN | natural disasters | UNKNOWN (WHITE COUNTY ) | NORTHERN INDIANA PUBLIC SERVICE CO | HEAVY RAINS AND MELTING SNOW CAUSED EXTREMELY HEAVY WATER FLOW IN THE TIPPECANOE RIVER AND THROUGH THE NORWAY DAM IN MONTICELLO, IN. THE 6" STEEL GAS PIPE, REFERENCED IN THIS REPORT, WAS INSTALLED UNDER THE RIVER...JUST DOWNSTREAM FROM THE DAM. ON JANUARY | 0
583 | 2008-01-28 | AZ | natural disasters | UNKNOWN (GILA COUNTY ) | ENERGY WEST AZ | 1 1/4" ALDYL PIPE APPEARED TO HAVE BEEN PREVIOUSLY SQUEEZED OFF, CAUSING DAMAGE TO PIPE. ALSO A FACTOR WAS THAT THE GROUND HAD SUBSIDENCE IN THIS AREA. DURING EXCAVATION WE ALSO FOUND BROKEN SEWER PIPE IN THE GAS LINE TRENCH. APPRAISED VALUE FOR PROPE | 0
584 | 2008-01-14 | VA | other | UNKNOWN (FAIRFAX COUNTY ) | WASHINGTON GAS LIGHT CO | WASHINGTON GAS RESPONDED TO A HOUSE FIRE AT 3162 MARY ETTA LANE, HERNDON, VA AT THE REQUEST OF THE FAIRFAX COUNTY FIRE DEPARTMENT. THE REAR WALL OF THE STRUCTURE HAD COLLAPSED ON THE METER BUILD-UP. WASHINGTON GAS CUT AND CAPPED THE SERVICE IN THE YARD. | 500
585 | 2008-01-17 | CA | other | UNKNOWN (LOS ANGELES COUNTY ) | SOUTHERN CALIFORNIA GAS CO | ON JANUARY 17, 2008 A METER SET ASSEMBLY WAS DAMAGED BY A DUMP TRUCK THAT LOST CONTROL, LEAVING THE ROADWAY AND STRIKING INTO THE METER SET ASSEMBLY. THE ESCAPING GAS IGNITED, CAUSING A FIRE THAT DAMAGED A BUILDING. DUE TO BUILDING DAMAGE, THIS FACIL | 0
586 | 2008-01-17 | CA | other | UNKNOWN (SAN DIEGO COUNTY ) | SAN DIEGO GAS & ELECTRIC CO | ON JANUARY 17, 2008 A RISER AND METER SET ASSEMBLY WAS DAMAGED BY AN ELDERLY DRIVER WHO EXPERIENCED A SEIZURE, LOST CONTROL OF HIS VEHICLE AND CRASHED THROUGH A GARAGE, STRIKING INTO THE METER SET ASSEMBLY. THE ESCAPING GAS IGNITED, CAUSING A FIRE THA | 0
587 | 2005-07-07 | CA | maintenance | UNKNOWN (SANTA CLARA COUNTY ) | PACIFIC GAS & ELECTRIC CO | AT 0810, JULY 7, 2005, AN EXPLOSION OCCURRED AT THIS LOCATION. THE SINGLE FAMILY HOME WAS SEVERELY DAMAGED. TWO CHILDREN, 4 AND 6 YEARS OLD, WERE TRANSPORTED TO THE HOSPITAL AND LATER RELEASED WITH MINOR INJURIES. THE FATHER WAS TRAPPED UNDER DEBRIS FOR | 100
588 | 2006-06-13 | CA | other | UNKNOWN (SANTA CLARA COUNTY ) | PACIFIC GAS & ELECTRIC CO | ON JUNE 13, 2006, A PASSENGER VEHICLE CRASHED INTO A RESIDENTIAL GARAGE AND DAMAGED A GAS METER AT 935 MCCREERY AVENUE, SAN JOSE, CALIFORNIA. FIREFIGHTERS EXTINGUISHED TEH RESULTING STRUCTURAL FIRE AND VALVED OFF THE GAS RISER FOR SAFETY. THERE WERE N | 0
589 | 2006-12-03 | CA | other | UNKNOWN (SANTA CLARA COUNTY ) | PACIFIC GAS & ELECTRIC CO | OUR INVESTIGATION DETERMINED THAT, AT APPROXIMATELY 0120 HOURS ON DECEMBER 3, 2006, THERE WAS A STRUCTURE FIRE CAUSING DAMAGE TO THE ENTIRE RESIDENTIAL HOME. THIS STRUCTURE FIRE STARTED IN THE BACK OF THE HOME AND ADVANCED TOWARDS THE GAS METER SET LOCATE | 100
590 | 2006-12-05 | CA | other | UNKNOWN (SAN FRANCISCO COUNTY ) | PACIFIC GAS & ELECTRIC CO | ON 12/05/06 AN EXPLOSION AND RESULTING FIRE OCCURRED AT 1650 HOURS AT 456 14THSTREET, SAN FRANCISCO, CALIFORNIA. A RESIDENT WAS ATTEMPTING TO RELIGHT A NATURAL GAS STOVE WHEN THE STOVE UNIT EXPLODED RESULTING IN THE FIRE. TWO ADJACENT APARTMENTS INCLUDIN | 0
591 | 2008-01-19 | IL | other | UNKNOWN (MC HENRY COUNTY ) | NORTHERN ILLINOIS GAS CO | STRUCTURE FIRE AT THIS LOCATION. FIRE PROGRESSED THROUGH THE STRUCTURE AND REACHED THE OUTSIDE METER SET, CAUSING DAMAGE WHICH RESULTED IN A RELEASE OF NATURAL GAS INTO THE ATMOSPHERE. | 500
592 | 2008-01-03 | MA | other | UNKNOWN (MIDDLESEX COUNTY ) | NSTAR GAS COMPANY | NSTAR GAS WAS NOTIFIED OF A HOUSE FIRE BY THE MAYNARD FIRE DEPARTMENT AT 6:50 PM AND REQUESTED TO SHUT THE GAS TO THE BUILDING AT THE STREET. IT WAS BELIEVED THAT GAS MAY BE FUELING THE FIRE IN THE CRAWL SPACE AREA OF THE BASEMENT. THE HOMEOWNER HAD BEEN | 949
593 | 2008-01-22 | DC | other | UNKNOWN (nan COUNTY ) | WASHINGTON GAS LIGHT CO | INCIDENT IS STILL UNDER INVESTIGATION BY THE DC FIRE DEPARTMENT AND THE ATF. WASHINGTON GAS RESPONDED TO A FIRE AT 2412 WISCONSIN AVE, NW, WASHINGTON DC AT THE REQUEST OF THE DC FIRE DEPARTMENT. WASHINGTON GAS DID DIG THE SERVICE UP AND CAP IT OFF, HOWE | 0
594 | 2005-08-18 | CA | leaks and spills | UNKNOWN (STANISLAUS COUNTY ) | PACIFIC GAS & ELECTRIC CO | MIGRATING GAS ACCUMULATED IN AN UNVENTED WATER HEATER ENCLOSURE, EXPLODED AND CAUSED DAMAGE TO RESIDENT. THE CITED COPPER SERVICE LEAK MAY HAVE CAUSED OR CONTRIBUTED TO THE INCIDENT. THE GAS LEAK AND GAS METER WERE ON THE OPPOSITE SIDE OF THE BUILDING W | 100
595 | 2008-02-09 | NE | other | UNKNOWN (ANTELOPE COUNTY ) | SOURCEGAS LLC | SEMI-TRUCK ROLLED OVER WHILE MAKING CURVE ON HWY, SLID INTO HOUSE AND METER LOOP AT STRUCTURE. DAMAGED REGULATOR & METER. SHUT OFF BUSINESS DISTRICT VALVE AND INSTALLED SHORT STOP ON EAST SIDE OF L STREET. REMOVED DAMGAE SECTION OF ABOVE GRADE PIPING. PLU | 459
596 | 2008-01-31 | IA | maintenance | UNKNOWN (JASPER COUNTY ) | CONSUMERS ENERGY | RE: INCIDENT REPORT #861109, CONSUMER ENERGY ATTACHMENT TO RSPA FORM F7100.1 AND F7100.2 INCIDENT REPORTS. THIS NARRATIVE PROVIDE AS PER INSTRUCTION FOR PART G OF THE ABOVE REFERENCED FORMS. OVER PRESSURES OF MINGO/HARVESTER GAS TRANSMISSION AND DIS | 0
597 | 2008-01-27 | ND | leaks and spills | UNKNOWN (MORTON COUNTY ) | MONTANA - DAKOTA UTILITIES CO | THIS FAILURE WAS IN A SECTION OF THE PIPELINE THAT WAS MOVED DUE TO ROAD CONSTRUCTION. THE PIPELINE WAS MOVED TO THE EAST BY TWO FEET AND LOWERED BY 18 INCHES DUE TO THE CONSTRUCTION OF A NEW RETAINING WALL. THE FAILURE/RELEASE WAS AN ACETYLENE GIRTH WELD | 3500
598 | 2008-02-02 | CA | other | UNKNOWN (MONTEREY COUNTY ) | PACIFIC GAS & ELECTRIC CO | A DRUNK DRIVER CRASHED THROUGH A GARAGE AND SHEARED THE NATURAL GAS RISER BELOW THE SERVICE VALVE. THE ESCAPING GAS IGNITED AND THE ENSUING FIRE WAS CONFINED TO THE GARAGE. THE DRIVER ESCAPED WITHOUT INJURY AND WAS ARRESTED AT THE SCENE. THE METER SET AND | 100
599 | 2008-02-17 | PA | maintenance | UNKNOWN (JEFFERSON COUNTY ) | T W PHILLIPS GAS & OIL CO | A LEAK WAS FOUND IN THE MAINLINE IN FRONT OF THE HOUSE. THE PIPE WAS INSTALLED IN 1964. IT IS BARE STEEL. THE PIPE WAS LAID IN SOIL PRIMARILY COMPOSED OF SHALE AND CLAY. THE WEATHER CONDITIONS WERE SUCH THAT TEMPERATURES WERE FLUCTATING FOR SEVERAL DAYS W | 0
600 | 2008-02-01 | TX | sabotage | UNKNOWN (HARRIS COUNTY ) | ENTEX, A NORAM ENERGY COMPANY (FORM. DIV OF ARKLA | 3RD PARTY DAMAGE TO A 12" HP STEEL MAIN WITH A TRACK-HOE. | 5273
601 | 2008-01-27 | NM | sabotage | UNKNOWN (SAN JUAN COUNTY ) | PUBLIC SERVICE COMPANY OF NEW MEXICO - GAS SVCS | RESULTS OF PNM S INVESTIGATION INDICATE THAT THIRD PARTY DAMAGE WAS THE CAUSE OF THE INCIDENT. IT APPEARS THE PIPELINE WAS DAMAGED (BENT) DURING THE INSTALLATION OF A WATER MAIN IN 1998 THAT INTERSECTS THE GAS PIPELINE AT A 90 DEGREE ANGLE. IT APPEARS, F | 0
602 | 2008-01-16 | TX | sabotage | UNKNOWN (LAMAR COUNTY ) | ATMOS ENERGY CORPORATION, MID-TEX DIVISION | AN EXCAVATOR STRUCK A MAIN, CAUSING A LEAK. | 0
603 | 2008-01-24 | WI | maintenance | UNKNOWN (SAWYER COUNTY ) | WISCONSIN GAS CO | ON THE MORNING OF JANUARY 24, 2008, WITH TEMPERATURES AROUND -24 DEGREES , WE ENERGIES EXPERIENCED CONSECUTIVE FAILURES OF A REGULATOR AND RELIEF VALVE AT ITS HAYWARD, WISCONSIN DISTRICT REGULATOR STATION LOCATED ON U.S. HWY. 63, SOUTH OF GEHRTS ROAD IN T | 5833
604 | 2008-02-01 | TX | sabotage | UNKNOWN (VICTORIA COUNTY ) | ENTEX, A NORAM ENERGY COMPANY (FORM. DIV OF ARKLA | CITY OF VICTORIA SEWER CREW PULLED AN 1-1/4" STEEL SERVICE LINE SERVING 1402 E. WARREN OUT OF A 1-1/4" X 6" TWO BOLT MECHANICAL PIPE COUPLING WITH A GRADALL EXCAVATOR. ESCAPING GAS MIGRATED TO THE STRUCTURE AT 1401 E WARREN RESULTING IN AN EXPLOSION AND F | 380
605 | 2007-12-17 | TX | sabotage | UNKNOWN (LUBBOCK COUNTY ) | ATMOS ENERGY - WEST TEXAS DIVISION | A 2 INCH NATURAL GAS LINE WAS SEVERED BY A BACKHOE OPERATOR. DUE TO THE HIGH WINDS THE ESCAPING GAS WAS BLOWN IN THE GENERAL DIRECTION OF RAMIREZ CHARTER SCHOOL. COMPANY EMPLOYEES GAS IN THE SCHOOL. THE 400 STUDENTS AND STAFF WERE EVACUATED AS A PRECAUTIO | 50
606 | 2008-02-07 | PA | natural disasters | UNKNOWN (PHILADELPHIA COUNTY ) | PHILADELPHIA GAS WORKS | INCIDENT EXECUTIVE SUMMARY 709 SOUTH SIXTH ST. FEBRUARY 7, 2008 THE FOLLOWING IS AN ACCOUNT OF THE INCIDENT WHICH OCCURRED IN THE QUEEN VILLAGE SECTION OF PHILADELPHIA, 709 SOUTH SIXTH STREET ON THURSDAY AFTERNOON, AT 1602 HOURS. THURSDAY FE | 0
607 | 2008-03-05 | PA | sabotage | UNKNOWN (ALLEGHENY COUNTY ) | DOMINION PEOPLES | A RELEASE OF GAS IS SUSPECTED TO BE THE CAUSE OF AN EXPLOSION AT 171 MARDI GRAS DRIVE, PLUM BOROUGH, PENNSYLVANIA. SEVERAL ADJACENT HOUSES WERE DAMAGED BY THE EXPLOSION. ONE FATALITY AND ONE HOSPITALIZED INJURY OCCURRED. | 2000
608 | 2008-02-24 | ID | other | UNKNOWN (nan COUNTY ) | AVISTA CORP | AFTER A LENGTHY INVESTIGATION, MARK AAMODT, IDAHO DEPUTY STATE FIRE MARSHAL (208-769-1447), HAS DETERMINED THE CAUSE AS UNKNOWN. | 560
609 | 2008-03-10 | AK | other | UNKNOWN (MATANUSKA SUSITNA BOROUGH COUNTY ) | ENSTAR NATURAL GAS CO | ENSTAR RESPONDED TO A RESIDENTIAL STRUCTURE FIRE AT 621 CREEKSIDE DR, WASILLA, AK AT 2:57 AM ON 3/11/08. THE STRUCTURE FIRE MELTED THE 1/2" CTS HDPE SERVICE LINE INSIDE THE STEEL RISER CAUSING NATURAL GAS TO VENT TO THE ATMOSPHERE. THE GAS DID NOT IGNIT | 50
610 | 2006-02-25 | NY | sabotage | UNKNOWN (nan COUNTY ) | KEYSPAN ENERGY DELIVERY - NY CITY | ON FEBRUARY 25, 2006 AT APPROXIMATELY 0730 KEYSPAN ENERGY DELIVERY WAS NOTIFIED OF A GAS EXPLOSION AT BLDG 93 IN THE RED HOOK HOUSING PROJECTS CENTRE MALL BROOKLYN NY. AFTER AN INVESTIGATION IT WAS DETERMINED THERE WAS A GAS LEAK IN A 6" EAST IRON MAIN 9 | 0
611 | 2008-02-17 | MD | other | UNKNOWN (PRINCE GEORGES COUNTY ) | BALTIMORE GAS & ELECTRIC CO | THE GENERAL DESCRIPTION OF THE PROPERTY IS THREE(3) MULTI-FAMILY APARTMENT DWELLINGS. THE INVOLVED STRUCTURES ARE DESCRIBED AS AN ENCLOSED BUILDINGS, WHICH WERE UNDER MAJOR RENOVATION. THE FIRE OCCURRED ON THE FIRST FLOOR REAR APARTMENT THEN SPREAD BEYON | 0
612 | 2008-02-16 | MI | other | UNKNOWN (WAYNE COUNTY ) | MICHIGAN CONSOLIDATED GAS CO (MICHCON) | THIS IS TO NOTIFY THAT THE INVESTIGATION IS FINAL. THERE WERE NO CHANGES TO PREVIOUS INCIDENT REPORT DATED MARCH 14, 2008. | 0
613 | 2008-02-10 | GA | technical failure | UNKNOWN (FULTON COUNTY ) | ATLANTA GAS LIGHT CO | A COMPANY EMPLOYEE WAS ATTEMPTING TO LIGHT A HOT WATER HEATER WHEN ESCAPING GAS IGNITED CAUSING THE HOUSE TO BURN. AN INVESTIGATION DETERMINED THAT THE DELIVERY PRESSURE ON THE HOUSE PIPING WAS EXCESSIVE. THIS WAS DUE TO A REGULATOR NOT BEING INSTALLED ON | 0
614 | 2007-05-25 | MO | maintenance | UNKNOWN (JACKSON COUNTY ) | MISSOURI GAS ENERGY | CREW DIGGING TO EXPOSE GAS LEAK OVER 24 INCH CAST IRON MAIN. TOP OF PIPE WAS EXPOSED WHEN THE PIPE BEGAN TO COME APART CAUSING DEBRIS TO HIT 4 EMPLOYEES. TWO EMPLOYEES WERE HOSPITALIZED OVERNIGHT AND THE OTHER TWO TREATED AND RELEASED. NO IGNITION. NO | 55300
615 | 2007-12-07 | MS | other | UNKNOWN (COAHOMA COUNTY ) | ATMOS ENERGY CORPORATION - MISSISSIPPI DIVISION | WE HAVE ENGAGED SERVICES OF SEVERAL EXPERTS IN THE INVESTIGATION OF THIS INCIDENT, INCLUDING A METALLURGIST FOR ANALYSIS OF A BROKEN GAS MAIN FOUND IN A NEARBY ALLEY MORE THAN THREE DAYS AFTER THE INCIDENT OCCURRED. THE DEBRIS AND BURN PATTERNS AT THE SCE | 350
616 | 2008-02-23 | CA | other | UNKNOWN (RIVERSIDE COUNTY ) | SOUTHERN CALIFORNIA GAS CO | ON FEBRUARY 23, 2008, A STRUCTURE FIRE OCCURRED AT THE ABOVE ADDRESS. THE BUILDING WAS SEVERELY DAMAGED FROM FIRE DAMAGE. THE GAS METER SET ASSEMBLY WAS FOUND TO BE MELTED FROM THE INTENSE HEAT. THIS INCIDENT BECAME REPORTABLE WHEN IT WAS DETERMINED | 0
617 | 2008-02-23 | MI | sabotage | UNKNOWN (OAKLAND COUNTY ) | CONSUMERS ENERGY CO | GAS EXPLOSION AT VACANT HOME. A GAS SERVICE WORKER WAS THE FIRST RESPONDER TO THE SCENE. UPON ARRIVAL, THE FERNDALE FIRE DEPARTMENT KEPT THE FIRE CONTROL. A DISTRIBUTION CREW WAS CALLED IN TO RETIRE THE SERVICE. THE CREW CLAMPED 2" STEEL MEDIUM PRESSURE M | 0
618 | 2008-02-26 | AL | other | UNKNOWN (JEFFERSON COUNTY ) | ALABAMA GAS CORPORATION | AT THE REQUEST OF THE LOCAL FIRE DEPARTMENT, OPERATOR RESPONDED TO A HOUSE FIRE WHICH HAD BEEN REPORTED AT THE GAS METER. THE FIRE WAS REPORTED SHORTLY AFTER RESTORATION OF ELECTRIC SERVICE IN THE GENERAL AREA FOLLOWING A POWER OUTAGE. THE FIRE MAY HAVE R | 0
619 | 2007-04-20 | MD | sabotage | UNKNOWN (BALTIMORE COUNTY ) | BALTIMORE GAS & ELECTRIC CO |  | 12043
620 | 2008-02-28 | VA | other | UNKNOWN (LOUDOUN COUNTY ) | WASHINGTON GAS LIGHT CO | WASHINGTON GAS RESPONDED TO A HOUSE FIRE AT THE REQUEST OF THE LOUDOUN COUNTY FIRE DEPARTMENT. THE METER AND REGULATOR HAD BEEN COMPROMISED BY HEAT EXPOSURE CAUSING A RELEASE OF GAS. THE GAS MAIN WAS VALVED OFF AND SERVICE WAS INTERRUPTED TO SEVEN RESID | 100
621 | 2008-02-26 | MI | other | UNKNOWN (KENT COUNTY ) | MICHIGAN CONSOLIDATED GAS CO (MICHCON) | AT 14:56 ON FEBRUARY 26, 2008, MICHCON RECEIVED A REPORT OF A GAS LEAK INSIDE A TWO-STORY COMMERCIAL BUILDING AT 1500-1502 WEALTHY STREET SE, ON THE SOUTHEAST CORNER OF WEALTHY AND ETHEL AVENUE. THE CALLER REPORTED A STRONG ODOR OF GAS, PARTICULARLY IN T | 0
622 | 2006-07-27 | IA | other | UNKNOWN (HENRY COUNTY ) | WINFIELD MUNICIPAL GAS | CAR OUT OF CONTROL HIT GAS METER + BROKE IT OFF AFTER SHUT OFF VALVE. A FIRE STARTED AT FOUR MINUTES AFTER ACCIDENT + TOTALLY DESTROYED THE CAR + HEAVY DAMAGES TO THE HOUSE. | 44
623 | 2006-07-27 | MS | other | UNKNOWN (HINDS COUNTY ) | ATMOS ENERGY CORPORATION - MISSISSIPPI DIVISION | CAR RAN OFF ROAD AND STRUCK REGULATOR STATION. STATION WAS LEVELED AND THEN GA INGNITED. DRIVER ESCAPED UNINJURED. A SIX THOUSAND FEET SECTION OF 12" AND 8" H.P. STEEL MAIN HAD TO BE ISOLATED AND SEVERAL REGULATOR STATIONS AND INPUT STATIONS REQUIRED SH | 7397
624 | 2008-03-12 | CA | sabotage | UNKNOWN (LOS ANGELES COUNTY ) | SOUTHERN CALIFORNIA GAS CO | ON MARCH 12, 2008, AN EIGHTH INCH PE MAIN WAS DAMAGED BY A CONTRACTOR INSTALLING AN ELECTRICAL VAULT WITH A BACKHOE. THERE WAS NO USA REQUEST FOR THIS WORK. NO FIRE OR INJURIES RESULTED FROM THE ESCAPING GAS. THE LINE WAS REPAIRED, AND NO CUSTOMERS | 10000
625 | 2008-03-12 | MN | leaks and spills | UNKNOWN (OLMSTED COUNTY ) | MINNESOTA ENERGY RESOURCES CORPORATION | LEAK FROM CRACK IN ALDYL A 4" TEE. INCIDENT OCCURRED FROM MIGRATION OF GAS 3 HOUSES AWAY FROM LEAK. FITTING HAS BEEN SENT IN FOR TESTING. SUPPLEMENTAL REPORT TO FOLLOW WHEN TEST RESULTS ARE BACK. 2/13/2012: SEE APPARENT CAUSE ANALYSIS BY THIRD P | 0
626 | 2008-03-16 | UT | other | UNKNOWN (SALT LAKE COUNTY ) | QUESTAR GAS COMPANY | A 1999 CHEVROLET TAHOE WAS TRAVELLING EAST ON 2700 SOUTH IN SALT LAKE COUNTY, UTAH, WENT THROUGH AN INTERSECTION AT 8000 WEST, WHERE 2700 SOUTH ENDS, STRIKING A POWER POLE THAT WAS LOCATED ON THE EAST SIDE OF 8000 WEST AND THEN HITTING A QUESTAR GAS COMPA | 2000
627 | 2007-05-09 | KY | sabotage | UNKNOWN (HENDERSON COUNTY ) | HENDERSON MUNICIPAL GAS | A RELATIVE OF HOMEOWNER (RESIDENTIAL NEIGHBORHOOD) RENTED A WALK BEHIND TRENCHER TO PERFORM SMALL DIAMETER WATER LINE INSTALLATION. DURING THE COURSE OF TRENCHING, INDIVIDUAL CUT THROUGH ONE INCH POLYETHENE SERVICE LINE IN VERY NEAR PROXIMITY TO METER. | 319
628 | 2008-03-31 | ID | other | UNKNOWN (BONNERS COUNTY ) | AVISTA CORP | FIRE MARSHALL'S REPORT IS NOT PREPARED AT THIS TIME. HEAVY SNOW WAS PRESENT IN SANDPOINT AT THIS TIME. SHOW COULD HAVE FALLEN FROM ROOF ONTO METER CAUSING METER TO LEAK GAS, FIND IGNITION SOURCE AND CAUSE FIRE, OR FIRE CAUSED BY OTHER MEANS COULD HAVE C | 250
629 | 2008-03-19 | NE | technical failure | UNKNOWN (GAGE COUNTY ) | AQUILA NETWORKS | ON MARCH 19, AQUILA PERSONNEL WERE PERFORMING ANNUAL MAINTENANCE TASK ON AN 8" "KEY VALVE¿ AT 8TH & BELL. VALVE MAINTENANCE WAS NEEDED BECAUSE OF A BROKEN GREASE STEM, WAS TURNED TO OFF POSITION TO PERFORM WORK, WHEN WORK WAS COMPLETED, THE VALVE WAS NOT | 0
630 | 2008-03-22 | NM | other | UNKNOWN (BERNALLILO COUNTY ) | PUBLIC SERVICE COMPANY OF NEW MEXICO - GAS SVCS | A FIRE STARTED IN A SHED LOCATED DIRECTLY BEHIND A COMMERCIAL BUILDING. THE FIRE SPREAD TO OTHER FLAMMABLE MATERIALS WHICH EVENTUALLY STARTED THE COMMERCIAL BUILDING ON FIRE. THE GAS METER WAS LOCATED ON THE BACK SIDE OF THE COMMERCIAL BUILDING. THE CO | 300
631 | 2008-03-21 | CA | natural disasters | UNKNOWN (EL DORADO COUNTY ) | SOUTHWEST GAS CORP | PRELIMINARY INVESTIGATION INDICATES THAT A SLAB OF SNOW FELL ON TOP OF THE METER SET ASSEMBLY FROM A STRUCTURE'S ROOF, BREAKING THE RISER BELOW THE STOP COCK. THE ESCAPING GAS IGNITED. SOUTHWEST GAS IS STILL INVESTIGATING THE ROOT CAUSE OF THE INCIDENT TO | 36
632 | 2008-03-29 | CA | other | UNKNOWN (SANTA CLARA COUNTY ) | PACIFIC GAS & ELECTRIC CO | A CONTRACTOR HAD BEEN UPGRADING AN ELECTRIC PANEL FOR A RESIDENTIAL CUSTOMER. NO ONE WAS DIGGING AT THE TIME OF THE INCIDENT, HOWEVER THE UNDERGROUND UTILITIES WERE EXPOSED. THE PROBABLE CAUSE WAS THAT THE CONTRACTOR HAD NICKED THE ELECTRIC SERVICE LINE A | 500
633 | 2007-05-04 | KS | natural disasters | UNKNOWN (nan COUNTY ) | KANSAS GAS SERVICE | ON MAY 4, 2007 AT APPROXIMATELY 2230 HRS A MILE WIDE TORNADO HIT AND DESTROYED 90% TO 95% OF THE TOWN OF GREENSBURG, KS. MULTIPLE GAS FACILITIES WERE DAMAGED OR DESTROYED. THE GAS WAS SHUT OFF TO THE TOWN AT APPROXIMATELY 0000 HRS ON 5/5/07. DUE TO THE | 1000
634 | 2008-04-02 | VA | other | UNKNOWN (FREDERICK COUNTY ) | SHENANDOAH GAS CO | SHENANDOAH GAS RESPONDED TO A HOUSE FIRE AT 101 COOPWORTH COURT, STEPHENS CITY, VA ON 4/2/08. THE GAS WAS CONFIRMED TO BE OFF AT 15:12. SHENANDOAH GAS REMOVED THE METER BUILD-UP AND SECURED IT AS EVIDENCE. THE SERVICE WAS CAPPED OFF AT THE MAIN. A PRE | 100
635 | 2008-04-07 | CO | other | UNKNOWN (nan COUNTY ) | ATMOS ENERGY CORPORATION, COLORADO - KANSAS DIVISION | A THREADED FITTING SEPERATED ON THE UPSTREAM SIDE OF THE SERVICE VALVE ABOVE GROUND. THIS RELEASE OF GAS IGNITED, AND BURNED THE PREMISE. | 10000
636 | 2008-04-12 | CA | other | UNKNOWN (ALAMEDA COUNTY ) | PACIFIC GAS & ELECTRIC CO | TWO CARS SUSPECTED TO BE IN AN ILLEGAL "SIDE SHOW" (RECKLESS EXHIBITION DRIVING) CRASHED INTO HOME. ONE CAR STRUCK THE GAS METER SET AND RISER, RELEASING GAS. THE DRIVERS ABANDONED THEIR CARS AND FLED THE SCENE. THE GAS IGNITED AND CAUGHT THE HOME ON FI | 100
637 | 2008-04-07 | VA | other | UNKNOWN (CHESAPEAKE CITY COUNTY ) | VIRGINIA NATURAL GAS | AT APPROXIMATELY 2:12 AM ON 04/07/08, AN AUTOMOBILE TRAVELING SOUTH ON WILLIAMSON STREET IN CHESAPEAKE, VIRGINIA LOST CONTROL AND CRASHED THROUGH A ROAD BARRICADE NEAR THE INTERSECTION OF WILLIAMSON STREET AND LINSTER STREET. THE PURPOSE OF THE BARRICADE | 6050
638 | 2008-04-02 | SC | sabotage | UNKNOWN (ANDERSVILLE COUNTY ) | FORT HILL NATURAL GAS AUTH | WATER CONTRACTOR MISCALCULATED HIS MEASUREMENTS FOR THE BORE. WHEN PIPE WAS DAMAGED THE GAS MIGRATED BACK THROUGH THE BORE HOLE AND WAS IGNITED BY THE BORING MACHINE. | 874
639 | 2008-03-30 | ND | other | UNKNOWN (BURLEIGHT COUNTY ) | MONTANA - DAKOTA UTILITIES CO | A HOME WAS DESTROYED BY FIRE. NO ONE WAS HOME AND DUE TO THE HIGH WINDS (IN EXCESS OF 40 MPH), THE FIRE RAPIDLY PROGRESSED AND MELTED THE ALUMINUM METER AND REGULATOR. THE SERVICE LINE WAS DUG UP AND SQUEEZED OFF TO CONTROL THE RELEASE OF GAS. LATER, T | 50
640 | 2008-04-14 | CA | other | UNKNOWN (SAN JOAQUIN COUNTY ) | PACIFIC GAS & ELECTRIC CO | A YOUNG MAN LOST CONTROL OF HIS VEHICLE WHILE FLEEING A SCENE OF A STREET FIGHT IN WHICH HE WAS INVOLVED. THE VEHICLE CRASHED INTO A VACANT HOME AT 1731 CRESTWOOD CIRCLE, STOCKTON. THE VEHICLE ALSO STRUCK THE GAS METERSET AND RISER. THE RISER PIPE WAS | 200
641 | 2008-03-22 | TX | other | UNKNOWN (NACOGDOCHES COUNTY ) | BLUEBONNET NATURAL GAS LLC | ON SATURDAY, MARCH, 22, 2008 I RECEIVED A CALL FROM THE NACOGDOCHES SHERRIFF DEPT. I WAS INFORMED WE HAD A LEAK ON STATE HWY 21, AND TRAFIC WAS STOPED. TIME 1627. I ARRIVED ON LOCATION AT 1710, AND STOPED LEAK AT 1720. IT APPEARS LAND OWNER WAS BURNING BR | 120
642 | 2008-04-02 | WI | sabotage | UNKNOWN (WAUKESHA COUNTY ) | WISCONSIN ELECTRIC - GAS OPERATIONS, D/B/A WE ENERGIES | ON WEDNESDAY, APRIL 2, 2008 AT 12:22 P.M., A CONTRACTOR INSTALLING CATCH BASINS AND ASSOCIATED LATERALS IN THE INTERSECTION OF WISCONSIN AVENUE AND WORTHINGTON STREET IN THE CITY OF OCONOMOWOC, WISCONSIN, CALLED WE ENERGIES GAS EMERGENCY RESPONSE NUMBER. | 2088
643 | 2008-04-09 | NV | other | UNKNOWN (CLARK COUNTY ) | SOUTHWEST GAS CORP | WHILE A SOUTHWEST GAS CREW WAS WORKING TO REPAIR AN ABOVE GROUND LEAK ON THE STOPCOCK AT 1104 STONE RIVER DRIVE, THE STOPCOCK FAILED AND GAS IGNITED. TWO SOUTHWEST GAS EMPLOYEES SUFFERED INJURIES REQUIRING OVERNIGHT HOSPITALIZATION. SOUTHWEST GAS CREWS ST | 204
644 | 2008-04-13 | UT | other | UNKNOWN (WASHINGTON COUNTY ) | QUESTAR GAS COMPANY | THE FIRE DEPARTMENT DETERMINED THAT THE FIRE ORIGINATED IN THE PROXIMITY OF THE METER. THE EXACT IGNITION SOURCE WAS UNDETERMINED. FURNITURE AS WELL AS OTHER ITEMS WERE VERY CLOSE TO THE METER. THE RESIDENTS WERE IN THE PROCESS OF MOVING AND VEHICLES W | 0
645 | 2008-04-05 | NM | other | UNKNOWN (LEA COUNTY ) | PUBLIC SERVICE COMPANY OF NEW MEXICO - GAS SVCS | A MECHANIC SHOP CAUGHT FIRE AND A WALL COLLAPSED ON THE METER. THE METER MELTED, CAUSING THE RELEASE OF GAS. THE METER WAS REMOVED AND THE LINE WAS PLUGGED AT THE STOP. THE SERVICE LINE WAS REPAIRED, BAR TESTED AND PRESSURE TESTED ON 4/5/2008. NO LEAKS WE | 300
646 | 2008-05-10 | CA | other | UNKNOWN (SANTA CRUZ COUNTY ) | PACIFIC GAS & ELECTRIC CO | A CAR STRUCK AND SHEARED OFF A _¿ RISER AT THE METER SET. THE GAS IGNITED AND THE CAR CAUGHT FIRE. THE DRIVER OF THE VEHICLE SUSTAINED SIGNIFICANT BURNS AND WAS TAKEN TO THE HOSPITAL. NO STRUCTURES WERE INVOLVED BECAUSE THE METER SET IS LOCATED APPROXIMAT | 100
647 | 2008-01-18 | OH | sabotage | UNKNOWN (ALLEN COUNTY ) | DOMINION EAST OHIO | ON JANUARY 18, 2008, AT APPROXIMATELY 1:08 P.M. DOMINION EAST OHIO GAS CALL CENTER RECEIVED A REPORT FROM TOP QUALITY CABLE CONSTRUCTION OF A LINE HIT AT 880 SHAWNEE ROAD, LIMA, ALLEN COUNTY, OH. TOP QUALITY CABLE CONSTRUCTION, A CONTRACTOR DIRECTIONAL B | 4380
648 | 2008-04-08 | GA | sabotage | UNKNOWN (COBB COUNTY ) | ATLANTA GAS LIGHT CO | A CONTRACTOR WORKING FOR THE COBB COUNTY AND GEORGIA DEPARTMENT OF TRANSPORTATIONS BORED INTO A 6" HP GAS MAIN AT SANDY PLAINS ROAD AND WEST OAK PARKWAY WHILE INSTALLING SIGNAL CABLES. THE IMPACTED GAS MAIN WAS MIS-LOCATED BY THE COMPANY'S LOCATE CONTRACT | 954
649 | 2006-07-20 | GA | other | UNKNOWN (nan COUNTY ) | AUSTELL NATURAL GAS SYSTEM, CITY OF | JULY 20, 2006 AT APPROXIMATELY 0259 HRS, THIS INVESTIGATOR RESPONDED TO THE RESIDENTIAL PROPERTY LOCATED AT 4702 JAY BIRD LANE, POWDER SPRINGS, GEORGIA 30127 AFTER RECEIVING NOTIFICATION THERE WAS A POSSIBLE NATURAL GAS EXPLOSION. IT WAS REVEALED DURING | 0
650 | 2008-04-26 | NJ | other | UNKNOWN (HUNTERDON COUNTY ) | ELIZABETHTOWN GAS CO | BUILDING FIRE, UNRELATED TO GAS, DAMAGED METERS AND CAUSED THEM TO LEAK. EXCESS FLOW VALVE STOPPED GAS FLOW. GAS WAS NOT A CONTRIBUTING FACTOR DAMAGE. | 100
651 | 2008-04-14 | MN | other | UNKNOWN (SAINT LOUIS COUNTY ) | CITY OF DULUTH PUBLIC WORKS & UTILITIES | THE EXPLOSION OCCURED ON 4/14/08. THE UTILITY PERFORMED THE FOLLOWING ACTIVITIES: A. LEAK SURVEYED THE DISTRIBUTION SYSTEM IN THE AREA ON 4/14. B. LEAK SURVEYED INSIDE THE HOUSES IN THE AREA ON 4/14. C. BARHOLED OVER THE GAS MAIN ON W. 8TH ST ON 4 | 0
652 | 2008-05-13 | AK | other | UNKNOWN (ANCHORAGE COUNTY ) | ENSTAR NATURAL GAS CO | AT 0415, TUESDAY MAY 13, 2008, ENSTAR NATURAL GAS COMPANY WAS NOTIFIED OF A STRUCTURE FIRE BY THE ANCHORAGE FIRE DEPARTMENT AT 6258 41ST COURT, ANCHORAGE, AK. A SERVICE TECHNICIAN RESPONDED TO FIND AN 8 UNIT CONDO COMPLEX ON FIRE. THE FIRE HAD MELTED 2 | 200
653 | 2008-05-08 | NM | other | UNKNOWN (LUNA COUNTY ) | PUBLIC SERVICE COMPANY OF NEW MEXICO - GAS SVCS | UPON ARRIVAL...VALVE WAS TUNRED OFF BY SUNSHINE VOLUNTEER FIRE DEPARTMENT PERSONNEL. NIPPLE WAS BROKEN ABOVE STOP, PROBED ENTIRE AREA, 0% LEL - NO GAS. SOAP TESTED VALVE/FITTINGS AND BENT RISER...REFERRED TO C&M TO REPLACE 1" PE RISER AND TEST BACK TO MAI | 100
654 | 2008-04-29 | MI | sabotage | UNKNOWN (KENT COUNTY ) | MICHIGAN CONSOLIDATED GAS CO (MICHCON) | AT APPROXIMATELY 7:20 AM ON TUESDAY, APRIL 29, 2008, AN EXCAVATOR INSTALLING A SECTION OF CONCRETE SEWER STRUCK A 6-INCH PLASTIC NATURAL GAS DISTRIBUTION MAIN AT THE SOUTHEAST CORNER OF THE INTERSECTION OF SHELDON AVENUE AND WEALTHY STREET. THE 6-INCH MAI | 29000
655 | 2008-04-28 | VA | natural disasters | UNKNOWN (SUFFOLK CITY COUNTY ) | VIRGINIA NATURAL GAS | AT APPROXIMATELY 4:30 PM ON APRIL 28, 2008 AN EF-3 TORNADO HIT THE CITY OF SUFFOLK. APPROXIMATELY 1,200-HOMES WERE DAMAGED AND 145-HOMES WERE CONDEMNED AS A RESULT OF THE VIOLENT STORM. TWO SUBDIVISIONS, BURNETT'S MILL AND HILL POINT FARMS (OFF OF GODWIN | 6000
656 | 2008-04-29 | MD | maintenance | UNKNOWN (BALTIMORE CITY COUNTY ) | BALTIMORE GAS & ELECTRIC CO | MR. ADAMS WHILE ATTEMPTING TO SHUT OFF WATER TO THE HOUSE AT THE WATER METER VAULT AT 2252 ANNAPOLIS RD. MR. ADAMS WAS INJURED WHEN GAS ACCUMULATED IN THE WATER METER VAULT WAS IGNITED BY MS. JACKSON USING HER "BIC" LIGHTER AS A FLASH LIGHT. | 0
657 | 2008-04-17 | IN | sabotage | UNKNOWN (DECATUR COUNTY ) | FOUNTAINTOWN GAS CO INC | FARM EMPLOYEE REPAIRING FIELD DRAINAGE TILE CUT GAS MAIN IN COUNTY HIGHWAY RIGHT-OF-WAY UNDER WATER AT CULVERT UNDER COUNTY ROAD 650 S. NO LOCATE REQUEST WAS MADE. GAS LINE MARKER IS IN PROXIMITY TO DIG SITE. | 15000
658 | 2008-05-06 | CO | other | UNKNOWN (SUMMIT COUNTY ) | PUBLIC SERVICE CO OF COLORADO | BROKEN THREADS WERE FOUND ON A PIPE NIPPLE BETWEEN THE SERVICE VALVE AND THE METER SET REGULATOR. THERE WAS UNANTICIPATED STRESS ON THE CUSTOMER FUEL LINE THAT TRANSFERRED STRESS TO THE METER SET. THE LEAKING GAS FROM THE RUPTURED PIPE NIPPLE ENTERED THE | 150
659 | 2008-05-12 | MD | other | UNKNOWN (PRINCE GEORGE'S COUNTY ) | WASHINGTON GAS LIGHT CO | WASHINGTON GAS WAS CALLED BY THE PRINCE GEORGE'S FIRE BOARD TO ASSIST WITH A HOUSE FIRE AT 13005 MINETTA LANE IN BOWIE. THE FIRE IS BELIEVED TO HAVE STARTED IN THE HOUSE AND LATER INVOLVED THE WASHINGTON GAS FACILITIES. THE SERVICE WAS CUT OFF AT THE ME | 100
660 | 2008-04-03 | NY | sabotage | UNKNOWN (WESTCHESTER COUNTY ) | CONSOLIDATED EDISON CO OF NEW YORK | ON THURSDAY, APRIL 3, 2008 AT 14:22, CON EDISON¿S GAS EMERGENCY RESPONSE CENTER (GERC) RECEIVED A CALL FROM WESTCHESTER FIRE CONTROL REPORTING A GAS EXPLOSION AT 60 FAYETTE ROAD, SCARSDALE, NEW YORK. GAS DISTRIBUTION SERVICES (GDS) RESPONDED AND REPORTED | 200
661 | 2008-06-10 | CA | other | UNKNOWN (SANTA CLARA COUNTY ) | PACIFIC GAS & ELECTRIC CO | A FIRE, THE CAUSE OF WHICH IS CURRENTLY UNKNOWN, SEVERLY DAMAGED THE METER SET AT 5890 MACADAM COURT LEADING TO ESCAPING GAS BEING IGNITED. THE FIRE DAMAGED ONE HOUSE AND CAUSED MINOR DAMAGE TO A SECOND. A PG&E GAS CREW EXCAVATED THE SERVICE TEE AT THE G | 100
662 | 2008-05-03 | IL | sabotage | UNKNOWN (DOUGLAS COUNTY ) | CENTRAL ILLINOIS LIGHT CO | HOME OWNER RENTED A DITCHWITCH WALK BEHIND TRENCHER AND WAS IN THE PROCESS OF TRENCHING IN SEWER LATERALS WHEN THE 2" P.E. GAS MAIN WAS DAMAGE. THE DAMAGE TO THE GAS MAIN RESULTED IN A RELEASE OF GAS WHICH IGNITED. THE HOME OWNER AND HIS FATHER WERE EXPOS | 1000
663 | 2008-05-29 | NE | natural disasters | UNKNOWN (BUFFALO COUNTY ) | NORTHWESTERN ENERGY LLC | ON MAY 29, 2008 SEVERAL EF2 TORNADO HIT THE CITY OF KEARNEY, NE. AS A RESULT OF THE SEVERE WEATHER HIGH WINDS CAUSED DAMAGE TO THE STRUCTURE/BUILDING AT 4855 AIRPORT ROAD, AN AIRPLANE HANGER. THE COLLAPSE OF THE BUILDING AND DEBRIS CAUSED DAMAGE TO NORTH | 85
664 | 2008-05-19 | MI | sabotage | UNKNOWN (BERRIEN COUNTY ) | MICHIGAN GAS UTILITIES CO | CONTRACTOR HAD EXPOSED MAIN AND WAS USING A TRACK HOE TO SCRAPE THE COVER FROM THE TOP IN ORDER TO EXPOSE IT. HE SNAGGED A RETIRED SERVICE TEE WITH THE BUCKET AND TORE IT OFF THE MAIN. THE CONTRACTOR THEN CURLED THE TRACK HOE BUCKET AND SET IT ON THE DAMA | 125607
665 | 2008-05-16 | TX | sabotage | UNKNOWN (COLLIN COUNTY ) | ATMOS ENERGY CORPORATION, MID-TEX DIVISION | A COMPANY CONTRACTOR OPERATING A DIRECTIONAL DRILLING MACHINE PUNCTURED A MARKED 3 INCH GAS MAIN. | 1500
666 | 2008-05-21 | PA | sabotage | UNKNOWN (DAUPHIN COUNTY COUNTY ) | U G I CORP | ON WEDNESDAY MAY 21, 2008, A BACKHOE OPERATOR WITH HANDWERK MATERIALS STRUCK A 1975 3/4" MEDIUM PRESSURE STEEL SERVICE LINE AT 298 E. MAIN STREET, HUMMELSTOWN, PA. THE DAMAGE RESULTED IN THE SERVICE LINE BEING PULLED FROM THE METER SET IN THE BASEMENT, R | 400
667 | 2008-05-21 | IN | other | UNKNOWN (WHITLEY COUNTY ) | NORTHERN INDIANA PUBLIC SERVICE CO | NIPSCO CENTRAL OPERATIONS WAS ADVISED THAT A VEHICLE HAD HIT A REGULATOR STATION AT THE ABOVE LOCATION, AND GAS WAS BLOWING. NIPSCO¿S FIRST RESPONDER WAS ON SITE AT 8:13 P.M. THE WEATHER WAS CLEAR, NO CLOUDS, AROUND 49 DEGREES, AND A VERY SLIGHT WIND +- | 5000
668 | 2008-01-24 | OR | other | UNKNOWN (CLACKAMAS COUNTY ) | LEGACY PROPANE VANCOUVER, LLC | THE ACCIDENT OCCURRED AT THE COLLINS LAKE RESORT, A RESORT COMMUNITY WHICH SITS AT THE BASE OF MT. HOOD SKIBOWL SKI AREA LOCATED IN GOVERNMENT CAMP, OREGON. IT IS AN ELEVATION OF NEARLY 4000 FEET. LEGACY PROPANE INSTALLED THE PROPANE SYSTEM FROM 2003-2005 | 500
669 | 2007-03-08 | MA | other | UNKNOWN (ESSEX COUNTY ) | BOSTON GAS CO | UPDATED BY PHMSA ON 2/9/2016 PER OPERATOR'S MARK UP (PART F - APPARENT CAUSE, F4 - OTHER OUTSIDE FORCE DAMAGE, ITEM 10; AND PART I - NARRATIVE). PART G - KEYSPAN RECEIVED A CALL FROM THE PEABODY FIRE DEPARTMENT TO SHUT OFF GAS TO 19 DEARBORN ROAD, PEAB | 0
670 | 2008-05-29 | CA | maintenance | UNKNOWN (SAN JOAQUIN COUNTY ) | PACIFIC GAS & ELECTRIC CO | IN PREPARATION OF RECOATING A SHORT SECTION OF DISTRIBUTION FEEDER MAIN, A PG&E PAINT CREW WAS SANDBLASTING THE 8-INCH DIAMETER PIPE SURFACE. DURING THE SANDBLASTING, A PINHOLE LEAK WAS OBSERVED. A TEMPORARY BYPASS WAS INSTALLED AND A 5.5-FOOT SECTION O | 100
671 | 2004-05-10 | PA | other | UNKNOWN (GREENE COUNTY ) | COLUMBIA GAS OF PENNSYLVANIA | AIR WAS INTRODUCED INTO COLUMBIA GAS DISTRIBUTION LINE NEAR HUPP STATION. GATHERING 2" INLET LINE WAS CRACKED AND ALLOWING AIR TO BE SUCKED INTO GATHERING LINE, THEN PUMPED INTO COLUMBIA GAS LINE. NOTE: THIS IS A RE-SUBMITTAL OF THE ORIGINAL INCIDENT R | 0
672 | 2008-06-02 | VA | other | UNKNOWN (PRINCE WILLIAM COUNTY ) | WASHINGTON GAS LIGHT CO | WASHINGTON GAS RESPONDED TO A HOUSE FIRE AT 2563 SYLVAN MOOR LANE IN WOODBRIDGE AT THE REQUEST OF THE PRINCE WILLIAM COUNTY FIRE DEPARTMENT. UPON ARRIVAL, THE SERVICE LINE WAS DUG UP AT THE SERVICE TEE CONNECTION AT THE MAIN AND SQUEEZED-OFF TO STOP THE | 100
673 | 2008-06-18 | NE | other | UNKNOWN (RED WILLOW COUNTY ) | SOURCEGAS LLC | VEHICLE (PICKUP TRUCK) WENT OUT OF CONTROL AND LEFT ROADWAY STRIKING A POWER POLE FLIPPING VEHICLE INTO THE AIR. COMBINATION OF VEHICLE AND POWER POLE COLLIDED WITH PRESSURE REGULATION FACILITY/BARRICADE SHEARING OFF THREE NEEDLE VALVES. | 210
674 | 2008-06-07 | MD | natural disasters | UNKNOWN (MONTGOMERY COUNTY ) | WASHINGTON GAS LIGHT CO | WASHINGTON GAS RESPONDED TO A HOUSE FIRE AT 5826 CONWAY ROAD, BETHESDA AT THE REQUEST OF THE MONTGOMERY COUNTY FIRE BOARD ON SATURDAY, JUNE 7, 2008 AT 21:43. THE FIRE HAD REPORTEDLY BEEN STARTED BY A LIGHTNING STRIKE TO THE NATURAL GAS METER SET. WASHIN | 100
675 | 2008-06-10 | NY | natural disasters | UNKNOWN (DUTCHESS COUNTY ) | CENTRAL HUDSON GAS & ELECTRIC CORP | ON JUNE 10, 2008, AT APPROXIMATELY 21:23, THERE WAS A LIGHTNING STRIKE WHICH CAUSED AN ELECTRIC PRIMARY PHASE WIRE ON SWENSON DRIVE IN THE TOWN OF POUGHKEEPSIE TO FALL TO THE GROUND IN THE VICINITY OF THE SWENSON DRIVE GAS REGULATOR STATION RELIEF VALVE. | 6
676 | 2008-05-25 | IA | natural disasters | UNKNOWN (BUTLER COUNTY ) | MIDAMERICAN ENERGY COMPANY | THE CAUSE OF THE INCIDENT WAS AN EF-5 TORNADO THAT HIT THE TOWN OF PARKERSBURG, IOWA. THIS INCIDENT IS BEING REPORTED BECAUSE IT IS CONSIDERED TO BE A SIGNIFICANT EVENT. MIDAMERICAN ENERGY COMPANY'S FACILITIES THAT WERE DAMAGED BY THE TORNADO INCLUDE S | 0
677 | 2008-06-27 | UT | other | UNKNOWN (SUMMIT COUNTY ) | QUESTAR GAS COMPANY | A HOUSE FIRE MELTED THE METER WHICH RESULTED IN THE RELEASE OF GAS. THE CAUSE OF THE FIRE HAS NOT BEEN RELEASED TO THE PUBLIC, THE LEAD FIRE INVESTIGATOR DID INDICATE THAT NATURAL GAS WAS NOT INVOLVED IN THE ORIGIN OF THE FIRE. | 100
678 | 2008-06-28 | UT | other | UNKNOWN (SALT LAKE COUNTY ) | QUESTAR GAS COMPANY | A GRASS FIRE CAUGHT THE BUILDING ON FIRE AND MELTED THE METER SET. | 328
679 | 2008-07-02 | CA | other | UNKNOWN (TULARE COUNTY ) | SOUTHERN CALIFORNIA GAS CO | ON JULY 2, 2008, A FIRE ERUPTED AT A RESIDENTIAL HOME AND A METER SET WAS MELTED AND IGNITED. DAMAGE FROM FIRE EXCEEDED $50,000, AND AS A RESULT, THE INCIDENT WAS REPORTED TO DOT AND CPUC. FURTHER INVESTIGATION DETERMINED THAT THE FIRE STARTED INSIDE | 50
680 | 2008-07-17 | CA | technical failure | UNKNOWN (SAN DIEGO COUNTY ) | SAN DIEGO GAS & ELECTRIC CO | ON JULY 17, 2008, A FIRE ERUPTED WHILE AN SDG&E CREW WAS WORKING TO REPAIR A LEAK ON A MEDIUM PRESSURE 3¿ PE MAIN. SINCE ONE EMPLOYEE RECEIVED FIRST AND SECOND DEGREE BURNS AND WAS TRANSPORTED TO THE HOSPITAL, THE INCIDENT WAS REPORRTED TO DOT AND CPUC. | 0
681 | 2008-07-31 | TX | sabotage | UNKNOWN (DENTON COUNTY ) | COSEAY GAS | 6" POLY MAIN DAMAGED BY CONTRACTOR DRILLING HOLES FOR NEW POWER POLES. AUGER WAS PLACED AND OPERATED WITHIN TOLERANCE ZONE OF LOCATE MARKINGS. | 11500
682 | 2008-07-07 | LA | other | UNKNOWN (JEFFERSON COUNTY ) | ATMOS ENERGY CORP (LOUISIANA DIVISION) | INTOXICATED DRIVER RAN OVER NATURAL GAS LOW PRESSURE REGULATOR STATION WITH A TRUCK. THE TRUCK BROKE A 2" GAS LINE CAUSING A FIRE. NOTE: THE TRUCK WAS LOST IN THE FIRE. THERE WAS ALSO DAMAGE TO A UTILITY POLE, AND THE RESIDENT AT THE INCIDENT LOCATION HA | 6305
683 | 2008-01-11 | MN | maintenance | UNKNOWN (CARVER COUNTY ) | CENTERPOINT ENERGY RESOURCES CORP., DBA CENTERPOINT ENERGY MINNESOTA GAS | ABOUT A WEEK PRIOR TO THE INCIDENT, HOMEOWNER SMELLED GAS. HOMEOWNER CONTACTED A LOCAL APPLIANCE REPAIR COMPANY, SUSPECTING HIS OLD FURNACE WAS THE SOURCE OF THE LEAK. THE REPAIR TECHNICIAN SOLD THE HOMEOWNER A USED FURNACE AND INSTALLED THE FURNACE ON | 0
684 | 2008-08-22 | AK | other | UNKNOWN (ANCHORAGE COUNTY ) | ENSTAR NATURAL GAS CO | A FIRE STARTED INSIDE A TRAVEL TRAILER THAT WAS PARKED UNDER A CARPORT AT THIS ADDRESS. THE FIRE PROGRESSED FROM THE TRAVEL TRAILER TO THE HOUSE AND SUBSEQUENTLY BURNED THE GAS METER AND REGULATOR. ENSTAR CREWS DUG UP THE SERVICE LINE AND SHUT IF OF AT | 50
685 | 2008-07-25 | NY | technical failure | UNKNOWN (QUEENS COUNTY ) | CONSOLIDATED EDISON CO OF NEW YORK | ON FRIDAY, 7/25/2008 AT 16:50, CON EDISON'S GAS EMERGENCY RESPONSE CENTER (GERC) RECEIVED A CALL FROM THE FIRE DEPARTMENT OF NEW YORK (FDNY) REPORTING A GAS EXPLOSION AT 147-25 SANFORD AVENUE, FLUSHING, NEW YORK. GAS DISTRIBUTION SERVICES (GDS) RESPONDED | 0
686 | 2008-07-21 | CA | sabotage | UNKNOWN (HUMBOLDT COUNTY ) | PACIFIC GAS & ELECTRIC CO | A LARGE EXCAVATOR, DIGGING TO INSTALL A CULVERT, WAS MANEUVERING AROUND SOME GROUND SUBSIDENCE AND STRUCK A 4-INCH GAS TRANSMISSION LINE WITH ITS TRACK. THE GAS LINE WAS PROPERLY MARKED AND PG&E HAD STOOD BY DURING CONSTRUCTION ON PRIOR DAYS. NO STANDBY W | 500
687 | 2008-08-07 | UT | technical failure | UNKNOWN (SALT LAKE COUNTY ) | QUESTAR GAS COMPANY | THE RELEASE OF GAS AND THE RESULTING EMPLOYEE INJURY WAS THE RESULT OF THE EMPLOYEE INADVERTENTLY OPERATING A SLIDE GATE VALVE RESULTING IN INJURIES TO THAT EMPLOYEE. THE EMPLOYEE WAS INJURED IN THE FACE AND WAS HOSPITALIZED FOR SEVERAL DAYS. THE EMPLOY | 0
688 | 2008-08-07 | MD | sabotage | UNKNOWN (CECIL COUNTY ) | ELKTON GAS SERVICE - DIV PENNS & SOUTHERN GAS CO | THOMPSON ELECTRIC, CONTRACT FOR MD STATE HIGHWAY ADMINISTRATION, HIT ELKTON GAS 4" STEEL WHILE PREPARING A TRENCH FOR INSTALLATION OF ELECTRIC FOR NEW TRAFFIC LIGHTS AT THE INTERSECTION OF NORTH STREET AND RAILROAD AVENUE, IN ELTON MD 21921. GAS LINE WAS | 343
689 | 2008-08-05 | TX | other | UNKNOWN (HARRIS COUNTY ) | ENTEX, A NORAM ENERGY COMPANY (FORM. DIV OF ARKLA | ESCAPING GAS FROM A 1" STL SERVICE LINE ENTERED STRUCTURE & REACHED AN UNKNOWN IGNITION SOURCE. | 313
690 | 2008-08-24 | CA | other | UNKNOWN (TULARE COUNTY ) | SOUTHERN CALIFORNIA GAS CO | ON AUGUST 24, 2008, A STRUCTURE FIRE OCCURRED AT THE ABOVE ADDRESS. THE BUILDING WAS SEVERELY DAMAGED FROM FIRE. THE GAS METER WAS MELTED FROM THE INTENSE HEAT, AND ESCAPING GAS IGNITED. IGNITED GAS DID NOT CREATE FURTHER DAMAGE, NOR DID IT IMPACT FIRE | 0
691 | 2008-08-07 | KS | other | UNKNOWN (SHAWNEE COUNTY ) | KANSAS GAS SERVICE | A DELIVERY VAN USED BY DRY CLEANING BUSINESS WAS BEING STOLEN FROM THE PROPERTY WHEN THE DRIVER BACKED OVER THE CUSTOMERS METER SET AND RISER LOCATED AT THE PROPERTY LINE. THE COLLISION WITH THE METER SET AND RISER BROKE THE RISER JUST BELOW GROUND LEVEL | 7000
692 | 2008-08-27 | WY | other | UNKNOWN (UINTA COUNTY ) | QUESTAR GAS COMPANY | GAS FROM THE METER IGNITED AS A RESULT OF THE BUILDING BEING ON FIRE. | 0
693 | 2008-09-02 | ND | leaks and spills | UNKNOWN (CASS COUNTY ) | NORTHERN STATES POWER CO OF MINNESOTA |  | 0
694 | 2008-09-12 | CA | other | UNKNOWN (LOS ANGELES COUNTY ) | SOUTHERN CALIFORNIA GAS CO | ON SEPTEMBER 13, 2008 A METER SET ASSEMBLY WAS DAMAGED BY A VEHICLE THAT LOST CONTROL, LEAVING THE ROADWAY, CRASHING THROUGH A BLOCK WALL AND STRIKING INTO THE METER SET ASSEMBLY. THE ESCAPING GAS IGNITED, CAUSING A FIRE THAT DAMAGED A BUILDING. DUE | 0
695 | 2008-09-16 | CA | other | UNKNOWN (RIVERSIDE COUNTY ) | SOUTHERN CALIFORNIA GAS CO | ON JUNE 18TH, 2007, A STRUCTURE FIRE OCCURRED AT THIS LOCATION. THE BUILDING WAS SEVERELY DAMAGED FROM FIRE. THE INTENSE HEAT ALSO DAMAGED THE _ PE SERVICE RISER, WITH ESCAPING GAS ULTIMATELY IGNITING. THIS INCIDENT BECAME REPORTABLE WHEN TOTAL FIRE | 0
696 | 2008-07-09 | WA | sabotage | UNKNOWN (KING COUNTY ) | PUGET SOUND ENERGY | A CONTRACTING FIRM RETAINED BY A LOCAL MUNICIPAL HOUSING AUTHORITY TO INSTALL SITE UTILITIES AND PERFORM GENERAL CONSTRUCTION ACTIVITIES DAMAGED (SEVERED) THE 2¿ WELDED TEE SECTION WELDED ON A 6¿ DISTRIBUTION WELD. ALL APPLICABLE PSE (PUDGET SOUND ENERGY | 30614
697 | 2008-09-11 | VA | other | UNKNOWN (FAIRFAX COUNTY ) | WASHINGTON GAS LIGHT CO | WASHINGTON GAS RESPONDED TO THE REPORT OF A COMMERCIAL BUILDING FIRE AT 6065 RICHMOND HIGHWAY, ALEXANDRIA ON THE EVENING OF SEPTEMBER 11, 2008. THE CREW DUG DOWN ON THE TWO-INCH PLASTIC SERVICE, SQUEEZED IT OFF, AND THEN CAPPED IT OFF. A SUBSURFACE LEAK | 1000
698 | 2008-09-20 | MI | other | UNKNOWN (OAKLAND COUNTY ) | CONSUMERS ENERGY CO | A CALL FROM 911 CAME INTO THE CUSTOMER SERVICE CENTER AND A SERVICE WORKER WAS DISPATCHED TO 850 S. PEMBERTON. UPON ARRIVAL THE SERVICE WORKER FOUND A HOME DESTROYED BY AN EXPLOSION AND SUBSEQUENT FIRE. ONE RESIDENCE AT THE HOME DIED IN THE EVENT. A CO | 20
699 | 2008-09-25 | UT | other | UNKNOWN (SWEETWATER COUNTY ) | QUESTAR GAS COMPANY | GAS FROM THE METER IGNITED AS A RESULT OF THE BUILDING BEING ON FIRE. | 0
700 | 2008-09-20 | IN | other | UNKNOWN (MARION COUNTY ) | CITIZENS GAS & COKE UTILITY | UPON A COMPLETE INVESTIGATION IT WAS DETERMINED THIS RESIDENTIAL FIRE ORIGINATED INSIDE THE BUILDING AND THE HEAT, FROM THE FIRE, IMPINGED ON THE RISER CAUSING THE RELEASE OF GAS. | 0
701 | 2008-10-01 | CA | sabotage | UNKNOWN (ORANGE COUNTY ) | SOUTHERN CALIFORNIA GAS CO | ON OCTOBER 1, 2008 A 3 INCH PE MAIN WAS DAMAGED BY A BACKHOE EXCAVATING FOR STREET LIGHTING. THE ESCAPING GAS IGNITED, CAUSING A FIRE THAT DAMAGED THE BACKHOE. NO INJURIES OR OUTAGES RESULTED FROM THIS INCIDENT. REPAIRS WERE COMPLETED THE SAME DAY. | 500
702 | 2008-10-02 | MD | other | UNKNOWN (MONTGOMERY COUNTY ) | WASHINGTON GAS LIGHT CO | WASHINGTON GAS RESPONDED TO A HOUSE FIRE AT THE REQUEST OF THE MONTGOMERY COUNTY FIRE DEPARTMENT AT 219 FREDERICK AVENUE, ROCKVILLE, MD. THE FIRE IS BELIVED TO HAVE STARTED ON A MATTRESS AND THEN CONSUMED THE METER BUILD-UP. WASHINGTON GAS PERFORMED A L | 100
703 | 2008-10-16 | CO | sabotage | UNKNOWN (EL PASO COUNTY ) | BLACK HILLS ENERGY | PRIVATE CONTRACTOR INSTALLING ELECTRIC SERVICE AT NEW RESTAURANT STRUCK A 2" GAS SERVICE PREVIOUSLY INSTALLED AT THE SAME LOCATION. LOCATES WERE NOT CALLED IN PRIOR TO EXCAVATION. RESULTING FIRE DESTROYED A TRENCHER BELONGING TO THE EXCAVATOR AND DID EXTE | 150
704 | 2008-10-15 | CA | other | UNKNOWN (CONTRA COSTA COUNTY COUNTY ) | PACIFIC GAS & ELECTRIC CO | TRASH FIRE SPREAD FROM RESIDENCE GREEN CAN TO THE ADJACENT FENCE, THEN TO THE HOME AND THE GAS METER SET. THE GAS METER, REGULATOR, AND RISER MELTED, AND THE ESCAPING GAS CONTRIBUTED TO THE FIRE. IT IS BELIEVED THAT RAGS SOAKED WITH CHEMICALS CAUSED THE | 0
705 | 2008-10-22 | AZ | leaks and spills | UNKNOWN (YUMA COUNTY ) | SOUTHWEST GAS CORP | ON 10/22/08 AT 2016 HOURS, SOUTHWEST GAS CORPORATION (SWG) WAS NOTIFIED OF A STRUCTURE FIRE AT THE ABOVE ADDRESS BY THE YUMA RURAL METRO FIRE DEPARTMENT. THE SWG TECHNICIAN ARRIVED ON SITE AT 2048 HOURS AND FOUND THE FIRE, WHICH HAD BEEN EXTINGUISHED, HA | 0
706 | 2008-10-18 | NC | other | UNKNOWN (GUILFORD COUNTY ) | PIEDMONT NATURAL GAS CO INC | AT 11:49 AM ON OCTOBER 18, 2008, PIEDMONT NATURAL GAS (PNG) RECEIVED A CALL FROM THE LOCAL FIRE DEPARTMENT IN GREENSBORO, NC NOTIFYING US OF A FIRE AT 2215 TEXTILE DRIVE. THE FIRST RESPONDER WAS DISPATCHED TO THE SCENE SHORTLY THEREAFTER. PNG PERSONNEL | 0
707 | 2008-10-18 | MD | other | UNKNOWN (PRINCE GEORGES COUNTY ) | WASHINGTON GAS LIGHT CO | WASHINGTON GAS WAS CALLED BY THE PRINCE GEORGES FIRE DEPARTMENT TO ASSIST WITH A HOUSE FIRE LOCATED AT 6600 TROWBRIDGE PLACE, FORT WASHINGTON, MARYLAND. THE FIRE DAMAGED THE METER AND REGULATOR ASSEMBLY LOCATED IN THE BASEMENT. THE FIRE DEPARTMENT TURNE | 100
708 | 2008-10-22 | CA | other | UNKNOWN (SAN FRANCISCO COUNTY ) | PACIFIC GAS & ELECTRIC CO | A FLASH FIRE IN A WORKING TRENCH WAS CAUSED BY A 3RD PARTY WHO WAS SOLDERING A WATER PIPE AND INADVERTENTLY LET THE FLAME DAMAGE A 1/2 INCH PG&E PLASTIC GAS PIPE NEARBY. THE USA TICKET WAS EXPIRED IN THIS AREA. ACCORDING TO THE 3RD PARTY, THE WORKER WAS | 50
709 | 2008-10-18 | WY | other | UNKNOWN (SWEETWATER COUNTY ) | QUESTAR GAS COMPANY | AT APPROXIMATELY 4:30 A.M. ON SATURDAY, OCTOBER 18, 2008 A VEHICLE TRAVELING EAST ON FOOTHILL BOULEVARD APPROXIMATELY 1.5 MILES WEST OF ROCK SPRINGS WYOMING, LEFT THE ROADWAY AND IMPACTED AN ABOVE GROUND QUESTAR FACILITY CONSISTING OF A 2" TAP AND RISER, | 2640
710 | 2008-11-15 | CA | technical failure | UNKNOWN (COLUSA COUNTY ) | PACIFIC GAS & ELECTRIC CO | A PG&E EMPLOYEE WAS INJURED WHILE INSTALLING AND PURGING A COMMERCIAL METER SET. WHILE GAS WAS VENTING, THE EMPLOYEE BEGAN TIGHTENING THE FLANGE BOLTS WITH AN 18-VOLT WRENCH WHEN THE FIRE IGNITED. THE EMPLOYEE WAS TRANSPORTED TO THE HOSPITAL WHERE HE SPE | 0
711 | 2008-10-22 | VA | other | UNKNOWN (PRINCE WILLIAM COUNTY ) | WASHINGTON GAS LIGHT CO | WASHINGTON GAS RESPONDED TO A HOUSE FIRE LOCATED AT 3225 CONKLIN WAY, HAYMARKET, VA AT THE REQUEST OF THE PRINCE WILLIAM FIRE DEPARTMENT. UPON ARRIVAL WASHINGTON GAS FOUND THE METER VALVE HAD BEEN TURNED OFF BY THE FIRE DEPARTMENT. WASHINGTON GAS ALSO D | 100
712 | 2008-11-03 | CA | other | UNKNOWN (LOS ANGELES COUNTY ) | SOUTHERN CALIFORNIA GAS CO | ON NOVEMBER 3, 2008, A SERVICE RISER WAS DAMAGED WHEN A FORK LIFT STRUCK A CUSTOMER HOUSELINE, SHIFTING THE METER SET ASSEMBLY AND CRACKING THE RISER BELOW THE SHUTOFF VALVE. ESCAPING GAS IGNITED, DAMAGING THE FORKLIFT AND NEARBY TRUCK. FORKLIFT OPERA | 0
713 | 2008-11-04 | NJ | other | UNKNOWN (MONMOUTH COUNTY ) | NEW JERSEY NATURAL GAS CO | IT IS NJNG UNDERSTANDING FROM INFORMATION GATHERED THAT THE HOMEOWNER WAS TRYING TO RELIGHT HIS HOUSE FURNACE AT WHICH TIME THE GAS IGNITED AND AN EXPLOSION OCCURED. THIS INCIDENT IS UNDER INVESTIGATION BY THE AUTHORITIES. UPDATE: THE FINAL CAUSE OF THI | 0
714 | 2008-10-31 | OH | sabotage | UNKNOWN (FRANKLIN COUNTY ) | COLUMBIA GAS OF OHIO INC | THIS INCIDENT WAS CAUSED BY 3RD PARTY DAMAGE RESULTING IN THE RELEASE OF GAS AND SUBSEQUENT EXPLOSION. NOTE. PART A SECTION 8-A WILL ALLOW ONLY WHOLE NUMBERS WITH NO DECIMALS TO BE ENTERED AND THAT 1.0 WAS ENTERED WHILE THE ACTUAL MAOP FOR THIS SYSTE | 1480
715 | 2008-10-31 | KY | sabotage | UNKNOWN (FAYETTE COUNTY ) | COLUMBIA GAS OF KENTUCKY INC | ATS CONTRACTING WAS GRADING ALONG THE SHOULDER OF NEW CIRCLE ROAD ON THE OUTER LOOP SHOULDER FOR ROAD CONSTRUCTION, THEY HAD CALLED FOR CURRENT LOCATES AND DPS LOCATING HAD PROPERLY LOCATED THE 12" HIGH PRESSURE MAIN. (LOCATE TICKET #810160081). ATS ASSU | 375810
716 | 2008-10-25 | OH | other | UNKNOWN (RICHLAND COUNTY ) | COLUMBIA GAS OF OHIO INC | COLUMBIA'S INVESTIGATION HAS DETERMINED THAT THIS EVENT DID NOT INVOLVE A RELEASE OF NATURAL GAS FROM A DOT JURISDICTIONAL FACILITY. THEREFORE, COLUMBIA HAS CONCLUDED THAT THIS WAS NOT A REPORTABLE INCIDENT. PLEASE CLOSE YOUR FILE IN THIS MATTER. | 11
717 | 2008-11-07 | MD | sabotage | UNKNOWN (nan COUNTY ) | BALTIMORE GAS & ELECTRIC CO | MILLER PIPELINE A CONTRACTOR WORKING FOR BALTIMORE GAS & ELECTRIC COMPANY INSTALLING A 12" STEEL MAIN FOR A REINFORCEMENT/REPLACEMENT PROJECT STRUCK 1-1/4" STEEL SERVICE TO 8860 GORMAN RD CAUSING GAS LEAK. | 54000
718 | 2008-11-13 | CA | other | UNKNOWN (nan COUNTY ) | SOUTHERN CALIFORNIA GAS CO | ON NOVEMBER 13, 2008 A FIRE BROKE OUT IN THE CITY OF MONTECITO, DAMAGING SERVICES, RISERS AND METER SET ASSEMBLIES. DAMAGE TO SOCALGAS GAS FACILITIES WAS LIMITED TO THESE COMPONENTS. NO DAMAGE TO DISTRIBUTION MAINS OR TRANSMISSION LINES OCCURRED. WHI | 5000
719 | 2008-11-15 | CA | other | UNKNOWN (LOS ANGELES AND ORANGE COUNTY ) | SOUTHERN CALIFORNIA GAS CO | ON NOVEMBER 15, 2008 NUMEROUS FIRES BROKE OUT ACROSS SOUTHERN CALIFORNIA GAS COMPANY (SOCALGAS) SERVICE TERRITORY, DAMAGING SERVICES, RISERS AND METER SET ASSEMBLIES. DAMAGE TO SOCALGAS GAS FACILITIES WAS LIMITED TO THESE COMPONENTS. NO DAMAGE TO DISTRI | 5000
720 | 2008-11-13 | CO | sabotage | UNKNOWN (PUEBLO COUNTY ) | PUBLIC SERVICE CO OF COLORADO | AFTER THE EXPLOSION, A LEAK WAS DISCOVERED ON THE NATURAL GAS SERVICE FOR 105 W. C STREET. THIS SERVICE SUPPLIED NATURAL GAS TO THE BUILDING ACROSS C STREET FROM 301 S. UNION. THE SERVICE TO 105 W. C STREET WAS A 3/4" PLASTIC CAB LINE (CELLULOSE ACETATE B | 200
721 | 2008-12-03 | MO | sabotage | UNKNOWN (ADAIR COUNTY ) | ATMOS ENERGY CORPORATION - KY/MID-STATES (KENTUCKY) | C-COM WAS TRENCHING IN TV CABLE ON 12/03/2008 FOR SMOYER TRENCHING AND CABLE COMPANY. AT APPROXIMATELY 7:30 AM ON THE MORNING OF 12/03/2008, C-COM OPERATOR OF TRENCHING MACHINE HIT AND DAMAGED 6" STEEL MAIN OF ATMOS ENERGY. THIS MAIN LINE SERVED CUSTOMERS | 6035
722 | 2008-11-09 | DE | other | UNKNOWN (NEW CASTLE COUNTY ) | DELMARVA POWER & LIGHT COMPANY | NEW CASTLE COUNT POLICE REPORT INVESTIGATIVE SUMMARY (CPL. SOMMERS): PRELIMINARY INVESTIGATION REVEALS THAT FOR UNKNOWN REASONS, POSSIBLY MECHANICAL, VEH-1 (1992 CHEVROLET CAPRICE WHITE IN COLOR WITH DELAWARE REGISTRATION 57903) STRUCK THE FRONT OF THE R | 264
723 | 2008-11-01 | GA | sabotage | UNKNOWN (COWETA COUNTY ) | ATLANTA GAS LIGHT CO | A CONTRACTOR WORKING FOR COWETA COUNTY STRUCK AND KNOCKED A 2-INCH TEE OFF A 6" HP GAS MAIN ALONG RAYMOND HILL ROAD AT FISHER ROAD WHILE WORKING ON A ROAD WIDENING PROJECT. THE CONTRACTOR WAS ATTEMPTING TO REMOVE AN ABANDON GAS MAIN WITH WITH A TRACK HOE | 2322
724 | 2008-12-13 | AK | other | UNKNOWN (MATANUSKA SUSITNA BOROUGH COUNTY ) | ENSTAR NATURAL GAS CO | ON SATURDAY, DECEMBER 13, 2008 AT 0958 AN ENSTAR SERVICE TECHNICIAN RESPONDED TO A RESIDENTIAL STUCTURE FIRE AT LOT 6, BLOCK 2 KNIK HIGHLANDS SUBDIVISION NEAR WASILLA, ALASKA TO FIND THE PRESSURE REGULATOR AND METER BURNED AND HDPE SERVICE LINE RISER ON F | 100
725 | 2008-09-19 | WA | sabotage | UNKNOWN (KING COUNTY ) | PUGET SOUND ENERGY | THE INCIDENT OCCURRED ON SEPT. 19, 2008, AND PSE RESPONDED TO THE INCIDENT REPORT IMMEDIATELY. THE 3RD PARTY CONTRACTOR, WILDER CONSTRUCTION, DAMAGED A 2" STW GAS DISTRIBUTION MAIN WHILE PLACING A SHORING BOX UNDER A WATER DRAINPIPE. PSE'S FIRST RESPONDER | 4542
726 | 2008-11-27 | OH | leaks and spills | UNKNOWN (CUYAHOGA COUNTY ) | COLUMBIA GAS OF OHIO INC | Columbia Gas of Ohio, Inc. (Columbia) has completed its investigation and concluded that the incident was the result of an improperly assembled mechanical compression fitting. The property owner’s representative took possession of the pertinent portions o | 51
727 | 2008-12-12 | VA | sabotage | UNKNOWN (PRINCE WILLIAM COUNTY ) | COLUMBIA GAS OF VIRGINIA INC | ON 12/12/08, COLUMBIA GAS OF VIRGINIA SUSTAINED A FACILITY DAMAGE TO A 6" PLASTIC, MEDIUM PRESSURE MAIN ON HEATHCOTE BLVD, GAINESVILLE, VIRGINIA. THE NEAREST CROSS STREET IS HERITAGE HUNT DRIVE. ACCORDING TO STAN PENROD OF TEAM FISHEL, THE MAIN WAS DAMAGE | 10721
728 | 2008-12-16 | AZ | other | UNKNOWN (GILA COUNTY ) | SEMSTREAM ARIZONA PROPANE LLC | 1 1/4" ALDYL PIPE APPEARED TO HAVE BEEN PREVIOUSLY SQUEEZED OFF, CAUSING DAMAGE TO THE PIPE. THERE WAS NO SEPERATION BETWEEN THE WATER AND GAS PIPE. INVESTIGATION COMPLETE, FINAL REPORT | 0
729 | 2008-12-19 | TN | other | UNKNOWN (DAVIDSON COUNTY ) | PIEDMONT NATURAL GAS CO INC | AT 6:58 PM CST, A PIEDMONT CUSTOMER SERVICE REPRESENTATIVE RECEIVED A LEAK CALL FOR 416 MURFREESBORO RD. AT 8:00 PM CST, PIEDMONT RECEIVED A CALL REGARDING AN EXPLOSION AT 416 MURFREESBORO RD. THE COMPANY'S SERVICE TECHNICIAN ARRIVED ON THE SCENE AT APP | 200
730 | 2008-12-26 | WA | leaks and spills | UNKNOWN (LINCOLN COUNTY ) | AVISTA CORP | ROCK IMPINGEMENT APPEARS TO HAVE CAUSED CRACK IN P.E. PIPE WALL. SNOW AND FROST IN GROUND CAUSED GAS TO MIGRATE TO NEARBY STRUCTURE. GAS ACCUMULATED IN UNDERGROUND AREA OF STRUCTURE AFTER PASSING THROUGH CRACK IN WALL. ONE RESIDENT STATED THAT HE ENTERED | 200
731 | 2009-01-02 | ID | natural disasters | UNKNOWN (KOOTENAI COUNTY ) | AVISTA CORP | HEAVY SNOW SLID OFF THE ROOF OF THE BUSINESS BUILDING DAMAGING THE METER SET. THE METER SET BROKE JUST BELOW THE REGULATOR CAUSING THE GAS TO ESCAPE AND MIGRATE INTO THE BUILDING WHICH RESULTED IN IGNITION AND A STRUCTURE FIRE. 6/2/09 CLICKED "FIN | 424
732 | 2008-12-19 | CO | natural disasters | UNKNOWN (PUEBLO COUNTY ) | PUBLIC SERVICE CO OF COLORADO | 3/4 INCH CAB SERVICE SEPARATED FROM A MECHANICAL COUPLING, LIKELY DUE TO THERMAL EXPANSION/ CONTRACTION. | 200
733 | 2009-01-16 | FL | sabotage | UNKNOWN (ALACHUA COUNTY ) | GAINESVILLE REGIONAL UTIL GAS DEPT | CONTRACTOR HAD BUILT A CAMP FIRE TO STAY WARM. THEIR LOCATES WERE OLD AND HAD WASHED AWAY. CONTRACTOR STRUCK 1 1/4 INCH MAIN WITH EXCAVATOR. CAMP FIRE IGNITED NATURAL GAS. NO INJURIES OR FATALITIES. | 400
734 | 2008-12-24 | CA | other | UNKNOWN (SACRAMENTO COUNTY ) | PACIFIC GAS & ELECTRIC CO | ON WEDNESDAY, DECEMBER 24, 2008 AT APPROXIMATELY 1335 THE HOUSE AT 10708 PAIUTE WAY, RANCHO CORDOVA EXPLODED, SEVERELY DAMAGING HOUSES ON EITHER SIDE. FIVE PEOPLE, INCLUDING TWO PG&E EMPLOYEES DISPATCHED TO THE SITE, WERE INJURED AND THERE WAS ONE FATALIT | 0
735 | 2008-12-29 | VA | natural disasters | UNKNOWN (FAIRFAX COUNTY ) | WASHINGTON GAS LIGHT CO | WASHINGTON GAS WAS CALLED AT 08:48 BY THE FAIRFAX FIRE BOARD FOR AN ODOR OF GAS. THE LEAK WAS PINPOINTED TO THE INTERSECTION OF BACKLICK ROAD AND INDUSTRIAL ROAD. PRESSURE ON THE LINE WAS REDUCED. UPON EXCAVATION OF THE SITE, THE LEAK WAS FOUND TO BE C | 1000
736 | 2009-01-12 | CA | other | UNKNOWN (MADERA COUNTY ) | PACIFIC GAS & ELECTRIC CO | PG&E RESPONDED TO A CALL FROM THE MADERA FIRE DEPARTMENT REPORTING A STRUCTURE FIRE AT THE PARKWOOD SHOPPING CENTER. THE FIRE DEPARTMENT HAD TURNED OFF THE GAS AT THE METER SET VALVE. AS A RESULT OF THE FIRE THE STRUCTURE FELL ON TO ONE OF THE METERS AF | 0
737 | 2008-12-24 | NH | other | UNKNOWN (GENIE COUNTY ) | NORTHERN UTILITIES, INC. (NH) | DOUBLE METER SET FEEDING TWO UNITS, 5 + 6 AT 86 CHURCH STREET, SNOW WAS PILED ON TOP OF SET CAUSING PRESSURE ON RISER, THE RELEASE OF GAS CAME FROM THIS LOCATION, NIPPLE BETWEEN INLET OF REGULATION AND RISER VALVE. | 0
738 | 2008-12-28 | NY | maintenance | UNKNOWN (SUFFOLK COUNTY ) | KEYSPAN ENERGY DELIVERY - LONG ISLAND | AT 1755 ON DECEMBER 28, 2008, NATIONAL GRID LI RECEIVED A CALL FRO THE AMITYVILLE POLICE DEPARTMENT REPORTING A BURST PIPE AND EVACUATION AT 34 MEADOW LANE, AMITYVILLE. AT 1759, A SECOND CALL WAS RECEIVED INDICATING THAT THE HOUSE HAD "EXPLODED". NATIONAL | 0
739 | 2008-12-24 | MS | sabotage | UNKNOWN (HINDS COUNTY ) | ATMOS ENERGY CORPORATION - MISSISSIPPI | 12/17/2014: THE INVESTIGATION SHOWED THAT THE COATED STEEL SERVICE LINE WAS PROPERLY CONNECTED TO THE GAS MAIN WITH AN APPROPRIATE DRESSER EII COUPLING. ATMOS HAD NO INDICATION OF ANY LEAKS OF THIS STEEL SERVICE PIPE OR THE COMPRESSION COUPLING BEFORE | 0
740 | 2009-01-17 | TN | other | UNKNOWN (SHELBY COUNTY ) | MEMPHIS LIGHT GAS & WATER DIVISION | MEMPHIS LIGHT GAS AND WATER DIVISION, UPON COMPLETION OF INVESTIGATION OF THE HOUSE FIRE AT 1903 THE OAKS AVENUE ON 1/17/09 IN WHICH THE GAS METER AND REGULATOR WERE CONSUMED BY FIRE, HAS DETERMINED THAT OUR FACILITIES DID NOT CREATE THE FIRE BUT THAT OUR | 0
741 | 2009-01-13 | IL | other | UNKNOWN (MCLEAN COUNTY ) | NORTHERN ILLINOIS GAS CO | DRIVER LOST CONTROL OF HIS CAR DUE TO SNOW AND ICE AND HIT METER SET TO 1210 ADELAIDE, NORMAL IL. GAS IGNITED. NOTE: THIS INCIDENT WAS ORIGINALLY REPORTED TO THE NRC AS 1210 ADELAIDE, BLOOMINGTON, IL | 500
742 | 2009-02-11 | AK | other | UNKNOWN (nan COUNTY ) | ENSTAR NATURAL GAS CO | ENSTAR RESPONDED TO A STRUCTURE FIRE AT 13021 ADMIRALTY DRIVE, ANCHORAGE, ALASKA AT 1432 ON 2/11/2009. THE FIRE IS BELIEVED TO HAVE STARTED FROM A CHARCOAL GRILL. HEAT FROM THE STRUCTURE FIRE MELTED ENSTAR'S METER AND PRESSURE REGULATOR,CAUSING A RELEAS | 100
743 | 2009-01-17 | CA | sabotage | UNKNOWN (ORANGE COUNTY COUNTY ) | SOUTHERN CALIFORNIA GAS CO | ON JANUARY 17, 2009, A 3¿ DISTRIBUTION MAIN WAS DAMAGED BY A CONTRACTOR USING POWER EXCAVATING EQUIPMENT TO INSTALL A TRANSMISSION POLE. INVESTIGATION OF THE INCIDENT SHOWED THAT THE CONTRACTOR HAD A CURRENT USA TICKET, AND HAD POTHOLED A STEEL PIPE | 1000
744 | 2008-12-30 | MO | sabotage | UNKNOWN (ST LOUIS CITY COUNTY ) | LACLEDE GAS CO | A PLUMBING COMPANY EXCAVATED AROUND AND UNDERMINED APPROXIMATELY SEVEN FEET OF THE 4-INCH CAST IRON NATURAL GAS MAIN ON OR ABOUT NOVEMBER 19, 2008. THIS EXCAVATION WAS BACKFILLED WITH ROCK AND PAVED ON DECEMBER 24, 2008, WITHOUT PROVIDING SUPPORT TO THE C | 0
745 | 2009-01-21 | OK | sabotage | UNKNOWN (TULSA COUNTY ) | OKLAHOMA NATURAL GAS CO | CITY OF TULSA WATER DEPARTMENT CREW DAMAGED A 4" POLYETHYLENE MAIN AT THE CORNER OF EAST 11TH AND S. ERIE AVE. THE CITY CALLED IN A LOCATE REQUEST BUT EXCAVATED OUTSIDE OF THE DEFINED WHITE LINE LIMITS OF THEIR REQUEST. THE ONG LINE WAS NOT MARKED OUTSIDE | 19751
746 | 2009-01-19 | OK | sabotage | UNKNOWN (OKLAHOMA COUNTY ) | OKLAHOMA NATURAL GAS CO | CIMARRON CONSTRUCTION COMPANY DAMAGED ONG'S 6" (INCH) HDPE MAIN WHILE INSTALLING SHORING PYLONS AND SHORE BOXES TO PIT BORE FOR THE RELOCATION OF OKLAHOMA CITY'S WATER LINE. LAPSED TIME IN REPORTING WAS A RESULT OF COLLABORATION OF ENGINEERING AND OPERATI | 911
747 | 2009-01-19 | OH | other | UNKNOWN (MUSKINGUM COUNTY ) | COLUMBIA GAS OF OHIO INC | A WATER MAIN LEAK ERODED A HOLE IN A COLUMBIA OWNED THREE INCH LOW PRESSURE STEEL GAS MAIN LINE. THE WATER LEAK FORCED WATER INTO AND FILLED THE COLUMBIA OWNED MAIN LINE AND CAUSED A 115 CUSTOMER SERVICE FAILURE (OUTAGE). THE COST OF WATER REMOVAL AND GAS | 0
748 | 2009-01-27 | IL | natural disasters | UNKNOWN (LAKE COUNTY ) | NORTH SHORE GAS CO | ATTACHMENT TO PART G- NARRATIVE DESCRIPTION OF FACTORS CONTRIBUTING TO THE EVENT FROM 5/3/09 REPORT: ON THE EVENING FOLLOWING THE INCIDENT, NORTH SHORE GAS EXCAVATED AND EXPOSED THE 3/4 INCH MILL WRAPPED STEEL SERVICE LINE; FINDING IT BROKEN A FEW INC | 1200
749 | 2009-01-24 | NY | maintenance | UNKNOWN (WESTCHESTER COUNTY ) | CONSOLIDATED EDISON CO OF NEW YORK | ON SATURDAY, JANUARY 24, 2009 AT 04:20, THE EMERGENCY RESPONSE CENTER (ERC) RECEIVED NOTFICATION OF A BUILDING FIRE AT 4 DRAKE ROAD, CALLED IN BY THE SCARSDALE FD. UPON ARRIVAL AT 04:50, GDS REPORTED THAT THE FD HAD THE FIRE UNDER CONTROL, AND THERE WAS W | 0
750 | 2009-01-28 | OH | other | UNKNOWN (LAK COUNTY ) | DOMINION EAST OHIO | AT APPROXIMATELY 21:30 HOURS ON JANUARY 28, 2009, A SINGLE FAMILY HOME LOCATED AT 37845 LAKESHORE, EASTLAKE, OHIO SUSTAINED AN EXPLOSION CAUSING SERIOUS INJURY TO THE TWO OCCUPANTS. BOTH PARTIES WERE LIFE FLIGHTED TO METRO HOSPITAL AND WERE PLACED IN THE | 0
751 | 2009-01-12 | NM | other | UNKNOWN (CHAVEZ COUNTY ) | NEW MEXICO GAS COMPANY | A VEHICLE LOST CONTROL ON6956 OLD DEXTER ROAD AND ROLLED OVER THE METER SET, HIT THE RISER VALVE CAUSING A RELEASE OF GAS. THE METER WAS REMOVED AND THE SERVICE LINE PLUGGED. BECAUSE OF HIPAA PRIVACY RULES, THE COMPANY WAS UNABLE TO VERIFY WHETHER ANYONE | 100
752 | 2009-02-11 | MI | leaks and spills | UNKNOWN (MACOMB COUNTY ) | CONSUMERS ENERGY CO | AT 0725 ON FEBRUARY 11, 2009, CONSUMERS ENERGY RESPONDED TO AN EMERGENCY CALL AT 21103 BEACONSFIELD, EASTPOINTE, MICHIGAN, AND DETERMINED THAT AN EXPLOSION AND SUBSEQUENT FIRE OCCURRED. THE FIRE DEPARTMENT TURNED OFF THE GAS AT THE METER AT 0830. TWO RE | 50
753 | 2009-01-27 | OH | other | UNKNOWN (DELWARE COUNTY ) | COLUMBIA GAS OF OHIO INC | AN INVESTIGATION WAS CONDUCTED BY THE PROPERTY OWNER'S INSURANCE CARRIER WHO HAS MAINTAINED POSSESSION OF ALL OF THE CUSTOMERS OWNED MATERIAL. IT IS COLUMBIA'S POSITION THAT ITS OWN INVESTIGATION AND THE INVESTIGATION BY THE PROPERTY OWNER'S INSURANCE CA | 212
754 | 2009-02-07 | AZ | sabotage | UNKNOWN (MARICOPA COUNTY ) | SOUTHWEST GAS CORP | NRC REPORT NUMBER 896853 A NATURAL GAS LEAK ON A SOUTHWEST DISTRIBUTION LINE CONTRIBUTED TO A HOUSE FIRE. THE CAUSE OF THE LEAK WAS DUE TO PRIOR THIRD PARTY DAMAGE TO A 1" STEEL SERVICE LINE. THERE WERE NO INJURIES OR A FATALITIES AS A RESULT OF THE | 0
755 | 2009-02-07 | NY | natural disasters | UNKNOWN (SUFFOLK COUNTY ) | KEYSPAN ENERGY DELIVERY - LONG ISLAND | UPDATED BY PHMSA ON 2/9/2016 PER THE OPERATOR'S MARK UP (PART D - MATERIAL SPECIFICATION, ITEM 1 - NOMINAL PIPE SIZE; ITEM 2 - WALL THICKNESS (NOTE: THE .10 IS THE THICKNESS AT THE DAMAGE LOCATION); PART F - APPARENT CAUSE; F2 - NATURAL FORCES, ITEM 6 - T | 0
756 | 2009-02-01 | WI | natural disasters | UNKNOWN (MILWAUKEE COUNTY ) | WISCONSIN GAS CO | ON SUNDAY, FEBRUARY 1, 2009, AT 2:17AM, THE CITY OF MILWAUKEE POLIECE DEPARTMENT (MPD) NOTIFIED WE ENERGIES CUSTOMER CONTACT CENTER THAT THERE WAS A GAS LEAK IN THE AREA OF 2435 N.10TH STREET, IN THE CITY OF MILWAUKEE, WISCONSIN. MPD ALSO SAID THAT THE MI | 420
757 | 2009-01-25 | MA | natural disasters | UNKNOWN (ESSEX COUNTY ) | BOSTON GAS CO | UPDATED BY PHMSA ON 2/9/2016 PER OPERATOR'S MARK UP (PART F - APPARENT CAUSE, F2 - NATURAL FORCES, ITEM 6 - TEMPERATURE --> FROST HEAVE). SIX INCH BROKEN CAST IRON WAS FOUND IN FRONT OF 76 EASTERN AVE, GLOUCESTER, MASSACHUSETTS. CAUSE IS DETERMINED TO | 0
758 | 2009-01-08 | NV | sabotage | UNKNOWN (CLARK COUNTY ) | SOUTHWEST GAS CORP | ON THE MORNING OF JANUARY 8, 2009, SOUTHWEST GAS DISPATCH WAS NOTIFIED OF NATURAL GAS ODORS IN THE VICINITY OF EASTERN AVENUE AND RENO AVENUE IN LAS VEGAS. NATURAL GAS WAS DETECTED DURING THE INITIAL LEAK SURVEY INVESTIGATION IN AN ADJACENT TRAFFIC SIGNAL | 5438
759 | 2009-03-04 | TX | sabotage | UNKNOWN (COLLIN COUNTY ) | COSEAY GAS | CONTRACTOR DRILLING PEIR HOLES FOR SINGAL LIGHT INSTALLATION DAMAGED A 4" STEEL MAIN. TWO LANES ON A MULTIPLE LANE FM HWY WAS BLOCKED WHILE GAS WAS BROUGHT UNDER CONTROL AND REPAIRS WERE MADE. | 1200
760 | 2009-02-22 | WY | other | UNKNOWN (WESTON COUNTY ) | SOURCEGAS LLC | A PICKUP TRUCK RAMMED ANOTHER VEHICLE INTO A METER SET APPURTENANCE LOCATED AT THE OUTSIDE BUILDING WALL BREAKING OFF THE PIPE AT THE THREADS JUST BELOW THE METER STOP/SHUT OFF VALVE THE LEAKING GAS IGNITED STARTING A FIRE WHICH DESTROYED THE VEHICLE AND | 202
761 | 2009-02-27 | AZ | other | UNKNOWN (GILA COUNTY ) | SEMSTREAM ARIZONA PROPANE LLC | AT 2:00 AM ON FRIDAY THE 27TH A PICK UP TRUCK WENT OFF THE ROAD AND RAN INTO A TRAILER HOUSE. WHEN IT HIT THE HOUSE, THE TRUCK SHEARED OF THE GAS METER AND THE ELECTRICAL METER. A FIRE ENSUED. THE ELECTRIC CURRENT WAS PASSING THROUGH THE PICK UP TRUCK. | 180
762 | 2009-03-14 | IL | other | UNKNOWN (WABASH COUNTY ) | MT CARMEL PUBLIC UTILITY CO | THE ILLINOIS STATE FIRE MARSHAL INVESTIGATOR DETERMINED THAT THE SOURCE OF THE LEAK WAS ON CUSTOMER OWNED, NON-JURISDICTIONAL PIPING. | 0
763 | 2009-03-01 | CA | other | UNKNOWN (SAN DIEGO COUNTY ) | SAN DIEGO GAS & ELECTRIC CO | ON MARCH 1, 2009, A FIRE ERUPTED INSIDE A RESIDENTIAL HOME, ULTIMATELY SPREADING TO A NATURAL GAS METER THAT MELTED AND IGNITED. AN ELDERLY RESIDENT SUCCUMBED TO FIRE-RELATED INJURIES, AND PROPERTY DAMAGE EXCEEDED $50,000. AS A RESULT, THE INCIDENT WAS | 100
764 | 2009-03-05 | MT | natural disasters | UNKNOWN (GALLATIN COUNTY ) | NORTHWESTERN ENERGY LLC | THIS IS NORTHWESTERN ENERGY’S FINAL REPORT FOR THIS INCIDENT. SINCE LAST UPDATE THE METALLURGY TESTING HAS BEEN COMPLETED AND THE FINAL METALLURGICAL REPORT WAS SUBMITTED TO THE MONTANA PUBLIC SERVICE COMMISSION ON DECEMBER 9, 2009. THE REPORT STATE | 0
765 | 2009-03-20 | AK | other | UNKNOWN (ANCHORAGE COUNTY ) | ENSTAR NATURAL GAS CO | ENSTAR RESPONDED TO A HOUSE FIRE AT 5623 DALZELL CIRCLE AT 0615 ON MARCH 20, 2009 AT THE REQUEST OF THE ANCHORAGE FIRE DEPARTMENT. THE METER ASSEMBLY WAS ENGULFED IN FLAMES FROM THE SPREAD OF THE STRUTURE FIRE. ENSTAR CREWS DUG UP THE SERVICE LINE AND P | 100
766 | 2009-02-19 | MA | sabotage | UNKNOWN (BRISTOL COUNTY ) | NEW ENGLAND GAS COMPANY | THE SECTION OF THE MAIN APPEARS TO HAVE BEEN PHYSICALLY DAMAGED BY A THIRD PARTY CONTRACTOR SOMETIME AFTER IT WAS INSTALLED IN THE 1960'S. THIS MATTER IS STILL UNDER INVESTIGATION AND NEGG MAY AMEND OR SUPPLEMENT THIS REPORT. | 0
767 | 2009-03-26 | CA | sabotage | UNKNOWN (FRESNO COUNTY ) | PACIFIC GAS & ELECTRIC CO | A THIRD PARTY LANDSCAPER STRUCK A 6 INCH STEEL GAS DISTRIBUTION MAIN WHILE PERFORMING TRENCHING WORK CAUSING GAS TO ESCAPE. PG&E PERSONNEL ARRIVED ON THE SCENE AT 0851 HOURS. THE AREA WAS BLOCKED OFF. GAS FLOW WAS STOPPED AT 1017 HOURS; AND PERMANENT R | 10000
768 | 2009-01-15 | IL | natural disasters | UNKNOWN (TAZEWELL COUNTY ) | CENTRAL ILLINOIS LIGHT CO | ON THE MORNING OF JANUARY 15, AMERENCILCO REGULATOR TECHNICIANS INSTALLED A TEMPORARY CATALYTIC HEATER AND A TARP AS A WIND BARRIER TO PROTECT THE PILOTS FROM FREEZING AND RESTORED GAS SERVICE TO A CUSTOMER. LATER THAT MORNING AT 11:20 A.M. AMERENCILCO RE | 500
769 | 2009-03-10 | VA | other | UNKNOWN (RICHMOND COUNTY ) | RICHMOND, CITY OF | ALL INDICATIONS FROM THE CITY OF RICHMOND'S FIRE DEPT ARE THAT THE FIRE STARTED ON THE FRON PORC IN A COUCH AND SPREAD TO THE REMAINING STRUCTURE. THE FIRE EVENTUALLY REACHED THE GAS METER CAUSING IT TO FAIL AND IGNITE. | 0
770 | 2009-03-29 | AK | other | UNKNOWN (MATANUSKA SUSITNA BOROUGH COUNTY ) | ENSTAR NATURAL GAS CO | ENSTAR RESPONDED TO A STRUCTURE FIRE AT 901 N. LEATHERLEAF LOO, WASILLA, AK AT 0125 MARCH 29,2009. THE STRUCTURE FIRE MELTED THE HDPE PIPE INSIDE THE SERVICE LINE RISER CAUSING A RELEASE OF NATURAL GAS. THE GAS METER AND REGULATOR WERE CONSUMED IN THE F | 100
771 | 2009-02-12 | KY | sabotage | UNKNOWN (OLDHAM COUNTY ) | LOUISVILLE GAS & ELECTRIC CO | <P>ATTACHED LG&E REPORT TO THE KPSC REPORT SUBMITTED SIMULTANEOUSLY. </P> <P>CASE SUMMARY: </P> <P>ON FEBRUARY 12, 2009 AT APPROXIMATELY 3:00 P.M., LG&E'S GAS EMERGENCY OPERATIONS CENTER RCEIVED A CALL REPORTING A NATURAL GAS MAIN STRIKE AND LEAK ON HWY | 0
772 | 2009-02-23 | ID | leaks and spills | UNKNOWN (BONNER COUNTY ) | AVISTA CORP | THIS IS A REPORTABLE BECAUSE OF THE ACCUMULATED DOLLAR VALUE OF THE INCIDENT. THE INCIDENT WAS DUE TO A FAILED MECHANICAL JOINT THAT WAS IMPROPERLY INSTALLED IN 2005. THE RESIDENCE WAS VACANT AT THE TIME OF THE INCIDENT. THE MAJOR PART OF THE COST WAS D | 4998
773 | 2009-03-11 | AR | sabotage | UNKNOWN (WASHINGTON COUNTY ) | ARKANSAS WESTERN GAS CO | CONTRACTOR WAS DREDGING OUT A DUCK POND AT BEVERLY MANOR APARTMENTS WHEN THEIR EXCAVATOR BECAME STUCK IN SOFT MUD. IN THE PROCESS OF TRYING TO FREE THE EQUIPMENT THEY HOOKED AND PULLED EXISTING 1.250 INCH SERVICE LINE FEEDING 14 METERS OF THE COMPLEX WHIC | 1000
774 | 2009-03-04 | FL | sabotage | UNKNOWN (SARASOTA COUNTY ) | PEOPLES GAS SYSTEM INC | COUNTY WAS WIDENING THE ROAD. CONTRACTOR HIT OUR PIPE WITH A ROAD MIXER. | 1800
775 | 2009-03-21 | KY | other | UNKNOWN (DAVIESS COUNTY ) | ATMOS ENERGY CORPORATION - KY/MID-STATES (KENTUCKY) | A FORD RANGER PICKUP CRASHED INTO A GAS DISTRIBUTION LOW PRESSUREE REGULATOR STATION LOCATED AT 2ND AND HALE AVENUE. THE PICKUP TRUCK LEFT THE STREET, RAN OVER (3) 4 INCH STEEL BARRICADES AND STRUCK THE REGULATOR STATION ON THE INLET PIPING SEVERING THE I | 14558
776 | 2009-03-23 | TX | sabotage | UNKNOWN (DENTON COUNTY ) | COSERV GAS, LTD | INLET BOX FOR STORM DRAIN WAS BEING INSTALLED AND A 4" POLY MAIN WAS DAMAGED. SITE WAS NEAR A DISTRICT REGULATOR STATION AND NOT ALL LINES WERE IDENTIFIED AND MARKED LEAVING THE STATION. | 5800
777 | 2009-03-31 | TX | sabotage | UNKNOWN (DENTON COUNTY ) | COSERV GAS, LTD | INLET BOX FOR STORM DRAIN WAS BEING INSTALLED AND A 6" POLY MAIN WAS DAMAGED. THIS IS A LARGE PROJECT AND POOR COMMUNICATION WITH EXCAVATOR AND LOCATOR CAUSED THE LINE NOT TO BE MARKED. EXCAVATOR FAILED TO MAKE A SECOND REQUEST | 2272
778 | 2009-03-10 | CA | maintenance | UNKNOWN (NEVADA COUNTY ) | AMERIGAS PROPANE LP | THE ROOT CAUSE OF THE INCIDENT WAS DUE TO 12 TO 14 FOOT WALL OF SNOW THAT WAS SNOW BLOWN ONTO THE PROPANE TANK THAT IS SET BACK FROM A MAIN DRIVEWAY ENTRANCE TO THE CONDOMINIUM. THE ENTIRE TANK WAS INCASED IN SNOW AND ICE WHEN AMERIGAS BUG OUT THE SNOW AN | 688
779 | 2009-03-03 | MN | other | UNKNOWN (RAMSEY COUNTY ) | NOTHERN STATES POWER CO. OF MINNESOTA | CUSTOMER WAS IN THE PROCESS OF INSTALLING AN EGRESS WINDOW IN BASEMENT AND WAS USING A TORPEDO HEATER TO THAW THE GROUND FROM INSIDE THE HOUSE. THE HEATER MELTED THE GAS SERVICE APPROXIMATELY 10 FEET UPSTREAM FROM THE GAS METER SET, CAUSING A PIPE FAILURE | 0
780 | 2009-02-20 | NJ | other | UNKNOWN (nan COUNTY ) | CONSOLIDATED EDISON CO OF NEW YORK | ON 2/20/09 @ 19:01 HRS., A TRANSCO TECHNICIAN NOTIFIED CON EDISON GAS CONTROL OF A STRONG GAS ODOR AT THE MEADOWLANDS HEATERS WITH FIRE DEPT AND POLICE ON LOCATION. CON EDISON PRESSURE CONTROL WAS NOTIFIED TO RESPOND. AN UNKNOWN CONDITION CAUSED A SHUT DO | 0
781 | 2009-03-09 | VA | other | UNKNOWN (FAIRFAX COUNTY ) | WASHINGTON GAS LIGHT CO | WASHINGTON GAS WAS CALLED BY THE FAIRFAX COUNTY FIRE BOARD TO ASSIST WITH A HOUSE FIRE LOCATED AT 4001 DAVID LANE IN ALEXANDRIA, VA 22312. THE WASHINGTON GAS SERVICE TECH, MR. DONALD FENTON, TURNED THE GAS OFF AT THE CURB VALVE AT 22:50. A LEAK SURVEY W | 100
782 | 2009-03-12 | AK | natural disasters | UNKNOWN (ANCHORAGE COUNTY ) | ENSTAR NATURAL GAS CO | THIS LEAKING COUPLING WAS EVALUATED AT A FORENSICS LAB AND WAS DETERMINED TO HAVE PULLED APART FROM THE COPPER TUBING DUE TO FROST MOVEMENT. | 0
783 | 2009-03-04 | TX | other | UNKNOWN (HARRIS COUNTY ) | ENTEX, A NORAM ENERGY COMPANY (FORM. DIV OF ARKLA | 1/2' PLASTIC SERVICE LINE CAUGHT FIRE DUE TO AN AT&T EMPLOYEE MAKING REPAIRS TO PHONE CABLE USING A PROPANE TORCH TO APPLY A HEAT SHRINK SLEEVE. | 382
784 | 2009-03-16 | TX | other | UNKNOWN (HARRIS COUNTY ) | ENTEX, A NORAM ENERGY COMPANY (FORM. DIV OF ARKLA | VEHICLE LEFT ROADWAY AND ENTERED DITCH STRIKING AND DAMAGING AN ABOVE GROUND 4" STEEL CROSSING. | 3427
785 | 2008-06-18 | IN | sabotage | UNKNOWN (DEARBORN COUNTY ) | LAWRENCEBURG GAS CO | CONTRACTOR WAS INSTALLING WATER SERVICES ACROSS BIELBY ROAD/SR 48 (A TWO-LANE STATE HIGHWAY) TO A RECENTLY INSTALLED WATER MAIN. THIS REQUIRED CROSSING THE 8-INCH STEEL GAS FEEDER MAIN OWNED BY THE LAWRENCEBURG GAS COMPANY AT THE LOCATION IN QUESTION. T | 298
786 | 2009-03-09 | MA | other | UNKNOWN (nan COUNTY ) | CAPE COD GAS CO (DIV OF COLONIAL GAS CO) | THE MASSACHUSETTS FIRE MARSHAL DETERMINED THAT CAUSE OF FIRE WAS THE ARCHING OF ELECTRICAL LINES THAT COMPROMISED GAS SERVICE LINE. | 0
787 | 2009-03-27 | NY | other | UNKNOWN (WESTCHESTER COUNTY ) | CONSOLIDATED EDISON CO OF NEW YORK | ON FRIDAY, MARCH 27, 2009, AT 13:53, THE CROTON FIRE DEPARTMENT (FD) REPORTED A GAS EXPLOSION AND BUILDING FIRE TO THE GAS EMERGENCY RESPONSE CENTER. CON EDISON GAS DISTRIBUTION SERVICES (GDS) RESPONDED AND THE CROTON FD REPORTED THAT A PRIVATE VEHICLE B | 0
788 | 2009-04-01 | UT | other | UNKNOWN (SALT LAKE COUNTY ) | QUESTAR GAS COMPANY | QUESTAR GAS WAS NOTIFIED AT 5:20 AM THAT A DUPLEX WAS ON FIRE. QUESTAR PERSONNEL ARRIVED ON SITE AND FOUND THAT THE FIRE DEPARTMENT HAD SHUT THE SERVICE VALVE. THE DUPLEX WAS TOTALLY DESTROYED AND THE METER AND REGULATOR WERE MELTED AND LEAKED AN UNDETE | 100
789 | 2009-04-06 | CA | sabotage | UNKNOWN (LOS ANGELES COUNTY ) | SOUTHERN CALIFORNIA GAS CO | ON APRIL 6, 2009, A 12¿ GAS MAIN WAS PUNCTURED BY A CONTRACTOR USING A TRACKHOE TO REMOVE A BROKEN CONCRETE WATER MAIN. THERE WAS A USA REQUEST FOR THIS AREA, AND FACILITIES WERE PROPERLY MARKED. NO FIRE OR INJURIES RESULTED FROM THE ESCAPING GAS. T | 15000
790 | 2009-02-02 | TX | other | UNKNOWN (TRAVIS COUNTY ) | TEXAS GAS SERVICE COMPANY | A NATURAL GAS LEAK OCCURED WITH ACCIDENTAL IGNITION CAUSING A RESIDENTIAL DWELLING TO BURN. THE LEAK WAS DUE TO AN ILLEGAL ACT WHEN A NON-GAS COMPANY EMPLOYEE REMOVED THE VALVE CAUSING AN UNCONTROLLED RELEASE OF GAS. THIS EVENT DID NOT INVOLVE THE FAI | 328
791 | 2009-03-17 | TX | other | UNKNOWN (TRAVIS COUNTY ) | TEXAS GAS SERVICE COMPANY | AN ACCIDENTAL STRUCTURE FIRE WAS STARTED IN THE GARAGE OF 5210 PINE PLACE. THE RADIANT HEAT FROM SAID FIRE MELTED INTERNAL COMPONENTS OF THE REGULATOR AND METER, CAUSING NATURAL GAS TO BE RELEASED; BECOMING THE SECONDARY FUEL TO THE FIRE. RADIANT HEAT F | 194
792 | 2009-03-05 | TX | other | UNKNOWN (TRAVIS COUNTY ) | TEXAS GAS SERVICE COMPANY | THE FIRE INVOLVED TWO SINGLE FAMILY RESIDENCES. THE FIRE ORIGINATED IN A TRASH REFUSE CART LOCATED BETWEEN THE STRUCTURES. THE HEAT FROM THE FIRE IGNITED THE STRUCTURE AND CAUSED A FAILURE AT THE METER SETS FOR BOTH RESIDENCES. AT THIS JUNCTURE NATURAL | 71
793 | 2009-04-15 | MI | sabotage | UNKNOWN (OAKLAND COUNTY ) | MICHIGAN CONSOLIDATED GAS CO (MICHCON) | AT 12:23 ON APRIL 15, 2009, MICHCON RECEIVED A REPORT OF LEAKING GAS AT WEST SUMMIT STREET IN THE CITY OF MILFORD, OAKLAND COUNTY, MICHIGAN. MICHCON PERSONNEL ARRIVED AT THE SCENE AT 12:37 AND DETERMINED THAT A WATER MAIN CONTRACTOR HAD BORED INTO A STEE | 5835
794 | 2009-04-25 | CA | other | UNKNOWN (LOS ANGELES COUNTY ) | SOUTHERN CALIFORNIA GAS CO | ON APRIL 25, 2009 A 4 INCH STEEL MEDIUM PRESSURE MAIN WAS DAMAGED WHEN A CROSSING WATER SERVICE WAS ELECTRICALLY ENERGIZED. DUE TO THE CLOSE PROXIMITY, ELECTRICITY ARCED FROM THE WATER SERVICE ONTO THE GAS MAIN, BURNING A HOLE IN BOTH THE WATER SERVICE A | 0
795 | 2008-05-20 | MN | other | UNKNOWN (COOK COUNTY ) | INTERSTATE ENERGY DBA COMO OIL AND PROPANE | FIRE AT CUSTOMER LOCATION, SYSTEM SHUT DOWN. SYSTEM WAS TESTED AND FOUND TO BE LEAK FREE. GAS NOT SUSPECTED AS CAUSE. STATE OF MN REPORTS THAT IT IS A NON-JURISTICTIONAL INCIDENT. SYSTEM WAS RESTARTED ONCE AREA WAS SECURE. | 0
796 | 2009-05-25 | AK | other | UNKNOWN (nan COUNTY ) | ENSTAR NATURAL GAS CO | ENSTAR WAS NOTIFEID OF A HOUSE FIRE AT 33515, CUMULUS ROAD, EAGLE RIVER, AK AT 0741 ON MONDAY, MAY 25, 2009. ENSTAR'S GAS METER AND SERVICE LINE RISER BURNED IN THE FIRE. THE FIRE DEPARTMENT RESPONDERS PINCHED OFF THE RISER TO STOP THE FLOW OF NATURAL G | 10
797 | 2009-05-07 | CA | other | UNKNOWN (SANTA BARBARA COUNTY ) | SOUTHERN CALIFORNIA GAS CO | ON MAY 7, 2009 A WILDFIRE BROKE OUT IN THE VICINITY OF TUNNEL ROAD AND SPYGLASS ROAD IN SANTA BARBARA, DAMAGING SERVICES, RISERS AND METER SET ASSEMBLIES. DAMAGE TO SOCALGAS GAS FACILITIES WAS LIMITED TO THESE COMPONENTS. NO DAMAGE TO DISTRIBUTION MAINS | 500
798 | 2009-05-31 | FL | other | UNKNOWN (ALACHUA COUNTY ) | GAINESVILLE REGIONAL UTIL GAS DEPT | CUSTOMER WAS BURNING A STUMP IN HIS BACK YARD. HE STARTED THE FIRE ON 5/30/09 AND ON THE MORNING OF 5/31/09, WAS STARTLED WHEN THE FIRE HAD BURNED DOWN TO THE GAS SERVICE AND MELTED THE POLY. THE NATURAL GAS IGNITED. THE INCIDENT RESULTED IN NO PERSONA | 50
799 | 2009-05-19 | TX | sabotage | UNKNOWN (COLLIN COUNTY ) | COSERV GAS, LTD | 6" POLY MAIN WAS CUT BUT CREW DIRECTIONAL BORING. CUT CAUSE THE INTERSECTION OF ELDERADO AND CUSTER TO BE CLOSED AND TRAFFIC REROUTED. | 7886
800 | 2009-05-05 | WA | other | UNKNOWN (YAKIMA COUNTY ) | CASCADE NATURAL GAS CORP | DRIVER WAS TRYING TO FLEE FROM THE YAKIMA POLICE DEPARTMENT, MISSED TURN, LOST CONTROL OF CAR AND RAN INTO THE SIDE OF THE HOUSE AT 901 E ARLINGTON ST, RUNNING OVER THE GAS METER CAUSING THE NATURAL GAS TO IGNITE. THE DRIVER AND PASSENGER WERE TAKEN TO TH | 0
801 | 2009-05-30 | AK | other | UNKNOWN (ANCHORAGE COUNTY ) | ENSTAR NATURAL GAS CO | ON MAY 30, 2009, AT 2150, ENSTAR WAS NOTIFIED OF A STRUCTURE FIRE AT 11627 CELESTIAL STREET IN EAGLE RIVER, AK. EXTREME HEAT FROM THE FIRE CAUSED THE HDPE TUBING INSIDE THE SERVICE LINE RISER ON A NEARBY DUPLEX (11617 AND 11615 CELESTIAL ST) TO MELT AND | 10
802 | 2009-05-07 | MD | other | UNKNOWN (PRINCE GEORGES COUNTY ) | WASHINGTON GAS LIGHT CO | AFTER CONSIDERING INFORMATION OBTAINED AND THE OPINIONS OF EXPERTS, THE PREVIOUS SUBMISSIONS ARE REPLACED AS FOLLOWS: WASHINGTON GAS RESPONDED TO A REPORT OF AN ODOR OF GAS AT THE RANGE INSIDE 3432 DONNELL DRIVE IN DISTRICT HEIGHTS, MD. UPON ARRIVAL BY WA | 500
803 | 2009-05-15 | IL | sabotage | UNKNOWN (COOK COUNTY ) | NORTHERN ILLINOIS GAS CO | THIRD PARTY EXCAVATOR STRUCK 4" GAS MAIN AND CAUSED 23" LONG BY 1.25" WIDE PUNTURE IN THE MAIN. | 8300
804 | 2009-05-19 | MD | other | UNKNOWN (PRINCE GEORGE'S COUNTY ) | WASHINGTON GAS LIGHT CO | WASHINGTON GAS RESPONDED TO A HOUSE FIRE REPORTED BY THE PRINCE GEORGE'S COUNTY FIRE DEPARTMENT AT 2616 FELTER LANE IN BOWIE, MD. UPON ARRIVAL, WASHINGTON GAS FOUND THE GAS OFF BY THE FIRE DEPARTMENT AT THE SERVICE RISER LOCATED ON THE OUTSIDE REAR OF TH | 5
805 | 2009-05-09 | RI | other | UNKNOWN (PROVIDENCE COUNTY ) | NEW ENGLAND GAS COMPANY | A HIGH SPEED DRIVES HEADING WEST ALONG RUGBY STREET LEFT THE LANE OF TRAVEL, VEERED RIGHT UP A SLIGHT EMBANKMENT FOR APPROXIMATELY 30 FEET, AND THEN STRUCK AN OUTSIDE METER SET AT 99 RUGBY ST. AS A RESULT OF THE MECHANICAL FORCE CAUSED BY THIS ACCIDENT, A | 0
806 | 2009-06-01 | UT | other | UNKNOWN (SALT LAKE COUNTY ) | QUESTAR GAS COMPANY | TRUCK RUNS RED TRAFFIC LIGHT AND CRASHES INTO CAR. DRIVER OF CAR LOOSES CONTROL AND COLLIDES WITH HOME AND GAS METER. IMPACT OF CRASH BREAKS GAS METER CAUSES A NATURAL GAS LEAK. GAS WAS QUICKLY SHUTOFF AT THE SERVICE RISER TO THE METER BY EMERGENCY RES | 0
807 | 2009-05-18 | TN | sabotage | UNKNOWN (CUMBERLAND COUNTY ) | UPPER CUMBERLAND GAS UTILITY DISTRICT | A CONTRACTOR USING A 1996 VERMEER 755 TRENCHER WAS INSTALLING A NEW SEWER LINE WHEN HE HIT THE END OF A 2" SDR-11, 3408 STUB APPROXIMATELY 8 FOOT LONG THAT HAD APPARENTLY BEEN PUT IN WHEN THE MAIN WAS INSTALLED IN 1996. THE SHORT STUB WAS NOT ON ANY MAPS | 0
808 | 2009-06-05 | TN | other | UNKNOWN (SHELBY COUNTY ) | MEMPHIS LIGHT GAS & WATER DIVISION | AT APPROXIMATELY 0034 HOURS ON FRIDAY, JUNE 5, 2009, A DRIVER FOR ALLIED WASTE SERVICES SET A TRASH DUMPSTER DOWN ON TOP OF OUR GAS METER REGULATOR IN THE REAR OF 5143 QUINCE ROAD. THE IMPACT BROKE THE BODY OF THE REGULATOR OFF AND CAUSED A CATASTROPHIC | 75
809 | 2009-05-29 | PA | sabotage | UNKNOWN (WASHINGTON COUNTY ) | COLUMBIA GAS OF PENNSYLVANIA | ON MAY 29, 2009, AT APPROXIMATELY 5:30 PM, AN EMPLOYEE OF JK FOSTER COMPANY STRUCK A 2 INCH PLASTIC GAS MAIN LINE WHILE EXCAVATING THE AREA TO REPAIR AN UNDERGROUND WATER LINE 121 LAZY-D-TR COURT, ROSCOE, WASHINGTON COUNTY PENNSYLVANIA. THE TRAILER COURT | 344
810 | 2009-05-12 | MO | other | UNKNOWN (ST. LOUIS COUNTY ) | LACLEDE GAS CO | AN AUTOMOBILE STRUCK THE ABOVE GROUND CASE, INSTRUMENTATION, AND ASSOCIATED SCADA EQUIPMENT OF A PRESSURE LIMITING AND REGULATING FACILITY. THE COLLISION RESULTED IN A MINOR RELEASE OF NATURAL GAS FROM A THERMOPLASTIC NYLON CORE HIGH PRESSURE SENSING LINE | 0
811 | 2009-05-21 | MD | other | UNKNOWN (WASHINGTON COUNTY ) | COLUMBIA GAS OF MARYLAND INC | IN HAGERSTOWN, WASHINGTON COUNTY, MARYLAND A FIRE OCCURRED AT 104 DOUB WAY IN THE AREA OF THE OUTSIDE AIR CONDITIONING UNIT. THE GAS METER AND REGULATOR WERE APPROXIMATELY 2 FEET AWAY. THE HEAT FROM THE FIRE MELTED THE METER AND REGULATOR CAUSING THE GAS | 1
812 | 2009-06-24 | CA | other | UNKNOWN (PLACER COUNTY ) | PACIFIC GAS & ELECTRIC CO | A RESIDENTIAL STRUCTURE FIRE STARTED AT APPROXIMATELY 0300 HOURS ON 6/24/09. PG&E WAS NOTIFIED OF THIS INCIDENT BY THE ROCKLIN FIRE DEPARTMENT AT APPROXIMATELY 0338 HOURS, AND PG&E PERSONNEL ARRIVED ON THE SCENE AT 0404 HOURS. GAS FLOW WAS STOPPED AT AP | 0
813 | 2009-07-06 | CA | other | UNKNOWN (SANTA CLARA COUNTY ) | PACIFIC GAS & ELECTRIC CO | A RESIDENTIAL HOUSE FIRE STARTED AT APPROXIMATELY 1030 HOURS ON 7/6/09. PG&E WAS NOTIFIED OF THIS INCIDENT BY THE SAN JOSE FIRE DEPARTMENT AT APPROXIMATELY 1103 HOURS, AND PG&E PERSONNEL ARRIVED ON THE SCENE AT 1141 HOURS. GAS FLOW WAS STOPPED BY THE FI | 0
814 | 2009-07-06 | CA | other | UNKNOWN (CONTRA COSTA COUNTY ) | PACIFIC GAS & ELECTRIC CO | A MOBILE HOME FIRE STARTED AT APPROXIMATELY 1300 HOURS ON 7/6/09. PG&E WAS NOTIFIED OF THIS INCIDENT BY THE CONTRA COSTA FIRE DEPARTMENT AT APPROXIMATELY 1312 HOURS, AND PG&E PERSONNEL ARRIVED ON THE SCENE AT 1336 HOURS. GAS FLOW WAS STOPPED BY THE FIRE | 0
815 | 2009-05-29 | GA | sabotage | UNKNOWN (LAURENS COUNTY ) | DUBLIN, CITY OF | ON MAY 28,2009, AT APPROXIMATELY 1725 HOURS, I RECEIVED A CALL FROM MR. GARY DUTY, ONE OUR GAS DEPARTMENT'S ON-CALL EMPLOYEES, STATING HE WAS ON JORDAN STREET, IN EAST DUBLIN GA. HE INFORMED ME THAT THE SEWER CONTACTOR FOR THE CITY OF EAST DUBLIN, POPCO I | 1500
816 | 2009-07-17 | CA | other | UNKNOWN (NAPA COUNTY ) | PACIFIC GAS & ELECTRIC CO | A HOUSE FIRE STARTED APPROXIMATELY 0500 HOURS ON 7/17/09. THE HOUSE IS LOCATED ON HILLY TERRAIN WITH DIFFICULT ACCESS. THE FIRE DEPARTMENT CALLED AT PG&E AT 0605 HOURS. THE PG&E GAS SERVICE REPRESENTATIVE ARRIVED AT 0625 HOURS. GAS CREWS SHUT OFF GAS A | 0
817 | 2009-07-15 | NE | sabotage | UNKNOWN (DOUGLAS COUNTY ) | METROPOLITAN UTILITIES DISTRICT | ON JULY 15 2009 A PRIVATE PLUMBING CONTRACTOR HIT THE GAS SERVICE LINE TO 6814 S. 26TH STREET IN OMAHA, DOUGLAS COUNTY, NE 68107 AS THE CONTRACTOR WAS PREPARING TO INSTALL A UPDATED WATER SERVICE AND SEWER LATERAL LINE. WHEN THE GAS SERVICE WAS STRUCK, AT | 200
818 | 2009-04-24 | NY | other | UNKNOWN (QUEENS COUNTY ) | CONSOLIDATED EDISON CO OF NEW YORK | ON FRIDAY, APRIL 24, 2009, AT APPROXIMATELY 4:50 P.M., AN EXPLOSION OCCURRED IN A SINGLE FAMILY HOME AT 80-50 260TH STREET, BETWEEN 80TH AND 81ST AVENUES, IN FLORAL PARK, QUEENS. THERE WAS ONE FATALITY; ONE REPORTED INJURY TO A MEMBER OF THE PUBLIC; AND M | 0
819 | 2009-06-24 | IL | sabotage | UNKNOWN (WILL COUNTY ) | NORTHERN ILLINOIS GAS CO | A THIRD PARTY EXCAVATOR STRUCK A 3/4" STEEL SERVICE LINE WHILE REPLACING CURBS. A RELEASE OF NATURAL GAS OCCURRED RESULTING IN A FIRE AND POSSIBLE EXPLOSION AT A PRIVATE RESIDENCE. | 500
820 | 2009-06-30 | FL | other | UNKNOWN (HILLSBOROUGH COUNTY ) | PEOPLES GAS SYSTEM INC | WATER MAIN BROKE WASHING EARTH FROM UNDER CONCRETE DRIVEWAY WHICH THEN COLLAPSED AND BROKE 2 INCH GAS MAIN. | 2960
821 | 2009-07-11 | AK | other | UNKNOWN (ANCHORAGE COUNTY ) | ENSTAR NATURAL GAS CO | ON SATURDAY, JULY 11, 2009, ENSTAR WAS NOTIFED OF A FIRE AT 132 DEETTE CIRCLE IN GIRDWOOD, AK. THE FIRE BURNED THE HDPE SERVICE LINE, METER AND REGULATOR RELEASING NATURAL GAS. THE SERVICE LINE WAS DUG UP AND PINCHED OFF TO STOP THE FLOW OF GAS. THE FI | 100
822 | 2009-06-15 | TX | natural disasters | UNKNOWN (TARRANT COUNTY ) | ATMOS ENERGY CORPORATION - MID-TEX | EARTH MOVEMENT ON THE SLOPE OF RAILROAD RIGHT-OF-WAY RELOCATED A 10" HIGH PRESSURE STEEL MAIN, CAUSING PIPE SEPARATION AND RESULTING LOSS OF GAS. | 123577
823 | 2009-07-08 | KS | other | UNKNOWN (HARPER COUNTY ) | ATMOS ENERGY CORPORATION - COLORADO/KANSAS | RELEASE OF GAS WAS A RESULT OF HEAT APPLIED FROM AN EXTERNAL SOURCE TO THE POLYETHYLENE GAS MAIN THAT RESIDED IN A VOID UNDER THE CONCRETE ALLEY. OPERATOR UNDERSTANDS THAT THE THIRD PARTY SOURCE AND/OR CAUSE OF THE FIRE, WHICH IMPINGED ON OPERATOR’S | 1440
824 | 2009-07-10 | KS | other | UNKNOWN (SHAWNEE COUNTY ) | KANSAS GAS SERVICE | AN ABANDONED HOME AT 5636 NW ROCHESTER RD IN TOPEKA, KS CAUGHT FIRE DUE TO ARSON PER THE FIRE MARSHALLS INVESTIGATION AND BURNT TO THE GROUND ON JULY 10, 2009. BECAUSE OF THE FIRE AN EMPTY (METER REMOVED 3/08) FLEX RISER WITH A PLASTIC SERVICE INSIDE BECA | 100
825 | 2009-07-17 | TX | sabotage | UNKNOWN (NUECES COUNTY ) | CORPUS CHRISTI, CITY OF - GAS DIV | THE EIGHT INCH PIPELINE CROSSING WAS LOCATED BY THE GAS DEPARTMENT ON JULY 7, 2009 PER LOCATE REQUEST TICKET 091812909. THE PIPELINE WAS ADEQUATELY MARKED AND THE MARKINGS WERE CLEARLY VISIBLE WHEN THE PIPELINE WAS INITIALLY LOCATED. THE EXCAVATOR WAS F | 800
826 | 2009-06-29 | TX | sabotage | UNKNOWN (BEXAR COUNTY ) | CPS ENERGY | THE EXCAVATION AREA WAS MARKED BY A CPS ENERGY LOCATOR RESPONDING TO A LOCATE REQUEST TICKET WHICH WAS CREATED ON JUNE 8, 2009. THE HIT MAIN OCCURRED AT THE BEGINNING POINT OF AN OFFSET AT THE INTERSECTION OF N.W. MILITARY HWY AND GREEN RUN THAT HAD BEEN | 9800
827 | 2009-06-08 | MO | sabotage | UNKNOWN (BATES COUNTY ) | ATMOS ENERGY CORPORATION - COLORADO/KANSAS | PROPERTY OWNER'S BROTHER DROVE A FENCE POST IN THE GROUND AND INTO THE COMPANY'S SERVICE LINE, PUNCTURING THE LINE. | 1000
828 | 2009-07-17 | UT | other | UNKNOWN (SALT LAKE COUNTY ) | QUESTAR GAS COMPANY | GAS FROM THE METER IGNITED AS A RESULT OF THE BUILDING BEING ON FIRE AND MELTED THE METER. | 100
829 | 2009-08-02 | CA | other | UNKNOWN (STANISLAUS COUNTY ) | PACIFIC GAS & ELECTRIC CO | A STRUCTURE FIRE STARTED APPROXIMATELY 0000 HOURS ON 8/02/09. THE MODESTO FIRE DEPARTMENT CALLED AT PG&E AT 0045 HOURS. THE PG&E GAS SERVICE REPRESENTATIVE ARRIVED AT 0110 HOURS. A GAS CREW WAS DISPATCHED BECAUSE THE FIRE PREVENTED ACCESS TO THE SERVICE | 0
830 | 2009-07-27 | WA | other | UNKNOWN (KITSAP COUNTY ) | CASCADE NATURAL GAS CORP | ARSON FOUND TO BE CAUSE. REPORTS FROM FIRE DEPARTMENT SAY BUILDING WAS ON FIRE WHEN THEY ARRIVED, BUT METER WAS NOT ON FIRE UNTIL LATER. LEAK INVESTIGATIONS OF GAS SERVICE LINE AND BUILDING FOUND NO LEAKS. ODORANT CHECKS THE NEXT MORNING SHOW ADEQUATE | 1000
831 | 2009-08-01 | OR | other | UNKNOWN (MARION COUNTY ) | NORTHWEST NATURAL GAS CO | AT APPROXIMATELY 23:10 P.M. PDT ON AUGUST 1, 2009, NW NATURAL RECEIVED NOTIFICATION OF AN EXPLOSION AND FIRE INVOLVING THE RESIDENCE AT 1501 E. BURNETT STREET, STAYTON, OREGON. THE RESIDENCE WAS COMPLETELY DESTROYED. THE EXPLOSION CAUSED THE WALL OF T | 100
832 | 2009-07-31 | VA | other | UNKNOWN (CALVERT COUNTY ) | WASHINGTON GAS LIGHT CO | WASHINGTON GAS RESPONDED TO AN APARTMENT FIRE AT 270 SHORE ACRES WAY IN PRINCE FREDERICK AT THE REQUEST OF THE FIRE DEPARTMENT. UPON ARRIVAL, THE GAS WAS FOUND TO BE OFF AT THE RISER VALVE. THE PIPING ABOVE THE RISER VALVE HAD BEEN DAMAGED BY A VEHICLE | 100
833 | 2009-08-06 | UT | other | UNKNOWN (WEBER COUNTY ) | QUESTAR GAS COMPANY | QUESTAR WAS NOTIFIED AT 7:00 PM ON AUGUST 6TH THAT A HOUSE LOCATED AT 4894 OLD POST ROAD IN OGDEN UTAH WAS ON FIRE. THE FIRE DEPARTMENT INITIALLY CORDONED OFF THE AREA AND DID NOT ALLOW QUESTAR’S CREW ACCESS TO THE PROPERTY. THE FIRE DEPARTMENT TURNED O | 100
834 | 2009-08-04 | CA | other | UNKNOWN (RIVERSIDE COUNTY ) | SOUTHERN CALIFORNIA GAS CO | ON AUGUST 4, 2009, A FIRE ERUPTED INSIDE A BUILDING, ULTIMATELY CAUSING BUILDING TO COLLAPSES ON THE METER SET ASSEMBLY, SHEARING OFF THE RISER. A FIREFIGHTER WAS INJURED, BUT HIS INJURY TOOK PLACE PRIOR TO THE COLLAPSE AND RESULTING ESCAPING GAS. FIRE | 100
835 | 2009-08-04 | MN | sabotage | UNKNOWN (OLMSTED COUNTY ) | MINNESOTA ENERGY RESOURCES CORPORATION | ROAD CONSTRUCTION WAS READY FOR CONCRETE AND CONTRACTOR DECIDED TO TURN GRAVEL TO DRY OUT WHAT WAS WET. | 32900
836 | 2009-08-07 | CA | sabotage | UNKNOWN (VENTURA COUNTY ) | SOUTHERN CALIFORNIA GAS CO | ON AUGUST 7, 2009, A 6” PLASTIC MEDIUM PRESSURE PLASTIC MAIN WAS DAMAGED BY A CONTRACTOR USING A BACKHOE TO EXCAVATE FOR A SEWER WORK. THERE WAS USA REQUEST FOR THIS WORK, HOWEVER, LOCATE MARKS PROVIDED WERE NOT ACCURATE. NO FIRE OR INJURIES RESULTE | 2000
837 | 2009-08-08 | CO | sabotage | UNKNOWN (LARIMER COUNTY ) | PUBLIC SERVICE CO OF COLORADO | EXCAVATOR WAS WORKING ON SEWER PROJECT. GAS SERVICE LINE WAS MISLOCATED. EXCAVATOR PULLED STEEL PORTION OF THE SERVICE OUT OF THE GROUND WITH TRACKHOE, AND THE STEEL TO POLYETHYLENE COMPRESSION COUPLING SEPARATED ON THE STEEL SIDE. | 200
838 | 2009-08-13 | HI | maintenance | UNKNOWN (nan COUNTY ) | THE GAS COMPANY | ACCORDING TO THE HONOLULU FIRE DEPARTMENT (HFD) REPORT, ON 8/12/09 HFD RESPONDED TO A GAS ODOR COMPLAINT AT 235 SOUTH BERETANIA STREET AROUND 10:22 PM. THE REPORT NOTES THAT HFD USED GAS DETECTORS TO CHECK FOR GAS INSIDE THE BUILDING WITH NEGATIVE RESULT | 10000
839 | 2009-08-15 | NM | other | UNKNOWN (BERNALILLO COUNTY ) | NEW MEXICO GAS COMPANY | SOLID WASTE VEHICLE HIT METER SET WHILE SETTING DOWN A GARBAGE BIN NEXT TO A BUSINESS. TWO EMPLOYEES FROM THE BUSINESS COMPLAINED OF SMELLING GAS AND WERE TRANSPORTED TO THE HOSPITAL. BECAUSE OF PRIVACY LAWS, IN-PATIENT HOSPITALIZATION COULD NOT BE CONFI | 50
840 | 2009-08-18 | GA | technical failure | UNKNOWN (FULTON COUNTY ) | ATLANTA GAS LIGHT CO | AN AGL EMPLOYEE BROKE A STEEL SERVICE RISER WHILE ATTEMPTING TO LOOSEN A SERVICE REGULATOR WITH PIPE WRENCHES CAUSING A RELEASE OF GAS. A BYSTANDER FELL DOWN SOME NEARBY STAIRS ATTEMPTING TO AVOID EXPOSURE TO THE GAS AND WAS INJURED. THE BYSTANDER ALSO | 16
841 | 2009-08-12 | GA | sabotage | UNKNOWN (FULTON COUNTY ) | ATLANTA GAS LIGHT CO | AN AGL CONTRACTOR INSTALLING NATURAL GAS FACILITIES BORED INTO A 2" PLASTIC MAIN. AS A RESULT, A MARTA TRANSIT STATION WAS EVACUATED AND TRANSIT SERVICE WAS TEMPORARILY HALTED. IN ADDITION, A MAJOR THOROUGHFARE WAS CLOSED FOR A PERIOD OF TIME AS A PRECA | 0
842 | 2009-06-24 | AZ | sabotage | UNKNOWN (YAVAPAI COUNTY ) | UNISOURCE ENERGY SERVICES | HIGHWAY TECHNOLOGY, A GUARDRAIL COMPANY CONTRACTED BY YAVAPI COUNTY, WAS INSTALLING GUARDRAILS ALONG IRONSPRINGS RD. IN PRESCOTT ARIZONA, HIGHWAY TECHNOLOGY WAS EXCAVATING WITHOUT A VALID BLUE STAKE. THE BLUE STAKE DATABASE HAS BEEN RESEARCHED AND NO VALI | 436
843 | 2009-01-22 | AL | maintenance | UNKNOWN (BALDWIN COUNTY ) | GULF COAST MINERAL, LLC | CORROSION. REASON BELIEVED TO BE CAUSED BY WATER. REPLACING THE SECTION UNDER WATER WITH HIGH PRESSURE "POLY PIPE." | 0
844 | 2009-06-01 | TX | sabotage | UNKNOWN (HARRIS COUNTY ) | ENTEX, A NORAM ENERGY COMPANY (FORM. DIV OF ARKLA | 3RD PARTY WHILE HAND DIGGING FOR FOUNDATION REPAIR DAMAGED A PROPERLY MARKED 3/4 POLY SERVICE-LINE, ESCAPING GAS IGNITED AND DIRECT FLAME IMPINGEMENT CAUSED STRUCTURE FIRE. | 374
845 | 2009-08-15 | IL | technical failure | UNKNOWN (LASALLE COUNTY ) | ILLINOIS POWER CO | THE GAS CONSTRUCTION CREW WAS SCHEDULED TO REBUILD A METER SET REPLACING TWO AL 5000 DIAPHRAGM METERS WITH ROATARY METERS. THE PROJECT WAS SCHEDULED FOR SATURDAY, AUGUST 15TH TO MINIMIZE CUSTOMER IMPACT DUE TO THE OUTAGE REQUIRED TO COMPLETE THIS REBUILD. | 0
846 | 2009-08-19 | WA | sabotage | UNKNOWN (KING COUNTY ) | PUGET SOUND ENERGY | <P>THE INCIDENT OCCURED ON AUGUST 19, 2009: PSE'S CONTRACTOR DAMAGED A 6" HP STW MAIN BY PULLING AN UNMARKED 1 1/4" STUB OFF THE MAIN WHILE EXCAVATING WITH A TRACK HOE. PSE'S FIRST RESPONDER CONTROLLED THE FLOW OF GAS BY CLOSING A HP VALVE IN THE VICINITY | 8667
847 | 2009-09-17 | AK | other | UNKNOWN (ANCHORAGE COUNTY ) | ENSTAR NATURAL GAS CO | ON SEPTEBMEER 17, 2009, ENSTAR RESPONDED TO A CALL TO ASSIST THE ANCHROAGE FIRE DEPARTMENT ON A FIRE AT 7316 TANAGA CIRCLE. HEAT FROM THE FIRE DRIED OUT THE GREASE IN THE SERVICE LINE SHUT OFF VALVE CAUSING A SMALL GAS LEAK AT THE VALVE. THE X-TUBE STEE | 10
848 | 2009-08-27 | GA | technical failure | UNKNOWN (FULTON COUNTY ) | ATLANTA GAS LIGHT CO | AN AGL CONTRACTOR WAS WELDING ON A 20" STEEL GAS MAIN WITH MECHANICALLY COUPLED JOINTS. DURING WELDING OPERATIONS, THE 20" PIPE SEPARATED FROM A BURIED MECHANICAL COUPLING IN CLOSE PROXIMITY TO THE WORK AREA CAUSING A CONCUSSIVE RELEASE OF GAS. AS A RES | 99000
849 | 2006-07-10 | WI | sabotage | UNKNOWN (DOOR COUNTY ) | CEDAR GROVE RESORT & HARBOR | ON JULY 10, 2006, AT APPROXIMATELY 2:30 A.M., A SERIES OF EXPLOSIONS OCCURRED IN THE AREA OF CEDAR GROVE RESORT, IN ELLISON BAY, WISCONSIN. THE EXPLOSIONS RESULTED IN THE DEATHS OF TWO RESORT GUESTS, AND INJURIES TO 12 OTHERS, SOME REQUIRING HOSPITALIZAT | 833
850 | 2009-09-19 | OR | other | UNKNOWN (JACKSON COUNTY ) | AVISTA CORP | A HIGH SPEED IMPACT FROM A VEHICLE STRUCK A DRIVEWAY BRIDGE, KILLING 3 OCCUPANTS. THE IMPACT SEVERED THE GAS SERVICE. 12/3/09 I FINALIZED THIS REPORT WITH NO ADDITIONAL CHANGES. KRIS BUSKO | 500
851 | 2009-09-02 | PA | sabotage | UNKNOWN (BEDFORD COUNTY ) | UGI CENTRAL PENN GAS, INC | A CONTRACTOR WHILE EXCAVATING A TRENCH TO INSTALL A WATER MAIN STRUCK AND DAMAGED A 4" STEEL HIGH PRESSURE DISTRIBUTION GAS MAIN WHICH RESULTED IN AN ESCAPE OF GAS. | 24567
852 | 2009-09-07 | IA | leaks and spills | UNKNOWN (HENRY COUNTY ) | ALLIANT ENERGY - INTERSTATE POWER AND LIGHT COMPANY | A PICKUP TRUCK LEFT THE ROADWAY AND HIT THE GAS METERSET AT 509 E. MONROE ST. IN MT. PLEASANT, IOWA ON MONDAY SEPTEMBER 7, 2009 AT 1:28 AM. THE FORCE OF THE TRUCK BROKE THE METERSET BETWEEN THE SHUT-OFF VALVE AND THE SERVICE REGULATOR. THE GAS IGNITED A | 0
853 | 2009-09-30 | AK | other | UNKNOWN (ANCHORAGE COUNTY ) | ENSTAR NATURAL GAS CO | ON WEDNESDAY EVENING, 9/30/2009, ENSTAR WAS NOTIFIED OF A HOUSE FIRE AT 12341 AUDUBON CIRCLE, ANCHORAGE, AK. THE FIRE ORIGINATED ON A DECK NEAR THE GAS METER. HEAT FROM THE FIRE DAMAGED THE RISER AND METER CAUSING A RELEASE OF NATURAL GAS. THE LINE WAS | 10
854 | 2009-08-25 | MO | other | UNKNOWN (SAINT LOUIS CITY COUNTY ) | LACLEDE GAS CO | GUNFIRE AT 4724 HIGHLAND AVENUE RESULTED IN A BULLET PUNCTURING A NATURAL GAS METER LOCATED INSIDE A METER CLOSET THAT WAS ACCESSIBLE EXCLUSIVELY THROUGH THE OUTSIDE OF THE BUILDING. THE BULLET PUNCTURE CAUSED NATURAL GAS TO LEAK FROM THE METER AND IGNITE | 0
855 | 2009-09-16 | CO | technical failure | UNKNOWN (DENVER COUNTY ) | PUBLIC SERVICE CO OF COLORADO | THE CREW FUSED ON A 2" HIGH VOLUME ELECTROFUSION TEE ONTO A 2" PE MAIN. THE CREW WAS USING AN ELECTRIC DRILL TO DRIVE THE TAPPING TOOL THAT CONNECTED TO THE CUTTER. WHEN BACKING OUT THE CUTTER THE TAPPING CHAMBER ALSO WAS REVERSED THEREBY ALLOWING GAS TO | 50
856 | 2009-10-06 | CA | other | UNKNOWN (SAN JOAQUIN COUNTY ) | PACIFIC GAS & ELECTRIC CO | ON 10/6/09 AT APPROXIMATELY 1645 HOURS A VEHICLE STRUCK 1 OF 7 BARRIER POSTS AROUND A MANIFOLD METER SET BENDING THE BARRIER INTO THE MANIFOLD CAUSING GAS TO BE RELEASED. THE VEHICLE ALSO STRUCK AN APARTMENT BUILDING CAUSING SIGNIFICANT DAMAGE. THE DRIV | 0
857 | 2009-10-02 | CA | other | UNKNOWN (RIVERSIDE COUNTY ) | SOUTHERN CALIFORNIA GAS CO | ON OCTOBER 2, 2009 A METER SET ASSEMBLY WAS DAMAGED WHEN A VEHICLE LOST CONTROL, LEAVING THE ROADWAY AND STRIKING INTO THE METER SET ASSEMBLY. THE ESCAPING GAS IGNITED, CAUSING A FIRE THAT DAMAGED A BUILDING. DUE TO BUILDING DAMAGE, THIS FACILITY WIL | 0
858 | 2009-10-03 | LA | leaks and spills | UNKNOWN (JEFFERSON COUNTY ) | ATMOS ENERGY CORPORATION - LOUISIANA | THE 18" STEEL MAIN LINE INVOLVED IN THIS INCIDENT WAS INSTALLED AROUND 1928 AND HAD NO HISTORY OF JOINT FAILURES. THIS SECTION OF THE 18" MAIN LINE IS INVOLVED IN A REPLACEMENT PROJECT WITH 12" PE PIPE. EVENT DESCRIPTION: FAILURE OCCURED UNDERGROUND APPR | 3674
859 | 2009-10-04 | MD | other | UNKNOWN (MONTGOMERY COUNTY ) | WASHINGTON GAS LIGHT CO | WASHINGTON GAS RESPONDED TO A HOUSE FIRE AT 1226 CLAGETT DRIVE IN ROCKVILLE, MARYLAND ON SUNDAY, OCTOBER 4, 2009, AT THE REQUEST OF THE MONTGOMERY FIRE DEPARTMENT. UPON ARRIVAL, WASHINGTON GAS CONFIRMED THAT THE GAS WAS OFF AT THE INSIDE METER VALVE AND | 100
860 | 2009-09-30 | VA | other | UNKNOWN (FAIRFAX COUNTY ) | WASHINGTON GAS LIGHT CO | WASHINGTON GAS RESPONDED TO A HOUSE FIRE AT 7651 ROYSTON STREET IN ANNANDALE ON WEDNESDAY, SEPTEMBER 30, 2009, AT THE REQUEST OF THE FAIRFAX FIRE DEPARTMENT. UPON ARRIVAL, WASHINGTON GAS SHUT THE GAS OFF AT THE CURB VALVE. WASHINGTON GAS ASSISTED THE FA | 100
861 | 2009-10-12 | TX | other | UNKNOWN (EL PASO COUNTY ) | TEXAS GAS SERVICE COMPANY | TEXAS GAS SERVICE RESPONDED TO A NATURAL GAS FIRE LOCATED AT 7646 KINGMAN DR. EL PASO, TEXAS 79915. A ONE INCH POLYETHYLENE NATURAL GAS LINE HAD BEEN MELTED AND IGNITED BY A SOLDERING TORCH USED BY A PRIVATE PLUMBING CREW THAT WAS MAKING REPAIRS TO A WATE | 119
862 | 2009-05-03 | TX | other | UNKNOWN (DALLAS COUNTY ) | ATMOS ENERGY CORPORATION - MID-TEX | DURING THE INVESTIGATION OF THIS INCIDENT, ATMOS ENERGY DETERMINED THROUGH INDEPENDENT INVESTIGATIONS THAT THE SMALL LEAK FOUND IN THE INVESTIGATION DID NOT CAUSE OR CONTRIBUTE TO THIS INCIDENT. TESTING OF THE STRUCTURE INDICATED THE PRESENCE OF GASOLINE | 0
863 | 2009-07-16 | IL | sabotage | UNKNOWN (COLES COUNTY ) | AMERENCIPS | ON 7/15/09 COLE FARM DRAINAGE OBTAINED AN EMERGENCY JULIE TO REPAIR TILE DUE TO A SINK HOLE IN THE ROAD AND TO LOCATE THE NORTH SIDE OF RT 16. THE TICKET WAS DUE AT 10AM ON 7/16. THE DIRECTIONS SAID APPROXIMATELY 1/4 MILE WEST OF ASHMORE AND 1 MILE EAST F | 38202
864 | 2009-10-28 | CA | other | UNKNOWN (MARIN COUNTY ) | PACIFIC GAS & ELECTRIC CO | A STRUCTURE FIRE STARTED APPROXIMATELY 0100 HOURS ON 8/28/09. THE FIRE DEPARTMENT CALLED AT PG&E AT APPROXIMATELY 0245 HOURS. THE PG&E GAS SERVICE REPRESENTATIVE ARRIVED ON SCENE AT 0330 HOURS. THE GAS WAS SHUT OFF AT APPROXIMATELY 0350 HOURS AT THE SER | 0
865 | 2009-11-19 | TX | sabotage | UNKNOWN (DENTON COUNTY ) | COSERV GAS, LTD | CONTRACTOR WAS INSTALLING ELECTRIC SERVICE. LINE HAD BEEN EXPOSED AND DAMAGE OCCURRED WHILE CLEANING OUT BELL HOLE WITH TRACKHOE. | 3200
866 | 2009-09-18 | NY | other | UNKNOWN (QUEENS COUNTY ) | CONSOLIDATED EDISON CO OF NEW YORK | ON FRIDAY, 9/18/09 AT 13:16, TWO CONSOLIDATED EDISON GAS OPERATIONS EMPLOYEES WERE INJURED AT 6-03 119 ST. QUEENS NY WHEN GAS IGNITED WHILE THEY WERE PREPARING TO INSTALL A CLAMP ON A CORROSION LEAK ON A 1955 - 4" LP UNCOATED STEEL GAS MAIN. BOTH EMPLOYEE | 100
867 | 2009-10-25 | NY | maintenance | UNKNOWN (WESTCHESTER COUNTY COUNTY ) | CONSOLIDATED EDISON CO OF NEW YORK | ON 10/25/2009 AT 00:46 HRS, MOUNT PLEASANT FIRE DEPARTMENT REPORTED A BUILDING FIRE WITH AN ODOR OF GAS AT 376 BRADHURST AVE IN HAWTHORNE, NEW YORK. CON EDISON EMERGENCY PERSONNEL RESPONDED AND FOUND THAT AN UNOCCUPIED GAS STATION ATTENDANT'S BOOTH HAD B | 0
868 | 2009-11-01 | NM | other | UNKNOWN (CHAVES COUNTY ) | NEW MEXICO GAS COMPANY | THERE WERE 2 VEHICLES INVOLVED IN THIS ACCIDENT. THE ACCIDENT OCCURRED NEXT TO AN APPARTMENT COMPLEX. VEHICLE A, WHICH ALSO HAD A HITCHED TRAILER, WAS PARKED CLOSE TO THE METER AND WAS LOADED WITH HOME FURNISHING. VEHICLE B HIT THE TRAILER FROM BEHIND, C | 50
869 | 2009-10-22 | TX | other | UNKNOWN (HARRIS COUNTY ) | ENTEX, A NORAM ENERGY COMPANY (FORM. DIV OF ARKLA | ON JANUARY 11, 2010 THIS OPERATOR WAS NOTIFIED THAT (1) OF THE INDIVIDUALS INJURED AT THE TIME OF THIS INCIDENT, DIED FROM THE INJURIES ON OR ABOUT JANUARY 9TH, 2010. | 50
870 | 2009-11-04 | CA | other | UNKNOWN (SAN JOAQUIN COUNTY ) | PACIFIC GAS & ELECTRIC CO | A HOUSE FIRE STARTED APPROXIMATELY 1430 HOURS ON 11/4/09. PG&E WAS NOTIFIED AT APPROXIMATELY 1440 HOURS. THE PG&E GAS SERVICE REPRESENTATIVE ARRIVED ON SCENE AT APPROXIMATELY 1510 HOURS. PG&E CREWS SHUT OFF THE GAS AT 1605 HOURS BY SQUEEZING OFF THE SE | 0
871 | 2009-11-23 | NJ | sabotage | UNKNOWN (WARREN COUNTY ) | ELIZABETHTOWN GAS CO | EMPCO CONTRACTOR 70-A WASHINGTON AVE, DUMONT, NJ 07628 PH# 201 385-2700, WAS DIGGING FOOTERS FOR BRIDGE AND DAMAGED 4" PE MAIN WITH TRACK HOE. ETG INSTALLED 2" PE BYPASS OVER BRIDGE AND SCHEDULED WITH OUR CONTRACTOR TO REPLACE 4" PE MAIN. COMPLETED ON | 8406
872 | 2009-11-12 | MI | sabotage | UNKNOWN (MUSKEGON COUNTY COUNTY ) | MICHIGAN CONSOLIDATED GAS CO (MICHCON) | <P>At, 08:29 on November 12, 2009, MichCon received a report of leaking gas on Marquette Avenue east of Harvey Street in the Township of Muskegon, Muskegon County, Michigan. MichCon personal arrived at the scene at 08:40 and determined that a sewer contra | 8954
873 | 2009-11-11 | IN | other | UNKNOWN (LAKE COUNTY ) | NORTHERN INDIANA PUBLIC SERVICE CO | DESCRIPTION OF ACCIDENT – ON THE ABOVE DATE AND TIME, NIPSCO WORK MANAGEMENT CENTER RECEIVED A CALL FROM THE HAMMOND FIRE DEPARTMENT INDICATING THERE WAS BLOWING GAS AT THE SUBJECT VALVE STATION AS RESULT OF VEHICULAR IMPACT. BASED ON PUBLIC REPORTS, THE | 151506
874 | 2009-11-28 | CA | other | UNKNOWN (TEHAMA COUNTY ) | PACIFIC GAS & ELECTRIC CO | A FIRE AT A MOBILE HOME PARK OCCURRED AT APPROXIMATELY 1145 HOURS ON 11/28/09. THE FIRE DEPARTMENT CALLED AT PG&E AT APPROXIMATELY 1220 HOURS. THE PG&E GAS SERVICE REPRESENTATIVE (GSR) ARRIVED AT 1300 HOURS. THE GSR SHUT OFF THE SERVICE VALVES AT THE ME | 0
875 | 2009-11-18 | NM | other | UNKNOWN (BERNALILLO COUNTY ) | NEW MEXICO GAS COMPANY | THE BUILDING AT THE SUBJECT ADDRESS CAUGHT FIRE AND THE BUILDING COLLAPSED ON THE METER CAUSING A RELEASE AND IGNITION OF GAS. THE CAUSE OF THE FIRE WAS UNKNOWN AT THE TIME OF THIS REPORT. THERE WERE NO INDICATIONS OF ANY GAS LEAKS FROM THE OPERATOR'S F | 2091
876 | 2009-11-25 | IL | sabotage | UNKNOWN (MCDONOUGH COUNTY ) | BUSHNELL MUNICIPAL GAS UTILITY | <P><FONT face="Times New Roman, Times, serif">BUSHNELL MUNICIPAL UTILITIES, BUSHNELL ILLINIOS ON NOVEMBER 25, 2009, A WATER COMPANY CONTRACTOR WAS INSTALLING A WATER LINE BY THE DIRECTIONAL DRILLING PROCESS, BUSHNELL, IL. THE CONTRACTOR HAD MADE A TIMELY | 1000
877 | 2009-11-24 | TX | sabotage | UNKNOWN (NUECES COUNTY ) | CORPUS CHRISTI, CITY OF - GAS DIV | THE EXCAVATOR DAMAGED THE 6 INCH MAIN WHILE DRILLING A HOLE FOR THE INSTALLATION OF A UTILITY POLE. THE CAUSE OF THE INCIDENT WAS THE EXCAVATOR FAILED TO MAINTAIN CLEARANCE BY DRILLING WITH A POWER AUGER INSIDE THE TOLERANCE ZONE OF THE PIPELINE MARKINGS | 0
878 | 2009-12-06 | AZ | maintenance | UNKNOWN (MARICOPA COUNTY ) | SOUTHWEST GAS CORP | 2009-1570 SOUTHWEST GAS SERVICE TECHNICIAN RESPONDED TO AN ODOR COMPLAINT AT 11304 E. SONRISA AVE. AND FOUND 164.917 PSIG IN DISTRIBUTION SYSTEM WITH AN MAOP OF 60 PSIG. OVERPRESSURIZATION WAS DETERMINED TO BE CAUSED BY DEBRIS THAT DAMAGED THE DIAPHRAMS I | 0
879 | 2009-11-22 | TX | leaks and spills | UNKNOWN (DALLAS COUNTY ) | ATMOS ENERGY CORPORATION - MID-TEX | IN RESPONSE TO A FIRE AT 503 MARTINDALE, A NATURAL GAS LEAK ON THE THREE INCH POLY MAIN WAS IDENTIFIED AT THE CORNER OF MARTINDALE AND STEWART. THERE WAS NO EVIDENCE OF A LEAK ON THE MAIN AT ANY TIME BEFORE THE FIRE. BARHOLING IN THE YARD AT 503 MARTIND | 0
880 | 2009-12-04 | MS | sabotage | UNKNOWN (RANKIN COUNTY ) | ENTEX, A NORAM ENERGY COMPANY (FORM. DIV OF ARKLA | THREE RIVERS CONTRACTORS (THIRD PARTY CONTRACTOR WORKING FOR ATT) DAMAGED OUR (CENTERPOINT ENERGY) NATURAL GAS LINE CAUSING IT TO IGNITE AND BURN A BORING RIG. THE CONTRACTOR CALLED IN THE INITIAL LOCATE AND ACCORDING TO THE STATE DAMAGE PREVENTION LAWS, | 1451
881 | 2009-12-07 | OH | other | UNKNOWN (MAHONING COUNTY ) | DOMINION EAST OHIO | AT APPROXIMATELY 01:57 HOURS ON DECEMBER 7, 2009, A 16” HP DISTRIBUTION MAINLINE OPERATING AT 120# LOCATED ON MIDLOTHIAN RD, YOUNGSTOWN, OHIO RUPTURED. TWO MAINLINE VALVES WERE SHUT AT 03:35 TO ISOLATE THE SEGMENT OF PIPELINE AND MAINTAIN SERVICE TO THE | 51000
882 | 2009-12-09 | MS | sabotage | UNKNOWN (HOLMES COUNTY ) | MISSISSIPPI RIVER GAS LLC | ELECTRIC POWER CO. HAD A BROKEN POLE THEY NEEDED TO REPLACE AND THEY ASSUMED THEY COULD DRILL A NEW HOLE BESIDE THE BROKEN POLE. WHEN THEY DRILLED, THE AUGER BIT GOUGED INTO THE PIPE. THERE WERE NO STRUCTURES WITHIN 300 FT. OF THE POINT OF DAMAGE. WE WE | 5600
883 | 2009-12-11 | CO | technical failure | UNKNOWN (ADAMS COUNTY ) | PUBLIC SERVICE CO OF COLORADO | STOPPLES SET AND BYPASS INSTALLED FOR MAIN RENEWAL PROJECT. UN-RESTRAINED 20" MECHANICAL COUPLING SEPARATED DUE TO TENSILE FORCE FROM INTERNAL PRESSURE. BLOWING GAS AND PIPE MOVEMENT CONTRIBUTED TO INJURY. THE GAP REFERENCED IN F6 NUIMBER 23 WAS WORK PERF | 135000
884 | 2009-11-20 | TX | leaks and spills | UNKNOWN (DALLAS COUNTY ) | ATMOS ENERGY CORPORATION - MID-TEX | AFTER FURTHER INVESTIGATION (FLOW RATE TEST) A LEAK WAS FOUND ON THE THREADS OF THE FITTING TO THE SERVICE LINE FEEDING 2502 CATALINA DR. | 0
885 | 2009-12-18 | NJ | other | UNKNOWN (UNION COUNTY ) | ELIZABETHTOWN GAS CO | A CREWPERSON WAS EXCAVATING BY HAND TO REPAIR A CLASS TWO JOINT LEAK ON A 6” DIAMETER CAST IRON MAIN. THE CREWPERSON WAS USING A PROBE BAR WITH INSULATED SLIDING HANDLE ON TOP. THE BAR CAME IN CONTACT WITH AN UNDERGROUND ELECTRICAL DUCT WHICH HAD NOT BE | 25
886 | 2009-12-09 | TN | other | UNKNOWN (KNOX COUNTY ) | KNOXVILLE UTILITIES BOARD |  | 5000
887 | 2009-12-12 | CA | leaks and spills | UNKNOWN (LOS ANGELES COUNTY ) | SOUTHERN CALIFORNIA GAS CO | ON DECEMBER 12, 2009 AN EXPLOSION OCCURRED IN AN ELECTRICAL ROOM AT AN APARTMENT COMPLEX IN CANOGA PARK, CA. THE EXPLOSION DAMAGED THE ELECTRICAL ROOM AND ADJACENT APARTMENT UNITS. NO INJURIES OCCURRED AS A RESULT OF THIS INCIDENT. INITIAL FIELD RE | 0
888 | 2009-12-11 | VA | sabotage | UNKNOWN (nan COUNTY ) | VIRGINIA NATURAL GAS | INFRASOURCE CONSTRUCTION COMPANY WAS INSTALLING AN 8" PLASTIC GAS PIPELINE BY HYDRAULIC DIRECTIONAL DRILL UNDER THE EXISTING 8" STEEL PIPELINE AS A RELOCATION PROJECT. THE UNDERSIDE OF THE EXISTING STEEL PIPELINE WAS DAMAGED DURING THE BACK REAMING OPERA | 48210
889 | 2009-12-20 | LA | natural disasters | UNKNOWN (TERREBONNE PARISH COUNTY ) | TERREBONNE PARISH CONSOLIDATED GOVERNMENT | ON DECEMBER 20, 2009, THE TPCG UTILITIES DEPARTMENT GAS DIVISION RESPONDED TO ASSIST THE HOUMA FIRE DEPARTMENT RESPONDING TO A FIRE AND/OR EXPLOSION AT 300 RAILROAD AVE. (LAT 90°43'34.73"W, LONG 29°35'38.34"N). DIVISION PERSONNEL WERE ASKED TO ISOLATE SU | 10
890 | 2009-12-19 | NE | natural disasters | UNKNOWN (nan COUNTY ) | BLACK HILLS ENERGY | DAMAGE TO PIPING AND METER SET WAS CAUSED BY LARGE AMOUNT OF SNOW WHICH HAD ACCUMULATED ON ROOF FALLING OFF AT ONE TIME CAUSING STRESS ON THE PIPING SYSTEM AND CAUSING IT TO FAIL. | 0
891 | 2009-12-20 | AR | natural disasters | UNKNOWN (PULASKI COUNTY ) | RELIANT ENERGY ARKLA, DIV OF RELIANT ENERGY RESOURC | CUSTOMER PHONED LITTLE ROCK FIRE DEPARTMENT TO REPORT AN ODOR OF GAS INSIDE 3501 LONGCOY AT 3:00 A.M. ON 12/20/2009. RESPONDING FIRE DEPT. PERSONNEL EVACUATED THE RESIDENCE, AND CALLED CNP AT 3:15 TO REPORT ODOR OF GAS OUTSIDE. SERVICE TECH ARRIVED AT 4 | 46
892 | 2009-12-26 | PA | other | UNKNOWN (MONTGOMERY COUNTY ) | PECO ENERGY CO | INITIAL CALL FROM MONTGOMERY COUNTY 911 WAS IDENTIFIED AS A HOUSE FIRE CALL. ONCE ON SITE, A LEAK WAS FOUND BY PECO. SOURCE WAS FOUND TO BE A CAST IRON MAIN BREAK UNDER THE ROADWAY ADJACENT TO PROPERTY. GAS WAS IGNITED AND RESULTED IN A LOW LEVEL EXPLOSIO | 0
893 | 2009-12-22 | CT | natural disasters | UNKNOWN (FAIRFIELD COUNTY ) | YANKEE GAS SERVICES CO | THE STATEMENTS AND CONCLUSIONS WITHIN THIS REPORT ARE BASED ON PRELIMINARY FINDINGS. THE INVESTIGATION INTO THIS INCIDENT IS ONGOING, AND YANKEE GAS SERVICES COMPANY (THE "COMPANY") RESERVES THE RIGHT TO AMEND THIS REPORT. A SUPPLEMENTAL REPORT WILL BE FI | 100
894 | 2009-12-11 | AZ | maintenance | UNKNOWN (MARICOPA COUNTY ) | SOUTHWEST GAS CORP | 2009-1718 SOUTHWEST CONSTRUCTION CREW RESPONDED TO A REPORTED LINE BREAK AT 8921 N ARROYO GRANDE AND FOUND GAS BLOWING AT THE SERVICE WITH NO EXCAVATION. THE CREW EXPOSED A 2" X 1" SERVICE SADDLE WITH THE 1" SERVICE PULLED FROM THE SERVICE SADDLE DUE TO | 0
895 | 2009-12-04 | IL | other | UNKNOWN (COOK COUNTY ) | NORTHERN ILLINOIS GAS CO | REGULATOR SET SCREW CAP WAS REMOVED BY UNKNOWN AND UNAUTHORIZED ENTITY. RAIN WATER ENTERED THE TOP OF THE REGULATOR DIAPHRAGM CASE AND FROZE, RESULTING IN PRESSURE PROBLEMS AT THE FURNACE WHICH RESULTED IN A FIRE IN THE STRUCTURE. | 100
896 | 2009-03-29 | AL | other | UNKNOWN (DEKALB COUNTY ) | DEKALB - CHEROKEE COUNTIES GAS DISTRICT |  | 100