## incident_gas_distribution_mid19
| Date | State | Cause of Loss | Name of Installation | Name of Owner | Text | Loss Estimated ($) | Link
0 | 1984-08-20 | AZ | other | GRADE 2 | ARIZONA PUBLIC SERVICE CO | EQUIPMENT OPERATED DURING A ROUTINE MAINTENANCE SURVEY STRUCK A 2" PVCMAIN ALLOWING GAS TO ESCAPE. A NEARBY BUILDING WAS TEMPORARILY EVACUATEDUNTIL THE FLOW OF GAS WAS STOPPED. */! CAUS CHANGED TO B (DAMAGE BYOUTSIDE FORCES) | 405 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1 | 1984-12-30 | FL | other | ROCKWELL | ST. JOE NATURAL GAS COMPANY | GAS DISTRICT STATION REGULATORS REMOVED FROM SERVICE, CLEARED OF ICE, AND RETURNED TO SERVICE BY 10:00 A.M. ON 12/30/83 | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2 | 1984-08-21 | TX | other |  | SOUTHERN UNION GAS CO | A CONTRACTOR WAS BORING UNDER WALLINGWOOD AND STRUCK A 6" MAIN. | 2000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
3 | 1984-05-07 | TN | other |  | PARSONS NATURAL GAS SYSTEM | A TORNADO STRUCK PARSONS ON MAY 7TH, 1984 TURNING A TRAILOR COMPLETELY OVER. GAS SERVICEMAN WERE DISPATCHED TO THE SCENE. THE ELECTRICAL CURRENT WAS STILL GOING TO THE TRAILOR AFTER TORNADO. ELECTRICAL SPARKS IGNITED GAS AND CAUSED TRAILOR TO BE DESTROYE | 3500 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
4 | 1984-05-08 | TX | other |  | HOUSING AUTHORITY OF THE CITY OF WICHITA FALLS, TE | NO COMMENTS | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
5 | 1984-05-25 | GA | other | UNKNOWN (COLQUITT COUNTY) | MOULTRIE GAS DEPT, CITY OF | STRESS ON PIPELINE BY EARTH MOVEMENT | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
6 | 1984-11-14 | NH | other |  | NORTHERN UTILITES INC - NEW HAMPSHIRE DIV | CONTRACTOR'S VIBRATORY COMPACTOR BROKE THREADED JOINT ON 1 1/4" BURIED MAIN. SPARKS CREATED BY DRAGGING BUCKET OF FRONT END LOADER IGNITED ESCAPING GAS AT SURFACE OF GROUND. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
7 | 1984-09-18 | TX | other |  | D & H GAS, INC. | THE COUNTY TOOK A NEW MAN ON THE EQUIPMENT. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
8 | 1984-04-05 | PA | other |  | NATIONAL FUEL GAS DISTRIBUTION CORPORATION | NO COMMENTS PROVIDED. | 70000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
9 | 1984-06-15 | NV | other | PHILLIPS | SOUTHWEST GAS CORP | A 2" POLYETHYLENE GAS SERVICE RUNNING BETWEEN BUILDINGS IN A CONDOMINIUM COMPLEX HAD BEEN HIT AND PULLED UPWARD 16" OUT OF POSITION BY A BACKHOE USED FOR A SEWER LINE CROSSING. THREE 2" X 5/8" MECHANICAL SERVICE CONNECTION TEES WERE DISPLACED FROM THEIR | 5000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
10 | 1984-06-16 | NM | other |  | GAS CO OF NEW MEXICO | A 1" UNIVERSAL REGULATOR ON A SINGLE RESIDENTAL GAS METER WAS ALLEGEDLY STRUCK BY AN UNKNOWN FORCE, CAUSING DAMAGE TO THE PRESSURE REGULATOR. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
11 | 1984-06-17 | AL | other | UNKNOWN | BREWTON GAS DEPT, CITY OF | ON JUNE 17, 1984, SHORTLY AFTER 9:00 A.M., OUR FOREMAN EDDIE FRAZIER WAS NOTIFIED THAT THEY WANTED US TO CUT THE GAS OFF AT CLUB SHERWOOD ON OLD U.S. HIGHWAY 31 SOUTH. HE HAD THE POLICE DEPARTMENT CONTACT J.W. ROWELL, JR., ASSISTANT SUPERINTENDENT, AND TH | 145000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
12 | 1984-06-17 | NV | technical failure |  | TROPICANA EAST M.H.P. | TENANT IN THE PARK DECIDED TO RE-LANDSCAPE A PORTION OF HIS PROPERTY ON A WEEKEND. THE TENANT RENTED A SMALL TRACTOR TO DO HIS GRADING AND UNKNOWLING HIT THE RISER DAMAGE WAS MINIMAL AND REPAIRED WITHIN A SHORT PERIOD OF TIME. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
13 | 1984-06-18 | TX | other |  | MORAN UTILITIES CO | SOME SHOT A HOLE IN A GAS METER. AT SOME POINT THE GAS IGNITED BY AN UNKNOWN SOURCE & A 14 YEAR OLD BOY WAS BURNED & TAKEN TO THE HOSPITAL. THE METER HAD BEENSHOT WITH A PELLET GUN. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
14 | 1984-06-20 | IL | other | STUPP CORP. | NORTHERN ILLINOIS GAS CO | BULLDOZER STRUCK 16" GAS MAIN CAUSING LEAK WHICH WAS IGNITED BY CUTTING TORCH NEARBY. MAN USING TORCH WAS BURNED. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
15 | 1984-06-20 | TX | other |  | ENERGAS CO | CUSTOMER CALLED IN LEAK TO COMPANY DISPATCHER. WHEN SERVICEMAN ARRIVED, CUSTOMER HAD BURNED HAND. WE RAN SHUT-IN TEST AND LEFT METER OFF AND LOCKED DUE TO EX-CESSIVE LEAKAGE INSIDE HOUSE. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
16 | 1984-06-22 | AZ | other | GRADE 1 | ARIZONA PUBLIC SERVICE COMPANY | A LABORER FOR WATERLINE CONTRACTOR WAS POT HOLING MAIN - HIT 2" PVC MAIN WITH SHOVEL WHICH CAUSED A RUPTURE. THE LABORER HAD MINOR EYE AND FACIAL ABRASIONS AND WAS TAKEN TO VALLEY LUTHERN HOSPITAL'S EMERGENCY ROOM, TREATED AND RELEASED.*?/! INJURIES CHA | 415 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
17 | 1984-06-22 | PA | technical failure | FISHER | PHILADELPHIA GAS WORKS | MECHANIC FAILED TO CLOSE MAIN OUTLET VALVE OF DISTRICT REGULATOR STATION BEFOREATTEMPTING TO REMOVE SIDE PLATE OF REGULATOR. BOLTS WERE LOOSENED AND GAS ENTERED THE MANHOLE. THIS RESULTED IN TEMPORARY ASPHYXIATION TO TWO EMPLOYEES. ONEEMPLOYEE WAS HELD | 20 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
18 | 1984-06-22 | TX | maintenance |  | GEORGE WEST, CITY OF | MAN WENT TO LITE HOT WATER HEATER AND OWNER OF HOUSE DID NOT TELL HIM SHE HAD LEAKS ON SIDE UNDER THE HOUSE. HE LIT A MATCH AND THERE WAS AN EXPLOSION. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
19 | 1984-06-25 | TX | other | UNKNOWN | SOUTHERN UNION GAS CO | A TRAILER USED FOR MOVING A HOUSE AT THE INCIDENT SITE SNAGGED A CLOSED STOP COCK AND TORE IT LOOSE FROM ITS RISER. TRAFFIC WAS REROUTED BY THE LOCAL FIRE DEPARTMENT UNTIL LEAK WAS SHUT OFF. | 100 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
20 | 1984-06-25 | KS | other |  | UNION GAS SYSTEM INC | WE LOWERED OUR 4" GAS MAIN 3 1/2 FEET ABOUT 2 1/2 MONTHS AGO PER THE ENGINEERS REQUEST AND INSPECTION. STREET GRADE WORK WAS DONE AND ON 6-25-84, THE CONTRACTOR, MAX RIEKE AND BROS., 15400 MIDLAND DR., SHAWNEE, CAME IN AND STARTED TO USE A LARGE ROTOTILL | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
21 | 1984-08-15 | AZ | other | GRADE 1 | ARIZONA PUBLIC SERVICE COMPANY | EQUIPMENT OPERATED BY APS PERSONNEL STRUCK A 2" ABS MAIN ALLOWING GAS TO ESCAPE. A NEARBY BUILDING WAS EVACUATED AND THE STREET BLOCKADED AND TRAFFIC REROUTEDTEMPORARILY UNTIL THE FLOW OF GAS WAS STOPPED.*/! CAUS CHANGED TO B(OUTSIDE FORCE) | 1316 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
22 | 1984-06-27 | AR | other |  | ARKANSAS LOUISIANA GAS CO (ARKLA GAS CO) | METER RISER TORN OUT BY EARTH MOVING EQUIPMENT DURING DEMOLITION OF VACANT HOUSE | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
23 | 1984-06-28 | NE | other |  | METROPOLITAN UTILITIES DISTRICT | RESURFACING STREET CONTRACTOR FOREMAN REMOVED BARRICADE MARKING & PROTECTING GAS DRIP. CONTRACT HAULER'S TRUCK RAN OVER DRIP STEM BREAKING IT. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
24 | 1984-07-02 | NC | technical failure | JONES & LAUGHLIN | PIEDMONT NATURAL GAS CO INC | WE, PIEDMONT NATURAL GAS CO. AND TAR HEEL PAVING CO., OUR CONTRACTOR, HAD JUST INSTALLED 399 OF 6" STEEL GAS MAIN. AFTER PRESSSURE TEST WAS COMPLETED AND THE NEW MAIN WAS TIED IN TO THE OLD MAIN BY MEANS OF A 6" DRESSER COUPLING (A COMPRESSION TYPE FITTI | 150 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
25 | 1984-07-05 | AR | other |  | ARKANSAS LOUISIANA GAS CO (ARKLA GAS CO) | STATE HWY. DEPT. HAD CLEANED DRAINAGE DITCH EXPOSING PIPE. ELECTRIC LINE FELL ON MAIN-BURNED HOLE IN IT. GAS IGNITED. LIGHTNING ARRESTER ON POWER POLE FAILED DURING THUNDER STORM CAUSING POWER LINE TO FALL ACROSS MAIN. | 5 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
26 | 1984-07-05 | IN | other |  | NORTHERN INDIANA PUBLIC SERVICE CO | THE LOCATE REQUEST WAS RECEIVED ON 07-02-84. THE SCHEDULED WORK START, DATE ANDTIME WAS 07-05-84 AT 1:00 P.M. WORK STARTED AND DAMAGE OCCURED AT 9:20 A.M. ON 07-05-84 A.M. ON 07-05-84 BEFORE LOCATE WAS PROVIDED. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
27 | 1984-08-08 | AZ | other | GRADE I | ARIZONA PUBLIC SERVICE COMPANY | ESCAPE. THE STREET WAS BLOCKADED AND TRAFFIC REROUTED TEMPORARILY UNTIL THE FLOW OF GAS WAS STOPPED. | 924 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
28 | 1984-07-09 | IN | maintenance |  | NORTHERN INDIANA PUBLIC SERVICE CO | A LEAK WAS DISCOVERED AT THE ABOVE LOCATION. INVESTIGATION REVEALED THREE SMALL CORROSION LEAKS WITHIN A 10' LENGTH OF THE MAIN. TRAFFIC WAS REROUTED WHILE THE MAIN WAS REPLACED. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
29 | 1984-07-11 | AZ | other | GRADE 2 | ARIZONA PUBLIC SERVICE COMPANY | EQUIPMENT OPERATED BY AN OUTSIDE CONTRACTOR STRUCK A 2" A.B.S. MAIN ALLOWING GAS TO ESCAPE. THE STREET WAS BLOCKADED AND THE TRAFFIC REROUTED TEMPORARILY UNTIL THE FLOW OF GAS WAS STOPPED. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
30 | 1984-07-13 | AZ | other |  | SOUTHERN UNION GAS CO | A CONTRACTOR'S CATERPILLAR RIPPED A 4" STEEL MAIN WHILE GRADING FOR A DRIVEWAY. THE LINE HAD BEEN MARKED. | 4191 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
31 | 1984-07-13 | OH | technical failure |  | COLUMBIA GAS OF OHIO INC | TWO COMPANY EMPLOYEES WERE WORKING IN AN EXCAVATED AREA IN THE PROCESS OF REPLACING A COMPANY SERVICE LINE. NATURAL GAS WAS INDUCED IN THE WORK AREA BY ONE EMPLOYEE WHILE TAPPING THE SERVICE LINE TEE AT THE MAIN LINE.THE SECOND EMPLOYEE WAS IN THE PROCES | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
32 | 1984-07-14 | FL | other |  | CENTURY, TOWN OF | REASON FOR FIRE WAS SUSPECTED ARSON, WHICH IS UNDER INVESTIGATION. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
33 | 1984-07-17 | AZ | other | GRADE 2 | ARIZONA PUBLIC SERVICE COMPANY | ESCAPE. THE STREET WAS TEMPORARILY BLOCKADED AND TRAFFIC REROUTED UNTIL THE FL | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
34 | 1984-08-10 | AZ | other |  | ARIZONA PUBLIC SERVICE COMPANY | EQUIPMENT OPERATED BY AN OUTSIDE CONTRACTOR STRUCK A 1 1/4" STEEL RISER AT GROUND LEVEL. THE STREET WAS BLOCKADED AND TRAFFIC REROUTED TEMPORARILY UNTIL THE FL | 243 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
35 | 1984-07-18 | AL | other |  | SOUTHEAST ALABAMA GAS DISTRICT | LIGHTNING STRUCK METER SET BURNING A HOLE IN THE REGULATOR, CAUSING GAS TO ESCAPE AND IGNITE.GAS BURNED UNDER 4 OUNCES PRESSURE FOR 15 MINUTES BEFORE BEING CUT OFF BY FIRE DEPARTMENT.THE GAS COMPANY WAS THEN CALLED TO MAKE REPAIRS AND RESTORE GAS SERVICE. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
36 | 1984-07-20 | IN | maintenance |  | CITIZENS GAS & COKE UTILITY | WE RECEIVED A REPORT OF AN EXPLOSION AT 4500 STRATFORD AVENUE AT 5:03 PM ON JULY 20, 1984 FROM THE INDIANAPOLIS FIRE DEPARTMENT. THE FIRST UTILITY REPRESENTATIVE AT THE SCENE FOUND THAT AN APPARENT EXPLOSION HAD OCCURRED AND THE ONE STORYHOUSE WAS STILL | 135000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
37 | 1984-07-23 | IL | other |  | PEOPLES GAS LIGHT & COKE CO | THE PIPELINE LOCATION HAD BEEN MARKED IN RESPONSE TO A ONE-CALL SYSTEM REQUEST FROM A SEWER CONTRACTOR, WEEKS BEFORE THIS INCIDENT. AFTER THE SEWER WAS INSTALLED, A GRADING CONTRACTOR FAILED TO CALL FOR A LOCATE OR GIVE NOTIFICATION OF INT | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
38 | 1984-07-27 | AZ | other | GRADE 2 | ARIZONA PUBLIC SERVICE COMPANY | CUSTOMER AT 1330 5TH ST. INSTALLED NEW SEWER TAP THAT WENT UNDER THE GAS MAIN AT SERVICE TEE. THE TRENCH WAS NOT PROPERLY COMPACTED. THE CREW FOUND THE DITCHHAD SETTLED 6" ON TOP OF THE TEE CAUSING THE 1/2" ABS TO BREAK AT AN ELL. | 300 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
39 | 1984-07-27 | TX | other |  | ENERGAS CO | FIRE BEGAN AT YORK TIRE WHEN A SPARK FROM A FUSEBOX IGNITED FLAMMABLE RUBBER CEMENT IN RETREAD SHOP. RESULTANT FIRE AND DAMAGED FOUR METERS. | 1500 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
40 | 1984-08-01 | CO | technical failure |  | PUBLIC SERVICE CO OF COLORADO | FIRE VALVES WERE BEING INSTALLED ON 2 INTEGRATED STATIONS. STATION #1 HAD BEENSHUT OFF INCLUDING CONTROL LINE FOR STATION REGULATOR. WORK WAS COMPLETED AND STATION TURNED ON; HOWEVER THE CONTROL LINE WAS NOT. CREW SET STOPPER FITTING AT SECOND STATION | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
41 | 1984-07-25 | AZ | other | GRADE 2 | ARIZONA PUBLIC SERVICE COMPANY | EQUIPMENT OPERATED BY AN OUTSIDE CONTRACTOR STRUCK A 2" ABS MAIN, ALLOWING GAS TO ESCAPE WHICH IN TURN IGNITED CAUSING 2ND DEGREE BURN ON CONTRACTORS RIGHT ARM. HE WAS TREATED AT THE LINCOLN METRO EMERGENCY CENTER AND RELEASED. | 325 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
42 | 1984-08-09 | AZ | technical failure | DUPONT | SOUTHWEST GAS CORP | A SUBCONTRACTOR WELDER WAS ACETYLENE WELDING TOO CLOSE TO STEEL/PLASTIC TRANSITION FITTING. A SUBCONTRACTOR WAS REPLACING A SECTION OF 1 1/4" PLASTIC MAIN ANDWAS WELDING A TEE ON A SECTION OF STEEL MAIN IN THE PROXIMITY OF A TRANSITION FITTING, CAUSING T | 100 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
43 | 1984-08-30 | AZ | other | GRADE 2 | ARIZONA PUBLIC SERVICE COMPANY | CUSTOMER AT 14842 N. 33RD PLACE WAS LOOKING FOR SEWER SERVICE AND BROKE A 2" ABS MAIN AT THE COUPLING. | 1800 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
44 | 1984-08-30 | AZ | other |  | ARIZONA PUBLIC SERVICE COMPANY | EQUIPMENT OPERATED DURING A ROUTINE MAINTENANCE SURVEY STRUCK A 3/4" STEEL SERVICE ALLOWING GAS TO ESCAPE. A NEARBY BUILDING WAS TEMPORARILY EVACUATED UNTIL TH | 900 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
45 | 1984-08-28 | TX | other | NIPAK PE 2306 | LONE STAR GAS CO | 3" POLY MAIN HIT BY DALLAS CITY WATER DEPT. LAYING 2" WATER SERVICE.NO INJURIES OR EVACUATION. PART OF 7300 BLK. JULIUS SCHEPPS FRWY BLOCKED OFF FROM OVERTON TO MCCOLLOUGH. | 1000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
46 | 1984-08-27 | AZ | other |  | ARIZONA PUBLIC SERVICE COMPANY | CONTRACTOR'S EMPLOYEE WAS FOUND UNCONSCIOUS IN AN EXCAVATION WHERE ESCAPING GASFROM THE SERVICE LINE WAS PRESENT. | 270 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
47 | 1984-09-13 | KY | technical failure |  | WESTERN KENTUCKY GAS CO | AT APPROXIMATELY 10:45 AM, SEPTEMBER 13, 1984, WE HAD TWO EMPLOYEES, JOHN WAYNEMCGREGOR AND JOHN WOODS MAKING A ROUTINE INSPECTION OF A REGULATOR STATION AT THE CORNER OF BRANCH AND HARRIG STREET.DURING THIS INSPECTION THEY REALIZED THAT THEY HAD INADVERT | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
48 | 1984-08-13 | KY | other |  | LOUISVILLE GAS AND ELECTRIC COMPANY | 4" CAST IRON MAIN WAS LEAKING AT JOINTS.A KENTUCKY STATE HIGHWAY CREW WAS PAINTING TRAFFIC STRIPES IN THE INTERSECTION OF LOGAN AND MARY STREETS. THEY WERE USING A MACHINE THAT THROWS A FLAME. AS THE MACHINE PASSED OVER A MANHOLE, A GAS THAT HAD MIGRATE | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
49 | 1984-08-26 | OK | other |  | ARKANSAS LOUISIANA GAS CO (ARKLA GAS CO) | GAS FROM FLOOR FURNACE PILOT WAS IGNITED BY REFRIGERATOR IN VACANT GARAGE APARTMENT. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
50 | 1984-08-31 | GA | other |  | ATLANTA GAS LIGHT CO | A THIRD PARTY OPERATING A BACKHOE IN YARD STRUCK GAS SERVICE WHICH APPARENTLY BROKE UNDER THE HOUSE. AN EXPLOSION RESULTED FROM THE LINE BREAK. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
51 | 1984-08-30 | TX | other |  | LONE STAR GAS CO | 1" BLEEDER VALVE NIPPLE BROKE OFF OF 4" WR. ST. IHP. MAIN IN CO MAN HOLE - DUE TO SETTLING OF MANHOLE.100 PEOPLE WERE EVACUATED INVOLVING 2 BUSINESSES (3919 IRVING AND 3817 IRVING) ONE LANE WAS BLOCKED BY FIRE DEPT. IN THE 3700, 3800 AND 3900 BLK. IRVING. | 327 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
52 | 1984-08-23 | TX | technical failure |  | LONE STAR GAS CO | MANUFACTURING DEFECT AND STRESS. | 600 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
53 | 1984-08-15 | TX | other | NIPAK | LONE STAR GAS CO | CONTRACTOR FOR TESCO DRILLED HOLE IN POLY MAIN.TEXAS ELECTRIC SERVICE COMPANY PERSONNEL HAD CALLED FOR LINE LOCATION. LINE WAS STAKED BY OUR FACILITIES COORDINATOR, BUT HE MISSD LOCATED LINE APPROXIMATELY 3 | 1500 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
54 | 1984-09-08 | AZ | other | GRADE 2 | ARIZONA PUBLIC SERVICE COMPANY | DURING A ROUTINE LEAK SURVEY A LEAK WAS DETECTED WHICH RESULTED IN A 1/2 DRESSING COUPLING BEING REPLACED. A NEARBY BUILDING WAS TEMPORARILY EVACUATED UNTIL THE FLOW OF GAS WAS STOPPED. | 240 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
55 | 1984-09-11 | AZ | other | GRADE 3 | ARIZONA PUBLIC SERVICE COMPANY | DUE TO UNKNOWN REASON, SERVICE CRACKED AT THE SQUEEZE. A NEARBY BUILDING WAS TEMPORARILY EVACUATED UNTIL THE FLOW OF GAS WAS STOPPED. | 120 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
56 | 1984-09-11 | AZ | other | GRADE 1 | ARIZONA PUBLIC SERVICE COMPANY | THE DRESSING COUPLING FAILED RESULTING IN A LEAK AT THE RUBBER SEAL. A NEARBY BUILDING WAS EVACUATED AND THE STREET BLOCKADED AND TRAFFIC REROUTED TEMPORARILYUNTIL THE FLOW OF GAS WAS STOPPED. | 960 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
57 | 1984-09-11 | AZ | other | GRADE 2 | ARIZONA PUBLIC SERVICE COMPANY |  | 540 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
58 | 1984-01-27 | PA | maintenance |  | NATIONAL FUEL GAS DISTRIBUTION CORPORATION | PITTING AND LEAK OCCURRED ON THE MAIN UNDER A DRIVEWAY. THE PIPE CONDITION ON EITHER SIDE OF THE DRIVEWAY WAS GOOD. | 1500 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
59 | 1984-09-05 | OH | other | SUPERIOR | COLUMBIA GAS OF OHIO INC | UNOCCUPIED HOUSE BEING REMODELLED CAUGHT FIRE AND HEAT FROM FIRE MELTED TIN METER. HEAT FROM FIRE MELTED TIN METER IN BASEMENT. ESCAPING GAS POSSIBLY CONTRIBUTED TO A LOW LEVEL EXPLOSION. HOUSE AND THREE ADJOINING STRUCTURES DAMAGED. | 51800 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
60 | 1984-09-08 | TX | other |  | LONE STAR GAS CO | CAR RAN OVER METER AND SERVICE RISER. | 975 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
61 | 1984-09-07 | TX | other | NIPAK | LONE STAR GAS CO | CITY OF FT. WORTH WATER DEPT. TRYING TO LOCATE WATER VALVE CUT LINE IN TWO. | 5000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
62 | 1984-09-06 | WI | other | CONTINENTAL INDUSTRIES | WISCONSIN NATURAL GAS CO |  | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
63 | 1984-09-05 | TX | other |  | ENTEX INC | CONTRACTOR BROKE MAIN WITH BACKHOE. TRAFFIC WAS REROUTED. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
64 | 1984-09-07 | TX | other |  | LONE STAR GAS CO | APPARENT FAULTY WELD PLUS SLIGHT EARTH MOVEMENT DUE TO DRY WEATHER. | 1000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
65 | 1984-09-16 | TX | other |  | SOUTHERN UNION GAS CO | A 3/4" SERVICE LINE WAS SEVERED BY A CONTRACTOR'S DITCHING MACHINE. WHEN THE CONTRACTOR CONTINUED DITCHING, HIS MACHINE CAUGHT FIRE. THE LINE HAD BEENMARKED . SUPPLEMENTAL: THE DITCHING MACHINE CAUGHT FIRE AND WAS DAMAGED. THESERVICE LINE HAD BEEN REL | 1500 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
66 | 1984-09-01 | TX | other |  | ARKANSAS LOUISIANA GAS CO (ARKLA GAS CO) | SIX INCH MAIN WAS PUNCTURED WHEN HIT BY BACKHOE BUCKET WHILE THIRD PARTY WAS CLEANING DRAINAGE DITCH. | 4000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
67 | 1984-09-06 | TX | other | DRESSER | ENTEX INC | CONTRACTOR PULLED COMPRESSION COUPLING LOOSE WITH BACKHOE. TRAFFIC WAS REROUTED | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
68 | 1984-08-29 | NY | other |  | LONG ISLAND LIGHTING CO | INCIDENT IS UNDER INVESTIGATION. PIPE AND COMPRESSION COUPLING SAMPLES SENT TOLAB TO DETERMINE IF COUPLING WAS LEAKING PRIOR TO INCIDENT. BOTTLE SAMPLES TAKEN AT THE FOUNDATION ON #14 FLORENCE DRIVE FOUND TO CONTAIN NATURAL GAS. GAS SERVICE PRESSURE TE | 200000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
69 | 1984-09-12 | NC | other | PHILLIPS DRISCO PIPE | PIEDMONT NATURAL GAS CO INC | DURING EXCAVATION TO REPAIR A #2 SURVEY LEAK, THE MACHINE OPERATOR PUNCTURED MAIN WITH BACKHOE TOOTH. | 30 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
70 | 1984-09-12 | PA | other |  | PHILADELPHIA ELECTRIC CO | DRIVER OF VEHICLE SUFFERED FATAL HEART ATTACK. RUNAWAY VEHICLE STRUCK TREES AND OTHER CARS AND CAME TO REST AGAINST DAMAGED HOUSE. GASOLINE TANK RUPTURED ANDIGNITED AND INCIDENT CAUSED DAMAGE TO PHILADELPHIA ELECTRIC COMPANY OUTDOOR RESIDENTIAL GAS METE | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
71 | 1984-09-12 | MI | other | UNITED STATES STEEL | MICHIGAN GAS UTILITIES CO | CUSTOMER CUT CONCRETE SLAB PERMITTING CONCRETE TO FALL ONTO UNDERMINED SERVICE LINE. NOTIFIED MR. AMBROZEWICZ AT 10:40 P.M., SEPTEMBER 12, 1984, AND TALKED TOCHARLES BATTEN AT 11:00 P.M., SEPTEMBER 12, 1984. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
72 | 1984-09-25 | AZ | other | KERONA | ARIZONA PUBLIC SERVICE COMPANY | A LONGITUDINAL SPLIT OCCURRED IN AN 1 1/4" MAIN (CAUSE UNKNOWN). GAS MIGRATED INTO NEARBY APARTMENT BUILDINGS AND A SUBSEQUENT EXPLOSION OCCURRED. SOURCE OF IGNITION IS UNKNOWN.*/! INJURIES CHANGED TO 6*/! DEATHS CHANGED TO 5*/! FOUR OF REPORTED INJUR | 300 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
73 | 1984-09-17 | IL | maintenance |  | ILLINOIS POWER CO | CORROSION LEAK CAUSED GAS IN SEPTIC SYSTEM AND HOUSE. ONE PERSON RECEIVED 1ST DEGREE BURNS TO FACE AND HANDS. SECOND PERSON RECEIVED 2ND DEGREE BURNS TO FACE AND HANDS AND 3RD DEGREE BURNS ON BACK DUE TO CLOTHING BURN. .50 O.D. BARE COPPERSERVICE INSULATE | 30000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
74 | 1984-08-31 | CA | maintenance |  | SOUTHERN CALIFORNIA GAS CO | DAMAGE DUE TO FAILURE TO BOTH MAIN AND SERVICE LINE. | 1000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
75 | 1984-09-03 | CA | other |  | SOUTHERN CALIFORNIA GAS CO | OUT OF CONTROL VECHICLE STRUCK A BUILDING SUBSEQUENTLY DAMAGING THE METER SET ASSEMBLY ALLOWING GAS TO ESCAPE AND IGNITE. | 60000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
76 | 1984-09-10 | TX | other | NIPAK | LONE STAR GAS CO | MAIN CUT BY BACKHOE DIGGING DITCH LAYING STORM SEWER. | 1216 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
77 | 1984-09-21 | TX | other |  | ENERGAS CO | THERE WAS A LEAK ON THE CUSTOMER'S YARD LINE. THE GAS MIGRATED TO AN OFFICE BUILDING WHERE IT ACCUMULATED IN SUFFICENT CONCENTRATIONS TO CAUSE AN EXPLOSION; THE SOURCE OF IGNITION IS UNKNOWN. THERE WAS SIGNIFICANT DAMAGE TO THE OFFICE OFPECO FEEDYARDS. | 5000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
78 | 1984-09-28 | TX | other |  | ENERGAS CO | WE WERE NOTIFIED OF THE INCIDENT BY THE FIRE DEPARTMENT. A SHUT-IN AND LEAK CHECK WERE MADE OF THE PIPING AT 2318 - 2ND PLACE AND NO LEAK WAS FOUND AND PIPINGWAS GAS TIGHT. THE FIRE MARSHALL STATED THAT APPARENTLY THE RANGE CONNECTOR CONNECTING THE GAS | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
79 | 1984-04-05 | PA | other |  | NATIONAL FUEL GAS SUPPLY CORPORATION | ON 4/5/84, AT APPROXIMATELY 11:38 A.M. AN EXPLOSION, FOLLOWED BY FIRE, TOOK PLACE AT 1402 ROSELY RD., ST. MARYS, PA. HOME OWNED BY JOHN AND MARILYN NICKEL, WHOWERE INSIDE THE HOUSE AT THE TIME OF THE INCIDENT. INVESTIGATION SHOWED THAT INDEPENDENT CONTRA | 70000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
80 | 1984-09-11 | CA | other |  | PACIFIC GAS & ELECTRIC CO | STRUCTURE FIRE, DAMAGED NEARBY METER SET, ALLOWING GAS TO ESCAPE AND IGNITE. NEARBY BUILDINGS WERE EVACUATED AND TRAFFIC REROUTED. | 200000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
81 | 1984-09-21 | TN | other |  | MEMPHIS LIGHT GAS & WATER DIVISION | CONTRACTOR STABILIZING ROAD BASE DAMAGED 4" COATED STEEL GAS MAIN. ESCAPING GAS IGNITED DESTROYING THE ROAD GRADING MACHINE AND DAMAGING SHUTTERS, SHINGLES AND WINDOWS OF NEARBY APARTMENT BUILDING. | 76797 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
82 | 1984-09-17 | NV | technical failure | GROVE | SOUTHWEST GAS CORP | AT 1600 HRS. ON SEPTEMBER 17, 1984, A 16" VALVE, WHICH HAD BEEN CLOSED, OPENED A VENTED OUT A 6" UNIT BLOW DOWN VALVE. THE ESD VALVES WERE CLOSED AT 0830 HRS.THE NEXT DAY. | 500000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
83 | 1984-09-21 | OH | other | REPUBLIC STEEL | CINCINNATI GAS & ELECTRIC CO | WHILE GRADING IN PREPARATION OF ROAD CONSTRUCTION AND INSTALLATION OF A NEW BRIDGE, 12" STEEL PIPE WAS STRUCK BY BULLDOZER BLADE. NEWTOWN FIRE DEPT. EVACUATEDNEARBY SCHOOL AND RESIDENCES.THREE (3) TEST HOLES HAS BEEN EXCAVATED & WERE LEFT OPEN SO CONTRAC | 3000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
84 | 1984-05-18 | PA | technical failure |  | NATIONAL FUEL GAS DISTRIBUTION CORPORATION | THE FIRE ORIGINATED IN A SMALL UTILITY CLOSET, JUST OFF THE FAMILY ROOM IN THE REAR OF THE DWELLING. THE HOT WATER HEATER AND THE GAS METER WERE LOCATED ADJACENT TO ONE ANOTHER IN THE CLOSET, NOT MORE THAN SIX INCHES APART WITH THE METER SETTING ON THE F | 6000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
85 | 1984-05-14 | NV | other |  | SOUTHWEST GAS CORP | A 45" SEWER LINE WAS BEING INSTALLED ALONG ST. LOUIS STREET. TWO PIPE INSTALLERS WERE IN OR NEAR THE END OF THE PIPE SECTION JUST INSTALLED. AN ACCUMULATION OF GAS WITHIN THE PIPE WAS IGNITED APPARENTLY WHEN ONE OF THE MEN LIT A CIGARETTE. AN EXPLOSION | 2000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
86 | 1984-08-01 | CA | other | EASTMAN CHEMICAL | SOUTHERN CALIFORNIA GAS CO | CAUSE STILL BEING INVESTIGATED. | 200000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
87 | 1984-07-20 | TX | other | DUPONT | ENTEX INC | INTERFERENCE FROM AN AC POWER LINE CAUSED PIPE LOCATOR TO GIVE AN INACCURATE LOCATION OF MAIN.CONTRACTOR BROKE MAIN WITH SMALL TRENCHER. GAS IGNITED BY SPARK FROM TRENCHER BLADE STRIKING CONCRETE. | 6500 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
88 | 1984-08-06 | GA | other |  | ATLANTA GAS LIGHT CO | STATE DOT CONTRACTOR'S FRONT END LOADER CUT LARGE HOLE IN 4" HP STEEL MAIN. | 778 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
89 | 1984-08-08 | UT | other | DUPONT(ALDYL A) | MOUNTAIN FUEL SUPPLY CO | OUTSIDE PARTY WAS EXCAVATING WITH A BACKHOE TO INSTALL FIRE-HYDRANT, AND RUPTURED 2" INTERMEDIATE HIGH PRESSURE NATURAL GAS MAIN. THE BACKHOE WAS STRADDLING THE TRENCH WHEN THE ACCIDENT OCCURRED. EQUIPMENT OPERATOR WAS BURNED WHEN HE ATTEMPTED TO START | 230 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
90 | 1984-08-15 | NY | other | DUPONT | LONG ISLAND LIGHTING CO | CONTRACTOR INSTALLING SEWER SEVERED GAS SERVICE WITH BACKHOE & CONSUMER EVACUATED FROM HOUSE BY SUFFOLK COUNTY SEWER INSPECTOR WHILE GAS WAS BLOWING. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
91 | 1984-08-07 | IN | other |  | NORTHERN INDIANA PUBLIC SERVICE CO | LIGHTNING STRIKE OF AN UNKNOWN LOCATION, BURNED A 1/16" X 3/16" HOLE IN THE 3/4" STEEL SERVICE PIPE APPROXIMATELY TEN FEET AWAY FROM 4" STEEL GAS MAIN. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
92 | 1984-08-11 | IN | other | DUPONT | NORTHERN INDIANA PUBLIC SERVICE CO | PARTY WAS INSTALLING AN UNDERGROUND WATER LINE USING A TRENCHER AND CUT 5/8" PLASTIC GAS SERVICE. | 150 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
93 | 1984-08-09 | AZ | other |  | ARIZONA PUBLIC SERVICE COMPANY | EQUIPMENT OPERATED ON A ROUTINE MAINTENANCE SURVEY STRUCK A 3/4" STEEL SERVICE ALLOWING GAS TO ESCAPE. A NEARBY BUILDING WAS EVACUATED TEMPORARILY UNTIL THE FL | 253 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
94 | 1984-08-20 | AZ | other |  | ARIZONA PUBLIC SERVICE COMPANY | EQUIPMENT OPEARTED DURING A ROUTINE MAINTENANCE SURVEY STRUCK A 3/4" STEEL SERVICE ALLOWING GAS TO ESCAPE. A NEARY BUILDING WAS TEMPORARILY EVACUATED UNTIL THE FLOW OF GAS WAS STOPPED. | 500 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
95 | 1984-08-01 | PA | other | YOUNGSTOWN SHEET & TUBE | ALLIED GAS COMPANY, ASHLAND DISTRICT | PIPELINE DAMAGED BY EXCAVATING EQUIPMENT. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
96 | 1984-08-22 | GA | other | PLEXCO | ATLANTA GAS LIGHT CO | CITY OF CARROLLTON PERSONNEL MAKING A BORE FOR WATER MAIN CUT PLASTIC MAIN WITHAUGER. ESCAPING GAS WAS IGNITED BY BORING RIG ENGINE. | 400 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
97 | 1984-08-17 | TX | other |  | ENERGAS CO | DRIVER OF AUTOMOBILE (1974 MERCURY) BACKED INTO METER SETTING, DAMAGING METER.AS THE DRIVER PULLED AWAY FROM SETTING, LOST CONTROL OF AUTOMOBILE AND STRUCK ANOTHER METER SETTING. CAR STOPPED ON TOP OF THIS SETTING. CAR CAUGHT FIRE AND BURNED. DRIVER WA | 2000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
98 | 1984-08-15 | TX | other | CERTAINTEED | WEST END GAS COMPANY | WORKMEN UNDER CONTRACT TO SW BELL - INCIDENT REPORTED TO SW BELL IN DEVINE, TEXAS. LINE WAS DUG OUT AND EXPOSED IN 4 LOCATIONS APPROXIMATELY 1 WEEK BEFORE BREA | 1849 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
99 | 1984-08-12 | TX | other |  | LONE STAR GAS CO | LOOSE BOLTS ON THE METER INSTALLATION INDICATES POSSIBLE TAMPERING WITH THE METER AND INSTALLATION OCCURED BEFORE THE FIRE. | 4000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
100 | 1984-08-14 | CA | other |  | PACIFIC GAS & ELECTRIC CO | CAR STRUCK GAS METER SET BREAKING GAS RISER ALLOWING GAS TO ESCAPE AND IGNITE.TRAFFIC WAS REROUTED AND NEWS MEDIA WAS ON THE SCENE.THE FATALITY IN THIS INCIDENT WAS THE DRIVER OF THE VEHICLE WHICH STRUCK THE METER SET. IT COULD NOT BE DETERMINED WHETHER | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
101 | 1984-10-08 | WY | other | PLEXCO | PETROLANE WYOMING GAS SERVICE |  | 12000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
102 | 1984-09-29 | IA | technical failure |  | IOWA GAS COMPANY | SERVICE PIPING WAS TWISTED IN TWO WHEN A PLUG WAS INSTALLED IN THE SERVICE ENTRANCE INTO THE BASEMENT. EXPLOSION OCCURED THE FOLLOWING DAY.*/! CAUS CHANGED TO C (CONSTRUCTION/OPERATING ERROR) | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
103 | 1984-09-17 | AZ | other | GRADE 2 | ARIZONA PUBLIC SERVICE COMPANY | EQUIPMENT OPERATED BY AN OUTSIDE CONTRACTOR STRUCK A 2" ABS MAIN ALLOWING GAS TO EXCAPE. THE STREET WAS BLOCKADED AND TRAFFIC REROUTED TEMPORARILY UNTIL THE FL | 765 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
104 | 1984-10-06 | NM | other |  | GAS CO OF NEW MEXICO | OPERATOR OF FRONT-END LOADER OWNED BY ALBQ. MATERIAL, INC. TORE INTO A 4" VHP LINE. | 25665 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
105 | 1984-08-01 | TX | other |  | SOUTHERN UNION GAS CO | NARRATIVE DESCRIPTION OF FACTORS CONTRIBUTING TO THE INCIDENT: A CONTRACTOR PUNCHED A HOLE IN A 6" MAIN WHILE USING A BULLDOZER TO MOVE A LARGE ROCK. THE CONTRACTOR HAD NOT CALLED FOR A LINE LOCATION. | 2000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
106 | 1984-07-23 | TX | other | NIPAK | LONE STAR GAS CO | EAGLE P/L EMPLOYEE, EMILIO SALADANA, OVERCOME BY GAS AND WAS HOSPITALIZED AFTERBORING RIG HIT AND BROKE L.S.G. SERVICE LINE. MR. SALADANA PASSED AWAY AUGUST 6, 1984. | 25 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
107 | 1984-08-19 | NE | other |  | NORTHWESTERN PUBLIC SERVICE CO | UNKNOWN VEHICLE DAMAGED SERVICE REGULATOR CAUSING FIRE IN DWELLING | 35000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
108 | 1984-08-09 | TX | other | NIPAK P.E. 2306 | LONE STAR GAS CO | BACKHOE OWNED BY WEAVER CONST. COMPANY DIGGING STORM SEWER DITCH. CUT 3" POLY SERVICE TO 310 W. MOCKINGBIRD. | 10001 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
109 | 1984-01-27 | PA | maintenance |  | NATIONAL FUEL GAS SUPPLY CORPORATION | NATIONAL FUEL ARRIVED AT THE ABOVE ADDRESS AT APPROXIMATELY 10:35 AM. A MINOR FIRE WAS ALREADY EXTINGUISHED BY THE FIRE DEPARTMENT. THE GAS WAS IMMEDIATELY SHUT OFF AT THE METER. THE HOUSE WAS COMPLETELY VENTILATED AND SAFE. THE OWNER AND A FRIEND WERE | 1500 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
110 | 1984-08-09 | WI | other | FISHER | WISCONSIN GAS CO | FLASH FIRES AT GAS RANGES, IN A NUMBER OF INDIVIDUAL APARTMENTS, OCCURED AT 1 130 UNIT APARTMENT BUILDING LOCATED AT 5634 W. OKLAHOMA AVENUE. THE FIRES APPARENTLY COMMENCED WHEN A LAWN TRACTOR STRUCK A SERVICE REGULATOR HEAD AND RUPTURED IT THE POINT OF | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
111 | 1984-07-19 | CO | other |  | PUBLIC SERVICE CO OF COLORADO | CONTRACTOR PUNCTURED MAIN WITH BACKHOE. | 75000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
112 | 1984-08-15 | AZ | other | GRADE I | ARIZONA PUBLIC SERVICE COMPANY | EQUIPMENT OPERATED BY AN OUTSIDE CONTRACTOR STRUCK A 2" PVC MAIN ALLOWING GAS TO ESCAPE. THE STREET WAS BLOCKADED AND TRAFFIC REROUTED TEMPORARILY UNTIL THE FLOW OF GAS WAS STOPPED. | 708 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
113 | 1984-08-10 | AZ | other | GRADE 2 | ARIZONA PUBLIC SERVICE COMPANY | THE GROUND APPEARED TO BE ERODED OVER SERVICE TRENCH CAUSING PIPE TO FAIL, ALLOWING GAS TO ESCAPE. A NEARBY BUILDING WAS EVACUATED TEMPORARILY UNTIL THE FLOW OF GAS WAS STOPPED. | 828 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
114 | 1984-09-20 | TX | other |  | LONE STAR GAS CO | TRACTOR CUT INTO MAIN | 2518 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
115 | 1984-09-21 | TX | other |  | LONE STAR GAS CO | BUILDING WALL FELL ON LOOP BREAKING PIPE AND IGNITING ESCAPING GAS. ARSON WAS THE CAUSE. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
116 | 1984-10-12 | TX | other |  | ENTEX INC | CONTRACTOR BROKE GAS LINE WITH FRONT-END LOADER. GAS WAS IGNITED BY UNKNOWN SOURCE CAUSING EXPLOSION AND FIRE AND DESTROYING HOUSE. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
117 | 1984-10-15 | CT | other |  | CONNECTICUT LIGHT & POWER CO | ON 9/20/84, MET AND DISCUSSED WITH CONTRACTOR THE SCOPE OF THE JOB AND LOCATIONOF FACILITIES. BASED ON CONTRACTOR'S DESCRIPTION OF JOB, CONTRACTOR INDICATED NO MARKOUT WAS REQUIRED. WHILE MILLING THE PAVEMENT OF WALL STREET PRIOR TO PLACING PERMANENT PA | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
118 | 1984-10-11 | TX | other |  | SAN ANTONIO CITY PUBLIC SERVICE BOARD | GAS MAIN WAS UNCOVERED BY OUTSIDE CONTRACTOR IN THE PROCESS OF INSTALLING A STORM SEWER. COMPRESSION COUPLING AT 90 DEGREES CORNER FAILED BECAUSE SOIL SUPPORTWAS NO LONGER PRESENT. OUTSIDE CONTRACTOR DID NOT PHYSICALLY CONTACT GAS MAIN. | 24000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
119 | 1984-10-22 | AL | other |  | ALABAMA GAS CORP | GAS LEAKED FROM 4" MAIN BREAK APPARENTLY THROUGH THE GROUND INTO TWO HOUSES, IGNITED AND EXPLODED, DESTROYING ONE AND SEVERELY DAMAGING THE OTHER. | 150000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
120 | 1984-10-05 | IN | other |  | OHIO VALLEY GAS CORPORATION | AT 9:30 A.M. ON FRIDAY, OCTOBER 5, 1984, KAY PARKS RECEIVED A CALL FROM THE CONERSVILLE POLICE DEPARTMENT THAT THERE WAS A FIRE AT A GAS METER AT 915 W. 3RD STREET, THE RESIDENCE OF ELIZABETH GOLDEY. THE CALL WAS IMMEDIATELY DISPATCHED TO SERVICEMAN HAR | 40000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
121 | 1984-09-23 | KY | other |  | LOUISVILLE GAS AND ELECTRIC COMPANY | AN AUTOMOBILE OPERATED BY A SEVENTEEN YEAR OLD BOY, WENT OUT OF CONTROL AND STRUCK THE CUSTOMER'S GAS SERVICE LINE AND GAS METERS LOCATED ON THE SIDE OF THE BUILDING, SEVERING THE GAS SERVICE LINE IN TWO PLACES. A RESULTING EXPLOSION OCCUR | 75000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
122 | 1984-10-03 | TX | other |  | LONE STAR GAS CO | BACKHOE HIT LINE AND PULLED LINE OUT OF 2" DRESSER COUPLING. 170 CUSTOMERS AFFECTED. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
123 | 1984-08-27 | LA | other |  | HOUMA MUNICIPAL GAS SYSTEM | RECEIVED THE CALL AT HOME FROM POLICE DISPATCH AT 6:24 A.M. TO RESPOND TO A HOUSE FIRE AT 115 MUNSON. ARRIVED AT THE SCENE AT 6:34 A.M. AND CHECKED WITH DISTRICT CHEIF RONALD LEBOUF OF THE FIRE DEPARTMENT. HOUSE WAS STILL BURNING, BUT FIRE WAS UNDER CONT | 20000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
124 | 1984-10-16 | TX | other |  | LONE STAR GAS CO | WHILE IN THE PROCESS OF PREPARING THE STREET SURFACE TO REPAIR A PAVING CUT OVER THE GAS MAIN MADE BY OPERATOR, FIRST PATCH PAVING COMPANY HIT AND BROKE A WELDED NIPPLE OFF OF 6" IP GAS MAIN MAKING 2" HOLE IN TOP OF THE MAIN. THEY KNEW THE MAIN LOCATION, | 5000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
125 | 1984-08-01 | TX | other | JET STREAM | SOUTH RUSK COUNTY GAS CO | J & D SEPTIC SERVICE WAS LAYING A SEPTIC TANK LINE FOR AUSTIN HUDMAN. MR HUDMANTOLD THE PARTY TO CALL US AND WE WOULD LOCATE THE LINE AND THEY JUST IGNORED THAT A DUG THE LINE AND CUT OUR MAIN LINE. MR. HUDMAN THEN CALLED US AND WE HAD THE LINE REPAIRED | 1153 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
126 | 1984-10-18 | NY | other |  | CONSOLIDATED EDISON CO OF NEW YORK | A 13" LONG X 5' DIAMETER STEEL, HYDRO-PNEUMATIC WATER TANK EXPLODED AND WAS EXPLODED AND WAS PROPELLED INTO THE GAS METER BANK SHEARING OFF GAS METERS AND RISER PIPES, CAUSING A SECONDARY GAS EXPLOSION. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
127 | 1984-10-28 | NM | other |  | GAS CO OF NEW MEXICO | 1980 TOYOTA STRUCK METER BREAKING SWIVEL ON METER LOOP. | 5000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
128 | 1984-11-30 | LA | other | CERTAIN-TEED | MORGANZA, VILLAGE OF | ON NOVEMBER 30, 1984, AT APPROXIMATELY 10:30 PM CHIEF RONNIE PAGE OF MORGANZA DISCOVERED A SMELL OF GAS AS HE WAS DRIVING BY THE AREA WHERE TRANCONTINENTAL PIPELINE IS CROSSING A 42 INCH PIPELINE. CHIEF PAGE CALLED GAS & WATER SUPT. MARK RAMAGOS AND MAYO | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
129 | 1984-11-19 | TX | technical failure |  | ENERGAS CO | CUSTOMER SERVICE REGULATOR OVER-PRESSURED FACILITIES DUE TO FREEZING MOISTURE DUE TO BROKEN AND MISSING FITTING ON REGULATOR VENT. | 750 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
130 | 1984-12-06 | NM | other |  | GAS CO OF NEW MEXICO | UNKNOWN VEHICLE STRUCK BARRICADED METER LOOP, BREAKING NIPPLE OFF AT REGULATOR ABOVE GROUND ALLOWING GAS TO ESCAPE AND TO ENTER ELECTRICAL OUTLET BOXES DIRECTLY ABOVE METER CAUSING IGNITION OF GAS. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
131 | 1984-11-24 | IA | other |  | PEOPLES NATURAL GAS | CAST IRON MAIN CRACKED FROM WHAT APPEARS TO BE GROUND STRESS. THERE WAS 8"-12"SURFACE FROST. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
132 | 1984-11-13 | MT | other | DUPONT | MONTANA - DAKOTA UTILITIES CO | ON 11-08-84, PHIL LETZ OF MONTANA POWER CO. (MPC) CALLED AND ASKED FOR A LINE LOCATION FOR 11-09-84. ON 11-09-84 DON MEYERS OF M.D.U. LOCATED THE LINE AND MARKED IT WITH YELLOW PAINT. MPC CREW DID NOT ARRIVE UNTIL 11-13-84, AND THE PAINTHAD BEEN OBLITER | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
133 | 1984-11-14 | NY | other |  | BROOKLYN UNION GAS CO | WHILE IN THE PROCESS OF RELIGHTING A DUAL FUEL BOILER IN AN APARTMENT BUILDING WHICH WAS UTILIZING OIL FOR FUEL AT THE TIME, OIL VAPORS IGNITED CAUSING EXTENSIVE DAMAGE TO BOTH THE BOILER AND BASEMENT. THE SERVICEPERSONS WERE REPLACONG ANOIL SOLENOID VAL | 30000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
134 | 1984-09-26 | AZ | other | GRADE 3 | ARIZONA PUBLIC SERVICE COMPANY | THE SERVICE FAILED FROM AN UNKNOWN CAUSE. THE STREET WAS BLOCKADED AND NEARBY HOUSES WERE TEMPORARILY EVACUATED FOR SAFETY REASONS. | 16140 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
135 | 1984-09-24 | AZ | maintenance |  | ARIZONA PUBLIC SERVICE COMPANY |  | 27837 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
136 | 1984-09-20 | AZ | other | GRADE 3 | ARIZONA PUBLIC SERVICE COMPANY | A LEAKING 3/4" AMP FITTING WAS FOUND ON A SERVICE RISER RESULTING IN A NEARBY BUILDING BEING EVACUATED TEMPORARILY UNTIL THE FLOW OF GAS WAS STOPPED. | 240 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
137 | 1984-08-02 | AZ | other |  | ARIZONA PUBLIC SERVICE COMPANY | CUSTOMERS HOUSE LINE WAS DETERMINED TO BE FAULTY WHICH RESULTED IN A SECONDARY | 50 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
138 | 1984-10-20 | AZ | other | GRADE 2 | ARIZONA PUBLIC SERVICE COMPANY | ABS PIPE WAS SPLIT FROM PRESSURE EXERTED ON PROTECTIVE SLEEVE EDGE INSTALLED WHEN SERVICE WAS RELOCATED AROUND ROOM ADDITION. A NEARBY BUILDING WAS TEMPORARILY EVACUATED UNTIL THE FLOW OF GAS WAS STOPPED. | 584 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
139 | 1984-09-10 | AZ | maintenance |  | ARIZONA PUBLIC SERVICE COMPANY |  | 120 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
140 | 1984-09-07 | AZ | technical failure |  | ARIZONA PUBLIC SERVICE COMPANY | A FIELD WELD FAILED RESULTING IN A LEAK. A NEARBY BUILDING WAS EVACUATED TEMPORARILY UNTIL THE FLOW OF GAS WAS STOPPED. | 210 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
141 | 1984-09-10 | AZ | maintenance |  | ARIZONA PUBLIC SERVICE COMPANY |  | 450 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
142 | 1984-10-01 | AZ | other | GRADE 2 | ARIZONA PUBLIC SERVICE COMPANY | A 1/2" ABS SERVICE CRACKED AT THE END OF THE STIFFNER FROM AN UNKNOWN CAUSE. THE STREET WAS BLOCKAEDED TEMPORARILY UNTIL THE FLOW OF GAS WAS STOPPED. | 600 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
143 | 1984-10-05 | AZ | maintenance |  | ARIZONA PUBLIC SERVICE COMPANY | DURING A ROUTINE LEAK SURVEY A CORROSION LEAK WAS FOUND RESULTING IN A NEARBY BUILDING BEING TEMPORARILY EVACUATED UNTIL THE FLOW OF GAS WAS STOPPED. | 3150 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
144 | 1984-10-09 | AZ | other | GRADE 1 | ARIZONA PUBLIC SERVICE COMPANY | A LONGITUDINAL SPLIT OCCURRED IN A 2" MAIN (CAUSE UNKNOWN). A NEARBY BUILDING WAS EVACUATED TEMPORARILY UNTIL THE FLOW OF GAS WAS STOPPED. | 780 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
145 | 1984-10-12 | AZ | other | GRADE 2 | ARIZONA PUBLIC SERVICE COMPANY | A LONGITUDINAL SPLIT OCCURRED IN A 2" MAIN (CAUSE UNKNOWN). THE STREET WAS BLOCKADED AND A NEARBY BUILDING WAS EVACUATED TEMPORARILY UNTIL THE FLOW OF GAS WASSTOPPED. | 960 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
146 | 1984-10-30 | AZ | other | GRADE 1 | ARIZONA PUBLIC SERVICE COMPANY | EQUIPMENT OPERATED BY AN OUTSIDE CONTRACTOR STRUCK A 2" ABS SERVICE LINE ALLOWING GAS TO ESCAPE. THE STREET WAS BLOCKADED AND TRAFFIC REROUTED TEMPORARILY UNTIL THE FLOW OF GAS WAS STOPPED. | 390 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
147 | 1984-07-17 | AZ | other |  | ARIZONA PUBLIC SERVICE COMPANY | BOLT OF LIGHTNING STRUCK BACK SIDE OF REGULATOR WHICH BURNED A SMALL HOLE AND IN TURN IGNITED. CUSTOMER TURNED GAS OFF AND NOTIFIED APS THE NEXT DAY. | 50 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
148 | 1984-06-27 | AZ | other | GRADE 2 | ARIZONA PUBLIC SERVICE COMPANY | EQUIPMENT OPERATED BY AN OUTSIDE CONTRACTOR STRUCK A 1 1/4" ABS MAIN WITH A HAND PICK CAUSING GAS TO ESCAPE. A BUILDING WAS EVACUATED AND THE STREET BLOCKADEDAND A TRAFFIC REROUTED UNTIL THE FLOW OF GAS WAS STOPPED. | 390 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
149 | 1984-07-31 | AZ | maintenance |  | ARIZONA PUBLIC SERVICE COMPANY | CORROSION CAUSED A LEAK AT THE SERVICE CONNECTION ON A 2" GAS MAIN WHICH RESULTED IN A BUILDING BEING EVACUATED UNTIL THE RESIDUAL GAS IN THE GROUND AND BUILDING HAD DISSIPATED. | 996 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
150 | 1984-07-30 | AZ | maintenance |  | ARIZONA PUBLIC SERVICE COMPANY | CORROSION CAUSED LEAKS ON A 2" GAS MAIN RESULTING IN A BUILDING BEING EVACUATEDUNTIL THE RESIDUAL GAS IN THE GROUND AND BUILDING HAD DISSIPATED. | 1169 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
151 | 1984-09-24 | IL | other |  | ILLINOIS POWER CO | DAMAGE CAUSED WHEN VEHICLE HIT HOUSE AND METER SET BROKE SERVICE RISER BELOW METER STOP. VEHICLE STOPPED OVER SERVICE. DUG UP AT MAIN TO TURN OFF GAS. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
152 | 1984-09-24 | IL | other |  | ILLINOIS POWER CO | STATE OF ILLINOIS, DEPARTMENT OF TRANSPORTATION WAS AUGERING ALONG WEST SIDE OFRT. 127 IN HILLSBORO TO MAKE HOLE FOR SETTING HIGHWAY WARNING SIGN POST WHEN THEY HIT 2" STEEL GAS LINE. NO PRIOR NOTIFICATION FOR LOCATE WAS GIVEN. | 1 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
153 | 1984-11-24 | TX | other |  | SOUTHERN UNION GAS CO | CONTRACTOR WAS GRADING FOR DRIVEWAY APPROACH WHEN HE HIT MAIN, SEPARATING ITAT A BUTT WELD. | 3693 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
154 | 1984-07-06 | TX | other |  | ENTEX INC | CONTRACTOR REMOVING OLD PAVEMENT HIT OUR 2" STL. MAIN AND PULLED IT OUT OF A 2" | 1330 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
155 | 1984-08-03 | NY | other |  | LONG ISLAND LIGHTING CO | CONTRACTOR CONNECTING SEWER PULLED & SEVERED TEE FROM MAIN REQUIRING SHUTDOWN TO12 CONSUMERS. | 200 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
156 | 1984-07-26 | NY | other |  | LONG ISLAND LIGHTING CO | CONTRACTOR EXCAVATING RUPTURED 3" GAS MAIN ALLOWING GAS TO ESCAPE. | 100 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
157 | 1984-06-08 | NY | other | DUPONT | LONG ISLAND LIGHTING CO | CUSTOMER USING POST HOLE DIGGER BROKE AND SEVERED PLASTIC GAS SERVICE; FIRE DEPARTMENT EVACUATED OCCUPANTS. | 100 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
158 | 1984-06-07 | TX | other |  | GAS LIGHT SQ. M.H.E. | CABLE TV WAS TRENCHING, HIT .75" POLYETHYLENE PIPELINE WAS TO EMPTY LOT. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
159 | 1984-05-30 | TX | other | YOUGSTOWN | SHERMAN HOUSING AUTHORITY | THE METER WAS KNOCKED OVER BY A CAR THAT WENT OUT OF CONTROL. | 900 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
160 | 1984-11-29 | AZ | other | SWANSON | SOUTHWEST GAS CORP | ON NOVEMBER 29, 1984, AT APPROXIMATELY 14:30 HOURS, A WORKMAN FOR ARIZONA PIPELINE COMPANY, UNDER CONTRACT, WITH SOUTHWEST GAS CORPORATION, WAS EXPOSING A 5/8" O.D. POLYETHYLENE TUBING SERVICE. HE WAS DIGGING NEAR THE METER SET ASSEMBLY. THE WORKMAN STRUC | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
161 | 1984-05-15 | OH | technical failure |  | DAYTON POWER & LIGHT CO | GAS ESCAPING FROM LOW PRESSURE (4 OZ) SERVICE AND IGNITED DURING CONSTRUCTION WORK.*/! CAUSE CHANGED TO C (CONSTRUCTION/OPERATING ERROR) | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
162 | 1984-11-22 | GA | other |  | ATLANTA GAS LIGHT CO | VEHICLE STRUCK REGULATOR STATION RELIEF VALVE STACK BREAKING PIPING. DRIVER BURNED WHEN ENGINE IGNITED ESCAPING GAS. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
163 | 1984-12-07 | TX | technical failure |  | SOUTHERN UNION GAS CO | GAS MIGRATED FROM A DEFECTIVE WELD TO A SIGN POLE. WHEN A CONTRACTOR'S WELDING TORCH CONTACTED THE MIGRATING GAS, A FLASH OCCURED. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
164 | 1984-11-28 | TX | other | PHILLIPS | SAN ANTONIO CITY PUBLIC SERVICE BOARD | OUTSIDE CONTRACTOR DUG INTO GAS SERVICE AND URD ELECTRIC IN SAME TRENCH. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
165 | 1984-11-26 | PA | other | RELIANCE | U G I CORP | AT 0030 ON THE MORNING OF NOVEMBER 26, 1984, UGI RECEIVED A CALL FOR A GAS ODORIN THE 100 BLOCK OF RIDGE STREET, FREELAND. IT WAS DETERMINED THAT THE ORIFICE SEAL ON A FARM TAP REGULATOR FEEDING THE 20 PSIG SYSTEM ON RIDGE STREET AND WYOMING STREET FAILED | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
166 | 1984-11-27 | TX | maintenance |  | SOUTHERN UNION GAS CO | MIGRATING GAS COLLECTED IN A TRAFFIC SIGNAL CHANGER BOX & IGNITED, BLOWING THE DOOR OPEN. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
167 | 1984-12-04 | TX | other |  | LONE STAR GAS CO | ON DECEMBER 4, 1984 THE ABILENE UNIT OF WEST TEXAS UTILITY COMPANY WAS DRILLINGA HOLE TO INSTALL A NEW LIGHT POLE. THE HOLE WAS BEING DRILLED BY A GASOLINE DRIVEN HYDRAULIC AUGER MOUNTED ON TOP OF LONE STAR GAS COMPANY'S 6" MILLWRAP STEELGAS MAIN. WHEN GA | 2100 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
168 | 1984-11-28 | OH | other |  | COLUMBIA GAS OF OHIO INC | RECEIVED CALL TROUGH DISPATCHER AT 5:29 AM. RESPONED WITHIN 10 MINUTES. EXPLOSION AND WORKING FIRE. DURING INVESTIGATION, DISCOVERED CRACKED ELBOW LOCATED IN CRAWL SPACE ON SERVICE INLET BEFORE METER. CAUSE UNDER INVESTIGATION TO DETERMINECAUSE OF CRACK. | 80000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
169 | 1984-11-12 | MT | maintenance |  | BELLE CREEK GAS ASSOCIATION | TWO STEEL PIPES WERE JOINED IMPROPERLY WITH PLASTIC PIPE USING "RADIATOR HOSE" CLAMPS. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
170 | 1984-10-23 | VA | other |  | COMMONWEALTH GAS DIST. CORP. | A WELDER FROM A LOCAL WELDING COMPANY HAD ENTERED A STEAM MANHOLE TO REPAIR A STEAM LINE. AS HE STRUCK AN ARC TO PROCEDE TO WELD, THERE WAS A FLASH IGNITION INTHE MANHOLE. NEITHER THE WELDER NOR THE EMPLOYEES OF VIRGINIA STATE UNIVERSITY HAD TESTED THE AT | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
171 | 1984-10-26 | OH | maintenance |  | HAMILTON GAS DEPT, CITY OF | NOTIFED BY HAMILTON FIRE DEPT THAT THEY WERE RESPONDING TO A CALL OF AN EXPLOSION AND FIRE. FROM THE AMOUNT OF GAS BLOWING OUT AT EDGE OF BLACKTOP ROAD, WE SUSPECTED A BROKEN MEDIUM PRESURE 8" C.I. GAS MAIN. VALVES WERE CLOSED SHUTTING OFFGAS IN THIS SECT | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
172 | 1984-11-23 | TX | other | DUPONT | ENTEX INC | CABLE CONTRACTOR HIT SERVICE LINE WITH TRENCHER. GAS IGNITED, DESTROYING TRENCHE | 3000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
173 | 1984-11-01 | KS | other |  | UNION GAS SYSTEM INC | SUSPECTED HOUSE WAS BLOWN APART BY AN EXPLOSIVE DEVICE. | 200000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
174 | 1984-11-08 | MN | other | PLEXCO | MINNEGASCO INC |  | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
175 | 1984-11-18 | AR | other | MCWANE | ARKANSAS LOUISIANA GAS CO (ARKLA GAS CO) | CAST IRON MAIN BROKE DUE TO SOIL STRESS. GAS MIGRATED INTO HOUSE RESULTING IN EXPLOSION AND FIRE. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
176 | 1984-10-30 | WI | other |  | WISCONSIN SOUTHERN GAS CO INC | 1.25" STEEL PIPE WAS HIT AND BENT BY A BACKHOE WHILE DIGGING FOR 2" MAIN. RESIDENTS OF HOUSE COMPLAINED OF GAS ODOR IN THE HOUSE THAT THE 1.25" PIPE WAS ATTACHED TO. RESIDENTS WERE TOLD TO LEAVE THE HOUSE UNTIL THE LEAK COULD BE FOUND. LEAK WAS FOUND OUTS | 60000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
177 | 1984-07-08 | KS | other |  | KANSAS POWER & LIGHT CO | PART 2 EXPLOSION OCCURED IN THE WARM AIR CHAMBER OF THE FURNACE AND ATTACHED DUCTWORK. THERE WAS NO EVIDENCE OF AN EXPLOSION IN THE COMBUSTION CHAMBER OF TH FIRST FLOOR. THE ONLY FIRE IN THE BASEMENT WAS AN UPHOLSTERED CHAIR NEXT TO THE DAMAGED COLD AIR | 20000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
178 | 1984-05-26 | KS | other | FISHER | KANSAS POWER & LIGHT CO | HAYSWATHER HIT SERVICE REGULATOR; BFOKE IT OFF, ALLOWING 30 PSI INTO HOUSE. PILOT LIGHT STARTED FIRE. | 30000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
179 | 1984-10-04 | KS | other |  | SEVERY GAS COMPANY, INC. | FARM BUSH HOG HIT LINE. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
180 | 1984-11-06 | TX | other |  | LONE STAR GAS CO | PART D: A SHORT 1.25" BOLTLESS COUPLING WAS PULLED ALMOST OUT OF THE 1.24" STEEL PIPE AT THE MAIN TIE-IN. | 20000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
181 | 1984-12-10 | LA | other | CERTAIN TEED | BAKER UTILITY SYSTEM | LEAK CAUSED FROM PIPE DOPE ON PVC LINE. PIPE DOPE WAS PUT ON METAL FITTINGS FORPROTECTION AND SOME WAS ON PIPE NEAR FITTINGS WHICH SOFENED MATERIAL. | 15000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
182 | 1984-12-06 | TX | other |  | LONE STAR GAS CO | SERVICE TECHNICIAN TURNED OFF APPLIANCES IN HOUSE, SET METER, MADE SLOW FIRE TEST, AND SET PRESSURE ON REGULATOR. HE MADE METER TEST ON YARD LINE AND HOUSE PIPING. THIS TEST SHOWED NO LEAKS. SERVICE TECHNICIAN WENT IN HOUSE TO LIGHT APPLIANCES AND HAD NO | 30000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
183 | 1984-12-15 | KS | other |  | ARKANSAS LOUISIANA GAS CO (ARKLA GAS CO) | CONTRACTOR REMOVED SOIL FROM AROUND 1.25" SERVICE LINE RUNNING ADJACENT TO HOUSE. WHEN THE SOIL WAS REPLACED, THE WEIGHT OF THE SOIL ON THE PIPE CAUSED THE PIPE TO CRACK IN THE THREADS OF THE COLLAR. LEAKING GAS THEN LEAKED INTO THE HOUSE THRU CRACKS IN T | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
184 | 1984-12-05 | TX | other | NIPAK | LONE STAR GAS CO | LINE HIT BY HEAVY EQUIPMENT. | 2149 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
185 | 1984-12-16 | IA | other | AMERICAN | CEDAR FALLS MUNICIPAL UTILITIES | WHILE A GAS LEAK WAS BEING REPAIRED ON A 5 LB. LINE AT 13TH & WATERLOO ROAD WITH A FULL CIRCLE CLAMP, IGNITION OF THE GAS OCCURED BURNING FOUR EMPLOYEES. THE SOURCE OF THE IGNITION HAS NOT BEEN POSITIVELY IDENTIFIED. ONE EMPLOYEE WAS TREATED AT A LOCAL H | 30000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
186 | 1984-12-31 | NJ | other |  | PUBLIC SERVICE ELECTRIC & GAS CO | OCCUPANT OF HOUSE AND HELPER EXCAVATING TREE STUMP WITH MACHINE PULLED GAS SERVICE CAUSING IT TO BREAK INSIDE THE BUILDING. | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
187 | 1984-12-17 | TX | other |  | SOUTHERN UNION GAS CO | CONTRACTOR WAS DITCHING TO INSTALL A WATER LINE AND HIT THE 6 INCH GAS MAIN. | 6000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
188 | 1984-12-13 | TX | other |  | SOUTHERN UNION GAS CO | A CONTRACTOR HIT A 1 1/4 INCH SERVICE LINE WITH A ROCK SAW AND CAUSED EVACUATION OF FRANKLIN SAVINGS. | 500 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
189 | 1984-12-31 | TX | other |  | ENERGAS CO | THIS INCIDENT WAS CAUSED BY A CAR STRIKING A DISTRICT REGULATOR SETTING THAT ISLOCATED APPROXIMATELY 15 FEET BEHIND THE CURB NEAR 10TH AND LYNN STREETS. AFTERTHE CAR HIT A FIRE HYDRANT AND THE REGULATOR SETTING, THREE OCCUPANTS ABANDONEDTHE CAR AND FLED F | 8300 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
190 | 1984-12-15 | GA | other |  | ATLANTA GAS LIGHT CO | PART 3: I-BEAM GUARDRAIL SUPPORT WAS DRIVEN INTO MAIN BY PILEDRIVER. TRAINS STOPPED AND TRAFFIC REROUTED AS A PRECAUTIONARY MEASURE UNTIL AREA MADE SAFE.PART C: WHEN COMPANY WAS NOTIFIED BY THIRD PARTY, HE WAS MISTAKENLY NOTIFIED THAT IT WAS OK TO PROCEED | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
191 | 1984-12-29 | TX | other |  | ENTEX INC | CITY CREW BROKE SERVICE LINE WHILE DIGGING TO LOCATE A WATER LEAK. TRAFFIC WAS REROUTED. | 550 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
192 | 1984-12-17 | TX | other |  | LONE STAR GAS CO | DRIVER BACKED HER CAR OVER GAS METER. | 4000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
193 | 1984-12-15 | MT | other |  | MONTANA - DAKOTA UTILITIES CO | PART B: CITY HAD CONTRACTOR INSTALL NEW SEWER AND WATER LINES IN THIS IMMEDIATEAREA DURING THE FALL OF 1984. SOMEONE HIT 2" NATURAL GAS MAIN AND DID NOT NOTIFY UTILITY COMPANY. WHEN FROST CONDITIONS WENT DOWN, IT CAUSED A CIRCUMFERENTIAL BREAK IN THE MAIN | 17400 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
194 | 1984-12-06 | TX | other |  | ENERGAS CO |  | 1000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
195 | 1984-12-29 | RI | other |  | SOUTH COUNTY GAS CO. | PART 2: SERVICE PIPE CRACKED. AFTER EXPLOSION 1 | 30000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
196 | 1984-12-26 | CT | other |  | CONNECTICUT LIGHT & POWER CO | AT 1419, WE RECEIVED A CALL FROM THE NAUGATUCK FIRE DEPARTMENT THAT AN EXPLOSION OCCURED AT 18 BRIDGE ST (APT. #1M), UNION CITY, CONN. A CUSTOMER SERVICEMAN WAS DISPATCHED TO THE SCENE AND ARRIVED AT 1430. HE WENT TO THE BASEMANT ADJACENT TO THE AFFECTED | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
197 | 1984-12-29 | NY | maintenance |  | BROOKLYN UNION GAS CO | THE HOMEOWNER TO 122 PENN AVENUE WAS MAKING A REPAIR TO HIS SEWER TRAP PLUG IN THE BASEMENT AND LIT A MATCH NEAR THE SEWER TRAP CEMENT WALL WHICH IGNITED LEAKING GAS THAT HAD ACCUMULATED UNDER THE FLOOR SPACE. FLAME HEIGHT AT THE SEWER TRAP WAS 8 INCHES, | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
198 | 1985-01-24 | NY | other |  | COLUMBIA GAS OF NEW YORK INC | A 2" STEEL MAIN OPERATING AT 13.5 PSIG AND BURIED 32" DEEP UNDER THE PAVED STREET FAILED AT A SCREW COLLAR. THE CAUSE IS UNDER INVESTIGATION AND RESULTS HAVE NOT BEEN DETERMINED CONCLUSIVELY. APPARENTLY THE ESCAPING GAS MIGRATED INTO THE STRUCTURE AT 10 N | 75000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
199 | 1984-12-27 | TX | other |  | LONE STAR GAS CO | OUTSIDE PARTY CUT 3" MAIN WITH BAHHOE WHILE INSTALLING COMPUTER CABLE. | 1000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
200 | 1985-01-22 | TX | other |  | LONE STAR GAS CO | CONSTRUCTION COMPANY EMPLOYEE RAN OVER SERVICE RISER WITH A 1979, MODEL 931 CATERPILLAR TRACTOR. GAS IGNITED FROM TRACTOR FLASH BURNING OPERATION. | 200 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
201 | 1985-01-11 | TX | other |  | LONE STAR GAS CO | DRIVER WENT TO SLEEP, LOST CONTROL OF VEHICLE RAN OVER METER INSTALLIATION. | 3000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
202 | 1985-01-22 | TX | other | DRESSER IND. | LONE STAR GAS CO | LEAK ON OUR SERVICE LINE. | 5000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
203 | 1985-01-15 | TX | maintenance |  | LONE STAR GAS CO | LEAKING GAS IGNITED IN CULVERT BY TWO YOUNG MEN. THE YOUNG MEN RECEIVED FIRST AND SECOND DEGREE BURNS ON THEIR FACES AND HAND. | 900 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
204 | 1985-01-03 | UT | other | WHEELING CO. | MOUNTAIN FUEL SUPPLY CO | AN OUTSIDE PARTY UNDER THE INFLUENCE OF ALCOHAL INTENTIONALLY RAMMED HIS AUTOMOBILE INTO THE SIDE OF A BUILDING WHICH HOUSED THE WEST JORDAN CITY POLICE AND FIRE DEPARTMENTS. OUR METER SET ASSEMBLY WAS LOCATED AT THE POINT OF IMPACT AND WAS UNDER THE VEHI | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
205 | 1985-01-24 | TX | other |  | SOUTHERN UNION GAS CO | A CONTRACTOR WAS GRADING AN ENTRANCE TO LOOP 360 WHEN HE RIPPED A 12" MAIN. | 7800 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
206 | 1985-01-08 | TX | other |  | SOUTHERN UNION GAS CO | A 2" DISTRIBUTION MAIN IN THE ALLEY BEHIND 3000 HARRISON IN EL PASO, TEXAS WASSEPARATED AT A THREADED CONNECTION BETWEEN A 2" FLATHEAD COCK AND 2" GRADE A PIPE. BOTH THE FEMALE THREADS IN THE IRON VALVE FAILED. IT IS NOT KNOWN WHAT THE CAUSE OF THIS FAILU | 500000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
207 | 1985-01-16 | TX | technical failure |  | SOUTHERN UNION GAS CO | A 6" C.I. MAIN CRACKED IN A STREET, NECESSITATING BLOCKING THE ROADWAY AND REROUTING TRAFFIC. | 400 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
208 | 1985-01-08 | TX | other |  | SOUTHERN UNION GAS CO | A SOUTHERN UNION GAS OPERATOR WAS REQUESTED TO PROVIDE LINE LOCATION ON N. LAMAR, 2000 FEET SOUTH OF THE ACCIDENT SITE. THE OPERATOR IS NOT SURE THAT THE PARTYRESPONSIBLE FOR THIS DAMAGE WAS THE SAME PARTY THAT REQUESTED THE AFORMENTIONED LOCATIONS.PART 3 | 6000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
209 | 1985-02-03 | TX | other |  | SOUTHERN UNION GAS CO | A 2 INCH CAST IRON GAS MAIN CRACKED UNDER PRESSURE OF A 4" SANITARY SEWER SERVICE WHICH HAD SETTLED ON TOP OF IT. | 600 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
210 | 1985-01-19 | AZ | other |  | SOUTHERN UNION GAS CO | A PICKUP HIT THE METER SET AT A SERVICE STATION. THE DAMAGE ALLOWED LINE PRESSURE TO ENTER THE SERVICE STATION. HEATERS IN THE BUILDING IGNITED THE GAS CAUSINGAN EXPLOSION WHICH DAMAGED A ROLL-DOWN DOOR. | 1800 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
211 | 1985-01-28 | TX | ACCIDENTALLY CAUSED BY OPERATOR | DUPONT | ENTEX INC | CONTRACTOR WAS PURGING NEW STEEL MAIN TROUGH STEEL-TO-PLASTIC TRANSTION FITTING. GAS WAS IGNITED BY UNKNOWN SOURCE. MAN IN BELLHOLE RECEIVED BURNS TO FACE, HANDS, AND STOMACH, REQUIRING HOSPITALIZATION. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
212 | 1985-02-02 | TX | other |  | ENTEX INC | PART D: GAS MAIN HAD A CIRCUMFERENTIAL CRACK HALF AROUD. PIPE APPEARED TO HAVE BEEN DAMAGED BY EXCAVATING EQUIPMENT SEVERAL YEARS AGO. TRAFFIC WAS REROUTED ANDRESIDENTS IN THE VICINITY WERE EVACUATED. | 500 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
213 | 1985-01-22 | TX | other | NORDSTROM | ENTEX INC | GROUND SHIFTING CAUSED 6" VALVE TO CRACK IN HOUSING. TRAFFIC WAS REROUTED. | 500 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
214 | 1985-01-09 | TX | other |  | ENTEX INC | PART D: GAS FROM AN UNDETERMINED SOURCE EXPLODED AND BURNED THIS HOUSE. INVESTIGATION REVEALED A LEAK ON A FITTING AT THE WALL HEATER WHICH WAS NEAR THE POINT OF EXPLOSION. OUR CREW ALSO FOUND AND REPAIRED A LEAK ON THE GAS MAIN. MAIN BROKE AT A WELD. DUE | 5000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
215 | 1985-01-29 | TX | other |  | ENTEX INC | TEXAS NEW MEXICO POWER COMPANY DRILLED HOLE IN GAS MAIN WHILE SETTING NEW POWERPOLE. TAFFIC WAS REROUTED. | 540 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
216 | 1985-01-08 | TX | other | DUPONT | ENTEX INC | MAIN BROKEN BY CONTRACTOR. TRAFFIC WAS REROUTED. | 2000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
217 | 1985-01-11 | TX | other | DUPONT | ENTEX INC | CONTRACTOR CUT GAS LINE WITH TRENCHER - GAS IGNITED. TRENCHER DESTROYED. | 5000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
218 | 1985-01-25 | TX | other |  | ENERGAS CO | A CESSPOOL HAD BEEN DUG ADJACENT TO PIPELINE AT SOME TIME IN THE PAST. THE EXCAVATOR HAD HIT THE PIPELINE MAKING A GOUGE ON ONE SIDE. THIS WEAKENED PIPE EVENTUALLY FAILED. THE LEAKING GAS CAUGHT FIRE FROM AN UNKNOWN IGNITION SOURCE AND BURNED THE HOUSE. T | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
219 | 1985-02-22 | PA | other | DUPONT | NATIONAL FUEL GAS DISTRIBUTION CORPORATION | PART 3: CONSTRICTION AND EXPANSION OF PLASTIC PIPE NEAR A RAILROAD CASING CAUSED THE PIPE TO PULL FROM A DRESSER 700. LEAKING GAS THEN MIGRATED APPROXIMATELY 150' TO INCIDENT LOCATION. NATIONAL FUEL UTILIZED THE TECHNOLOGY AND MATERIAL AT THAT TIME APPROX | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
220 | 1985-01-23 | CA | other | DUPONT | PACIFIC GAS & ELECTRIC CO | DRILLING RIG HIT 2" GAS MAIN ALLOWING GAS TO ESCAPE TO ATMOSPHERE. THE BLOWING GAS IGNITED FROM AN UNKNOWN SOURCE. | 103000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
221 | 1985-02-11 | VA | ACCIDENTALLY CAUSED BY OPERATOR | DUPONT | WASHINGTON GAS LIGHT CO | A WGLCO CREW TESTING FOR A GAS LEAK IN FRONT OF 9458 ABINGDON COURT DROVE A TEST PIN THROUGH A 2" PLASTIC HIGH PRESSURE TRUCKLINE SERVICE. THE EARTH WAS FROZEN, AND IN THE PROCESS OF EXCAVATING TO REPAIR THE LEAK, GAS MIGRATED TO THE BUILDING WALL OF HOUS | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
222 | 1985-02-09 | OH | other |  | CINCINNATI GAS & ELECTRIC CO | A 3/4" I.P.S. PLASTIC SERVICE HAD PULLED OUT OF A 3/4" B.I. COMPRESSION COUPLING AT THE BASE OF THE 3/4" COPPER METER RISER. THE SOURCE OF IGNITION HAS NOT BEEN POSITIVELY IDENTIFIED. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
223 | 1985-02-13 | WY | other |  | NORTHERN UTILITIES INC | THE ATTACHED REPORT COVERS AN INCIDENT THAT OCCURED ON A 1-1/4" DISTRIBUTION MAIN IN EVANSVILLE, WYOMING ON FEBRUARY 13, 1985. THERE WERE NO INJURIES OR FATALITIES AS A RESULT OF THE LEAK. THE INCIDENT WAS DUE TO AN UNKNOWN THIRD PARTY STRIKING OUR 1-1/4" | 40000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
224 | 1985-01-11 | CO | other |  | PUBLIC SERVICE CO OF COLORADO | CONTRACTOR WAS EXCAVATING TO REPAIR WATER LINE AND ATTEMPING TO THAW DITCH AT THE SAME TIME. HE HIT THE 1.25" PE LINE, BROKE IT AND THE FIRE IN THE DITCH IGNITED THE GAS. THE GAS FIRE WAS EXTINGUISHED BY DRY CHEMICAL EXTINGUISHERS WITH THEFRISCO FIRE DEPA | 933 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
225 | 1985-02-10 | MN | other | PERFEX | MINNEGASCO INC | PART B: METAL COMPRESSOR FITTING FAILED TO HOLD PLASTIC (CAB) PIPE UNDER STRESS. REPAIR CONSISTED OF CUTTING AND ABANDONING SERVICE PIPE AT MAIN. | 125000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
226 | 1985-02-03 | NM | other |  | GAS CO OF NEW MEXICO | EXPOSION AND FIRE DAMAGE TO TWO COMMERCIAL BUILDINGS BY MIGRATING NATURAL GAS LEAKING FROM A DAMAGED 3/4" SERVICE LINE. SERVICE LINE FOUND TO HAVE CIRCUMFERENCIAL CRACK APPROXIMATELY 1.5" LONG AT POINT IN PIPE WHERE OTHER DAMAGE EXISTS. DAMAGE ALLEGEDLY C | 300000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
227 | 1985-02-18 | MA | other |  | BAY STATE GAS CO | PART 3: SEE ATTACHED *** THERE IS NO ATTACHED *** | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
228 | 1985-02-01 | NJ | other | INNERTITE | PUBLIC SERVICE ELECTRIC & GAS CO | CIRCUMFERENTIAL BREAK ON A 8" DIAMETER CAST IRON MAIN.PART 3: LEAKING GAS FROM A BROKEN C.I. MAIN APARENTLY ACCUMULTED IN THE BUILDING & WAS IGNITED BY AN UNKNOWN SOURCE. | 85000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
229 | 1985-02-01 | ID | other |  | INTERMOUNTAIN GAS CO | FROST IN THE GROUD, CAUSED BY SUBZERO TEMPERATURES, HAD PENETRATED 40 TO 50 INCHES DEEP, CAUSING A RUPTURE OF THE GAS LINE. | 89000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
230 | 1985-02-08 | TX | other |  | ENTEX INC | GROUND SHIFTING CAUSED 2" I.P. STEEL MAIN TO BREAK IN WELD. TRAFFIC WAS REROUTE | 500 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
231 | 1985-02-05 | TX | other |  | ENTEX INC | RISER BROKEN ABOVE GROUND BY UNKNOWN PARTY. GAS IGNITED BY UNDETERMINED SOURCE. FIRE DAMAGED ADJACENT FRAME HOUSE. IT APPEARS THAT A VEHICLE COLLIDED WITH OUR METER SET ASSEMBLY. | 5000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
232 | 1985-02-05 | TX | other | NIPAK | LONE STAR GAS CO | APPX. 65 CUSTOMERS OUT OF GAS AFTER FT. WORTH WATER DEPT. BROKE 4" L.P. MAIN AND FILLED IT WITH WATER WHITE REPAIRING WATER LEAK. | 30000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
233 | 1985-02-01 | MT | other |  | MONTANA - DAKOTA UTILITIES CO | OUR CONSTRUCTION CREW ARRIVED AT THE SCENE AT APPROXIMATELY 8:30 A.M. AND COMMENCED DIGGING A BELL-HOLE IN CLARK AVE. AT THE INTERSECTION OF THE SERVICE LINE AND MAIN, IN ORDER TO SHUT THE LINE OFF TO 1533 CLARK AVE. DUE TO THE EXTREME FROST CONDITIONS I | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
234 | 1985-01-28 | TN | other |  | SOUTH FULTON GAS DEPT, CITY OF | 6" CAST IRON MAIN CRACKED AND BROKE IN TWO DUE TO FROST HEAVE CAUSED BY UNUSUALLY COLD WEATHER. OPERATOR THINKS THIS SIGNIFICANT DUE TO THE LOSS OF 250 CUSTOMERS OUT OF A TOTAL OF 900. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
235 | 1985-01-31 | PA | other |  | NATIONAL FUEL GAS DISTRIBUTION CORPORATION | FROST CONDITION CAUSED STONE WALL TO MOVE WHICH THEN PUT LONGITUDINAL STRESS ONTHE SERVICE PULLING IT APART AT THE COMPRESSION COUPLING. | 35000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
236 | 1985-01-21 | IL | other | CLOW | PEOPLES GAS LIGHT & COKE CO | THE 6" CAST IRON LOW PRESSURE MAIN CRACKED. GAS MIGRATED INTO ADJOINTING BUILDING, WAS IGNITED BY AN UNKNOWN SOURCE, AND RESULTED IN MINOR DAMAGE TO THE BUILDING AND INJURIES TO TWO OCCUPANTS. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
237 | 1985-02-08 | OH | other |  | COLUMBIA GAS OF OHIO INC | EXPLOSION OCCURRED AT 523 N. CANTON ST., MALVERN, OH AND HOUSE DESTROYED. TWO PEOPLE TREATED FOR INJURIES AND RELEASED. COMPANY CREW STRIPPED SERVICE LINE FROM MAIN TO PROPERTY LINE. CURB VALVE ABOUT 1 FOOT FROM MAIN. DID NOT EXCAVATE CUSTOMER OWNED S | 65000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
238 | 1985-02-03 | PA | other |  | U G I CORP | A SUBSIDENCE OF UNKNOWN ORIGIN RESULTED IN THE PULLOUT OF A 1-INCH COPPER SERVICE FROM A COMPRESSION COUPLING. THE ESCAPING GAS ULTIMATELY RESULTED IN A LOW GRADE EXPLOSION AND FIRE AT 43 RASPBERRY ST., WHICH SPREAD TO 41 AND EVENTUALLY, 45 RASPBERRY ST. | 200000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
239 | 1985-02-18 | OH | other |  | HAMILTON GAS DEPT, CITY OF | AT 2:10PM ON MONDAY, FEBRUARY 18, 1985, THE GAS DEPARTMENT WAS CALLED TO 444 FAIR AVE. BY THE FIRE DEPARTMENT. THE UTILITY SERVICE REPRESENTATIVE ARRIVED AT THE SCENE ABOUT 2:25PM AND AFTER CHECKING WITH THE FIRE DEPARTMENT PERSONNEL, HE CALLED ME. I AR | 4000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
240 | 1985-02-05 | PA | other |  | EQUITABLE GAS CO | A THREE STORY WOODEN FRAME RESIDENTIAL HOME WAS DESTROYED BY AN EXPLOSION. THESTREET ON WHICH THE HOME IS SITUATED HAD FACILITIES OF TWO NATURAL GAS DISTRIBUTION COMPANIES THAT SERVE THE AREA. AT THE TIME OF THIS REPORT, IT HAS NOT BEEN DETERMINED THE E | 40000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
241 | 1985-02-16 | LA | other | BETHLEHEM | LOUISIANA GAS SERVICE CO | AN AUTOMOBILE RAN INTO A A COMMERICAL BUILDING HOUSING TWO STORES. THE AUTOMOBILE HIT A GAS METER INSTALLATION AT THE SIDE OF THE BUILDING AND KNOCKED A HOLE IN THE WALL. NATURAL GAS AT APPROXIMATELY 70 LBS. PRESSURE BLEW INTO THE BUILDING THROUGH THE H | 500000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
242 | 1985-02-06 | WI | other |  | WISCONSIN SOUTHERN GAS CO INC | AT APPROXIMATELY 10:33 AM A CALL WAS RECEIVED AT THE WISCOSIN SOUTHERN GAS COMPANY DISTRICT OFFICE IN TWIN LAKES FROM THE ABOVE ADDRESS REPORTING A GAS ODOR AND BUBBLING IN THE STREET IN FRONT ON THE 18 UNIT COMPLEX. THE TWIN LAKES OFFICE RELAYED THE MESS | 1000000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
243 | 1985-03-10 | MA | other |  | COMMONWEALTH GAS CO | PART D: ARSON - A FIRE WAS SET WITHIN THE BUILDING USING CONTAINERS OF KEROSENEAND RAGS WHICH WERE STREWN ABOUT THE INCIDENT SITE. AS A RESULT OF THE KEROSENEFIRE, DAMAGE WAS CAUSED TO THE GAS METER. WHEN FIREMAN RE-ENTERED THE BUILDING AND PUT ON ELECTRI | 20000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
244 | 1985-02-06 | MI | other |  | MICHIGAN CONSOLIDATED GAS CO (MICHCON) | THIRD PARTY BROKE 4"C.I. GAS MAIN. THE THEN LEAKING GAS WAS IGNITED FROM A SALAMANDER HEATER NEAR THE EXCAVATION. ONE PERSON HOSPITALIZED WITH BURNS.PART B: THIRD PARTY DAMAGED MAIN WHILE WORKING IN THE EXCAVATED AREA - OPERATOR RECEIVED A CALL 2 WEEKS B | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
245 | 1985-02-21 | TX | other |  | LONE STAR GAS CO | LINE HIT BY HEAVY EQUIPMENT IN TWO PLACES ABOUT 6.5 FEET APART. | 3500 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
246 | 1985-01-04 | KS | other | FISHER | KANSAS POWER & LIGHT CO | VENT TO INDOOR REGULATOR WAS PLUGGED WITH INSECT MATERIAL. THIS DID NOT ALLOW REGULATOR TO OPERATE PROPERLY. THE REGULATOR ALLOWED POUNDS PRESSURE DIRECTLY THROUGH IT INTO THE CUSTOMER'S PIPING. | 5000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
247 | 1985-02-11 | FL | other | EX-TRUBE | SUNNY HILLS UTILITIES | LIGHTNING HIT .5" GAS SERVICE AND IGNITED GAS, BLOWING HOLE IN EX-TRUBING BELOW | 160 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
248 | 1985-01-29 | NY | other |  | CONSOLIDATED EDISON CO OF NEW YORK | TWO COMPANY EMPLOYEES ENTERED THE BASEMENT. ONE EMPLOYEE TURNED ON A LIGHT SWITCH IN A STORAGE ROOM, RESULTING IN GAS IGNITION. BOTH EPLOYEES RECEIVED SECOND DEGREE BURNS AND WERE HOSPITALIZED. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
249 | 1985-03-08 | IA | other |  | IOWA GAS COMPANY | PART D - OTHER : NO APPARENT REASON FOR MAIN BREAK. NO FROST WAS ENCOUNTERED. RECENT LEAK SURVEY CONDUCTED AFTER NEARBY BUILDING CONSTRUCTION, INDICATED NO GASLEAKS. NO UNUSUAL GRAPHITIZATION NOTED.PART 3 : ELECTRICIAN BURNED FROM FLASH FIRE IN ELECTRICAL | 1350 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
250 | 1985-03-01 | RI | other |  | PROVIDENCE GAS CO | 4" CI MAIN BROKE, GAS LEAKED INTO BUILDING, WAS IGNITED WHEN PERSON TURNED ON LIGHT SWITCH, SLIGHT DAMAGE TO BUILDING. | 1000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
251 | 1984-12-19 | TX | other |  | BRITTON AND SON INC. | OERATOR WAS NOT NOTIFED EXCAVATOR WAS WORKING IN AREA. | 325 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
252 | 1985-03-10 | TN | technical failure | PLEXCO | TROY GAS DEPTARTMENT | 1. PLASTIC SERVICE WAS INSTALLED, RATED AT 60# AND WAS SUBJECTED TO 220#. DUE TO EXCESS PRESSURE, PLASTIC SERVICE RUPTURED. INSTALLED JUNE 11, 19842. ERROR IN OPERATING PROCEDURE DUE TO 220# PRESSURE APPLIED TO A 60# SERVICE LINE, ASTM 2513 PE 2306 MANUFA | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
253 | 1985-02-12 | TX | other |  | LONE STAR GAS CO | GAS SERVICE WAS HIT BY A BULLDOZER | 3580 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
254 | 1985-03-09 | TX | other | SPRAGUE | ENTEX INC | METER HIT BY CAR. GAS IGNITED BY UNKNOWN SOURCE. CAR DESTROYED. | 1000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
255 | 1985-02-13 | NJ | other |  | NEW JERSEY NATURAL GAS COMPANY | IN REFURBISHING BUILDING, CONTRACTOR CUT INTO ACTIVE GAS SERVICE WITH WELDING TORCH. | 225 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
256 | 1985-03-11 | TX | other | SPRAGUE 175 | ENTEX INC | PART D : WIND BLEW DOWN DEAD TREE IN CUSTOMER'S YARD. TREE FELL ON METER ASSEMBLY, BREAKING REGULATOR AND ALLOWING SYSTEM PRESSURE TO ENTER HOUSELINE. GAS IGNITED AT RANGE. FIRE DAMAGED KITCHEN. SMOKE DAMAGED THROUGHOUT HOUSE. | 10000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
257 | 1985-03-03 | TX | other | ROCKWELL | ENTEX INC | WIND BLEW DOWN DEAD TREE IN CUSTOMER'S YARD. TREE FELL ON METER ASSEMBLY, BREAKING REGULATOR AND ALLOWING SYSTEM PRESSURE TO ENTER HOUSELINE. GAS IGNITED AT RANGE. FIRE DAMAGED KITCHEN. SMOKE DAMAGE THROUGHOUT HOUSE. | 5000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
258 | 1984-11-17 | LA | maintenance |  | MARINGOUIN GAS SYSTEM |  | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
259 | 1985-02-28 | LA | other |  | ALEXANDRIA MUNICIPAL GAS SYSTEM, CITY OF | AT APPROXIMATELY 11:00 PM ON 2/28/85 THE DRIVER OF A PICKUP TRUCK TRAVELING NORTH ON BROADWAY STREET LOST CONTROL OF THE VEHICLE AND COLLIDED WITH A DISTRICT REGULATOR STATION. WET ROAD CONDITIONS CONTRIBUTED TO THE INCIDENT. THE VEHICLE LEFT THE ROAD AND | 5233 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
260 | 1985-03-07 | IA | other |  | IOWA PUBLIC SERVICE CO |  | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
261 | 1985-03-08 | TX | other | PHILLIPS | BRITTON AND SON INC. |  | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
262 | 1985-03-18 | TX | other |  | LONE STAR GAS CO | PART B - PERMANENT MARKER FOUND COVERED UP AT POINT WHERE LINE WAS CUT. | 1500 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
263 | 1985-03-20 | OK | other |  | UNION GAS SYSTEM INC |  | 25000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
264 | 1985-03-20 | MA | maintenance |  | COMMONWEALTH GAS CO |  | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
265 | 1985-03-09 | MA | other |  | BAY STATE GAS CO | COMPANIES INVESTIGATION FOUND THAT THE VALVE ON THE FURNACE IN THE BASEMENT WASRUSTED AND MALFUNCTIONING BECAUSE OF AT LEAST A FOOT OF WATER IN THE BASEMENT. THE DWELLING WAS UNOCCUPIED AT THE TIME OF THE INCIDENT. | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
266 | 1985-03-29 | GA | other |  | FORT VALLEY UTILITY COMMISSION | ON MARCH 29, 1985 THE GAS CREW WAS ENROUTE TO CULLODEN, GA. TO CHECK OUR TAP SITE AND OUR ODORANT LEVEL. AT APPROXIMATELY 8:20 AM THEY WERE PASSING A RESIDENCEAND NOTICED THE FRONT PORTION OF THE HOUSE WAS ON FIRE. THEY CALLED IN BY RADIOAND REQUESTED FIR | 2000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
267 | 1985-04-06 | OH | other | SPRAGUE | DAYTON POWER & LIGHT CO | PART B - INCIDENT CAUSE BY HOME OWNER INSIDE HOME.PART D - THE HOME OWNER WAS DISCHARGING A FIREARM IN BASEMENT AND ACCIDENTLY SHOT A HOLE INTO THE METER CASE. SOME TIME LATER WHEN OCCUPANT WAS ON FIRST FLOOR HE LITE A CIGARETTE AND HOUSE EXPLODED. TELEPH | 10000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
268 | 1985-03-22 | CO | other |  | PUBLIC SERVICE CO OF COLORADO | PART A - SERVICE HAD BEEN HIT, BENT, AND COATING DAMAGED BY OUTSIDE CONTRACTOR.COMPANY WAS NOT NOTIFIED OF DAMAGE, WHICH EVENTUALLY RESULTED IN A CORROSION LEAPART D - GAS EMERGENCY REPAIR RECEIVED A CALL FROM THE GAS SHOP DISPATCHER OF AFIRE AT 4350 SOUT | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
269 | 1985-03-25 | TX | other |  | ENTEX INC | OUTSIDE PARTY CLEARING PROPERTY AROUND VACANT BUILDING BROKE SERVICE RISER. FIRE DEPARTMENT REROUTED TRAFFIC. | 100 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
270 | 1985-03-12 | OH | other |  | EAST OHIO GAS CO | OWNER OF HOUSE WAS MAKING REPAIRS TO HOUSE LINE IN PREPARATION FOR SALE OF HOUSE. HOUSE LINE APPARENTLY WAS LEAKING RESULTING IN THE EXPLOSION AND FIRE. | 32000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
271 | 1985-03-13 | CA | other |  | PACIFIC GAS & ELECTRIC CO | CUSTOMER HOUSELINE WAS OPENED. GAS ACCUMULATED AND WAS IGNITED.*/! CHANGED INJ FROM 2 TO 0 | 1000000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
272 | 1985-03-11 | CA | maintenance |  | SOUTHERN CALIFORNIA GAS CO | PART 1 - INDICATIONS ARE THAT A ONE INCH NIPPLE AND RELATED CAP CORRODED OUT ATTHREADS WHERE SCREWED INTO A ONE INCH BRASS CROSS. | 70000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
273 | 1985-04-17 | TX | other |  | SOUTHERN UNION GAS CO | A CONTRACTOR WAS PERFORMING A PAVING CUT W/A/ ROCKSAW & HIT A 6" SEC. OF PIPE ON DOWNSTREAM SIDE OF A VALVE CRACKING BODY OF VALVE. | 1200 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
274 | 1985-04-21 | TX | other |  | SOUTHERN UNION GAS CO | A CITY CREW WAS REPAIRING A WATER LEAK. THEAIR DITCH CAVED IN CAUSING A 2 INCH ABS MAIN TO BREAK. | 1300 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
275 | 1985-04-17 | TX | other | TEXTUBE | BRENHAM UTILITIES, CITY OF | PART B - SCENIC ESTATES - A NEW SUBDIVISION. THE UTILITIES WERE COMPLETED IN DEC., 1984. THE STREET CONTRACTOR WAS CUTTING STREET TO GRADE - SOME HOW GOT BEHIND CURB DIGGING OUT SOFT SPOT AND CUT A 4" POLYSTHRNE MANI - GAS LOST 18 MCF - TOTAL COST $242.4 | 242 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
276 | 1985-03-28 | TX | other |  | SOUTHERN UNION GAS CO | PART B - LINES WERE LOCATED IN THE SAME AREA, BUT NOT AT THE INCIDENT LOCATION.PART 3 - A CONTRACTOR USING DITCHING EQUIPMENT HIT A SERVICE LINE. TRAFFIC WAS REROUTED BY LOCAL AUTHORITIES. | 250 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
277 | 1985-04-17 | TX | other |  | SOUTHERN UNION GAS CO | A CONTRACTOR WAS TRENCHING AND HIT A 6" DISTRIBUTION MAIN. MAIN HAD BEEN LOCATED | 1500 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
278 | 1985-04-26 | FL | maintenance |  | ECON-O-GAS INC. | INCIDENT HAPPENED WHILE REPAIRING LEAK FOUND BY LEAK SURVEY. SOURCE OF IGNITIONUNKNOWN. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
279 | 1985-04-15 | LA | other |  | ARKANSAS LOUISIANA GAS CO (ARKLA GAS CO) | PART 3 - AT APPROXIMATELY 9:30 AM AN APRIL 15, 1985, THE RESIDENCE OF MRS. D.H.HICKS (AN ELDERLY LADY) WAS DESTROYED BY AN EXPLOSION BELIEVED TO HAVE BEEN CAUSED BY A LEAK IN THE HOUSE PIPING OR BY IMPROPER USE OF GAS APPLIANCES. MRS. HICKS SUSTAINED CRIT | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
280 | 1985-04-08 | IA | other | KRALOY | PEOPLES NATURAL GAS | PART B - IT APPEARS BREAKAGE WAS CAUSED FROM A COMBINATION OF GROUD SETTLEMENT FROM A WATER LINE DITCH COMPLETED IN 1984 AND FROST MOVEMENT.PART 3 - 1 1/2" & PVC MAIN BROKE IN TWO NEXT TO SERVICE TEE BELIEVED TO BE FROMSTRESS CAUSED BY A COMBINATION OF FR | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
281 | 1985-03-07 | TX | maintenance | INSTALLED BY GULF | WARREN PETROLEUM COMPANY, NEW MEXICO GAS PIPELINE | LINE FAILED PRESSURE TEST AT 630 PSIG | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
282 | 1985-04-19 | TX | other | DRISCO PIPE | LONE STAR GAS CO | 6" POLY MAIN CUT INTO BY BACKHOE. | 2832 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
283 | 1985-04-21 | TX | other |  | ENERGAS CO | PART 2 - CUSTOMER LINE - SEE ATTACHED NARRATIVE | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
284 | 1985-04-28 | TX | other |  | ENERGAS CO | A FIRE OF UNKNOWN ORIGIN DESTROYED HOUSE. ONE INJURY TO OCCUPANT WHO RECEIVED MINOR BURNS AND SMOKE INHALATION. | 7000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
285 | 1985-04-25 | PA | other |  | COLUMBIA GAS OF PENNSYLVANIA | PART D - DOMESTIC METER/REGULATOR SETTING HIT BY TRACTOR TRAILER TRUCK. TRUCK WAS LAYING ON TOP OF CURB BOX. UNABLE TO SHUT OFF UNTIL TRUCK WAS REMOVER. DRIVERKILLED IN ACCIDENT. HOUSE WAS TOTALLY DESTORYED BY FIRE. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
286 | 1985-04-05 | CA | other |  | PACIFIC GAS & ELECTRIC CO | CONTRACTOR CAUGHT THE GAS METER AND RISER WITH HIS TRACTOR AND RIPPED IT IFF JUST BELOW THE STOP COCK. | 69200 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
287 | 1985-04-02 | AL | other |  | ALABAMA GAS CORP | PART D - THE FIRE INSPECTOR STATED THE FIRE STARTED IN THE BASEMENT, ON THE FLOOR ABOVE A GAS METER. THE SWIVEL CAPS HAD BEEN LOOSENED WITHIN ONE AND ONE-HALF TURNS OF BEING OFF THE METER SPUDS. THE ESCAPING GAS WAS IGNITED BY SOME UNKNOWNSOURCE. THE FIRE | 1000000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
288 | 1985-04-30 | IL | other |  | NORTHERN ILLINOIS GAS CO | WHILE GRADING FOR A ROAD IMPROVMENT, A 4" GAS MAIN WAS HIT BY THE ROAD GRADING MACHINE. THE ESCAPING GAS WAS IGNITED AND THE GRADER WAS COMPLETELY BURNED. THE OPERATOR SUSTAINED BURNS ON HIS UPPER BODY. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
289 | 1985-02-14 | AL | maintenance |  | LINDEN UTILITIES BOARD, CITY OF | THE CITY GAS WAS INSTALLED IN 1943. THE 4" C.I. WAS THE FIRST GAS MAIN. IT WAS PITTED FROM OUTSIDE. THIS GAS MAIN NEEDED TO BE RENEWED. THE UTILITIES BOARD IS IN THE PROCESS OF A NEW 4" 3408 SDR. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
290 | 1985-05-03 | WY | other |  | MOUNTAIN FUEL SUPPLY CO | A DIRT ROAD WAS GOING TO BE CONSTRUCTED CROSSING THE GAS PIPELINE. A PRE-CONSTRUCTION MEETING WAS HELD AND IT WAS DETERMINED THERE WOULD BE NO PROBLEM CAUSED BY THE PIPELINE. THE PIPELINE WAS MARKED AND THE NEXT MORNING A HEAVY EQUIPMENT OPERATOR BEGAN EX | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
291 | 1985-05-13 | GA | ACCIDENTALLY CAUSED BY OPERATOR | USS | ATLANTA GAS LIGHT CO | WHILE WELDING FITTING ON MAIN, CONTRACTORS WELDER BURNED THROUGH MAIN CAUSING LEAK THAT IGNITED. A CONTRACTORS EMPLOYEE RECEIVED BURNS WHILE ATTEMPING TO STOP LEAK. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
292 | 1985-05-04 | NM | other |  | GAS CO OF NEW MEXICO | PART D - THE GAS SERVICE FOR 1400 EUBANK N.E. HAD APPARENTLY BEEN PULLED AND DAMAGED DURING THE INSTALLATION OF WHAT APPEARS TO BE AN 18" WATER MAIN. | 5000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
293 | 1985-05-10 | AZ | other | CUPPLES | SOUTHERN UNION GAS CO | A COUNTY ROAD CREW PUNCTURED A PVC LINE WHILE DRIVING IN A SIGN. GAS IGNITED WHILE A TAP WAS BEING MADE TO STOPPEL OFF THE LINE. | 2100 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
294 | 1985-04-01 | SC | ACCIDENTALLY CAUSED BY OPERATOR |  | SOUTH CAROLINA ELECTRIC & GAS CO | PART D - WHILE INSERTING AN EXISTING 1 1/4" BARE STEEL SERVICE WITH 5/8" PLASTIC PIPE, THE OPERATOR ON THE JOB LIT A CIGARETTE AND IGNITED THE GAS, BURNING THELEFT SIDE HIS FACE. THE OPERATOR, MR. TERRY KYZER OF FOREMOST PIPELINE, A SUB-CONTRACTOR OF SCE& | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
295 | 1985-05-07 | TX | other | CERTAINTEED | WEST END GAS COMPANY | SAN ANTONIO CITY PUBLIC SERVICE WORKMAN WERE SETTING ELECTRIC POLE. | 1500 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
296 | 1985-04-25 | TX | other | ROCKWELL | ENTEX INC | PART D - REGULATOR DIAPHRAGM COUPLING ASSEMBLY DETACHED FROM DIAPHRAGM. GAS PASSED THROUGH RESULTING HOLE IN DIAPHRAGM AND OUT VENT. GAS APPARENTLY ACCUMULATEDIN GARAGE AND ATTIC. IGNITION FROM UNDETERMINED SOURCE. | 4000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
297 | 1985-05-12 | TX | other |  | ENERGAS CO | BELIEVED TO BE A LEAK INSIDE HOUSE, IGNITED BY CUSTOMER LIGHTING STOVE. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
298 | 1985-05-04 | TX | other | UNIVERSAL | ENTEX INC | CONTRACTOR BROKE SERVICE REGULATOR WITH BULLDOZER. HOUSELINE WAS OVERPRESSURED.RESULTING FIRE AT WATER HEATERS DAMAGED KITCHENS AND ATTIC. | 25000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
299 | 1985-04-27 | FL | other |  | PEOPLES GAS SYSTEM INC |  | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
300 | 1985-05-23 | TX | other |  | ENERGAS CO | GAS ACCUMULATED NEAR A GAS WATER HEATER, AND A SMALL EXPLOSION OCCURED. THE EXPLOSION DAMAGED THE CLOSET, SOME WINDOWS AND STARTED A SMALL FIRE. THE CUSTOMER HAD BEEN REMODELING AND EVIDENTLY BROKE A GAS LINE NEAR THE HOUSE BUT DID NOT NOTIFY ENERGAS COMP | 1000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
301 | 1985-04-01 | NM | technical failure | PHILLIPS | RIO GRANDE NATURAL GAS ASSN | PART 3 - THIS ACCIDENT OCCURED DURING INSTALLATION OF A SECTION OF NEW MAIN. THE LINE WAS BEING BLOWN WITH NATURAL GAS TO CLEAR IT OF DIRT AND DEBRIS PRIOR TO A FINAL TIE-IN AND WAS NOT PROPERLY GROUNDED. THIS RESULTED IN A STATIC DISCHAREWHICH IGNITED TH | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
302 | 1985-05-11 | OH | other |  | COLUMBIA GAS OF OHIO INC | CONTRACTOR WAS EXCAVATING FOR COMMERCIAL DEVELOPMENT AND RUPTURED 6" MEDIUM PRESSURE LINE. ESCAPING GAS IGNITED AND DESTROYED THE EARTH MOVER, OVERHEAD WIRES, TREES, AND SHRUBBERY IN CLOSE PROXIMITY TO THE LINE BREAK. THE CONTRACTOR DID NOT CALL FOR CONSS | 60000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
303 | 1985-05-28 | WI | other | DUPONT | WISCONSIN PUBLIC SERVICE CORPORATION | 2" PLASTIC GAS LINE WAS HIT WHILE CONTRACTOR WAS PLOWING IN TV CABLE. | 40000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
304 | 1985-05-07 | MO | other | DUPONT | SPRINGFIELD UTILTIES, CITY OF | BACKHOE EXCAVATING TO REMOVE OLD GASOLINE TANKS AT ABANDONED SERVICE STATION SITE PUNCTURED ATURAL GAS MAIN RUNNING THROUGH AREA. AT TIME OF TELEPHONIC REPORTING IT WAS ESTIMATED THAT DAMAGES IN EXCESS OF $50,000 MIGHT EXIST. FINAL DAMAGE ESTIMATES ARE: O | 35000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
305 | 1985-04-28 | LA | other |  | TRANS LOUISIANA GAS COMPANY, INCORPORATED | 3RD PARTY RAN OVER OPERATOR'S METER. | 20500 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
306 | 1985-05-06 | NH | technical failure |  | NORTHERN UTILITES INC - NEW HAMPSHIRE DIV | A FRACTURE AT THE WELDED JOINT OF SIX INCH (6") STEEL GAS MAIN AT HIGH STREET, EXETER, NEW HAMPSHIRE RESULTED IN A LEAK REQUIRING THE EVACUATION OF APPROXIMATELY FORTY(40) PEOPLE WITHIN A ONE BLOCK AREA OF THE LEAK AND RE-ROUTING OF TRAFFIC AROUND THE LOC | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
307 | 1985-05-16 | TX | other |  | ENERGAS CO | A LADDER BEING USED BY A SCHOOL WORKMAN FELL STRIKING A GAS LINE IN SIDE THE KITCHEN AREA AT JAMES BOWIE JR. HIGH SCHOOL. THE LADDER BROKE A GAS LINE CAUSING ASMALL FIRE. | 1000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
308 | 1985-04-12 | TX | other |  | ENERGAS CO | PART 2 - APPARENT CAUSE - THIRD PARTYPART 3 - A CITY OF PLAINVIEW CREW WHILE INSTALLING SEWER LINE CUT GAS LINE TO MOBILE HOME PARK. APPROX. 50 CUSTOMERS WERE OUT OF GAS. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
309 | 1985-06-02 | WV | other | DRESSER IND | EQUITABLE GAS CO | DUE TO IMPROPER BACKFILL & COMPACTION IN SANDY TERRAIN BY SEWER CONTRACTOR, JAMES WHITE CONSTRUCTION, THE WEIGHT OF EQUIPMENT & UNSTABLE SOIL CONDITIONS CAUSEDEXCESSIVE PRESSURE ON 1" PLASTIC SERVICE LINE, WHICHCAUSED SERVICE LINE TO PULLFROM 1" COMPRESSI | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
310 | 1985-05-29 | TX | other |  | LONE STAR GAS CO | TWO EMPLOYEES OF HARPER RAMBO CONSTR. (TONZIE CAPLE AND JESUS RIOS) WERE IN LARGE STORM DRAIN. ONE MADE A TORCH AND IT CAUSED A FLASH FIRE. 30% BURNS TO ONE MAN AND 25% TO THE OTHER MAN. | 50 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
311 | 1985-06-01 | TX | other |  | LONE STAR GAS CO | CONTRACTOR JOB CLEAN-UP AND WHILE REMOVING TREE STUMPS AFTER INSTALLING 30" WATER MAIN KNOCKED HOLE IN 8" WP. ST. MAIN. | 2000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
312 | 1985-06-07 | TX | other | NIPAK | LONE STAR GAS CO | INDIVIDUAL OPERATING RENTED BACKHOE TRACTOR CUT 2" IP POLY MAIN. | 1200 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
313 | 1985-07-02 | TX | other |  | LONE STAR GAS CO | LINE HIT BY BACK HOE | 6500 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
314 | 1985-06-07 | NY | other | PHILLIPS | BROOKLYN UNION GAS CO | PART 3 - BUILDING UNDER RENOVATION. CONTRACTOR CUT ACTIVE GAS SERVICE WITH TORCH CAUSING IGNITION. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
315 | 1985-06-13 | TX | other |  | SOUTHERN UNION GAS CO | A CONTRACTOR PUNCTURED AN EXPOSED 12" PIPE WITH A ROCK HAMMER WHILE WORKING ADJACENT TO THE MAIN. | 6300 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
316 | 1985-05-30 | TX | other | NIPAK | LONE STAR GAS CO | PART 3 - PICKUP RAN OVER RISER BREAKING LINE AND IGNITING ESCAPING GAS. | 148 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
317 | 1985-05-24 | TX | other |  | LONE STAR GAS CO | PART D - INDEPENDENT CONTRACTOR CUT 3/4" SERVICE ON 4" STEEL MAIN CAUSING LEAK ON I.P. THINKING HE WOULD SHUT OFF GAS AT REGULATOR STATION, HE BROKE LOCK ON BYPASS OF REGULATOR STATION #2, THUS FEEDING IP INTO LP MAIN, CAUSING 4 MINOR FIRES AND OUTRAGE TO | 757 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
318 | 1985-06-28 | LA | other |  | NEW ORLEANS PUBLIC SERVICE INC | OCCUPANT ALLEGEDLY TURNED ON GAS AT METER WITH OPEN 3/4" LINE IN KITCHEN. | 60000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
319 | 1985-06-13 | WA | other | UNKNOWN | WASHINGTON NATURAL GAS CO | PART D - OUTSIDE METER APPARENTLY STRUCK BY VEHICLE BREAKING SERVICE RISER AT THREADED METER SHUT OFF VALVE. BLOWING GAS ENTERED BUILDING THROUGH FLOOR SLAB/WALL SEAM AND ACCUMULATED. IGNITION SOURCE WAS APPARENTLY AN AIR COMPRESSOR LOCATED INSIDE THE BUI | 150000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
320 | 1985-06-27 | TX | other |  | ENTEX INC | CONTRACTOR DAMAGED MAIN WHILE INSTALLING SEWER LINE , TRAFFIC REROUTED. | 2500 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
321 | 1985-06-22 | TX | other |  | SAN ANTONIO CITY PUBLIC SERVICE BOARD | PART B - AUTOMOBILE WENT OUT OF CONTROL; CRASHED INTO BUILDING, BROKE RISER/METER SET, LEAKING GAS IGNITED/ EXPLODED. | 200000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
322 | 1985-06-13 | TX | other |  | LONE STAR GAS CO | BACKHOE HIT LINE. | 1000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
323 | 1985-06-20 | TX | other |  | SOUTHERN UNION GAS CO | A CONTRACTOR WAS BORING UNDER U.S. HWY 183. HIS BORING BIT HIT A 12" LINE, CAUSEING LEAKAGE. | 2500 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
324 | 1985-06-24 | MI | other | PHILLIPS | CONSUMERS POWER CO | PART B - APPEARS THAT CITY FROZE WATER SERVICE TO MAKE REPAIRS, AND EMPLOYEE WAS THAWING PIPE WITH TORCH WHEN PLASTIC GAS SERVICE WAS DAMAGED. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
325 | 1985-06-13 | LA | other |  | HOUMA MUNICIPAL GAS SYSTEM | LEAKS OF GAS INSIDE RESIDENCE IN ATTIC. ELECTRICAL SHORT SUSPECTED CAUSE OF IGNITION. SEVERAL PLUMBING CODE VIOLATIONS NOTED. | 80000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
326 | 1985-06-27 | MO | other | MUELLER | MISSOURI PUBLIC SERVICE COMPANY | A FLASH FIRE OCCURED IN A SEWER MANHOLE AT 610 WEST DAKE STREET. THE SOURCE FORTHE FLASH FIRE WAS LOCATED AT 812 WEST DAKE STREET NEAR THE BASE OF A TAPED MUELLER TAP TEE OUTLET WHICH IS USED TO CONNECT THE SERVICE, TO THIS LOCATION , TO THE GAS MAIN. THE | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
327 | 1985-07-02 | TX | other | DUPONT | ENTEX INC | CONTRACTOR CUT MAIN WITH A DITCHING MACHINE, GAS IGNITED, DESTROYED MACHINE ANDDAMAGING ADJACENT GARAGE AND INJURING OPERATOR. | 20000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
328 | 1985-07-09 | WA | other |  | WASHINGTON WATER POWER CO | AN EXCAVATING CONTRACTOR ON A SEWER PROJECT FOR THE CITY OF SOPANE ADVISED OUR INSPECTOR DURING A ROUTINE VISIT THAT A GAS SERVICE HAD BEEN HIT AND WAS LEAKING. A CREW WAS ON THE SCENE WITHIN MINUTES AND STOPPED THE FLOW OF GAS AND DETERMINED IT WAS A STU | 150000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
329 | 1985-06-25 | MI | other | PHILLIPS | CONSUMERS POWER CO | EMPLOYEE OF BASEMENT WATERPROOFING CONTRACTOR PLASTIC GAS SERVICE WITH A TORCH AND CAUSED IGNITION. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
330 | 1985-07-03 | AZ | other |  | SOUTHWEST GAS CORP | PART B - DAMAGED LINE IS OWNED BY EL PASO NATURAL GAS CO., SOUTHWEST GAS SUPPLIEPART D - ON JULY 3, 1985, A CONSTRUCTION COMPANY WORKING ON MAGMA COPPER COMPANY PROPERTY BROKE A 2" HIGH PRESSURE TRANSMISSION LINE SERVING THE TOWNSITE OF MAMMOTH, AZ. INTER | 5000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
331 | 1985-07-14 | TX | other |  | ENERGAS CO | THERE WAS A LEAK UNDER THE HOUSE NEAR A FLOOR FURNACE. GAS ACCUMULATED AND WAS IGNITED BY UNKNOWN SOURCE CAUSING AN EXPLOSION. | 5000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
332 | 1985-07-02 | TX | other |  | LONE STAR GAS CO | RIPPER TOOTH ON BULLDOXER PUNCHED HOLE IN 12" MILLWRAPPED MAIN. | 1000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
333 | 1985-06-30 | TX | other |  | LONE STAR GAS CO | CAR HIT METER AND REGULATOR RESULTING IN A FIRE. | 1000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
334 | 1985-07-24 | AR | other |  | MANSFIELD GAS, INCORPORATED | CITY OF MANSFIELD HAD ASKED SEBASTIAN COUTY HIGHWAY DEPT. TO PULL SOME DITCHES IN CITY LIMITS. ACCORDING TO INFORMATION RECEIVED FROM THE CITY, (SEBASTIAN H.W.DEPT. HAD BEEN REQUESTED TO NOTIFY THEM WHEN THEY CAME TO TOWN WITH MOTOR PATROL;) THE CITY HAD | 240 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
335 | 1985-07-31 | KS | other | WAYNE MNF | UNION GAS SYSTEM INC |  | 7000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
336 | 1985-07-29 | TX | other |  | ENERGAS CO | A 1-TON TRUCK DROVE UPON AN IDLE SERVICE. ESCAPING GAS IGNITED, WHEREUPON THE TRUCK WAS BADLY BURNED. | 10000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
337 | 1985-07-21 | TX | other | METRIC | ENTEX INC | VEHICLE STRUCK GAS METER INSTALLATION. GAS IGNITED AND FIRE DESTORYED METER & REGULATOR. | 750 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
338 | 1985-07-16 | TX | other |  | SOUTHERN UNION GAS CO |  | 1600 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
339 | 1985-07-26 | CA | other | DU PONT | SAN DIEGO GAS & ELECTRIC CO | LABORER DIGGING WITH SHOVEL HIT AND CUT 1/2" POLY SERVICE LINE. THE ESCAPING GAS WAS IGNITED, INSTANTANEOUSLY. SUSPECT IGNITION SOURCE SPARK FROM SHOVEL IN ROCKY SOIL. | 200 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
340 | 1985-07-03 | TX | ACCIDENTALLY CAUSED BY OPERATOR |  | LONE STAR GAS CO | BOTH VALVES ON CHECK VALUE BY PASS WERE CLOSED. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
341 | 1985-07-15 | NY | other |  | CONSOLIDATED EDISON CO OF NEW YORK | PART D - EXPLOSION OCCURED ON THE 16TH FLOOR OF WEST 48TH STREET, MANHATTAN. INCIDENT WAS CAUSED WHEN THE OWNER OF AN ADJACENT JEWELRY FIRM TURNED ON 2 GAS VALVES, ONE OF WHICH LEAD TO AN OPEN ENDED 3/4 INCH PIPE. A PLUMBER HAD DISCONNECTED THE PIPING IN | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
342 | 1985-08-01 | NY | maintenance |  | CONSOLIDATED EDISON CO OF NEW YORK | EXPLOSION OCCURED IN ELECTRIC MANHOLE. TO DATE 120 FEET OF 24 INCH STEEL MAIN HAS BEEN REPLACED AND 550 FEET OF 12 INCH STEEL MAIN AND 120 FEET OF 20 INCH CASTIRON HAVE BEEN ABANDONED. ADDITIONAL INDICATIONS OF GAS ARE PRESENT IN THE VICINITY AND THE INVE | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
343 | 1985-08-06 | PA | other |  | PHILADELPHIA GAS WORKS | PART B - CONTRACTOR EXCAVATING FOR THE INSTALLATION OF SEWER INLET FAILED TO CALL FOR PIPE LOCATIONS AND DROVE POINT OF HYDRA-HAMMER INTO 12" CAST IRON GAS MAIN | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
344 | 1985-08-15 | TN | other |  | HUMPHREYS COUNTY UTILITY DISTRICT | LIGHTNING STRIKE HITTING REGULATOR DAMAGING IT AND SETTING IT ON FIRE DESTROYEDREGULATOR AND TWO METERS | 10000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
345 | 1985-08-08 | FL | technical failure |  | BOYE'S GAS, INC. | PART C - OUTSIDE COMPANY INSTALLED LINE COUPLING - WAS NOT PROPERLY TIGHTENED +IT SEPARATED. | 2000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
346 | 1985-08-04 | TX | other |  | ENERGAS CO | CUSTOMER (HI-PLAINS PARTNERS, A DAIRY) HAD BEEN REMODELING HOUSE FOR PAST TWO WEEKS. GAS METER HAD NOT BEEN TURNED OFF. GAS CONSUMPTION PREVIOUS MONTH = 0. | 20000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
347 | 1985-07-23 | CT | other |  | SOUTHERN CONNECTICUT GAS CO. | ON JULY 23, 1985, AT 11:05 AM THE MAINS AND SERVICES DEPARMENT OF THE SOUTHERN CONNECICUT GAS CO. (NEW HAVEN DIV) RECEIVED A TELEPHONE NOTIFICATIN FROM A REPRESENTATIVE OF SPINELLO CONSTRUCTION THAT THEY HAD ACCIDENTLY BROKEN A 4" CAST IRON LOW PRESSURE G | 210 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
348 | 1985-07-29 | TX | other |  | ENTEX INC | CONTRACTOR BROKE 2" MAIN WITH DITCHING MACHINE CAUSING LOSS OF SERVICE TO 103 CUSTOMERS. | 1000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
349 | 1985-08-09 | NE | other |  | KANSAS-NEBRASKA NAT GAS | THE ATTACHED REPORT COVERS AN INCIDENT WHICH WAS DETECTED ON THE COMPANY'S DISTRIBUTION SYSTEM IN THE VILLAGE OF WESTERN, NE, ON AUGUST 15, 1985. THERE WAS NO DEATH, INJURY, FIRE, EXPLOSION, OR PROPERTY DAMAGE OTHER THAN TO K N'S FACILITIES. SERVICE WAS I | 5400 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
350 | 1985-06-18 | KY | other |  | LOUISVILLE GAS AND ELECTRIC COMPANY | GAS ACCUMULATED IN MANHOLE AFTER MIGRATING FROM C.I. JOINTS. CITY OF LOUISVILLESTRIPPING CREW IGNITED GAS WHEN THEY PASSED OVER MANHOLE WITH STRIPPING MACHINE. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
351 | 1985-06-26 | KY | maintenance |  | LOUISVILLE GAS AND ELECTRIC COMPANY | METROPOLITAN SEWER DIST. CREW DETECTED GAS IN A MANHOLE. THEY CALLED THE POLICE& FIRE DEPT. WHO STOPPED TRAFFIC AND BARRICADED BROADWAY FROM 22ND TO 27TH ST. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
352 | 1985-08-24 | KY | other | PHILLIPS | CLAY NATURAL GAS SYSTEM, CITY OF | AT APPROXIMATELY 2:30AM ON SATURDAY MORNING, AUGUST 24TH, A FIRE OCCURRED AT WHEATCROFT, KY. AROUND ONE OF OUR GAS SERVICE METERS. THE WHEATCROFT VOLUNTEER FIRE DEPARTMENT REPORTED TO THE CLAY POLICE DEPRTMENT THAT THEY HAD PUT OUT THE FIRE AND IT HAD REI | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
353 | 1985-06-11 | AZ | ACCIDENTALLY CAUSED BY OPERATOR | NIPAK | BLACK MOUNTAIN GAS CO. | A BLACK MOUNTAIN GAS CO. CREW WAS PREPARING A BELL HOLE FOR A TIE IN ON A 2" POLYETHYLENE GAS MAIN AT 4:35PM JUNE 11TH, 1985 AN AQUA AVENUE IN PAGE, AZ. THE 2"MAIN WAS INADVERTANTLY RUPTURED BY THE COMPANYS OPERATOR DURING THE EXCAVATION.BOB SLASER, A COM | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
354 | 1985-08-10 | WI | other |  | WISCONSIN GAS CO | AT 11:15PM ON AUGUST 9, 1985, LIGHTNING APPARENTLY STTUCK THE PROPERTY AT 629 MAPLE AVENUE IN WILD ROSE, WI. THE LIGHTNING GROUNDED ITSELF ON THE STEEL GAS SERVICE LINE LEADING TO THIS PROPERTY, BURNING A HOLE IN THE UNDERGROUND 3/4" STEELSERVICE PIPE. AN | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
355 | 1985-08-19 | GA | other | DUPONT | ATLANTA GAS LIGHT CO | CONTRACTOR'S BACKHOE SEVERED GAS MAIN - ESCAPING GAS IGNITED BY UNKNOWN SOURCE. | 20000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
356 | 1985-08-09 | GA | other |  | ATLANTA GAS LIGHT CO | THIRD PARTY CONTRACTOR ATTEMPTED TO REPAIR SERVICE LINE HE DAMAGED WITHOUT CALLING GAS COMPANY. ESCAPING GAS IGNITED INJURING CONTRACTOR'S EMPLOYEE. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
357 | 1985-08-09 | PA | other |  | U G I CORP | CONTINENTAL BORING CO., A CONTRACTOR FOR THE LANCASTER AREA SEWER AUTHORITY, WAS TUNNELING UNDER AND PERPENDICULAR TO EAST KING STREET TO INSTALL A 54 INCH CASING FOR A 36 INCH SEWER MAIN. THE TOP OF THE CASING WAS 8FEET BELOW STREET LEVELAT THIS POINT. D | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
358 | 1985-02-20 | KY | other | INTERLAKE STEEL | LOUISVILLE GAS AND ELECTRIC COMPANY | ON 2/19/85 FISHEL CONSTRUCTION COMPANY BROKE A 2" SERVICE AT 709 S. 3RD STREET REAR (INCIDENT REPORT FILED PREVIOUSLY). ON 2/20/85 I CALLED FISHEL CONSTRUCTIONCOMPANY CONCERNING THE WORK THEY WERE DOING (LAYING A TV CABLE) ON THIRD STREETSOUTH OF BROADWAY | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
359 | 1985-02-19 | KY | other | US STEEL | LOUISVILLE GAS AND ELECTRIC COMPANY | ON 2/19/85 FISHEL CONSTRUCTION COMPANY WAS DIGGING A TRENCH WITH A TRENCHING MACHINE IN THE REAR OF 708 SOUTH THIRD STREET IN ORDER TO INSTALL A TV CABLE. AS THE TRENCHING MACHINE CROSSED THE 2" H.P. SERVICE FOR THIS ADDRESS IT STRUCK AND SEVERED THE 2" G | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
360 | 1985-08-06 | MI | other | YOUGSTOWN | LAKE SUPERIOR DIST. POWER CO. | BORING, INC., A SUBCONTRACTOR FOR CENTENNIAL CONSTRUCTION COMPANY WAS BORING ONLAKE ROAD IN IRONWOOD TOWNSHIP. NO CALLS WERE RECEIVED FOR GAS MAIN LOCATIONS AT ANY OF THE BORING SITES IN QUESTION (BORE #1, #2, #3). OUR SERVICE FOREMAN, WHO WAS LOCATING GA | 11548 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
361 | 1985-09-06 | CO | other |  | PUBLIC SERVICE CO OF COLORADO | CONTRACTOR INSTALLING STORM SEWER HAD BACKFILLED DITCH AND CAUSED GAS SERVICE AT 4707 CLAUDE COURT TO BE PULLED OUT OF 6" CAST IRON MAIN. THE LEAKAGE IS THEN SUSPECTED OF MIGRATING TO 2234 WEST 47TH AVENUE, THE SITE OF EXPLOSION | 70000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
362 | 1985-09-20 | IL | other |  | NORTHERN ILLINOIS GAS CO | KELLY CONSTRUCTION WAS EXCAVATING TO INSTALL A NEW WATER MAIN. THEY HAD THE SERVICE EXPOSED, BUT ACCIDENTALLY HIT AND BROKE IT, CAUSING GAS TO BLOW UP INTO THEAIR. AT THIS TIME THEY DECIDED TO MOVE THEIR TRUCK, WHICH WAS PARKED DIRECTLY IN FRONT OF THE BR | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
363 | 1985-09-05 | RI | other |  | PROVIDENCE GAS CO | APPARENTLY SOMEONE TURNED GAS VALVES FOR TOP BURNERS & OVEN ON WITHOUT BURNERS.GAS ACCUMULATED, HOUSE EXPLODED WHEN PERSON LIVING INSIDE LIT MATCH TO LIGHT CIGARETTE. | 25000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
364 | 1985-09-08 | TN | other | UNKNOWN (FAYETTE COUNTY) | SOMERVILLE LIGHT GAS & WATER | VEHICLE WAS TRAVELLING EAST ON HY 64 WEST, LEFT ROAD EAST OF OZIER DRIVE. TRAVELED SOME 200 FT BEFORE HITTING A SHED WHICH HOUSED THE NATURAL GAS REGULATORSTATION FEEDING THE TOWN OF SOMERVILLE. BUILDING AND GAS LINES COMPLETELY KNOCKED OFF FOUNDATION. RE | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
365 | 1985-09-23 | PA | other | AMERICAN METER | EQUITABLE GAS CO | SOURCE/CAUSE OF THE INITIAL FIRE HAS NOT BEEN CLEARLY DETERMINED BY AUTHORITIES. | 200000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
366 | 1985-10-16 | MA | other |  | BAY STATE GAS CO |  | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
367 | 1985-07-18 | TX | other |  | ENTEX INC | CONTRACTOR BROKE 6" MAIN WITH BACKHOE. FIRE DEPARTMENT REROUTED TRAFFIC. | 1000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
368 | 1985-10-10 | NY | maintenance |  | CONSOLIDATED EDISON CO OF NEW YORK | CORRODED STEEL MAIN. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
369 | 1985-09-30 | IL | maintenance |  | PEOPLES GAS LIGHT & COKE CO | NATURAL GAS LEAKED FROM A CORRODED SECTION 1 1/2" STEEL PIPE INSIDE A CLAY TILECASING GOING THROUGH A BRICK WALL BETWEEN A VAULTED WALK AND AN ENCLOSED AREA UNDER THE FRONT CONCRETE STAIRS TO THE BUILDING. A LATER CHACK OF THE CUSTOMER'S HOUSE PIPEING IND | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
370 | 1985-11-01 | GA | other | PLEXCO | ATLANTA GAS LIGHT CO | ON OCTOBER 27, 1985 AT APPROX. 11:00 PM, AN 11,000 VOLT UNINSULATED LINE FELL AND DAMAGED THE EXISTING 2" PLASTIC LINE IN HEARDS DRIVE. THE RESIDENTS NOTICED THE SMELL OF GAS FUMES, BUT DID NOT NOTIFY ANYONE. ON NOVEMBER 1, 1985, AN EXPLOSION OCCURRED IN | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
371 | 1985-10-27 | MS | other |  | ENTEX INC | PERSONS UNKNOWN PILED PAPER BOXES ON METER INSTALLATION, AIR CONDITIONERS, INCINERATOR AND BUILDING WALL. THE PILE OF BOXES IGNITED FROM THE HEAT OF THE INCINERATOR. THE RESULTING FIRE SPREAD TO THE BUILDING AND MELTED THE NYLON BUSHING ATTHE METER INSTAL | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
372 | 1985-10-16 | CO | technical failure | PHILLIPS | PUBLIC SERVICE CO OF COLORADO | AN EXISTING 3-INCH PE MAIN WAS EXTENDED IN JULY, 1985. THE 3" PE EXTENSION WAS JOINED TO THE EXISTING MAIN WITH A BUTT FUSION. THE FUSION FAILED ON OCTOBER 16,1985, ALLOWING NATURAL GAS TO ESCAPE. A SIX-PLEX APARTMENT BUILDING WAS DESTROYED AS A RESULT OF | 500000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
373 | 1985-10-02 | OH | other |  | COLUMBIA GAS OF OHIO INC | A MASONRY PLANTER HAD BEEN BUILT OVER THE CUSTOMER SERVICELINE AND THE FOOTER ENCASED PART OF THE SERVICELINE PIPING. CUSTOMER WAS IN THE PROCESS OF DISMANTLING THE PLANTER. CRACK IN THREADS OF PIPE WHERE IT WAS SCREWED INTO ELL AT BOTTOM OF RISER DISCOVE | 75000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
374 | 1985-11-12 | MS | other |  | MISSISSIPPI VALLEY GAS | A CONTRACTOR INSTALLING TRAFFIC CONTROL SYSTEM CABLES DAMAGED A 2" STEEL MAIN WITH A TRENCHING MACHINE. A LOCATE REQUEST WAS RECEIVED THROUGH MISSISSIPPI ONE-CALL, INC. ON OCTOBER 8, 1985 AND THE LINE WAS LOCATED AND MARKED WITH PAINT ON OPCTOBER 9, 1985. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
375 | 1985-09-22 | NY | other |  | BROOKLYN UNION GAS CO | THE LEAK OCCURRED AT THE FLANGE BOLT INSULATORS. THE INSULATORS WERE REMOVED ON10/08/85 AS A TEMPORARY REPAIR. A PLIDCO SLEEVE WAS INSTALLED ON 10/18/85 AS A PERMANENT REPAIR. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
376 | 1985-11-07 | PA | other |  | PHILADELPHIA GAS WORKS |  | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
377 | 1985-10-19 | CA | ACCIDENTALLY CAUSED BY OPERATOR | DUPONT | SOUTHERN CALIFORNIA GAS CO |  | 100 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
378 | 1985-11-13 | OK | other |  | OKLAHOMA NATURAL GAS CO | TRACKHOE BECAME STUCK AND APPARENTLY KNOCKED SERVICE TEE OFF THE 4" LINE WITH THE TRACK OF THE HOE. | 200000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
379 | 1985-11-22 | MA | ACCIDENTALLY CAUSED BY OPERATOR |  | COMMONWEALTH GAS CO | ACCIDENTAL IGNITION OF NATURAL GAS BY VEHICLE ENGINE IN OPERATION DURING PURGING PROCEDURE. COMMMONWELTH GAS COMPANY EMPLOYEE INJURED. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
380 | 1985-12-06 | MN | other |  | MINNEGASCO INC | A CIRCUMFERENTIAL CRACK DEVELOPED IN SIX INCH IRON MAIN AS A RESULT OF SOIL STRESSES INDUCED BY FREEZING. | 130000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
381 | 1985-12-06 | TX | technical failure | TEX TUBE | NAVASOTA, CITY OF | A 2" GAS LINE WAS NEGLIGENTLY BROKEN BY LANGE CONSTRUCTION CO ON 12/6/84. THE LINE WAS LOCATED FOR LANGE CO ON 12/5/85 BY CITY GAS CREW. | 856 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
382 | 1985-11-11 | TX | other |  | ENERGAS CO | A BIRD HAD BUILT A NEST IN THE CENTRAL HEATER FURNACE VENT PREVENTING PROPEREXHAUST OF COMBUSTION PRODUCTS. THIS LED TO A CARBON MONOXIDE BUILD UP IN THERESIDENCE. FOUR OCCUPANTS WERE HOSPITALIZED. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
383 | 1985-10-14 | TX | other |  | ENERGAS CO | FIRE OF UNKNOWN ORIGIN DAMAGED GARAGE APARTMENT INJURING RESIDENT. | 10000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
384 | 1985-10-10 | TX | other | NIPAK - POLY I | LONE STAR GAS CO |  | 1648 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
385 | 1985-11-30 | PA | technical failure | CENTRAL PLASTICS | EQUITABLE GAS CO | THE ESCAPE OF NATURAL GAS RESULTED FROM THE SEPARATION OF A 3" X 1" CENTRAL PLASTICS SERVICE TAPPING TEE (PE 2306) FROM A 3" IPS NIPAK PLASTIC PIPEL MAINLINE (PE 2306). THE NATURAL GAS APPARENTLY MIGRATED TO 228 VALLEY STREAM DRIVE CAUSINGAN EXPLOSION. TH | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
386 | 1985-12-05 | CO | other | ALDYL(A) | PUBLIC SERVICE CO OF COLORADO | APPROXIMATELY 14 MONTHS PRIOR TO THE EXPLOSION AT 16423-B, EAST RADCLIFF PLACE,A 16" WATER LINE WAS INSTALLED UNDERNEATH TWO 1.25" POLYETHYLENE MAINS. THE WATER MAIN DITCH WAS IMPROPERLY BACKFILLED WITH LARGE PIECES OF PAVEMENT AND WAS NOT PROPERLY TAMPED | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
387 | 1985-12-12 | LA | other | UNKNOWN | LOUISIANA GAS SERVICE CO | A BLOWN TRANSFORMER IN THE AREA CAUSED AN ELECTRICAL SURGE ON THE COSTUMER'SPIPING. HIGH VOLTAGE WAS TRANSFERRED TO THE SERVICE LINE CAUSING A LEAK AND | 2000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
388 | 1985-12-12 | IN | other | DUPONT | INDIANA GAS CO INC | IN NOVEMBER 1984, 1,947' OF 2" AND 4" PLASTIC PIPE WAS INSTALLED ON BEHALF OFINDIANA GAS COMPANY BY P. L. WRIGHT CONSTRUCTION COMPANY TO REPLACE 1,853' OF 2"AND 4" CAST IRON AND STEEL DISTRIBUTION MAIN ON CHARLESTOWN ROAD IN NEW ALBANY,SEVERAL SECTIONS OF | 75000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
389 | 1985-12-12 | NY | other |  | CONSOLIDATED EDISON CO OF NEW YORK | EXPLOSION IN BUILDING CAUSED BY CRACK IN 6 INCH CAST IRON MAIN. THE MAIN WASUNDERMINED BY RECENTLY INSTALLED 2 INCH WATER SERVICE AND WATER LEAKAGE PROIRAND AFTER INSTALLATION OF WATER SERVICE. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
390 | 1985-12-06 | CT | other |  | CONNECTICUT LIGHT & POWER CO | THE 3" CAST IRON GAS MAIN ON CAROLINE STREET NEAR MAIN STREET IN DERBY,CONNECTICUT WAS FOUND TO BE CRACKED. DETERMINATION OF CAUSE IS CURRENTLYUNDER INVESTIGATION BY NATIONAL TRANSPORTATION SAFETY BOARD. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
391 | 1985-11-07 | TX | other | DUPONT | ENTEX INC | CONTRACTOR CUT MAIN WITH DITCHING MACHINE. GAS IGNITED,DESTROYING MACHINE & ADJACENT HOUSES AND INJURING OPERATOR. | 40000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
392 | 1985-12-07 | OH | other |  | EAST OHIO GAS CO |  | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
393 | 1985-12-14 | IN | other |  | NORTHERN INDIANA PUBLIC SERVICE CO | INVESTIGATION BY AN INDEPEDENT INVESTIGATOR REVEALED THAT THERE WAS A GAS LEAKAT A LOOSE FITTING (NUNT) ON A FLEXIBLE CONNECTOR TO THE WATER HEATER. THEREWERE SIGNS OF SEVERE FIRE DAMAGE IN THE AREA AROUND THE WATER HEATER.THE FORCE OF THE EXPLOSION CAUS | 70000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
394 | 1985-12-11 | TX | other |  | LONE STAR GAS CO | LINE WAS HIT BY DOZER. | 12000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
395 | 1985-12-05 | TX | other |  | ENERGAS CO | APPARENTLY THE FIRE ORIGINATED IN FLOOR FURNACE, CAUSE UNKNOWN. OCCUPANT HOSPITALIZED, ANOTHER TENNANT AND 2 FIREMEN SUFFERED INJURIES. | 25000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
396 | 1985-12-16 | TX | other |  | ENERGAS CO | MOBILE HOME CAUGHT FIRE WHILE OCCUPANTS SLEPT. ALL EXCEPT A TWELVE YEAR OLD BOYESCAPED FROM THE STRUCTUR. THE ORIGIN OF THE FIRE IS UNKNOWN. | 10000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
397 | 1985-12-30 | TX | other |  | ENERGAS CO | FIRE OF UNKNOWN ORIGIN BURNED HOUSE. TWO YEAR OLD CHILD WAS TRAPPED INSIDE AND DIED. | 20000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
398 | 1986-01-02 | IL | technical failure |  | NORTHERN ILLINOIS GAS CO |  | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
399 | 1985-12-20 | SD | other | ROCKWELL | MONTANA - DAKOTA UTILITIES CO | APPARENT ICE BUILD UP ON REGULATOR ATMOSPHEREIC VENT. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
400 | 1985-12-21 | OH | other | ALDYL A | COLUMBIA GAS OF OHIO INC | PLASTIC INSERT PIPE PULLED OUT OF FITTING IN CUSTOMER OWNED SERVICE LINE NEAR METER SETTING AFTER APPROXIMATELY 15 YEARS OF SERVICE. CAUSE OF PULL OUT HAS NOT BEEN DETERMINED. | 102500 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
401 | 1986-01-13 | ID | other |  | INTERMOUNTAIN GAS CO |  | 55000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
402 | 1986-01-13 | LA | other |  | NEW ORLEANS PUBLIC SERVICE INC | BROKEN 6" CAST IRON MAIN - GAS MIGRATED THROUGH CRACKS IN CONCRETE AND WAS IGNITED BY SERVICE TRUCK. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
403 | 1985-09-30 | AL | ACCIDENTALLY CAUSED BY OPERATOR |  | SYLACAUGA GAS SYSTEM | AT APPROXIMATELY 1:45PM LARRY ATKINSON CALLED ON THE RADIO AND SAID ROLAND PUGHCONT. CO. HAD BROKE A GAS LINE ON NORTH NORTON IN FRONT OF MCCLURE MOTOR CO. ATAPPROXIMATELY 1:55PM THE GAS IGNITED FROM AN UNKNOWN SOURCE AND BURNT RALPH GRAY. HE WAS CARRIED | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
404 | 1985-12-25 | WI | other | DRESSER(METER BEND) | WISCONSIN NATURAL GAS CO | SERVICE RISER SEPARATED FROM METER ASSEMBLY; ATTRIBUTED TO ICE ACCUMULATION AT METER ASSEMBLY. NEW BERLIN FIRE DEPARTMENT EVACUATED APPROXIMATELY 55 PEOPLE FROM APRTMENT COMPLEX AS A PRECAUTIONARY MEASURE. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
405 | 1985-12-23 | CA | other |  | SOUTHERN CALIFORNIA GAS CO | LEAKING NATURAL GAS FROM AN UNATHORIZED EXTENSION OF THE OPERATOR'S 3/4" STEEL SERVICE LINE ACCUMULATED UNDER THE STRUCTURE IT SERVED AND SUBSEQUENTLY IGNITED. | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
406 | 1986-01-01 | OR | other |  | NORTHWEST NATURAL GAS CO | THE BLAST DESTROYED THIS HOME AND DID MAJOR DAMAGE TO FOUR MORE. BROKEN WINDOWSWERE PREVALENT IN A FOUR-BLOCK AREA. SEVERAL PEOPLE WERE TREATED AT LOCAL HOSPITALS, BUT NONE REQUIRED HOSPITALIZATION AS FAR AS WE KNOW. THE METER WAS FOUND SOME DISTANCE AWAY | 800000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
407 | 1985-07-15 | VT | other |  | GAS CO OF VERMONT INC | PART D - THE CITY OF BARRE DUG UP A GAS SERVICE AND PULLED IT IN CELLAR WALL AND BROKE THE BASEMENT TEE. ALSO THE MANAGER ST THIS TIME AS QUIT AND I HAVE SINCERETIRED THE LINES IN THE WHOLE CITY | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
408 | 1986-01-10 | AL | other |  | DOUBLE SPRINGS NATURAL GAS BOARD | PART D - THE STATE HIGHWAY DEPT. WAS INSTALLING A NEW CULVERT, THEY HUNG THE GAS SERVICE LINE AND RIPPED A 1.24 HOLE IN GAS MIN AT THE TAP. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
409 | 1986-01-27 | IL | other |  | NORTHERN ILLINOIS GAS CO | DURING THE YEAR OF 1985 A INSTALLING UNDER GROUND FACILITIES HIT AND DAMAGED A 2" GAS MAIN AT THE ABOVE ADDRESS. THIS ACCIDENT WAS NOT REPORTED TO NI-GAS AT THE TIME. SUBSEQUENTLY, A GAS LEAK RESULTED FROM THIS HIT AND IT MIGRATED INTO THEHOUSE CAUSING TH | 150000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
410 | 1986-01-11 | MA | other |  | BAY STATE GAS CO | FIRE IS UNDER INVESTIGATION BY STATE AUTHORITIES, FIRE MARSHALL'S OFFICE AND LOCAL ARSON SQUAD. ORIGIN IS UNKNOWN. THE DWELLING WAS UNOCCUPIED AT THE TIME OF THE INCIDENT. | 500000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
411 | 1986-02-04 | MS | other | DUPONT | ENTEX INC | 1/2" PLASTIC SERVICE LIEN WAS CUT APPROXIMATELY 7/85 BY OUTSIDE PARTY. EXTEX PERSONNEL HAD MARKED LOCATION OF PIPE WITH YELLOW PAINT PRIOR TO EXCAVATION. OUTSIDE PARTY REPAIRED PLASTIC PIPE WITH 1/2" DRESSER TYPE COUPLING AND DID NOT NOTIFY ENTEX. SOME | 250000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
412 | 1986-01-05 | MA | other | UNK | BOSTON GAS CO | INVESTIGATION FOUND BROKEN 6" CAST IRON MAIN IN PREVIOUSLY EXCAVATED WATER TRENCH APPROXIMATELY 14 FEET FROM HOUSE #69. BROKEN CAST IRON MAIN PROBABLY DUE TO PREVIOUS EXCAVATION. GAS MIGRATED INTO CELLAR CAUSING INCIDENT. SOURCE OF IGNITION UNKNOWN.PAR | 200000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
413 | 1986-01-13 | TX | ACCIDENTALLY CAUSED BY OPERATOR |  | SAN ANTONIO CITY PUBLIC SERVICE BOARD | OPERATOR'S EMPLOYEE VIOLATED SAFETY PROCEDURES CAUSING FIRE. FIRE WAS IMMEDIATELY EXTINGUISHED. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
414 | 1985-12-24 | FL | other |  | CITY GAS CO OF FLORIDA | SEE ATTACHED | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
415 | 1986-02-13 | IA | other |  | IOWA ILLINOIS GAS & ELECTRIC | AT APPROX. 5:10 A.M., THERE WAS AN EXPLOSION AND FIRE AT 2580 8TH AVENUE, MARION, IA. THERE WERE FOUR PERSONS IN THE HOUSE AT THE TIME OF THE EXPLOSION. TWO ADULTS REMAIN HOSPITALIZED AND TWO CHILDREN WERE TREATED AND RELEASED. THE APPARENT CAUSE OF THE I | 47000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
416 | 1986-01-17 | IA | other |  | IOWA PUBLIC SERVICE CO | HIGHWAY 18 IN CYLINDER MAKES A 90 DEGREES TURN WITH FLASHING YELLOW LIGHTS. TRUCK DRIVER, DRIVING A SEMI-TRAILER TRUCK, WENT TO SLEEP. AWOKE IN TIME TO SEE FLASHING LIGHTS AND VEERED OFF TO AVOID STRIKING THEM. DRIVER STRUCK ABOVE GROUND DISTRICT REGULATI | 1500 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
417 | 1986-02-02 | NY | other |  | BROOKLYN UNION GAS CO | ARSON IS THE SUSPECTED CAUSE OF THE INCIDENT. A COUPLING WAS REMOVED FROM THE INTERIOR PIPING AND THE ESCAPING GAS WAS IGNITED FROM THE FIRES THAT ARE BELIEVEDTO HAVE BEEN PURPOSELY SET. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
418 | 1986-02-20 | GA | other |  | ATLANTA GAS LIGHT CO | THE SERVICE LINE TO THIS RESIDENCE WAS DISCONNECTED AND AIR TESTED WITH 62# OF PRESSURE FOR ONE HOUR AND TEN MINUTES. THERE WAS NO LEAK ON SERVICE LINE. BAR HOLES WERE DRIVEN ABOVE THE MAIN AT THIS LOCATION. THE BAR HOLES WERE CHECKED WITH A COMBUSTIBL | 45000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
419 | 1986-02-11 | ND | other |  | MONTANA - DAKOTA UTILITIES CO | INCIDENT STILL UNDER INVESTIGATION - CAUSE UNKNOWN | 20000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
420 | 1986-02-13 | CO | other | EMCO-NORDSTORM | ROCKY MOUNTAIN NATURAL GAS CO | FROZEN WATER IN VALVE BOX SEEMS TO HAVE ACCUMULATED AND PRESSURE DOWN ON TOP OFVALVE BROKE THE BODY NEXT TO OUTGOING FLANGE. BECAUSE OF FROZEN GROUND AND CEMENT STREET COVER, THE GAS COULD NOT COME TO THE SURFACE AND DISSIPATE. THE ORDOR ALSO WAS REMOVE | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
421 | 1986-02-14 | PA | other |  | PHILADELPHIA GAS WORKS | ON FEB. 14, 1986 AT 9:45 P.M. PGW RECEIVED A CALL FROM A CUSTOMER AT 4631 NORTH10TH ST. REPORTING AN ODOR INSIDE (LIVING ROOM). A SERVICEMAN WAS DISPATCHED AT 9:53 P.M. AND FOUND FOUR HOMES WITH A READING OF 100% AT THE FRONT FOUNDATION WALLS. THE SERVI | 80000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
422 | 1985-01-10 | AL | other | MCWAYNE PIPE | ATHENS GAS DEPT, CITY OF | ON JAN 10, 1985, AT APPROXIMATELY 5:10 A.M., I RECEIVED A CALL FROM ATHENS FIREDEPT. DISPATCHER, KENNETH GILL. MR. GILL TOLD ME OVER THE PHONE THAT THERE WASA GAS LEAK ON NORTH BEATY STREET AND MY HELP WAS NEEDED. AS I WAS LEAVING MY HOME, I RECEIVED A | 3500 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
423 | 1986-02-26 | GA | other | L.B. FOSTER | UNITED CITIES GAS CO | POULTRY FARMER WAS DIGGING A LARGE HOLE TO BURY TRASH OR ETC. THE LARGE FRONT END LOADER RAN INTO AND DAMAGED PIPE WHILE DIGGING APPROXIMATELY FOUR FEET DEEP. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
424 | 1986-02-19 | IL | other |  | PEOPLES GAS LIGHT & COKE CO | GAS LEAKING FROM A CRACKED 6" CAST IRON MEDIUM PRESSURE GAS MAIN MIGRATED INSIDE A BUILDING WHICH WAS DESTROYED BY AN EXPLOSION.THE SOURCE OF IGNITION IS UNKNOWN | 65000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
425 | 1986-02-15 | LA | other |  | LOUISIANA GAS SERVICE CO | AUTOMOBILE RAN OVER GAS METER CAUSING GAS TO IGNITE. THE RESULTING FIRE COMPLETELY DESTROYED AUTOMOBILE AND CAUSED SOME DAMAGE TO SIDE OF HOUSE. METER REGULATOR INSTALLATION WAS ON PRIVATE PROPERTY AND OPERATOR OF VEHICLE DROVE OFF HIGHWAY STRIKING INST | 5000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
426 | 1986-02-20 | LA | other |  | LOUISIANA GAS SERVICE CO | CUSTOMER TURNED OVEN ON AND DIDN'T LIGHT BURNER. APPROXIMATELY 2 OR 3 MINUTES LATER, THE CUSTOMER OPENED OVEN DOOR AND LIT A MATCH CAUSING EXPLOSION AND FLASHBACK. THE CUSTOMER DIDN'T DETECT ANY GAS ODOR. LATER TESTS PROVED THAT ODORANTCONCENTRATION IN | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
427 | 1986-03-04 | NY | other |  | CONSOLIDATED EDISON CO OF NEW YORK | GAS LEAKING FROM A 6" CAST IRON MAIN MIGRATED INTO AN ELECTRIC MANHOLE AND WAS IGNITED BY AN UNKNOWN SOURCE. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
428 | 1986-02-25 | NJ | other |  | ELIZABETHTOWN GAS CO | PART 2 - VALVE AT METER SET WAS DELIBERATELY OPENED BY UNKNOWN PERSON(S) TO CREAT FIRE (EXPLOSION).PART 3 - INVESTIGATION BY ARSON SQUAD UNDERWAY. | 750000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
429 | 1986-03-13 | IL | other |  | NORTHERN ILLINOIS GAS CO | ALPHA CONSTRUCTION WAS INSTALLING A WATER MAIN ON THE SOUTH SIDE OF 14TH ST (RTE 30), CHICAGO HEIGHTS, ILL. A BACKHOE WAS DIGGING A TRENCH IN FRONT OF 204 W 14TH ST WHEN THE 3/4" SERVICE TO 204 WAS HIT AND PULLED UP ABOUT 1 FT CAUSING THE PIPE TO PULL OUT | 250000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
430 | 1986-02-19 | WI | other |  | WISCONSIN GAS CO | AN EXPLOSION AT 1506 19TH ST RESULTED IN INJURY REQUIRING INPATIENT HOSPITALAZATION OF TWO PERSONS. THE HOME WAS NOT SERVED BY NATURAL GAS. PROPERTY DAMAGE WASESTIMATED AT $40,000. AN INVESTIGATION OF THIS INCIDENT TO DATE, HAS REVEALED THAT A LEAK EXISTE | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
431 | 1986-01-03 | MO | other |  | UNION ELECTRIC CO |  | 53000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
432 | 1986-03-27 | CO | ACCIDENTALLY CAUSED BY OPERATOR |  | ROCKY MOUNTAIN NATURAL GAS CO | EQUIPMENT FAILURE ALLOWED MORE GAS THAN NORMAL INTO TRENCH - L.P. HEAVIER THAN AIR AND FILLED TRENCH AND OVERCAME 2 PERSONS.NEED TO MOVE 1 - 2" P.E. LINE AND 1 - 3" P.E. LINE. THE 2" LINE CLAMPED LOWERED AND ALL O.K. 3" SQUEEZE-OFF CLAMPS FAILED TO HOLD | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
433 | 1986-03-26 | TN | other | US STEEL | NASHVILLE GAS CO | EXPLOSION OF UNKNOWN ORIGIN BLEW OUT WALLS ON MIKE'S DELI AND GAME ROOM. CONCRETE ROOF FELL DOWN BREAKING GAS METER AND CRACKING SERVICE RISER PIPE AT VALVE.NO FIRE INVOLVED. SERVICE WAS SQUEEZED OFF BELOW RISER VALVE. AREA SURVEYED WITH FLAME PACK WITH | 400000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
434 | 1986-03-17 | GA | other | PITTSBURG STEEL | TRI - COUNTY NATURAL GAS | CONSTRUCTION CO. WAS PLOWING TELEPHONE CABLE IN STATE ROUTE 77 RIGHT-OF-WAY. MAIN WAS RUPTURED BY PLOW FOOT PENETRATING 4" MAIN HIGH PRESSURE DISTRIBUTION LINE. PROPER LINE LOCATION AND VERIFICATION WAS NOT ADEQUATE. APPROXIMATELY 400' OF MAIN WAS DAMA | 13000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
435 | 1986-03-04 | OH | maintenance |  | DAYTON POWER & LIGHT CO | WEATHER CONDITIONS, I.E., ICING OF METER-REGULATOR ASSEMBLY, MAY HAVE ADVERSELYAFFECTED PRESSURE REGULATOR OPERATION, ALLOWING HIGH PRESSURE GAS TO ENTER COSTOMER'S GAS PIPING AND APPLICANCES. APPLIANCE REGUALTOR FAILED, RESULTING IN FIRE AND PROPERTY DA | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
436 | 1986-02-28 | WI | other | FISHER | WISCONSIN NATURAL GAS CO | FREEZING WEATHER, ICING OF METER ASSEMBLY, AND/OR APPLIANCE FAUILURE MAY HAVE CONTRIBUTED TO INCIDENT. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
437 | 1986-03-20 | PA | maintenance |  | EQUITABLE GAS CO | INVESTIGATION OF THE EXPLOSION INDICATES THAT THE CUSTOMERS' SERVICE LINE, CURBTO METER, WAS CORRODED AND LEAKING. A SECTION OF THE HOUSE LINE WAS CRACKED ANDLEAKING. THE HOUSE LINE WAS LOCATED BETWEEN THE FLOOR JOISTS SEPARTING THE FLOOR OF THE SECOND F | 600000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
438 | 1986-03-18 | TX | other |  | EAGLE PASS NATURAL GAS CORP | AN EXPLOSION OCCURRED IN A SEWER MANHOLE ON MARCH 18, 1986, ABOUT 6:50 P.M. ANDA LITTLE BOY WAS BURNED ON THE FACE AND AROUND THE EYES. THE BOYS MOTHER RUSHED HIM TO THE HOSPITAL AND DIDN'T NOTIFY ANYONE. THE NEXT BY, MY OFFICE WAS NOTIFIED OF THE ACCID | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
439 | 1986-03-19 | TX | other |  | ENERGAS CO | A FIRE OF UNKNOWN ORIGIN DESTROYED HOUSE. STATE FIRE INSPECTOR DECLARED ARSON AS CAUSE. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
440 | 1986-03-29 | WA | other |  | WASHINGTON NATURAL GAS CO | TODD SHIPYARD CORP. SUBCONTRACTOR CONNECTED 100 PSI PURE OXYGEN LINE TO 25 PSI NATURAL GAS LINE IN ERROR, CREATING COMBUSTABLE MIXTURE IN SHIPYARD FUEL LINE. IGNITION PROBABLY CAUSED BY OXYGEN CONTACTING OIL IN PIPE. THREE LARGE GAS METERS OWNED BY OPER | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
441 | 1986-01-21 | TX | other |  | SOUTHERN UNION GAS CO | CONTRACTOR TRENCHED INTO THE PIPE AND PUNCTURED IT. GAS IGNITED AND TRAFFIC WASREROUTED. LOCATION REQUEST WAS MADE BY ANOTHER CONTRACTOR WHO PLANNEDTO WORK IN THE AREA. | 300000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
442 | 1986-03-03 | TX | other |  | SOUTHERN UNION GAS CO | A 2" ABS PLASTIC PIPELINE FRACTURED ON THE LOWER 120' OF THE PIPE'S CIRCUMFERENCE. GAS MIGRATED THROUGH AN IMPROPERLY COMPACTED WATER MAIN TRENCH THROUGH STRATA OF CLAY AND SANDY LOAM. THE GAS MIGRATED UNDER AND INTO AN ADOBE RESIDENCE AT 226 CANDALARIA | 20000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
443 | 1986-04-11 | OK | other |  | ARKANSAS LOUISIANA GAS CO (ARKLA GAS CO) | SPECIFIC LEAK WAS NOT EXPOSED. POUNDS PRESSURE GAS LINE WAS REPLACED IN ANOTHER LOCATION. OUNCE GAS LINE WAS RETIRED. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
444 | 1986-03-07 | TX | technical failure | PLEXCO | LONE STAR GAS CO | THREE MEN MAKING A SERVICE TAP AND 2 IN BELL HOLE WERE BURNED | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
445 | 1986-03-25 | CA | other |  | SOUTHERN CALIFORNIA GAS CO |  | 70000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
446 | 1986-04-08 | IL | other |  | NORTHERN ILLINOIS GAS CO | ARTHUR MARTIN, DRIVER OF THE VEHICLE, APPARENTLY THOUGHT A DRIVEWAY EXISTEDOFF OF NORTH AVENUE. HE TRAVELED THROUGH THE PARKWAY AND STRUCK THE METER SETAT PORTILLO'S RESTAURANT, 538 1/2 NORTH AVENUE, GLENDALE HEIGHTS. THE ACCIDENTDAMAGED THE GAS METER SET | 20000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
447 | 1986-04-15 | IL | other | EATON CORP. | NORTHERN ILLINOIS GAS CO | FIRE OF UNKNOWN CAUSE COMPLETELY DESTROYED VACATED HOUSE AND DETACHED GARAGE. THE HEART OF THE FIRE CAUSED THE SERVICE TO RUPTURE BELOW THE CLOSED AND LOCKED OFF SERVICE VALVE AND IGNITED THE ESCAPING 28 PSI GAS. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
448 | 1986-03-12 | TX | other |  | LONE STAR GAS CO |  | 1000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
449 | 1986-04-09 | OK | other |  | OKLAHOMA NATURAL GAS CO | PART 3 - VEHICLE CAUSING DAMAGE HAD BEEN INVOLVED IN A VEHICLE ACCIDENT IMMEDIATELY PRIOR TO THIS INCIDENT. IN AN ATTEMPT TO FLEE THE SCENE OF THE ACCIDENT, THE VEHICLE RAN INTO THE REGULATOR SETTNG - RESULTING IN A FIRE.PART 1-6 - INITIAL REPORTS FROM TH | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
450 | 1986-04-25 | IN | other |  | INDIANA GAS CO INC | BACKHOE STRUCK SERVICE LINE AND BROKE SERVICE AT SERVICE LINE RISER AT OUTSIDE METER SET. | 80000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
451 | 1986-04-18 | GA | other | PLEXICO | ATLANTA GAS LIGHT CO | CONTRACTOR MAKING ROAD BORE STRUCK GAS MAIN. ESCAPING GAS WAS APPARENTLY IGNITED BY FIRE TRUCK RESPONDING TO THE INCIDENT. | 185000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
452 | 1986-05-05 | MI | other |  | CONSUMERS POWER CO | SEWER CONTRACTOR BROKE GAS MAIN WITH BACKHOE. FACILITIES WERE LOCATED. SUSPECT CIGARETTE AS SOURCE OF IGNITION. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
453 | 1986-04-11 | IA | other |  | IOWA PUBLIC SERVICE CO | SEMI-TRUCK TRAILER BECAME DETACHED FROM TRACTOR AND TIPPED OVER ON ABOVE GROUNDREGULATOR STATION BREAKING OFF GAUGE LINES. EMERGENCY ACTION WAS NECESSARY TO CLEAR AREA. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
454 | 1986-03-28 | DE | other |  | DELMARVA POWER & LIGHT CO | AT ABOUT 2:55 AM ON MARCH 28, 1986, MRS. CATHERINE HUBER, AGE 43, ATTEMPTED TO LIGHT A RANGE TOP BURNER WITH A MATCH. THERE WAS AN EXPLOSION AND MRS. HUBER WASBLOWN INTO THE SIDE YARD. SHE SUFFERED 2ND DEGREE BURNS OVER THE TOP PART OF HER BODY AND WAS HO | 75000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
455 | 1986-04-11 | SC | other |  | SOUTH CAROLINA ELECTRIC & GAS CO | THE ORIGIN OF THE FIRE APPEARS TO HAVE BEEN WITH AN IGNITION SOURCE INSIDE OF THE BUILDING NEAR A COOK STOVE. ALTHOUGH THE FACILITIES OWNED BY THE OPERATOR DO NOT APPEAR TO HAVE BEEN THE CAUSE OF THE FIRE, NATIONAL GAS APPEARS TO HAVE BEENIGNITED BY BURNI | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
456 | 1986-04-16 | TX | other |  | SOUTHERN UNION GAS CO | TAMPERING WITH GAS VALVE AND METER RESULTED IN LEAKING GAS WHICH IGNITED AND SET FIRE TO HOUSE. | 45000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
457 | 1986-05-30 | TX | other |  | LONE STAR GAS CO | AN EXPLOSION OF UNDETERMINED ORIGIN BLEW WALLS OF HOUSE INTO YARD. NO FIRE, BUT SEVERAL PIECES OF PAPER SCORCHED IN SOUTHWEST CORNER BEDROOM. ALL METERED ANDUNMETERED LEAK INVESTIGATION PROVED NEGATIVE. (NO GAS LEAK FOUND.) | 25000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
458 | 1986-05-29 | TX | other | DRESSER | LONE STAR GAS CO |  | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
459 | 1986-04-26 | CA | other |  | PACIFIC GAS & ELECTRIC CO | THE FIRE INSPECTOR HAS NOT GIVEN A DETERMINATION AS TO THE CAUSE OF THE EXPLOSION AND SUBSEQUENT FIRE. THE GAS LEAK CAUSING THE EXPLOSION APPEARS TO HAVE ORIGINATED FROM THE CUSTOMER'S HOUSELINE LEADING TO THE WATER HEATER OR FROM THE CUSTOMER'S VALVE IN | 250 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
460 | 1986-05-10 | FL | other | POLYETHYLENE PRODUCTS INC. | CLEARWATER GAS DIV, CITY OF |  | 350000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
461 | 1986-05-21 | CA | other |  | SOUTHERN CALIFORNIA GAS CO |  | 70000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
462 | 1986-06-01 | CA | other |  | SAN DIEGO GAS & ELECTRIC CO | AUTOMOBILE HIT A GAS HEADER ASSEMBLY CONSISTING OF 3 GAS METER SETS SERVING THREE SMALL BUSINESSES. THE GAS IGNITED AND DID EXTENSIVE DAMAGE TO THE CONTENTS OF FOREMOST DRY CLEANERS, WHICH IS ADJACENT TO THE GAS METERS. THERE WERE NO INJURIES. | 83000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
463 | 1986-04-27 | NY | other |  | BROOKLYN UNION GAS CO | A CITY CONTRACTOR UPON COMPLETION OF AN EMERGENCY SEWER DID NOT OBTAIN PROPER CONSOLIDATION DURING BACKFILLING. EXCESSIVE SETTLEMENT OCCURRED CREATING VOIDS UNDER THE PAVEMENT. THIS RESULTED IN THE FAILURE OF A 6" CAST IRON MAIN AND A COPPER SERVICE PUL | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
464 | 1986-04-27 | TX | other |  | ENERGAS CO | J.M. FRENCH, COMPANY EMPLOYEE, WAS INFORMED OF FIRE AND EXPLOSION BY THE LEVELLAND FIRE DEPT. HE AND CLEO RANGEL MADE A SHUT-IN TEST OF CUSTOMER PIPING AND SLOW-FIRE TEST OF METER SETTING AT THE REQUEST OF THE FIRE DEPT. AND FOUND NO LEAKS AND NO PROBLEM | 5000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
465 | 1986-05-29 | OK | other |  | DRUMRIGHT GAS AUTH | STATEMENTS ATTACHED | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
466 | 1986-06-20 | TX | ACCIDENTALLY CAUSED BY OPERATOR |  | ENTEX INC |  | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
467 | 1986-06-25 | TX | other | DUPONT | ENTEX INC |  | 20000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
468 | 1986-06-27 | LA | other |  | NEW ORLEANS PUBLIC SERVICE INC | A FAILED INSULATED SLEEVE AT THE BASE OF A SERVICE RISER ADJACENT TO A SLAB HOUSE HAD BEEN REPLACED. WHILE USING BUTANE TORCH TO WRAP PIPE, A POCKET OF GAS INUNDETECTED VOID UNDER HOUSE SLAB IGNITED. EMPLOYEE RECEIVED FACIAL BURNS. SHEETROCK OF INTERIO | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
469 | 1986-05-29 | MI | other |  | CONSUMERS POWER CO |  | 90000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
470 | 1986-07-18 | OK | other |  | GUYMON MUNICIPAL GAS CO | REPORTED BY PHONE 7-21-86 TO PETTY OFFICER BRYAN SEE ENCLOSED STATEMENT | 60000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
471 | 1986-06-21 | AL | other |  | ALABAMA GAS CORP |  | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
472 | 1986-06-19 | TX | other |  | LONE STAR GAS CO |  | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
473 | 1986-06-17 | TX | other |  | LONE STAR GAS CO | R R STATION AND METER STRUCK BY DERAILED TRAIN. DPS REQUESTED TOWN PLANT SYSTEM BE TURNED OFF DURING RESCUE OPERATIONS. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
474 | 1986-05-28 | CA | other |  | PACIFIC GAS & ELECTRIC CO | RESIDENT ATTACHED PLASTIC BAG TO GAS HOUSELINE. TO COMMIT SUICIDE, RESIDENT THEN PLACED HIS HEAD INSIDE THE BAG. DEATH WAS BY ASPHYXIATION. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
475 | 1986-05-31 | CA | other | FISHER CONTROLS | SOUTHERN CALIFORNIA GAS CO |  | 130000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
476 | 1986-06-25 | CA | ACCIDENTALLY CAUSED BY OPERATOR |  | SOUTHERN CALIFORNIA GAS CO |  | 1350 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
477 | 1986-07-23 | NE | other |  | METROPOLITAN UTILITIES DISTRICT |  | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
478 | 1986-07-04 | MI | other |  | CONSUMERS POWER CO |  | 60000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
479 | 1986-08-27 | AZ | other |  | SOUTHERN UNION GAS CO | ON AUGUST 27, 1986, A 1" STEEL SERVICE LINE WAS HIT AND DAMAGED BY A CITY OWNEDAND OPERATED GRADER. THE GRADER PULLED THE LINE AWAY FROM THE METER AT A SCREW TYPE JOINT ( THE METER WAS LOCATED NEXT TO THE GARAGE). THE LINE WAS HIT BY THE GRADER APPROXIMAT | 105000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
480 | 1986-03-26 | CA | other |  | SOUTHERN CALIFORNIA GAS CO |  | 105000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
481 | 1986-08-12 | TX | ACCIDENTALLY CAUSED BY OPERATOR | TEX TUBE | NAVASOTA, CITY OF | WHEN MAKING REPAIRS TO WATER LINE OPERATOR OF BACKHOE CUT THE GAS LINE. | 650 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
482 | 1986-07-07 | IL | other |  | PEOPLES GAS LIGHT & COKE CO | AN OUTSIDE CONTRACTOR, USING HEAVY EQUIPMENT, BROKE A SERVICE TAP VALVE AT A 6"C.I. MAIN. DUE TO THE CLOSE PROXIMITY TO THE ESCAPING GAS, A NEARBY FACTORY WASEVACUATED. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
483 | 1986-08-08 | WY | technical failure | ENCOAT | NORTHERN UTILITIES INC | THE ATTACHED REPORT COVERS AN INCIDENT THAT OCURRED ON A 1" DISTRIBUTION STUB IN CASPER, WY ON 8/8/86. NATURAL GAS IGNITED RESULTING IN FIRST AND SECOND DEGREEBURNS TO THE FACE AND RIGHT ARM OF ONE COMPANY EMPLOYEE REQUIRING FIRST AID TREATMENT BUT NO FAT | 10000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
484 | 1986-08-04 | NY | other | DUPONT | LONG ISLAND LIGHTING CO | LEAK CAUSE IS CURRANTLY UNDER INVESTIGATION BY AN ANALYTICAL METALLURGICAL AND RESEARCH LABORATORY. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
485 | 1986-07-20 | WI | other |  | WISCONSIN NATURAL GAS CO | BASED UPON INFORMATION OBTAINED, APPEARS THAT CONNECTOR BEHIND GAS APPLIANCE FAILED, ALLOWING ACCUMULATION AND IGNITION OF GAS WITHIN CUSTOMER'S RESIDENCE. NO INDICATION THAT OPERATOR'S DISTRIBUTION SYSTEM WAS INVOLVED IN CAUSE AND ORIGIN OF OCCURANCE. | 70000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
486 | 1986-08-06 | WI | other |  | NORTHERN STATES POWER CO | THIS CUSTOMER IS THE CITY OF LA CROSSE SEWER DISPOSAL PLANT. IN THE PROCESS OF SWITCHING FROM METHANE GAS OFF OF THE DIGESTORS TO NSP SUPPLIED NATURAL GAS, THE"GAS" EXPLODED INSIDE THE BOILER. THIS CAUSED TWO INJURIES AND AN ESTIMATED $10,000 XDAMAGE TO B | 10000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
487 | 1986-07-24 | CA | other | NORDSTROM | SOUTHERN CALIFORNIA GAS CO | A THREE INCH BY-PASS VALVE IN A REGULATOR STATION WAS OPENED BY AN UNATHORIZED PERSON. NATURAL GAS AT 175 PSI WAS ALLOWED TO ENTER A SYSTEM WITH AN MAOP OF 39 PSI. | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
488 | 1986-08-14 | NJ | other | PHILLIPS | PUBLIC SERVICE ELECTRIC & GAS CO | CONTRACTOR DAMAGED A GAS MAIN WHILE INSTALLING SEWER LATERAL. IGNITION OCCURED CAUSING FIRST AND SECOND DEGREE BURNS TO CONTRACTOR'S EMPLOYEE. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
489 | 1986-08-08 | TX | other |  | ENTEX INC | CITY OF HOUSTON CREW BROKE 1" SERVICE OFF OF 2" MAIN. ONE CITY EMPLOYEE LIT A CIGARETTE CAUSING THE GAS TO IGNITE. TWO PEOPLE RECEIVED BURNS. ONE PERSON WAS HOSPITALIZED OVERNIGHT. | 500 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
490 | 1986-08-04 | LA | other |  | LOUISIANA GAS SERVICE CO | THE HOUSE AT 855 HOMESTEAD AVE EXPLODED AND BURNED AT 3:32PM ON 8/4/86. TWO ADJACENT HOMES ON EACH SIDE OF THE HOUSE WERE MODERATELY DAMAGED. NO ONE WAS HOME AT TIME OF THE EXPLOSION. GAS CO CREWS WERE IMMEDIATELY DISPATCHED TO THE AREA AND MAIN LINE VALV | 150000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
491 | 1986-07-28 | CA | other |  | SAN DIEGO GAS & ELECTRIC CO | A D-3 CATERPILLER HIT A 3/4" SERVICE LINE BETWEEN MAIN AND METER SET ASSEMBLY. THE SERVICE RISER AND MSA WERE PULLED AWAY FROM THE HOUSE APPLING A STRESS TO THE HOUSELINE WHICH FAILED. ESCAPING GAS IGNITED BY UNKNOWN SOURCE. | 176000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
492 | 1986-08-28 | NM | ACCIDENTALLY CAUSED BY OPERATOR | LONE STAR STEEL | GAS CO OF NEW MEXICO | HE WAS CLEANING TAPE OFF OF PIPE USING TORCH TO BURN TAPE. FIRE WAS APPARENTLY OUT AND HE WAS GOING TO HOOK UP BYPASS HOSE. HE OPENED SANDWICH VALVE IN PREPARATION OF PURGING GAS; BUT 3/4" VALVE ON BY-PASS ASSEMBLY WAS OPEN. HE HEARD GAS AND WAS ATTEMPTI | 5400 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
493 | 1986-09-05 | VA | other |  | WASHINGTON GAS LIGHT CO | A PRIVATE CONTRACTOR, ROSS MASONRY, WAS EXCAVATING AT 8912 CROMWELL DR TO REPAIR THE BASEMENT'S REAR BUILDING WALL. A 3/4" WRAPPED STEEL HP GAS SERVICE LINE WAS STRUCK AND BROKEN BY THEIR BACKHOE CAUSING GAS ESCAPEMENT WHICH POCKETED IN THE BASEMENT AND W | 150000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
494 | 1986-09-06 | IL | other |  | NORTHERN ILLINOIS GAS CO |  | 15000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
495 | 1986-10-11 | AL | other | DUPONT | ALABAMA GAS CORP | CONTRACTOR, USING VERMEER TRENCHING MACHINE TO CUT DITCH FOR TELEPHONE CABLE INSTALLATION, CUT 1.25" PLASTIC GAS SERVICE WITH DIGGING CHAIN. GAS IGNITED, DAMAGEING MACHINE AND INJURING OPERATOR. ALABAMA GAS CORP WAS NOTIFIED OF THE OPERATOR'S HOSPITALIZAT | 5000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
496 | 1986-09-14 | OH | other |  | CINCINNATI GAS & ELECTRIC CO | A FULL CIRCUMFERENTIAL BREAK OCCURED IN HTE GAS MAIN. FOLLOWING THE EXCAVATION A ROCK WAS FOUND BURIED 6" BELOW THE BOTTOM OF THE MAIN. THIS IS BELIEVED TO HAVE BEEN A CONTRIBUTING CAUSE TOGETHER WITH THE PROBABILITY OF HEAVY EXTERNAL DOWNWARD FORCE CAUSE | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
497 | 1986-09-15 | IL | other |  | NORTH SHORE GAS CO | AN OUTSIDE CONTRACTOR BROKE A 2" STEEL MP MAIN, PULLING 10 FEET OUT OF THE GROUND. FOUR HOUSES WERE SHUT OFF AND EIGHT HOUSES WERE EVACUATED. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
498 | 1986-09-25 | SD | other |  | NORTHWESTERN PUBLIC SERVICE CO | HIGH WINDS OR TORNADO TIPPED A NUMBER OF MOBILE HOMES, WITH SEVERAL FALLING ON METERS & REGULATORS. | 300000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
499 | 1986-09-21 | IA | other |  | GREAT RIVER GAS CO | ON 9/21/86, AT APPROXIMATELY 7:25AM, THE OCCUPANT OF 1428 MISSOURI AVE., MR. LARRY EVANS, REPORTED HE AWOKE, PUT HIS DOG OUT ON A CHAIN, RE-ENTERED THE HOUSE, LIT A CIGARETTE, AND AN EXPLOSION OCCURED. THE EXPLOSION COMPLETELY DESTROYED THE DWELLING AND B | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
500 | 1986-09-15 | NE | other |  | METROPOLITAN UTILITIES DISTRICT | SEWER CONTRACTOR EXCAVATING AND STRUCK 1" WRAPPED STEEL GAS SERVICE. PULLED OUTOF COMPRESSION COUPLING UNDERGROUND AT HOUSE. ESCAPING GAS ENTERED HOME AND RESULTED IN EXPLOSION. | 300000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
501 | 1986-08-30 | MI | other | PHILLIPS | CONSUMERS POWER CO | GAS MAIN HIT AND DAMAGED BY BACKHOE EXCAVATING TRENCH FOR WATER DRAIN. GAS IGNITED AND DESTROYED MOBILE HOME. | 51000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
502 | 1986-09-07 | TX | other |  | ENTEX INC | GAS FROM LEAK CAUSED BY STRESS FRACTURES ON THREADED END OF 1 1/4" SERVICES, MIGRATED INTO RESIDENCE. GAS WAS IGNITED WHEN OCCUPANT TURNED ON ELECTRIC LAMP AFTER ENTERING HOUSE. | 70000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
503 | 1986-08-22 | CA | other |  | PACIFIC GAS & ELECTRIC CO | A CONTRACTOR STRUCK OUR 3/4" STEEL SERVICE AND PULLED IT FROM THE 4" MAIN. GAS IGNITED AND A VACANT HOUSE WAS DESTROYED THREE BLOCKS WERE EVACUATED AS A PRECAUT | 171000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
504 | 1986-09-29 | NH | technical failure | DUPONT | GAS SERVICE INC | THE CONTRACTOR INSTALLING THE NEW SERVICE DID NOT INSTALL THE SERVICE PIPE ALL THE WAY INTO THE METER RISER PLASTIC COUPLING. GAS LEAKED INTO THE BUILDING AND WAS IGNITED BY THE WATER HEATER CAUSING AS EXPLOSION AND BRIEF FIRE. | 125000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
505 | 1986-10-21 | TX | other |  | ENERGAS CO | COMBUSTION FIRE AND EXPLOSION OCCURRED THIS MORNING ABOUT 5:00A.M. AT A HOUSE AT 4519 - 42ND ST. THE BODY OF MRS. EDGAR BRASCH WAS FOUND ADJACENT TO THE REAR DOOR IN THE KITCHEN OF THIS RESIDENCE. ACCORDING TO JOHN ANTHONY, FIRE MARSHALL FOR THE LUBBOCK F | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
506 | 1986-09-19 | CA | other |  | SOUTHERN CALIFORNIA GAS CO | OWNER OF PROPERTY, WHILE BACKING VEHICLE OUT OF DRIVEWAY, ALLOWED THE VEHICLE TO STRIKE AND DAMAGE A METER SET ASSEMBLY LOCATED IN AN AREA NOT NORMALLY SUBJECTED TO VEHICULAR TRAFFIC. A 3/4" NIPPLE IMMEDIATELY ABOVE THE SERVICE SHUT OFF VALVE WAS BROKEN A | 150000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
507 | 1986-09-23 | NJ | other |  | PUBLIC SERVICE ELECTRIC & GAS CO | THE CAUSE OF THE EXPLOSION IS UNKNOWN. AN EXPLOSION OF UNKNOWN ORIGIN OCCURRED WHICH COMPLETELY DESTROYED THE HOUSE AT 72 IRVING AVE., AND DAMAGED SURROUNDING PROPERTIES - NO PERSONAL INJURIES. | 150000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
508 | 1986-08-14 | NC | other | UNKNOWN | PUBLIC SERVICE CO OF NORTH CAROLINA | SEWER CONTRACTOR WORKING FOR CITY OF DURHAM, N.C., HIT AP PREVIOUSLY LOCATED SERVICE LINE WITH BACKHOE. GAS LINE SPEARATED AT METER SITE AND NOT A CONTACT POINT. THIS INCIDENT WAS REPORTED TO N.C. UTILITIES COMMISSION ON 8-14-86. AT THE TIME OF INCIDENT T | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
509 | 1986-10-08 | MA | other | WESTBORO MIDDLESEX | COMMONWEALTH GAS CO | CONSTUCTION WORKER WAS POURING GASOLINE INTO RUNNING WATER PUMP. ACCIDENTAL IGNITION OF GASOLINE OCCURRED. WORKER DROPPED GASOLINE CAN INTO EXCAVATION DAMAGING4" PLASTIC PIPE CAUSING ESCAPE AND IGNITION OF NATURAL GAS. | 1500 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
510 | 1986-09-26 | CA | other | ROCKWELL | PACIFIC GAS & ELECTRIC CO | REGULATOR MALFUNCTIONED ALLOWING PRESSURE TO INCREASE. | 70000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
511 | 1986-10-10 | IL | other | UNKNOWN | PEOPLES GAS LIGHT & COKE CO | A 6" STL. MP MAIN WAS PUNCTURED BY A SEWER DEPT. BACKHOE. AS A PRECAUTION, SEVERAL BLDGS. IN THE IMMEDIATE AREA WERE EVACUATED BY THE FIRE DEPT.THERE WAS NO IGNITION. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
512 | 1986-10-16 | WI | other | CONTINENTAL | WISCONSIN FUEL & LIGHT CO | POSSIBILITY OF PROBLEM WITH COUPLING AND/OR SERVICE LINE BEING INVESTIGATED. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
513 | 1986-11-03 | WA | other | UNKNOWN | WASHINGTON NATURAL GAS CO | NARRATIVE DESCRIPTION: CONTRACTOR (AZTECA ENTERPRISES, INC) WAS REMOVING CONCRETE PAVING AS PART OF A STREET REPAIR PROJECT. DURING REMOVAL THEY STRUCK A 3/4" STEEL GAS SERVICE THAT WAS ACCURATELY MARKED; PULLING IT FROM A CURB VALVE LOCATED ABOUT 2' FROM | 150000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
514 | 1986-10-04 | CO | other | PLEXCO/NORMAC | PUBLIC SERVICE CO OF COLORADO | PRELIMINARY INVESTIGATION REVEALED TWO POSSIBLE CAUSES OF THIS INCIDENT (1) A BROKEN 0.75 INCH FUEL PIPE APPROXIMATELY FOUR FEET REST OF THE HOT WATER HEATER IN THE BASEMENT OF 7495 JELLISON CT. THE BREAK WAS ON THE PIPE THREADS ON THE 0.75 INCH SIDE OF A | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
515 | 1986-08-27 | TX | other | PITTSBURG | ENTEX INC | TOMER PIPING. (PRESSURE EXCEEDED ALLOWABLE LIMITS). FURTHER LABORATORY TESTS INDLIMITS). AFTER FURTHER REVIEW OF FIELD DOCUMENTATION OF EVENTS, IT WAS DISCOVERE | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
516 | 1986-10-03 | MO | other |  | LACLEDE GAS CO | METROPOLITAN SEWER DISTRICTS' CONTRACTORS WORK IN STREET DAMAGED SERVICE LINE CAUSED LEAK AT SERVICE 'T' ON MAIN ALLOWING GAS TO MIGRATE INTO BUILDING AND IGNITE. MARKED LOCATION OF MAINS AND SERVICES ON PAVEMENT WITH SPRAY PAINT. | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
517 | 1986-09-25 | TX | other | DISCO PIPE | LONE STAR GAS CO | LINE CUT INTO. LABORER WALKED TO WHERE LINE WAS CUT AND LIT A CIGARETTE CAUSING | 1000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
518 | 1986-11-13 | OH | other |  | CINCINNATI GAS & ELECTRIC CO | THE 12: C.I. MAIN WAS LATER CRADLED BY A CONCRETE DUC ENCASEMENT. THIS DUC WASPART OF THE ELECTRICAL SYSTEM TO CARRY THE ELECTRICAL CONDUIT TO SUPPLY THE HOUSING PROJECT, WHICH WAS OWNED BY THE HOUSING PROJECT. THIS CONDITION ALONG WITHEARTH SETTLEMENT | 20000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
519 | 1986-11-14 | OH | other |  | CINCINNATI GAS & ELECTRIC CO | THE 12" C.I. MAIN WAS LATER CRADLED BY A CONCRETE DUC ENCASEMENT. THIS DUC WASPART OF THE ELECTRICAL SYSTEM TO CARRY THE ELECTRICAL CONDUIT TO SUPPLY THEHOUSING PROJECT, WHICH WAS OWNED BY THE HOUSING PROJECT. THIS CONDITION ALONGWITH EARTH SETTLEMENT AN | 15000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
520 | 1986-11-08 | OH | other |  | CINCINNATI GAS & ELECTRIC CO | CAUSE WAS DUE TO TRAIN DERAILMENT. THE WEIGHT OF THE TRAIN CARS PUSHED RAILROAD MAINTENANCE EQUIPMENT INTO SOFT GROUND. IT APPEARS WHEEL OF CRUSHED MAINTENANCE EQUIPMENT IMPEDED ITSELF IN SOFT GROUND STRIKING AND BREAKING C.I. MAIN. | 250000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
521 | 1986-11-07 | PA | other |  | EQUITABLE GAS CO | THE EQUITABLE GAS EMPLOYEES WERE TAPPING A 6" MAIN LINE IN A 3 1/2' DEEP EXCAVATION TO DRAIN WATER FROM THE MAIN LINE. WHILE INSTALLING A DOUBLE SADDLE, A SURGE OF WATER SQUIRTED OUT FROM UNDER THE LOOSE SADDLE AND HIT A UTILITY LIGHT ADJACENT TO THE EXC | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
522 | 1986-11-12 | PA | other |  | EQUITABLE GAS CO | EQUITABLE GAS EMPLOYEE WAS PURGING A HOUSELINE IN A SMALL UTILITY ROOM AT 2701 WEST CARSON STREET WHEN GAS IGNITED (UNKNOWN SOURCE) CAUSING A BRIEF FLASH FIRE. ONE EMPLOYEE WAS ADMITTED TO MERCY HOSPITAL ON 11/12/86 WITH BURNS TO THE FOREHEAD AND EARS. H | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
523 | 1986-11-25 | NE | other |  | METROPOLITAN UTILITIES DISTRICT | ON ARRIVAL, FIREMAN REPORTED GAS ODOR. COMPANY SERVICEMAN SHUT OFF METER INSIDE BASEMENT. INSPECTION REVEALED OPEN FUEL LINE TO KITCHEN RANGE. AFTER FIRE, METER TURNED BACK ON MOMENTARILY TO CONFIRM SUPPLY THRU OPEN FUEL LINE. SHUT METER OFF & CAPPED LINE | 35000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
524 | 1986-11-11 | OH | other |  | COLUMBIA GAS OF OHIO INC | OCUPANT WAS REMOVING OLD COAL FURNACE FROM BASEMENT OF DWELLING. LOST CONTROL OF FURNACE WHICH FELL AGAINST GAS LINE WHERE IT CAME THROUGH BASEMENT WALL AND TURNED TO ENTER THE INLET OF GAS METER. ESCAPING GAS EXPLODED. LINE BROKE AT APPROXIMATELY 1251 | 25000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
525 | 1986-11-24 | LA | other | PLEXCO | LOUISIANA GAS SERVICE CO | SERVICE LINE WAS CUT BY DIGGING MACHINE. GAS IGNITED AND BURNED DIGGING MACHINE. NO INJURY TO OPERATOR. | 8500 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
526 | 1986-12-03 | NY | other |  | CONSOLIDATED EDISON CO OF NEW YORK | GAS LEAKAGE IN BASEMENT APARTMENT RESULTED FROM BROKEN FLEXIBLE TUBING CONNECTION AT CUSTOMER'S COUNTER-TOP RANGE. BREAK APPARENTLY THE RESULT OF IMPACT FROM UTENSIL DRAWER UNDER COUNTER-TOP TANGE. EXPLOSION AND FLASH FIRE OCCURRED WHEN CUSTOMER LIT CIGAR | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
527 | 1986-12-07 | IL | maintenance |  | ILLINOIS POWER CO | AT 3:25 A.M. ON DECEMBER 7, 1986, ILLINOIS POWER COMPANY WAS NOTIFIED BY THE CAHOKIA POLICE DEPARMENT THAT GAS WAS "SPEWING" OUT OF THE STREET AT 100 ST. THOMAS LANE ON CAHOKIA. AT 3:31 A.M., THE CAHOKIA POLICE CALLED AGAIN REPORTING THAT THE HOUSE AT 101 | 54500 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
528 | 1986-11-27 | OH | other |  | EAST OHIO GAS CO | WATER FLOODED VAULT CAUSING REGULATORS AND RELIEF VALVE TO MALFUNCTION. REGULATORS WERE NOT VENTED. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
529 | 1986-11-26 | KS | other |  | MIAMI PIPE LINE CO | HOUSTON CONTRACTING SEVERED LINE WHILE LAYING TELEPHONE CABLE. | 500 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
530 | 1986-11-24 | AR | other | NIPAK | ARKANSAS LOUISIANA GAS CO (ARKLA GAS CO) | THIRD PARTY CONSTRUCTION COMPANY HAD EXCAVATED AROUND AND BENEATH THE GAS SERVICE LINE SERVING 2521 S. MARTIN. IN THE PROCESS OF BACK FILLING THE EXCAVATION, ALOAD OF DIRT FROM A FRONT END LOADER OF A BACK-HOE WAS DUMPED INTO THE EXCAVATION ON TOP OF THE | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
531 | 1986-11-21 | TX | other | FISHER | ENTEX INC | REGULATOR WAS BROKEN BY UNKNOWN PARTY, OVERPRESSURING HOUSELINE. IGNITION UNKNOWN. DAMAGE APPARENTLY CAUSED BY CAR HITTING METER LOOP | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
532 | 1986-05-25 | CA | other |  | PACIFIC GAS & ELECTRIC CO | STRUCTURE FIRE BURNED OUT FLANGE GASKET BETWEEN SERVICE RISER VALVE AND FILTER ON METER SET. ESCAPING GAS IGNITED. | 502600 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
533 | 1986-08-21 | TX | other | PITTSBURG | ENTEX INC | INITIAL FIELD TEST REPORTS INDICATED REGULATOR ALLOWED EXCESSIVE PRESSURE ON CUSTOMER PIPING. (PRESSURE EXCEEDED ALLOWABLE LIMITS.) FURTHER LABORATORY TESTS INDICATED REGULATOR FUNCTIONED PROPERLY. (NORMAL LOCK-UP PRESSURE WITHIN ALLOWABLELIMITS.) AFTER F | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
534 | 1986-12-10 | CA | other |  | PACIFIC GAS & ELECTRIC CO | A CONTRACTOR WORKING FOR THE CUSTOMER HAD REMOVED THE ORIGINAL VENT ON THE FLOORFURNACE AND COVERED THE OPENING WITH SHEET METAL. A NEW VENT WAS INSTALLED ON THE OTHER SIDE OF THE FURNACE BUT IT DID NOT EXTEND INTO THE COMBUSTION CHAMBER.THE ORIGINAL VENT | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
535 | 1987-01-05 | IL | other | NATIONAL U.S.A. | WESTVILLE GAS COMMISSION | CINTRACTOR FAILED TO NOTIFY WESTVILLE GAS & WATER SYSTEMS FOR LOCATION OF UTILITIES. CONTRACTOR DID NOT HAVE THE REQUIRED BUILDING PERMIT. CONTRACTOR WAS DIGGING A FOOTING TRENCH AT REAR OF HOUSE PRIOR TO BUILDING AN ADDITION TO THE HOUSE ON SAME LOCATION | 70000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
536 | 1986-12-22 | AL | other |  | JACKSONVILLE GAS & WATER BOARD | ON DECEMBER 22, 1986 AT APPROXIMATELY 2200 HOURS I WAS NOTIFIED BY BEEPER TO CUT THE GAS OFF AT 1314 SOUTH CHURCH STREET, JACKSONVILLE ALABAMA DUE TO A FIRE ONTHE SERVICE LINE. I ARRIVED APPROXIMATELY FIFTEEN MINUTES LATER AND DUG UP THE SERVICE LINE AND | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
537 | 1986-11-25 | MN | other | ALDYL-A | NORTHERN STATES POWER CO | LEAK OCCURRED WHEN CABLE TV COMPANY HIT 2" PLASTIC MAIN GAS TRAVELLED UNDERGROUND TO 3 HOUSES: ONE HOUSE EXPLODED; OTHER HOUSES EVACUATED AND MONITERED | 1200 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
538 | 1987-01-10 | NJ | other | INNERTITE | ELIZABETHTOWN GAS CO | CIRCUMFERENTIAL CRACK ON 4" CAST IRON ELEVATED PRESSURE MAIN. APPROXIMATELY 30'FROM HOUSE. | 1000000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
539 | 1986-12-13 | TX | technical failure |  | LONE STAR GAS CO | FOUND 1/2" POLY PIPE PULLED OUT OF COMPRESSION COUPLING AT INLET RISER WHICH SETAT THE HOUSE. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
540 | 1986-12-22 | OH | other |  | HAMILTON GAS DEPT, CITY OF | THE CITY OF HAMILTON HAS 6" CAST IRON MAIN CARRYING APPROXIMATELY 33 P.S.I. NATURAL GAS ON RIVER RD. PAST THE MAGIE AVE. INTERSECTION. CINCINNATI GAS AND ELECTRIC HAS A 4" STEEL MAIN PARALLEL WITH OUR MAIN APPROXIMATELY 4' AWAY. AFTER DETERMINING WHERE A | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
541 | 1986-12-25 | PA | other |  | PHILADELPHIA ELECTRIC CO | SIX INCH CAST IRON MECHANICAL JOINT PIPE WAS UNDER MONOLITHIC CURB AND GUTTER INSTALLED SUBSEQUENT TO MAIN INSTALLATION. SUDDEN CIRCUMFERENTIAL BREAK IN SIX INCH CAST IRON MECHANICAL JOINT MAIN APPARENTLY LED TO GAS MIGRATION INTO 449 W. MONUMENT AVENUE, | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
542 | 1986-12-15 | PA | other |  | PHILADELPHIA ELECTRIC CO | SUBSIDENCE OCCURRED ALONG THE SEWER LATERAL TRENCH TO 900 SUMMIT LANE UNDER THEFOUR INCH MECHANICAL JOINT CAST IRON PIPE. SUDDEN CIRCUMFERENTIAL BREAK IN A FOUR INCH MECHANICAL JOINT CAST IRON PIPE APPARENTLY LED TO GAS MIGRATION INTO3902 SUMMIT LANE, RES | 300000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
543 | 1987-01-03 | OH | other |  | CINCINNATI GAS & ELECTRIC CO | COMPANY RECEIVED A REPORT OF GAS ODOR. COMPANY PERSONNEL RESPONDED AND FOUND BUILDING DESTROYED BY EXPLOSION. UPON INVESTIGATION COMPANY FOUND A CIRCUMFERENTIALBREAK IN A 6" C. I. MAIN AND REPAIRED SAME. CAUSE IS UNKNOWN AT THIS TIME. STILL UNDER INVESTIG | 120000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
544 | 1986-12-09 | MI | other |  | MICHIGAN CONSOLIDATED GAS CO (MICHCON) | AUTOMOBILE RAN INTO THE BUILDING AND SHEARED OFF THE SERVICE LINE AT THE OUTSIDE BEND, BELOW THE SERVICE LINE SHUT OFF. | 55000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
545 | 1987-01-24 | OH | other |  | COLUMBIA GAS OF OHIO INC | INLET SERVICE LINE RISER BROKEN IN 90_ ELL WHERE IT COMES THROUGH FOUNDATIONS AS A RESULT OF GROUND MOVEMINT DUE TO FROST CONDITIONS, GAS IGNITED. PERSONAL INJURY WAS TO FACE, HANDS, AND HAIR OF ROY STEELE RELEASED ON 1/26/87 FROM HOSPITAL. | 25000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
546 | 1987-01-25 | NY | other | PHILIPS | NIAGRA MOHAWK POWER CORP |  | 500000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
547 | 1987-01-23 | GA | other | RELIANCE | ATLANTA GAS LIGHT CO | DURING FREEZING WEATHER WATER DRIPPING FROM A CUSTOMER'S ROOF COATED THE GAS REGULATOR WITH ICE PLUGGING THE VENT. THE REGULATOR THEN MALFUNCTIONED WHICH RESULTED IN THE HOUSE FIRE. TURNED OFF BY FIRE DEPT. PRIOR TO OUR ARRIVAL ON SITE. | 10000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
548 | 1987-02-03 | PA | other |  | PHILADELPHIA GAS WORKS | ON FEBRUARY 3, 1987, AT 3029 "F" STREET, A FIRE OCCURRED AT THIS RESIDENCE ON WHICH MR. W. TORRANCE BURNT HIS HAND AND HAIR. EXACT DETAILS OF THIS INCIDENT PRIOR TO 9:30 A.M. RELATE TO AN OBSERVATION OF THE SITE AND STATEMENTS MADE TO CUSTOMER SERVICE SUP | 20000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
549 | 1987-01-29 | MS | other |  | MOSS POINT MUNICIPAL GAS SYSTEM, CITY OF | CAMBELL CONSTRUCTION COMPANY WERE LAYING A 24" SEWER FORCE MAIN FOR THE REGIONALWASTEWATER AUTHORITY EAST ON JEFFERSON STREET. WHEN CROSSING OUR 2 INCH GAS MAIN, THERE BACKHOE OPERATOR PULLED UP ON THE 2" GAS MAIN TO INSTALL THEIR PIPE UNDER THE GAS MAIN. | 50 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
550 | 1986-12-14 | MI | other |  | MICHIGAN CONSOLIDATED GAS CO (MICHCON) | O EVIDENCE OF EARTH MOVEMENT. | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
551 | 1987-01-10 | UT | other | SPRAGUE | MOUNTAIN FUEL SUPPLY CO | AT 2040 HOURS ON JANUARY 10, 1987, A VEHICLE THAT WAS TRAVELING SOUTH ON THE WEST SIDE OF STATE STREET AT 4905 SOUTH TURNED LEFT CROSSING A 24" WIDE X 4" HIGH MEDIAN STRIP AND THREE LANES OF ONCOMING TRAFFIC AND THEN RAN INTO A BUILDING ONEAST SIDE OF STR | 550000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
552 | 1987-01-14 | AR | other |  | ARKANSAS LOUISIANA GAS CO (ARKLA GAS CO) | ON JANUARY 14, 1987 AT APPROXIMATELY 5:15 A.M AN EXPLOSION OCCURRED AT 5621 SHAMROCK DRIVE NORTH LITTLE ROCK, AR DESTROYING THE RESIDENCE. A COLD BREAK WAS FOUND IN A 2" CAST IRON GAS MAIN IN FRONT OF THE HOUSE. | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
553 | 1987-02-06 | CO | other |  | COLORADO SPRINGS, CITY OF | LEAKING NATURAL GAS MIGRATED INTO A WATER REGULATOR VAULT; WORKERS ENTERED THE NEWLY CONSTRUCTED VAULT TO INSPECT THE CONSTRUCTION AND WERE INJURED FROM A FLASHFIRE. THE PROBABLE CAUSE OF THE FIRE WAS A MATCH STRUCK BY ONE OF THE WORKERS. THE GAS DIVISION | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
554 | 1987-01-29 | CA | other |  | SOUTHERN CALIFORNIA GAS CO | AN EMPLOYEE OF THE OPERATOR SUFFERED BURNS WHEN GAS BEING USED TO PURGE AIR FROM A NEWLY REPLACED 3/4" STEEL SERVICE IGNITED. SERVICE WAS PRESSURED TO ONE HUNDRED TEN(110) PSIG. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
555 | 1987-02-20 | PA | other | AMER.-SINGER | PENNSYLVANIA GAS & WATER CO | ON FRIDAY, FEBRUARY 20, 1987, A FIRE, SUSPECTED TO BE ARSON, DESTROYED TWO STORES AND BADLY DAMAGED A THIRD IN THE BUSINESS DESTRICT OF BERWICK, PENNSYLVANIA. THE TOTAL MARKET VALUE OF THE THREE BUILDINGS WAS PLACED AT $310,000.00 BASED ONASSESSED VALUATI | 310000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
556 | 1987-02-22 | LA | other |  | LOUISIANA GAS SERVICE CO | CRESCENT CONSTRUCTION COMPANY, SUB CONTRACTOR FOR GRADY CRAWFORD CONSTRUCTION COMPANY, DUG AND SHEETED A TRENCH APPROXIMATELY 11' DEEP AND 4' WIDE AND CROSSINGOUR 6" C.I.-L.P. GAS MAIN ON A 45 DEGREE ANGLE AT A POINT 46' SOUTH OF METAIRIEON THE WEST SIDE | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
557 | 1987-02-19 | NJ | other |  | PUBLIC SERVICE ELECTRIC & GAS CO | A FIRE, OF UNKNOWN ORIGIN, DESTROYED A SINGLE FAMILY FRAME HOUSE. NO GAS LEAKAGEWAS FOUND. THERE WERE NO FATALITIES OR PERSONAL INJURIES. | 150000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
558 | 1987-02-06 | TX | other |  | ENERGAS CO | CUSTOMER WAS REMOVING RANGE FROM HOUSE. HE TURNED OFF WHAT HE BELIEVED WAS THE METER SERVING THE HOUSE, BUT HE TURNED OFF THE METER TO ANOTHER CUSTOMER LEAVINGHIS GAS ON. HE WENT BACK INTO THE HOUSE AND BEGAN TO REMOVE THE COOK STOVE. WHEN HE DISCONNECTED | 1000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
559 | 1987-01-30 | TX | other | AMER.MTR.CO. | ENTEX INC | CAR STRUCK METER, ESCAPING GAS IGNITED AND BURNED ADJACENT BUILDING. | 5000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
560 | 1987-02-13 | TX | other |  | SOUTHERN UNION GAS CO | RAILROAD COMMISSION WAS UNDULY NOTIFIED DUE TO THIS EXPLOSION BEING DOWNSTREAM OF THE METER. RESIDENT WAS THOUGHT TO BE ATTEMPTING TO COMMIT SUICIDE BY RELEASING NATURAL GAS. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
561 | 1987-02-10 | MN | other |  | WARREN GAS DEPT, CITY OF | WE WERE IN THE PROCESS OF TESTING RELIEF VALVES AT THE TOWN REGULATING STATION WHEN THE MAN WE HAD HIRED ASKED ME TO SHUT DOWN THE MAIN VALVES FOR THE TOWN SO HE COULD HEAR THE RELIEF VALVE START TO OPEN. THE VALVE WOULD NOT OPERATE SO HE TOLD ME TO GET A | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
562 | 1987-01-30 | CO | maintenance |  | COLORADO SPRINGS, CITY OF | AFTER IDENTIFYING A LEAK LOCATION ON AN UNDERGROUND GAS MAIN, GAS DIVISION PERSONNEL EXCAVATED TO PINPOINT THE LEAK ON THE PIPELINE. WHILE ATTEMPTING TO PIN POINT THE LEAK, THE LEAKING GAS WAS IGNITED BY AN UNKNOWN SOURCE. FOUR GAS DIVISION EMPLOYEES SUFF | 44000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
563 | 1987-02-18 | MA | other |  | COMMONWEALTH GAS CO | FIRE DEPARTMENT INFORMED RESPONSIBLE SERVICE PERSON THAT THERE WAS A POSSIBLE EXPLOSION. COM/GAS IS INVESTIGATING. PLUMBING CONTRACTOR WORKING ON SITE.(CONTINENTAL PLUMBING COMPANY) | 5000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
564 | 1987-02-19 | MI | other |  | MICHIGAN CONSOLIDATED GAS CO (MICHCON) | THE CAUSE OF THE CIRCUMFERENTIAL FRACTURE IN THE 4" CAST IRON MAIN IS UNKNOWN; NO EVIDENCE OF EARTH MOVEMENT | 75000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
565 | 1987-02-08 | CA | other |  | PACIFIC GAS & ELECTRIC CO | GASOLINE IN GARAGE SPREAD TO WATER HEATER PILOT LIGHT, IGNITING GASOLINE. RESULTING FIRE SPREAD TO METER SET, DESTROYING REGULATOR AND METER, IGNITING NATURAL GAS. | 150000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
566 | 1987-02-23 | LA | other | PLEXCO | LOUISIANA GAS SERVICE CO | SERVICE LINE WAS CUT BY DIGGING MACHINE. GAS IGNITED AND BURNED DIGGING MACHINE. NO INJURY TO OPERATOR OR OTHERS. CUT 3/4" GAS SERVICE LINE WHILE INSTALLING TVCABLE. | 4500 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
567 | 1987-02-16 | GA | maintenance |  | ATLANTA GAS LIGHT CO | 3/4" SERVICE CROSSED SEVERAL OTHER UTILITIES IN THE AREA.(SOUTHERN BELL TELEPHONE DUCT, 2" GALVANIZED WATER LINE, 4" TRANCITE WATER LINE, SOUTHERN BELL DIRECT BURIAL CABLE, 2 PLASTIC WATER SERVICES, 18" CONCRETE STORM DRAIN). GAS WAS LEAKING FROM A SERVIC | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
568 | 1987-02-12 | AZ | other |  | SOUTHWEST GAS CORP | THE PIPE BEARS DAMAGE MARK WHICH APPEARS TO BE THE CAUSE OF THE FAILURE. IT IS NOT KNOWN IF THE DAMAGE OCCURRED UPON INSTALLATION OR WHEN A CROSSING SUBSTRUCTURE WAS SUBSEQUENTLY INSTALLED. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
569 | 1987-02-19 | SC | technical failure |  | SOUTH CAROLINA ELECTRIC & GAS CO | ON FEBRUARY 19, 1987 SERVICE TO APPROXIMATELY 2,500 GAS CUSTOMERS IN COLUMBIA, SOUTH CAROLINA WAS INTERRUPTED. THE PROBLEM APPEARS TO HAVE ORIGINATED IN THE MIXING OPERATION OF A PROPANE AIR PLANT BEING CONSTRUCTED AND INSTALLED FOR US. FOR A SHORT PERIOD | 30000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
570 | 1987-03-14 | LA | other |  | NEW ORLEANS PUBLIC SERVICE INC | A 4' WIDE X 10' DEEP TRENCH CROSSING THE GAS MAIN HAD BEEN OPENED BY AN OUTSIDEPARTY FOR INSTALLATION OF A SEWER LINE AND BACKFILLED TWO DAYS PRIOR TO THE INCIDENT. THE ACTUAL BREAK IN THE GAS MAIN WAS LOCATED APPROXIMATELY 10' FROM THE CENTER OF THE AFOR | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
571 | 1987-03-01 | TX | other |  | ENERGAS CO | DRIVER OF PICKUP LOST CONTROL OF VEHICLE. HIT METER SETTING. FIRE DESTROYED PICKUP AND METER. | 5000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
572 | 1987-01-27 | TX | technical failure |  | SOUTHERN UNION GAS CO | CONTRACTOR WAS ATTEMPTING TO STOPPER OFF A SECTION OF EXPOSED MAIN DOWNSTREAM OF A DRESSER COUPLING. THE STOPPERING EQUIPMENT WAS NOT SECURELY ANCHORED AND THEPIPE PULLED LOOSE FROM THE DRESSER COUPLING AND IGNITED. | 30000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
573 | 1987-02-27 | TX | other | REPUBLIC STEEL | SOUTHERN UNION GAS CO | A CONSTRUCTION COMPANY EMPLOYEE WAS CUTTING GRADE WITH A FRONT-END LOADER WHEN HE HIT A 4" STEEL MAIN PRODUCING A 2" HOLE. THERE WAS NO IGNITION OF GAS AND NO INJURIES. | 1555 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
574 | 1987-02-24 | TX | other | REPUBLIC STEEL | SOUTHERN UNION GAS CO | AUTOMOBILE STRUCK METER AT 1278 RARM ROAD 1110 AT 12:30 A.M. ON FEBRUARY 24, 1987. THE 3/4" SERVICE RESER WAS BROKEN ON THE INLET SIDE OF THE SERVICE VALVE, RESULTING IN THE ESCAPE OF GAS. IGNITION OCCURRED AND THE AUTOMOBILE WAS DESTROYED. NO INJURIES OR | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
575 | 1987-03-11 | KY | other | DRISCOPIPE 6500 | DELTA NATURAL GAS CO INC | DELTA'S SOUTHERN CONSTRUCTION CREW CONSISTING OF CARL COX, FOREMAN, SHELBY SMITH, ELBERT BARGO, CLARENCE ABNER, HERMAN BROUGHTON, AND CHARLES LAMBDIN WAS REPLACING APPROXIMATELY FIVE HUNDRED(500) FEET OF FOUR(4) INCH STEEL MAIN WITH FOUR(4) INCH PLASTIC M | 1200 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
576 | 1987-05-08 | AL | other |  | ALABAMA GAS CORP | SOMEONE DISCONNECTED AN APPLIANCE AND THEN TURNED THE APPLIANCE VALVE TO THE OPEN POSITION. GAS IGNITED DESTROYING THE CUSTOMERS'S HOUSE AND INJURING THE CUSTOMER. THE BIRMINGHAM FIRE DEPARTMENT NOTIFIED ALABAMA GAS CORPORATION THAT THE CUSTOMER HAD BEE | 20000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
577 | 1987-04-17 | CA | other |  | PACIFIC GAS & ELECTRIC CO | FIRE STARTED BY UNKNOWN PARTY IN BASEMENT BELOW GAS METER CABINET, DAMAGING METERS AND ALLOWING GAS TO ESCAPE AND IGNITE. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
578 | 1987-04-09 | SD | other |  | MONTANA - DAKOTA UTILITIES CO | UKNOWN - RAPID CITY FIRE DEPARTMENT INVESTIGATION REPORT ATTACHED | 7500 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
579 | 1987-03-01 | TX | other |  | ENERGAS CO |  | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
580 | 1987-04-16 | TX | other |  | ENERGAS CO | BURNING TRASH AND WEEDS IN CLOSE PROXIMITY TO DAMAGED METER AND IGNITED THE ESCAPING | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
581 | 1987-03-06 | TX | other |  | ENERGAS CO | CLOTHES ON FLOOR IGNITED FROM OPEN FLAME OF SPACE HEATER. | 10000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
582 | 1987-03-31 | TX | other |  | ENERGAS CO | GAS ACCUMULATED UNDER FLOOR OF OUSE AND EXPLODED DESTROYING HOUSE AND DAMAGINGSEVERAL OTHER HOUSE NEARBY | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
583 | 1987-03-17 | KS | other | PHILLIPS | K P L GAS SERVICE | APPARENT FAILURE OF FUSION WELD THE CAUSE OF WHICH IS UNKNOWN AT THIS TIME. | 150000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
584 | 1987-04-12 | LA | other |  | NEW ORLEANS PUBLIC SERVICE INC | WHILE TRAVELING DOWN FLORIDA AVENUE, THE DRIVER OF AN AUTOMOBILE LOST CONTROL STRIKING AN ABOVE GROUND 3" HIGH PRESSURE GAS CANAL CROSSING, CAUSING THE PIPE TORUPTURE WHICH REQUIRED IMMEDIATE REPAIR | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
585 | 1987-04-14 | IL | maintenance |  | NORTHERN ILLINOIS GAS CO | A LEAKING SOURCE OF NATURAL GAS CAUSED AN EXPLOSION AND FIRE. | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
586 | 1987-04-06 | IL | other |  | NORTHERN ILLINOIS GAS CO | NORTHERN ILLINOIS GAS COMPANY PERSONNEL WERE RESPONDINGTO AN EMERGENCY CALL AT THE INTERSECTION OF MADISON AND MONTEREY, VILLA PARKA SEWER CONTRACTOR WAS EXCAVATING AND PULLED AND DAMAGES ASTEEL TWO INCH GAS MAIN. THE GAS IGNITED ABOVE GROUND, RESULTING | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
587 | 1987-03-15 | OR | other | R W LYALL | NORTHWEST NATURAL GAS CO | A SEWER CONTRACTOR LAYING A 72" STORM SEWER WAS CROSSING OUR 4" STEEL MAIN AND 1' PE SERVICE WITH A LARGE TRACK HOE. THE TRAC HOE CROSSING THE SERVICE VALVE CAUSED SOIL SUBSIDENCE, PUSHED THE VALVE BOX DOWN ENOUGH TO CREATE A CRACK IN THEBOTTOM QUADRANT | 300000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
588 | 1987-03-23 | AZ | technical failure | PHILLIPS | SOUTHWEST GAS CORP | CONTRACTOR EMPPLOYEE WAS PURGING A NEWLY INSTALLED 2" 3408 P.E. MAIN WHEN IGNITION COCCURRED CAUSING BURNS TO EMPLOYEE.THEMAIN BEING PURGED WAS BELOW GROUND AND IN A HORIZANTAL POSITION AND FLOW WASBEING CONTROLLED WITH WITH A PIPE SQUEEZING TOOL CONTROLL | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
589 | 1987-08-04 | NE | other | ROCKWELL NORDSTRUM | METROPOLITAN UTILITIES DISTRICT | WILSON CONCRETE WORKERS LOADING SAND KNOCKED OVER CONCRETE SLAB WALL BURYING THE ABOVE GROUND 2# 1ST CUT REGULATOR AND SERVICE VALVE. THE PIPE REMAINED INTACT.THE SERVICE VALVE WAS SEVERED THROUGH THE BODY : 1" ROCKWELL VALVE (FLANGED). NO FIRE OR EXPLOS | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
590 | 1987-07-31 | IL | other | PLEXCO | INTERSTATE POWER CO | EMPLOYEES WERE FUSING A POLYETHELENE PUNCH-IT TEE TO A 2" POLYETHELENE GAS MAIN. DURING FUSION OF THE TWO, THE GAS BEGAN TO LEAK BENEATH THE TEE DISCHARGING THROUGH THE SERVICE CONNECTION END. THIS GAS IGNITED, BURNING BOTH EMPLOYEES. | 2000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
591 | 1987-06-26 | NY | other |  | COLUMBIA GAS OF NEW YORK INC | A 6" COATED STEEL MAIN OPERATING AT 17 PSIG AND 32" DEEP, LOCATED BENEATH A STREET SIGN, WAS DAMAGED BY APPROXIMATELY 12,000 VOLTS THAT TRAVELED FROM A SEVEREDOVERHEAD POWER LINE THROUGH THE STREET SIGN AND ARCED ONTO THE MAIN CAUSING THREE 1" HOLES. GAS | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
592 | 1987-06-26 | TX | other | UNIVERSAL CONTROL | ENTEX INC | THE OUTSIDE PARTY SET A TRASH DUMPSTER DOWN ON THE REGULATOR WHICH KNOCKED THE REGULATOR OFF AND SENT LINE PRESSURE INTO THE HOUSE. A FIRE BROKE OUT AT WATER HEATER IN UTILITY ROOM RESULTING IN APPROXIMATELY $40,000.00 IN DAMAGES. | 40000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
593 | 1987-07-01 | TX | other |  | ENERGAS CO | A CUSTOMER CALLED INTO THE PAMPA ENERGAS OFFICE AT 9:31 A.M. SAYING HE SMELLED GAS NEAR HIS CLOTHES DRYER.THE ORDER WAS DISPATCHED TO A SERVICE TECHNICIAN BY RADIO AT 9:32 A.M.THE SERVICE TECHNICIAN ARRIVED AT 845 E. FREDERICK AT 9:35 A.M.BETWEEN THE TIME | 500 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
594 | 1987-07-07 | FL | other |  | SAWYER GAS INC | EMPLOYEE WAS IN PROCESS OF RELOCATING METER RISER AND REJOINING TO MAIN LINE. EMPLOYEE APPARENTLY PASSED OUT AND WAS FOUND BY RESIDENTS IN AN UNCONSCIOUS STATE. EMPLOYEE WAS HOSPITALIZED ON 7/7/87, AND WAS DECLARED DEAD ON 7/11/87 | 10 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
595 | 1987-06-06 | RI | maintenance |  | PROVIDENCE GAS CO | BELL JOINT CLAMP BOLT CORRODED AND FAILED, CAUSING LEAKING OF INTERMEDIATE PRESSURE GAS WHICH MIGRATED TO MANHOLE. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
596 | 1987-06-02 | NC | other | PHILLIPS | PIEDMONT NATURAL GAS CO INC | FROM INFORMATION I CAN RECEIVE, LIGHTNING STRUCK TRANSFORMER AROUND 7:30 PM, JUNE 1, 1987. DUKE POWER CREW REMOVED TRANSFORMER TO INSTALL NEW ONE; IN THE PROCESS OF SPLICING IN NEW WIRES, CREWMAN USED IMPACT WRENCH TO TIGHTEN SPLIT BOLT NUTS, IGNITION SOU | 5000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
597 | 1987-06-27 | TN | other |  | CROCKETT PUBLIC UTIL DIST | MRS. FORSYTHE INFORMED ME THE CAR ROLLED INTO THE GAS METTER AND BROKE THE GAS PIPE. AT THIS TIME THEY COULD DETECT THE SMELL OF GAS AND HEAR THE GAS ESCAPING FROM THE BROKEN PIPE SO THEY ATTEMPTED TO PUSH THE CAR ASIDE BY HAND. THIS WAS IMPOSSIBLE SO MR. | 15000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
598 | 1987-05-31 | CA | other |  | PACIFIC GAS & ELECTRIC CO | BRUSH FIRE DESTROYED 32 HOMES; ENSUING STRUCTURE FIRE DESTROYED METERS AND REGULATORS. 28 OTHER STRUCTURES HAD THEIR SERVICE. | 75000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
599 | 1987-06-08 | CA | other |  | PACIFIC GAS & ELECTRIC CO | STRUCTURE FIRE OF UNKNOWN ORIGIN DAMAGED HOUSELINE, ALLOWING GAS TO ESCAPE & IGNITE. BUILDINGS WERE EVACUATED & TRAFFIC REROUTED. | 1000000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
600 | 1987-06-17 | TX | other |  | ENERGAS CO | TWO PICKUPS COLLIDED AT RURAL INTERSECTION. THE VEHICLES HIT TWO METTER SETTINGS AT NW CORNER OF INTERSECTION. | 25000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
601 | 1987-05-29 | AZ | other |  | CITIZENS UTILITY CO | PART B # 3A GAS METER THAT WAS INACTIVE WAS OPENED BY PERSONS UNKNOWN. THE HOUSE WAS FILLED WITH GAS. AN UNKNOWN SOURCE OF IGNITION CAUSED THE EXPLOSION.SEE NARRATIVE! | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
602 | 1987-06-16 | IL | other |  | NORTHERN ILLINOIS GAS CO | ON JUNE 16, 1987, TWO AURORA WATER DEPARTMENT EMPLOYES MISTOOK A GAS MAIN FOR AWATER MAIN AND DRILLED INTO THE 16" MAIN ON RANDALL ROAD, AURORA, THE INCIDENT RESULTED IN A FIRE, CAUSING PERSONAL INJURY TO THE TWO CITY EMPLOYES. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
603 | 1987-04-09 | CA | other | SPRAGUE | PACIFIC GAS & ELECTRIC CO | DRIVER OF AUTOMOBILE WAS BEING PURSUED BY POLICE IN A HIGH SPEED CHASE, LOST CONTROL AND HIT A RESIDENTIAL GAS METER SET, ALLOWING GAS TO ESCAPE AND IGNITE. BUILDINGS WERE EVAUATED & TRAFFIC REROUTED. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
604 | 1987-06-22 | MD | other |  | WASHINGTON GAS LIGHT CO | INFORMATION PROVIDED BY COMPANY RECORDS, FIRE MARSHALL HARDING AND BACKHOE OPERATOR THOMAS. SHORTLY BEFORE 1:30 P.M. ON 6/22/87 THE VENTURE GROUP WAS DIGGING IN A FOOTING TO INSTALL A STOOP AT THE FRONT BUILDING WALL OF 10704 STANMORE DR.,MONT. CO., MARYL | 500000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
605 | 1987-04-16 | AZ | technical failure |  | SOUTHWEST GAS CORP | A 2" WILLIAMSON 3-WAY TEE WAS BEING WELDED TO A 2" STEEL MAIN APPROXIMATELY 18"FROM AN ABS TO STEEL TRANSITION FITTING. THE FLOW OF GAS IN THE PIPELINE WAS FROM THE STEEL TO PLASTIC MAIN AND IN THIS CASE THE GAS WAS HEATED AS IT PASSED THE STEEL MAIN ON W | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
606 | 1987-09-05 | WY | other |  | NORTHERN UTILITIES INC | THE ATTACHED REPORT COVERS AN INCIDENT THAT OCCURRED ON A 2" HIGH PRESSUREDISTRIBUTION REGULATOR SETTING IN RIVERTON, WYOMING ON SEPTEMBER 5, 1987. IGNITION DID OCCUR AND SEVERE BURN INJURIES WERE SUSTAINED BY A THIRD PARTY AS A RESULT OF THE LEAK. SERVIC | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
607 | 1987-08-31 | MN | other |  | IOWA ELECTRIC LIGHT & GAS POWER CO | (THIRD PARTY) CAUSE OPERATOR HIT 1" LINE STOPPER ON TOP OF 4" GAS MAIN. EQUIPMENT (OPERATOR) LARGE BACKHOE.PART D:HODGMAN CONSTRUCTION COMPANY WAS TAKING OUT THE OLD CONCRETE SURFACE IN THE ALLEY BETWEEN 1ST & 2ND STREET, DOWNTOWN PLAZA AND N. PARK ST. FA | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
608 | 1987-08-24 | DC | technical failure |  | WASHINGTON GAS LIGHT CO | ON AUGUST 24, 1987 AT APPROXIMATELY 3:00 P.M. A WGLCO CONSTRUCTION CREW HAD JUSTTIED-IN A 12" WRAPPED STEEL MAIN. TWO 4" C.I. MAINS WERE TO BE ABANDONED AS PART OF THE JOB AND WERE BEING PURGED BY NITROGEN. THE NITROGEN INJECTION POINT WASLOCATED 300' +/- | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
609 | 1987-07-17 | TX | other |  | ENERGAS CO | AT 12:46 P.M. ON JJULY 14, 1987, WE RECEIVED A CALL OF A STRONG GAS SMELL AT 1928 E. AUBURN. OUR SERVICEMAN, RONNIE SALMON TURNED THE GAS OFF AND LOCKED AND BLINDED THE METER. NO ONE WAS AT HOME.ON JULY 16, 1987, AT 2:30 A.M., THE LUBBOCK FIRE DEPARTMENT | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
610 | 1987-08-27 | TX | other |  | ENERGAS CO | ASPLUNDH COMPANY WAS TRIMMING TREES AND LIMB FELL HITTING SERVICE REGULATOR. RESULTED IN BROKEN REGULATOR WITH POUNDS PRESSURE TO HOT WATER HEATER. FIRE FLAREDOUT FROM BURNER, MELTING CONTROLS AND SCORCHING PAINT IN HEATER CLOSET.LADY OF HOUSE, TINA STOKE | 500 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
611 | 1987-07-28 | TX | ACCIDENTALLY CAUSED BY OPERATOR |  | ENTEX INC | PART 3 - NARRATIVE DESCRIPTION OF FACTORS CONTRIBUTING TO THE INCIDENT THE OPERATOR'S EMPLOYEES WERE EXCHANGING A METER. THEY DISCONNECTED THE INLET SIDE OF THE METER WITHOUT TURNING OFF THE LOCKWING VALVE ON THE RISER. THE ESCAPING GAS IGNITED, AND THE | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
612 | 1987-06-11 | NC | other |  | NORTH CAROLINA NATURAL GAS CORP | AT 8:43 A.M., JUNE 11, 1987, THE WILMINGTON DISTRICT OFFICE WAS CALLED BY THE EMERGENCY SERVICE'S DISPATCHER. THE DISPATCHER REPORTED THAT A HOUSE AT 915 S. 11TH STREET WAS ON FIRE AND THEY MIGHT NEED ASSISTANCE FROM THE GAS COMPANY. OTIS PELHAM AND LARRY | 46000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
613 | 1987-07-24 | LA | other |  | LOUISIANA GAS SERVICE CO | CUSTOMER DISCONNECTED GAS DRYER CONNECTION AND FILLED THE HOUSE WITH NATURAL GAS IN AN APPARENT SUICIDE ATTEMPT. HE THEN TURNED ON CENTRAL AIR CONDITIONER CAUSING AN EXPLOSION WHICH DESTROYED THE HOUSE. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
614 | 1987-07-13 | CT | technical failure | NORRIS | CONNECTICUT LIGHT & POWER CO | TWO EMPLOYEES WERE EDGAGED IN REMOVING AN AL5000 TX GAS METER FOR PERIODIC TEST. ONE EMPLOYEE ERRONEOUSLY REMOVED THE FLANGE BOLTS FROM THE PRESSURIZED SIDE OFA BLOCKING VALVE RESULTING IN GAS LEAKAGE AND SUBSEQUENT IGNITION. SECOND EMPLOYEE RECEIVED 2ND | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
615 | 1987-08-05 | OH | other | DUPONT ALDY 1-A | COLUMBIA GAS OF OHIO INC | COLUMBIA GAS OF OHIO, INC., EMPLOYEE, WILLIAM ALLEN WAS OVERCOME FROM BREATHINGTOO MUCH GAS WHILE ATTEMPTING REPAIR. THE EMERGENCY SQUAD WAS SUMMONED TO TRANSPORT MR. ALLEN TO THE HOSPITAL FOR CHECK-OUT. HE WAS HELD OVERNIGHT FOR OBSERVATION AND SUBSEQUEN | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
616 | 1987-08-05 | NC | other | L.B. FOSTER | NORTH CAROLINA NATURAL GAS CORP | AUGUST 5 11:14 A.M - NORTH CAROLINA NATURAL GAS CORPORATION'S DISTRICT OFFICE WAS NOTIFIED OF A LINE BROKEN AND GAS BLOWING AT MARKET STREET AND KERR AVENUE. TWO SERVICEMEN WERE DISPATCHED TO THE SCENE.AUGUST 5 11:15 A.M - THE CONSTRUCTION OFFICE WAS NOTI | 25000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
617 | 1987-07-27 | IL | other |  | PEOPLES GAS LIGHT & COKE CO | BAGS AND STOPPERS HAD BEEN INSERTED INTO A 6" C.I.L.P. MAIN THROUGH AN EXISTING1.5" TAP HOLE, TO PREVENT THE FLOW OF GAS DURING A SERVICE RENEWAL OFF THE END OF THE MAIN. THE EMPLOYEE HAD TROUBLE GETTING THE PLUG STARTED ON THE MAIN AFTERREMOVING THE BAGS | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
618 | 1987-07-23 | TX | other |  | LONE STAR GAS CO | LINE HIT BY TRACK LOADER MAKING 1" X 3" HOLE IN SIDE OF 6" MAIN. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
619 | 1987-07-29 | TX | other | STEEL | LONE STAR GAS CO | MAIN HIT BY BILLDOZER WHILE DIGGING TO BURY TRASH. | 4000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
620 | 1987-07-21 | TX | other |  | LONE STAR GAS CO | THE 3" X 4" STRAIGHT REDUCER APPEARED TO BE UNDER A STRESS CAUSING FITTING TO CRACK. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
621 | 1987-09-01 | LA | technical failure |  | LOUISIANA GAS SERVICE CO | A TRENCHING MACHINE OPERATED BY COMPANY PERSONNEL STRUCK A SERVICE LINE AND PULLED IT FROM A COMPRESSION COUPLING CAUSING A DISCHARGE OF NATURAL GAS. A WELDER AND HIS HELPER WERE WORKING NEARBY. NATURAL GAS WAS APPARENTLY IGNITED BY THE WELDING TORCH AND | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
622 | 1987-09-11 | AL | other |  | ALABAMA GAS CORP | CUSTOMER SMELLED GAS INSIDE PREMISES AND CLIMBED ATTIC STAIRS TO INVESTIGATE. UPON REACHING ATTIC, HE TURNED ON AN ELECTRIC LIGHT SWITCH AND A FLASH OCCURRED. GAS WAS TURNED OFF AT THE METER BY THE FIRE DEPARTMENT. AFTER AN INVESTIGATION, IT WAS DETERMINE | 1000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
623 | 1987-07-30 | TX | other |  | LONE STAR GAS CO | CUT LINE BY DITCHING CONTRACTOR. | 1200 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
624 | 1987-09-15 | TX | other |  | SOUTHERN UNION GAS CO | SOUTHERN UNION GAS LINE LOCATOR HAD MET WITH CITY CREW ON 9-8-87 AND LOCATED THE GAS MAIN AT SEVERAL POINTS. THE CITY CREW REPRESENTATIVE WAS PRESENT WHEN EACHMARK OVER MAIN WAS PLACED AND WAS SATISFIED. CITY ENG. DECIDED TO MOVE POLE LOCATION AND FAILED | 1200 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
625 | 1987-08-21 | TX | other |  | SOUTHERN UNION GAS CO | CONTRACTOR WAS EXCAVATING EXISTING STREET TO NEW SUB-GRADE WITH DOZER. FRONT BLADE OF DOZER SHIFTED TOO DEEP AFTER ENCOUNTERING LARGE ROCK. WHEN OPERATOR RAISED FRONT BLADE OF DOZER SHIFTED TOO DEEP AFTER ENCOUNTERING LARGE ROCK. WHEN OPERATOR RAISED FRON | 3000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
626 | 1987-08-15 | TX | maintenance |  | LONE STAR GAS CO | WHEN VAN HIT AND BROKE LIGHT POLE, THIS RESULTED IN A FIRE AT GATE VALVE BOX; SOURCE OF IGNITION UNKNOWN. | 2000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
627 | 1987-07-13 | TX | other |  | LONE STAR GAS CO | SUBCONTRACTOR LAYING A WATER LINE HIT OUR GAS MAIN WITH BACKHOE RUPTURING THE MAIN. | 10000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
628 | 1987-09-23 | TX | other |  | ENERGAS CO | AN UNKNOWN PERSON TURNED OFF VALVE IN BLOCK GATE SETTING -- CUT GAS TO 32 RESIDENCES. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
629 | 1987-09-24 | TX | other |  | ENERGAS CO | A FIRE OF UNKNOWN ORIGIN DESTROYED HOME. | 25000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
630 | 1987-10-02 | TX | other |  | ENERGAS CO | LEAK ON CUSTOMER PIPING-PLASTIC CONNECTION ON DRYER | 1750 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
631 | 1987-09-03 | TX | other |  | ENERGAS CO | TENANT HAD MOVED OUT OF RENTAL HOUSE. WHEN AN APPLIANCE WAS REMOVED, GAS VALVE WAS APPARENTLY LEFT PARTIALLY OPEN. GAS ACCUMULATED AND EXPLODED WHEN THE LANDLORD ENTERED THE HOUSE. | 5000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
632 | 1987-09-21 | TX | other |  | ENERGAS CO | RECEIVED A CALL FROM THE FIRE DEPT. AT 8:31A.M., 9/21/87 ADVISING THAT THERE HAD BEEN AN EXPLOSION AT 2706 AVENUE P. ONE WAS WAS INJURED AND HAD BEEN TAKEN TO THE HOSPITAL. INVESTIGATION SHOWED THAT TWO UNITS OF THE QUADRUPLEX HAD BEEN DAMAGED DUE TO AN E | 20000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
633 | 1987-04-25 | CA | other | AMERICAN | PACIFIC GAS & ELECTRIC CO | STRUCTURE FIRE OF UNKNOWN ORIGIN SPREAD TO METER, ALLOWING GAS TO ESCAPE AND IGNITE. BUILDINGS WERE EVACUATED & TRAFFIC WAS REROUTED AS A PRECAUTION. | 51000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
634 | 1987-05-12 | CA | other |  | PACIFIC GAS & ELECTRIC CO | STRUCTURE FIRE OF UNKNOWN ORIGIN CAUSED A ROOF-MOUNTED GAS FURNACE TO COLLAPSE ONTO HOUSELINE, ALLOWING GAS TO ESCAPE AND IGNITE. TRAFFIC WAS REROUTED AND BUILDINGS EVACUATED. | 1000000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
635 | 1987-07-24 | CA | other |  | PACIFIC GAS & ELECTRIC CO | A BOILER SERVICEMAN WAS WORKING ON A BOILER IN THE BASEMENT WHEN EXPLOSION OCCURRED. FIRE DEPT. STOPPED GAS FLOW PRIOR TO CO. ARRIVAL. | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
636 | 1987-08-23 | CA | other |  | PACIFIC GAS & ELECTRIC CO | A CUSTOMER'S BOILER FLASHED BACK WHEN CUSTOMER IMPROPERLY TRIED TO RELIGHT IT. SERVICE WAS SHUT DOWN & BUILDING EVACUATED. | 1000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
637 | 1987-10-13 | TX | other | CUPPLES | SOUTHERN UNION GAS CO | CITY CREW WAS EXCAVATING TO INSTALL 4" WATER MAIN WHEN THEY DAMAGED THE PVC SERVICE LINE THAT WAS SERVING 3700 JEFFERSON STREET. DAMAGE OCCURRED 140' NORTH OF THE NORTH PROPERTY LINE OF WEST 35TH ST. AND 20' EAST OF THE WEST PROPERTY LINE OF JEFFERSON ST. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
638 | 1987-07-28 | IL | other | PHILLIPS PRODUCTS | NORTH SHORE GAS CO | CONTRACTOR'S EQUIPMENT CUT THE 4" PLASTIC SERVICE TO A HIGH SCHOOL. FIFTY PEOPLE WERE EVACUATED FROM THE BLDG. BY THE FIRE DEPT. NO IGNITION, INJURIES OR OTHERDAMAGE OCCURRED. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
639 | 1987-07-07 | CA | other | PLEXCO | SOUTHERN CALIFORNIA GAS CO | A CONTRACTOR, WHILE MECHANICALLY TRENCHING TO INSTALL AN ELECTRICAL CONDUIT, STRUCK AND DAMAGED A 2" PE SERVICE ALLOWING GAS TO ESCAPE AT 42 PSIG. THE CONTRACTOR EXPERIENCED FIRST AND SECOND DEGREE BURNS TO HIS UPPER BODY AS THE ESCAPING GAS IGNITED. HE W | 2500 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
640 | 1987-06-25 | CA | other |  | SOUTHERN CALIFORNIA GAS CO | A PLUMBER EXPERIENCED SECOND AND THIRD DEGREES BURNS TO HIS ARMS AND FACE WHEN HE ALLOWED GAS TO ESCAPE AND SUBSEQUENTLY IGNITE FROM AN ADJACENT WATER HEATER. WITHOUT FIRST SHUTTING OFF THE SUPPLY OF GAS, THE PLUMBER WAS ATTEMPTING TO ALTER WHAT HE SURMIS | 500 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
641 | 1987-05-19 | CA | other |  | PACIFIC GAS & ELECTRIC CO | OUT OF CONTROL CAR STRUCK SIDE OF HOUSE SEVERING GAS SERVICE BELOW SHUTOFF, ALLOWING GAS TO ESCAPE AND IGNITE. BUILDINGS WERE EVACUATED AND TRAFFIC REROUTED. | 10300 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
642 | 1987-08-20 | OH | other | DRISCO | EAST OHIO GAS CO | EMPLOYEES WERE MAKING A 3-INCH HOT TAP CONNECTION TO A 4-INCH PLASTIC MAIN. AFTER THE TAP WAS MADE, THE 3-INCH CONNECTION WAS SQUEEZED OFF IN PREPARATION FOR A3-INCH VALVE TO BE BUTT FUSED ONTO THE 3-INCH OPENING. BECAUSE OF OBSTRUCTIONS FROM TELEPHONE AN | 4000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
643 | 1987-08-18 | MI | other |  | MICHIGAN CONSOLIDATED GAS CO (MICHCON) | BASED ON THE EXTENT OF DAMAGE TO THE STRUCTURE, THE PRELIMINARY DETERMINATION OF THE CAUSE OF THE FIRE AND EXPLOSION WAS UNCONFINED NATURAL GAS INSIDE THE STRUCTURE. THE SUSPECTED SOURCE OF THE GAS LEAK IS THE GAS METER. THE CAUSE OF THE LEAK CANNOT BE DE | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
644 | 1987-08-13 | CA | other |  | SOUTHERN CALIFORNIA GAS CO | TWO PARKED VEHICLES WERE STRUCK BY AN OUT OF CONTROL VEHICLE. ONE VEHICLE WAS PUSHED FORWARD OVER A SMALL CURB, STRIKING THE METER ASSEMBLY (MSA), SHEARING OFFTHE SERVICE RISER SHUT OFF VALVE. ESCAPING GAS AT 55 PSIG WAS IGNITED, MOST LIKELY FROM SPARKS C | 110000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
645 | 1987-09-09 | IA | other |  | MIDWEST GAS CO | THE EXPLOSION AT THIS LOCATION WAS CAUSED BY LEAKAGE ON THE GAS CUSTOMER'S FUELLINE PIPING, DOWNSTREAM OF THE MIDWEST GAS COMPANY METER. THE LEAKAGE OCCURRED AT THE JUNCTION OF THE CUSTOMERS COPPER FUEL LINE WITH HIS IRON PIPE FUEL LINE. AT THIS LOCATION, | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
646 | 1987-10-20 | DE | other |  | DELMARVA POWER & LIGHT CO | DELMARVA POWER WAS NOTIFIED BY THE FIRE BOARD AT 1:08 P.M. ON OCTOBER 20, 1987 OF AN EXPLOSION AND FIRE AT 119 PIERCE ROAD IN DEERHURST. THE SERVICE LINE TO THIS HOUSE HAD BEEN LOCATED AND MARKED WITH YELLOW PAINT ON OCTOBER 10, 1987 AS REQUESTED BY THE E | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
647 | 1987-10-03 | TX | other |  | ENERGAS CO | A FIRE OF UNKNOWN ORIGIN DAMAGED HOUSE. | 15000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
648 | 1987-10-09 | PA | technical failure |  | PEOPLES NATURAL GAS CO | REGULATION FACILITY WAS BEING PLACED BACK INTO SERVICE AFTER UNDERGOING REVISION. FACILITY INLET AND OUTLET TIE-INS HAD BEEN COMPLETED, AND FINAL PURGING OF EQUIPMENT WAS IN PROGRESS. ACCIDENTAL IGNITION OCCURRED, CAUSE UNKNOWN, INJURING TWO OF THE SEVEN | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
649 | 1987-10-20 | KS | other | 998MERKEL GAS OIL | LIBERAL GAS CO |  | 10000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
650 | 1987-10-31 | MI | other |  | MICHIGAN CONSOLIDATED GAS CO (MICHCON) | SEE PART "D". | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
651 | 1987-10-08 | VA | other |  | COMMONWEALTH GAS SERVICES INC | C&P TELEPHONE PRIVATE CONTRACTOR EMPLOYEE LIT A CIGARETTE IN MANHOLE CAUSING FLASH FIRE FROM WHAT WAS DETERMINED TO BE GASOLINE VAPOR ON 10/8/87.VAPOR ANALYS MADE ON 10/22/87 ALSO INDICATED PRESENCE OF NATURAL GAS IN MANHOLE. MINOR JOINT LEAKAGE IN ADJAC | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
652 | 1987-10-09 | OH | maintenance |  | DAYTON POWER & LIGHT CO | CHEMICALS USED IN PAPER PROCESS ALSO STORED IN AREA OF VAULT. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
653 | 1987-10-14 | PA | other |  | U G I CORP | CONTRACTOR PULLED MEDIUM PRESSURE SERVICE WITH BACKHOE CAUSING TO FRACTURE WITHIN BUILDING, ALLOWING UNCONTROLLED ESCAPE OF GAS. | 250000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
654 | 1987-10-05 | CA | other |  | PACIFIC GAS & ELECTRIC CO | CONTRACTOR USING A TRENCHER TO INSTALL CABLE TV STRUCK 3/4" STEEL SERVICE, ALLOWING GAS TO ESCAPE & IGNITE.TRAFFIC WAS REROUTED AS A PRECAUTION. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
655 | 1987-10-02 | CA | other | MUELLER | SOUTHERN CALIFORNIA GAS CO | THE CUSTOMER ATTEMPTED TO TURN ON THE GAS TO THE RESIDENCE AT THIS ADDRESS.IN DOING SO HE DISASSEMBLED THE SERVICE LINE VALVE AT THE INLET TO THE METER SET ASSEMBLR, PERMITTING GAS TO ESCAPE AT 40 PSIG. THE GAS IGNITED FROM AN UNKNOWN SOURCE AND THE RESI | 125000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
656 | 1987-11-04 | IN | other |  | CITIZENS GAS & COKE UTILITY | AT 7:15 P.M. SPEEDWAY FIRE DEPARTMENT REPORTED AN EXPLOSION ABD FIRE AT 1671 LINCOLN ROAD. VARIOUS UTILITY PERSONNEL WERE DISPATCHED TO THE SCENE. UPON ARRIVAL, UTILITY PERSONNEL FOUND THE RESIDENCE AT 16711 LINCOLN ROAD DEMOLISHED WITH INJURIES TO ONE | 80000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
657 | 1987-10-09 | TX | maintenance |  | LONE STAR GAS CO | GAS ACCUMULATED IN WATER METER BOX FROM LEAK ON 6"BARE STEEL IHP MAIN. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
658 | 1987-11-07 | TX | other |  | ENERGAS CO | THERE WAS AN EXPLOSION INSIDE THE HOUSE WHEN SOMEONE OPERATED A CIGARETTE LIGHTER. ACCORDING TO THE FIRE DEPARTMENT, IT WAS A NATURAL GAS EXPLOSION. THEY HADBEEN HAVING A PARTY AT THE HOUSE AND HAD BEEN THERE ALL DAY. THEY HAD NOT SMELLED THE ODOR OF G | 26000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
659 | 1987-11-13 | MD | technical failure | DUPONT | WASHINGTON GAS LIGHT CO | NO REMARKS | 103000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
660 | 1987-11-26 | WA | other |  | WASHINGTON WATER POWER CO | THIS LETTER IS A FOLLOW-UP TO THE TELEPHONIC NOTIFICATION OF AN INCIDENT WHICH OCCURRED AT WEST 1824 FIRST AVENUE ON NOVEMBER 26, 1987. THE EXPLOSION CAUSED APPROXIMATELY $6000-$8000 DAMAGE TO ONE APARTMENT IN A 24 UNIT APARTMENT BUILDING.ONE WINDOW IN A | 8000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
661 | 1987-11-06 | TX | other | DUPONT | ENTEX INC | PIPE WAS RUPTURED EARILER BY A HIGHWAY CONTRACTOR. RUPTURE WAS CLAMPED TO STOPBLOWING GAS. WHILE COMPANY CREW WAS PREPARING DAMAGED SECTION OF PLASTIC PIPE FOR REPLACEMENT, ESCAPING GAS WAS IGNITED BY UNKNOWN SOURCE, BUT PRESUSMED TO BESTATIC ELECTRICIT | 150 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
662 | 1987-11-16 | TX | other |  | ENTEX INC | LIGHTNING STRIKE ON METER. | 10000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
663 | 1987-10-17 | CA | other | AMERICAN | PACIFIC GAS & ELECTRIC CO | SRTUCTURE FIRE SPREAD TO THE METERS AND REGULATORS, ALLOWING GAS TO ESCAPE AND IGNITE. BUILDINGS WERE EVACUATED AND TRAFFIC REROUTED AS PRECAUTIONS. | 70000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
664 | 1987-11-04 | CA | other |  | SOUTHERN CALIFORNIA GAS CO | THE TENANT OF APARTMENT #208, ONE C. HASJIM, MALE APPROXIMATELY 23 YEARS OLD, ATTEMPTED SUICIDE BY OPENING THE RANGE TOP BURNERS AND DISMANTLING THE WALL FURNACE CONTROLS ALLOWING NATURAL GAS TO ACCUMULATE AND IGNITE FROM A LIGHTED CIGARETTE. THE RESULTI | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
665 | 1987-11-18 | TX | other |  | ENERGAS CO | A SMALL AMOUNT OF WATER CONDENSED IN A CONTROL-PILOT REGULATOR SUBSEQUENTLY FREEZING CAUSING THE PRIMARY REGULATOR TO CLOSE OFF. THE PRESSURE ON THE SYSTEM FELL CAUSING A PARTIAL LOSS OF CUSTOMER SERVICE. OF THE 104 CUSTOMERS SERVED FOR THIS STATION A T | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
666 | 1987-11-27 | TX | other |  | ENERGAS CO | DRIVER OF AUTOMOBILE LOST CONTROL OF VEHICLE, STRUCK PRESSURE REDUCING STATION. DAMAGE TO STATION CAUSED 65 CUSTOMERS TO LOSE GAS SERVICE. | 2000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
667 | 1987-11-25 | OH | ACCIDENTALLY CAUSED BY OPERATOR |  | HAMILTON GAS DEPT, CITY OF | AT PRESENT TIME THE INCIDENT APPEARS TO BE CAUSED BY A FRACTURE OF 4" CAST IRONPIPE AND THE ENTIRE INCIDENT IS STILL UNDER INVESTIGATION. | 20000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
668 | 1987-11-28 | AL | other |  | FAYETTE GAS BOARD, CITY OF | NO REMARKS. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
669 | 1987-11-03 | TX | other |  | LONE STAR GAS CO | A PICKUP HIT METER LOOP,BREAKING RISER OFF ABOVE STOP AND THE GAS IGNITED BURNING PICKUP,DRIVER,TWO GAS METERS AND REGULATOR. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
670 | 1987-12-18 | TX | other | UNKNOWN (TRAVIS COUNTY) | SOUTHERN UNION GAS CO |  | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
671 | 1987-11-21 | LA | other |  | ST JAMES PARISH UTILITIES | LA. STATE POLICE REPORT ATTACHED. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
672 | 1987-12-31 | TX | other |  | ENERGAS CO | A FIRE STARTED AROUND FLOOR FURNACE, DAMAGING HOUSE AND CONTENTS. | 30000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
673 | 1987-12-28 | OH | other | UNKNOWN | CINCINNATI GAS & ELECTRIC CO | CAUSE UNKNOWN AT THIS TIME. STILL UNDER INVESTIGATION. | 70000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
674 | 1988-01-11 | NE | other | UNKNOWN | MINNEGASCO INC | AT 0523, 01/11/88, THE SEWARD FIRE DEPARTMENT RECEIVED A CALL (911) THAT THERE HAD BEEN AN EXPLOSION AT 945 CHERRY LANE DRIVE. WHEN THEY ARRIVED AT THE SCENE,THEY FOUND THE HOME DEMOLISHED AND BURNING.UNDER THE DIRECTION OF CHIEF DEPUTY STATE FIRE MARSHA | 92000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
675 | 1987-12-17 | TX | other |  | ENERGAS CO | A FIRE OF UNKNOWN ORIGIN EOMPLETELY DESTROYED MOBILE HOME. | 15000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
676 | 1987-12-22 | TX | other | UNKNOWN (TRAVIS COUNTY) | SOUTHERN UNION GAS CO | SUG LOCATOR DAVID TWICHELL SPOTTED THIS MAIN ON DECEMBER 16, 1987. HE PICKED UPTWO SIGNALS. ONE, ON THE ASSIGNMENT INDICATED ONTHE ENGINEERING MAPS, AND A SECOND, WEAKER ONE, BEHIND THE P.L. HE MARKED THE SIGNAL ON THE INDICATED ASSIGNMENT, AND PLACED D | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
677 | 1987-12-18 | TX | other |  | ENERGAS CO | CUSTOMER ATTEMPTING TO LIGHT CENTRAL HEATING SYSTEM ALLOWED EXCESS ACCUMULATIONOF GAS TO OCCUR AND IGNITED IT CAUSING UNDETERMINED DAMAGE TO EYES AND SKIN. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
678 | 1987-12-03 | CA | other | UNKNOWN (RIVERSIDE COUNTY) | SOUTHERN CALIFORNIA GAS CO | THE L.S.I. ENGINEERING COMPANY, WHILE UTILIZING A D-9 CAT WITH A BACK RIPPER TOCONSTRUCT STORM DRAINS, STRUCK AND SEVERED A SIX-INCH SUPPLY LINE ALLOWING GAS PRESSURED TO 250 PSIG TO ESCAPE. SOCALGAS CREWS CONTROLLED THE ESCAPING GAS BY CLOSING THE REGUL | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
679 | 1987-12-25 | TX | other |  | ENERGAS CO | ENERGAS WAS NOT INFORMED OF THE OCCURRENCE. IT WAS LEARNED OF DURING CASUAL CONVERSATION ON MORING OF DECEMBER 28TH. ONE OF THE EMPLOYEES HAD LEARNED OF OCCURENCE OF THE FIRE.A SERVICEMAN WAS SENT TO CHECK ON IT. THE HOUSE WAS LOCATED 1 1/2 MILES SOUTH | 40000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
680 | 1988-01-10 | TX | other |  | ENERGAS CO | THE FIRE DEPT. NOTIFIED THE COMPANY OF THE EXPLOSION AND FIRE. A SERVICEMAN WASSENT OUT IN RESPONSE. THE FIRE DEPT. HAD ALREADY TURNED OFF THE METER WHEN HE ARRIVED.TED PEREZ WAS ONLY OCCUPANT IN THE HOUSE AT THE TIME OF THE EXPLOSION AND FIRE.HE WAS IN | 65000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
681 | 1988-01-15 | AL | technical failure | NORMAC | ALABAMA GAS CORP | AT 9:20 A.M. ON FRIDAY, JANUARY 15, 1988, AN ALABAMA GAS CORPORATION CONSTRUCTION CREW CLOSED THE VALVE ON A TWO INCH (2") HIGH PRESSURE MAIN TO MAKE REPARS TOA DAMAGED SECTION OF PIPE. FOLLOWING THE VALVE CLOSING, THE LINE WAS BLED DOWNAT A METER SETUP. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
682 | 1988-01-15 | AR | other | UNKNOWN | ARKANSAS WESTERN GAS CO | MAIN WAS APPARENTLY DAMAGED BY OUTSIDE FORCES SOME TIME IN PAST. RESULTING DENT IN PIPE CAUSED STRESS RISER. THIS IN COMBINATION WITH COLD GROUND CONDITIONS IS SUSPECTED TO HAVE LED TO STRESS CRACK FAILURE. | 150000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
683 | 1987-10-21 | NC | ACCIDENTALLY CAUSED BY OPERATOR |  | PUBLIC SERVICE CO OF NORTH CAROLINA | ABOUT 10:30 A.M., OCTOBER 21, 1987, THOMAS MOZINGO, LEADER WELDER; CLYDE SWANN,H.D. EQUIPMENT OPERATOR; RICHARD WILLIAMS, PIPE LAYER; AND JOHN EDWARDS, SERVICEMAN A. WERE WORKING AT THEIR TRUCK BOLTING A FLANGE ONTO A 2" VALVE THAT WAS TOBE INSTALLED IN T | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
684 | 1988-01-09 | SD | other | UNKNOWN | MONTANA - DAKOTA UTILITIES CO | ON SATURDAY, JANUARY 9, 1988, SHORTLY AFTER 11:00 P.M. KENNETH KNIGHT, SERVICEMAN-GENERAL, RECEIVED A FIRE CALL FROM OUR DISPATCH CENTER IN BISMARCK. THE EXPLOSION AND FIRE OCCURRED IN A PRIVATE DWELLING LOCATED AT 316 EAST PHILADELPHIA STREET IN RAPID C | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
685 | 1987-12-25 | MI | other |  | MICHIGAN CONSOLIDATED GAS CO (MICHCON) | THE GAS SERVICE LINE SUPPLYING 277 GENEVA HAD BEEN CUT AND 1-1/2" THREADED PLUGINSTALLED IN THE MAIN ON NOVEMBER 13, 1987 BECAUSE OF GAS THEFT. SOME TIME PRIOR TO DECEMBER 25, 1987, A TUNNEL HAD BEEN DUG THROUGH THE FRONT BASEMENT WALL OFTHE BUILDING (277 | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
686 | 1987-12-30 | PA | other |  | U G I CORP | A LOW-LEVEL EXPLOSION AND RESULTANT FIRE DESTROYED A DUPLEX DWELLING AT 328-330 WEST LEHIGH DR, WEST EASTON, PA. A BROKEN 12" CAST IRON MAIN WAS FOUND DIRECTLY IN FRONT OF THE DWELLING, APPROXIMATELY 45' FROM THE FRONT BUILDING WALL OF THE STRUCTURE. THE | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
687 | 1987-12-27 | AZ | other |  | SOUTHERN UNION GAS CO |  | 400000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
688 | 1988-01-19 | DE | other | DUPONT CO | DELMARVA POWER & LIGHT CO |  | 150000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
689 | 1988-01-19 | OH | other |  | HAMILTON GAS DEPT, CITY OF | AT PRESENT TIME THE INCIDENT APPEARS TO BE CAUSED BY A FRACTURE OF 6" CAST IRONPIPE. THE ENTIRE INCIDENT IS STILL LUNDER INVESTIGATION. APPEARS TO BE OUTSIDENATURAL FORCE. | 40000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
690 | 1988-01-10 | PA | other | UNKNOWN | PHILADELPHIA GAS WORKS | DUE TO GROUND SUBSIDENCE AT A SEWER AND WATER LATERAL, THE 4" CAST IRON MAIN BROKE. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
691 | 1988-01-16 | PA | other | UNKNOWN | PHILADELPHIA GAS WORKS | 16'4" OF 4" CAST IRON MAIN SETTLED INTO CAVITY IN STREET. CAVITY WAS DUE TO A SEWER AND WATER FAILURE IN THE STREET. | 125000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
692 | 1987-12-29 | NJ | other |  | SOUTH JERSEY GAS CO | ON 12-29-87 AT 6:50 P.M., THE COMPANY RECEIVED A CALL OF AN EXPLOSION AND FIRE AT 203 STEPHEN PL. MAGNOLIA. A COMPANY REPRESENTATIVE WAS DISPATCHED TO THE LOCATION AT 6:51 P.M. AND ARRIVED AT 7:10 P.M. IN WORKING WITH THE LOCAL FIRE DEPARTMENT, THE GAS | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
693 | 1988-01-07 | TX | technical failure |  | ENERGAS CO | INDICATION OF THE LEAK WAS FOUND UNDER THE HOUSE. RESIDENTS WERE EVACUATED ANDKEPT IN A MOTEL UNTIL THE GROUND COULD BE AERATED TO MAKE CONDITIONS SAFE. THE LEAK WAS REPAIRED AND THE PEOPLE WERE PERMITTED TO RETURN TO THE RESIDENCE THE NEXT DAY.MATERIAL | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
694 | 1987-12-15 | TX | other | UNKNOWN (TRAVIS COUNTY) | SOUTHERN UNION GAS CO | CONTRACTOR WAS DITCHING FOR A PORTION OF AN ON-GOING CAPITAL IMPROVEMENT PROJECT WHEN THEY STRUCK AND DAMAGED THIS GAS SERVICE LINE. THE CONTRACTOR HAD REQUESTED THAT ALL LINES IN THE AREA BE LOCATED AND MARKED. THE S.U.G. LOCATOR FAILEDTO MARK THIS PAR | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
695 | 1988-01-23 | PA | other | ROCKWELL#2848856 | PENNSYLVANIA GAS & WATER CO | FIRE OCCURRED AT CUSTOMER PREMISES IN REAR OF BASEMENT, SUSPECTED CAUSE BY ARSONIST. FIRE ENGULFED ENTIRE HOUSE CAUSING AN INCIDENT AT THE INSIDE GAS METER SET RESULTING IN AN IGNITION. TWO FIREFIGHTERS WERE INJURED RESULTING FROM THIS INCIDENT. | 40000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
696 | 1987-10-07 | MO | maintenance |  | KANSAS POWER & LIGHT CO | NATURAL GAS LEAKING BELOW GROUND FROM A 1" STEEL SERVICELINE MIGRATED INTO A DUPLEX AND IGNITED, POSSIBLY FROM A PILOT ON A STOVE, CAUSING A FIRE.ALTHOUGH GAS SUPPLY WAS NOT SHUT OFF FOR TWO HOURS AND TEN MINUTES THE FIRE DEPARTMENT HAD THE BLAZE UNDER CO | 80000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
697 | 1987-11-12 | MI | technical failure | PHILLIPS | MICHIGAN CONSOLIDATED GAS CO (MICHCON) | ON NOVEMBER 10, 1987, IN RESPONSE TO A LEAK CALL, ONE LEG OF A BURRIED COMPRESSION TEE WAS DISCOVERED TO HAVE PULLED OUT. THE PULL OUT WAS REPAIRED. THE CREWFAILED TO REPROSPECT THE AREA AFTER MAKING THE REPAIR AND THEREFORE, FAILED TO DETECT A HOLE MAD | 1000000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
698 | 1987-11-01 | CA | other | NORDSTROM | PACIFIC GAS & ELECTRIC CO | UNKNOWN PARTY GAINED FORCIBLE ENTRY TO VALVE PIT. 6" VALVE ON SINGLE FEED MAIN WAS CLOSED, TERMINATING GAS FLOW TO 2,325 CUSTOMERS. | 171600 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
699 | 1987-11-19 | CA | other | DUPONT | SAN DIEGO GAS & ELECTRIC CO | PIPE WALL FAILURE OCCURRED WHEN EXPOSED TO "ROSEBUD" TORCH. ESCAPING GAS IGNITE | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
700 | 1987-11-25 | CA | other | UNKNOWN | PACIFIC GAS & ELECTRIC CO | STRUCTURE FIRE OF UNKNOWN ORIGIN DESTROYED TWO METERS AND REGULATOR, ALLOWING GAS TO ESCAPE AND IGNITE. | 50110 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
701 | 1987-11-03 | TX | other |  | ENERGAS CO | A FIRE WAS DELIBERATELY SET AT THE BUILDING, RESULTING IN COMPLETE DESTRUCTION OF THE PREMISES. | 75000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
702 | 1987-11-03 | TX | other |  | ENERGAS CO | WE RECEIVED NOTIFICATION AT 11:15 A.M. ON NOVEMBER 4TH THAT A HOUSE BURNED DOWNIN TURKEY. IT HAD BURNED DURING THE PREVIOUS NIGHT.WAYNE ELLISTON, ENERGAS MANAGER AT TULIA, INVESTIGATED. THE FIRE WAS AT A HOUSE ON 2ND STREET ALEXANDER. THE VOLUNTEER FIR | 15000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
703 | 1987-09-20 | KS | other |  | UNION GAS SYSTEM INC | AN EXPLOSION AT 113 N. 6TH, INDEPENDENCE, KANSAS DESTROYED A TWO STORY BRICK BUILDING AND SUBSTANTIALLY DAMAGED THREE ADJACENT STRUCTURES. THE CAUSE OF THE EXPLOSION IS UNDETERMINED AT THIS TIME PENDING FURTHER INVESTIGATION. | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
704 | 1987-12-29 | KS | other | UNKNOWN | KANSAS POWER & LIGHT CO | SERVICE REGULATOR WAS STRUCK BY HIT & RUN DRIVER, ALLOWING MAIN PRESSURE TO ENTER THE STRUCTURE, CAUSING EXPLOSION. | 45000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
705 | 1987-12-19 | KS | maintenance |  | KANSAS POWER & LIGHT CO | COROSION LEAK AT SCREW COLLAR ON BARE STEEL YARD LINE ALLOWED GAS TO ENTER SEWERDRAIN TO HOUSE. YARD LINE WAS INSTALLED IN 1966, BY CUSTOMER. GAS WAS APPARENTLY IGNITED BY ELECTRIC FAN. CUSTOMER EXTINGUISHED FLAME BY COVERING DRAIN WITH BLANKET. SERVIC | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
706 | 1987-12-18 | KS | other | PHILLIPS DRISCO | KANSAS POWER & LIGHT CO | A PLUMBING CONTRACTOR (NEW COUNTRY PLUMBING), DIGGING WITH A BACKHOE IN ORDER TO INSTALL A WATER SERVICE TO A NEW HOUSE, STRUCK AND PUNCTURED OUR 2" PLASTIC MAIN. AS THE CONTRACTOR WAS DIGGING OUT THE AREA TO PREPARE FOR REPAIRS, THE BACKHOE BUCKET STRUC | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
707 | 1987-12-04 | KS | other | IMPERIAL EASTMAN | K P L GAS SERVICE | DISPATCHER RECEIVED A CALL FROM THE FIRE DEPARTMENT AT 0318 HOURS THAT A DISTRICT REGULATOR STATION HAD BEEN HIT AND WAS BLOWING. DUTY SUPERVISOR WIDICK WAS CALLED AT 0321 HOURS. THE DISPATCHER WAS INSTRUCTED TO CALL THE PRESSURE SUPT. QUIGGLE AT THAT T | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
708 | 1986-06-02 | KS | other | UNKNOWN | KANSAS POWER & LIGHT CO | A VEHICLE FAILED TO STOP AND / OR NEGOTIATE A TURN AT A T INTERSECTION, RESULTING IN DESTRUCTION OF A DISTRICT REGULATOR AND SUBSEQUENT FIRE TOTHE STATION AND VEHICLE. | 15000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
709 | 1986-04-30 | KS | other | PHILLIPS MFG. CO. | K P L GAS SERVICE | WHILE EXCAVATING FOR INSTALLATION OF WATER LINE, CHAIN TYPE TRENCHER STRUCK 2" PLASTIC GAS MAIN. GAS MAIN WAS CUT AND ESCAPING GAS IGNITED. TRENCHER OPERATORWAS BURNED AND WAS TRANSPORTED AND ADMITTED TO HOSPITAL. DIGGER CHAIN AND ENGINE OF TRENCHER WE | 20350 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
710 | 1987-12-19 | KS | technical failure | PHILLIPS | UNION GAS SYSTEM INC | THE PRELIMINARY INVESTIGATION INDICATES THE CAUSE OF THIS INCIDENT WAS SEPARATION OF THE SERVICE LINE FROM THE TAPPING TEE FITTING ATTACHED TO THE MAIN. THE FUSION FO THE SERVICE LINE TO THE TAPPING TEE DID NOT APPEAR TO MEET ESTABLISHED STANDARDS IN THA | 300000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
711 | 1987-10-03 | KS | other | ROCKWELL 3000 FISHER S-202 | UNION GAS SYSTEM INC | BETWEEN 11 & 11:30 P.M. 10-3-87 A CAR HIT METER SETTING AT FASONE'S RESTAURANT AT 57TH & STATE AVE., KCK (RESULTING IN FIRE). DRIVER SAID HE WAS LEAVING LOT BUT METER SITS - 20 FEET FROM PARKING LOT ENTRANCE. THE FIRE WAS LEFT TO BURN UNTIL GAS SHUT OFF | 6000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
712 | 1986-12-15 | KS | maintenance | UNKNOWN | UNION GAS SYSTEM INC |  | 3000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
713 | 1986-08-20 | KS | other | DISCOPIPE | UNION GAS SYSTEM INC |  | 6000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
714 | 1986-06-20 | KS | other | UNKNOWN | UNION GAS SYSTEM INC |  | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
715 | 1987-12-16 | AR | other | REYNOLDS | ARKANSAS WESTERN GAS CO | MOISTURE IN REGULATOR VENT FROZE ALLOWING HIGHER THAN NORMAL PRESSURE INTO BOTHHOMES. | 64000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
716 | 1988-01-29 | TX | technical failure |  | ENERGAS CO | ORIGINAL CONSTRUCTION OF THE PIPE WAS WITH THREADED PIPE ENDS AND COLLAR. THE TREADED PIPE END FAILED RESULTING IN A LEAK. THIRTY CUSTOMERS "DOWNSTREAM" OF THE LEAK WERE LOST. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
717 | 1988-01-15 | TX | other |  | ENTEX INC | CITY OF LAMARQUE WATER CREW, DIGGING WITH A BACKHOE TO REPAIR A WATER MAIN, CUTA 2" GAS SERVICE LINE AT THE TAP VALVE. GAS WAS IGNITED WHEN THE BACKHOW WAS SCRAPING DIRT AROUND THE BELL HOLE. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
718 | 1988-01-09 | TX | other |  | ENTEX INC | HOUSTON LIGHTING AND POWER COMPANY INSTALLED A COPPER GROUND ROD, FOR THEIR FACILITIES, IN CLOSE PROXIMITY WITH OUR SERVICE LINE. THIS RESULTED IN AN AC ARC-OVER BETWEEN THE SERVICE LINE AND THE COPPER GROUND ROD, CAUSING A TRANSFER OF METAL FROM OUR SER | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
719 | 1988-01-28 | TX | other | UNKNOWN (TRAVIS COUNTY) | SOUTHERN UNION GAS CO | CONTRACTOR WAS USING AUGER TO DRILL HOLE TO SET NEW UTILITY POLE FOR NEW SUBDIVDSION. CONTRACTOR HAD NOT REQUESTED ANY UTILITY LOCATIONS. AT 11 A.M., CONTRACTOR PUNCTURED 6" WRAPPED STEEL MAIN APPROXIMATELY 1' FROM D.E. OF MAIN LINE. SECTON WAS ISOLATE | 5500 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
720 | 1988-01-13 | MI | other | DRESSER | MICHIGAN CONSOLIDATED GAS CO (MICHCON) | GAS LEAKING FROM 1/2" COPPEER SERVICE LINE, WHICH PULLED OUT OF A DRESSER STYLE88 COUPLING, MIGRATED INTO A SCHOOL BUILDING AND WAS IGNITED BY AN UNKNOWN SOURC | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
721 | 1988-01-18 | MI | other | NORDSTROM | MICHIGAN GAS UTILITIES CO | AT 4:00 A.M. AN EXPLOSION AND FIRE OCCURRED AT 134 FRANK STREET, COLON. ROBERTAND DAWN WEINBERG EVACUATED THEIR HOME WITHOUT APPARENT INJURY.AT 4:27 A.M., MICHIGAN GAS UTILITIES' NIGHT ANSWERING SERVICE WAS NOTIFIED BY THE FIRE DEPARTMENT OF THE EXPLOSIO | 135000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
722 | 1988-02-06 | TX | other |  | ENERGAS CO | OUR DISPATCHER WAS NOTIFIED AT APPROXIMATELY 1:30 A.M. ON FEBRUARY 6, 1988 THATTHERE WAS AHOUSE ONFIRE ABOUT 1 1/2 MILES EAST OF KRESS. THE DISPATCHER SENT ONE OF OUR SERVIEMEN FROM TULIA TO THAT LOCATION.THE SERVCIE MAN FOUND THE HOUSE BURNED TOTHE GROU | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
723 | 1988-02-05 | TX | other | UNKNOWN (RANDALL COUNTY) | ENERGAS CO | DRIVER OF AUTOMOBILE HIT METER SETTING. THE RESULTING FIRE DESTROYED AUTOMOBILE. | 10000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
724 | 1988-02-08 | TX | other |  | ENERGAS CO | A FAULTY VALVE IN A WALL HEATER CAUSED FIRE. A FOUR YEAR OLD GIRL WAS KILLED. | 10000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
725 | 1987-12-28 | TX | other | ROCKWELL | LONE STAR GAS CO | A 1 1/4 ROCKWELL EMCO NO. 1 EJECTOR REGULATOR FAILED TO LOCK UP ALLOWING 20 OZ.TO FLOW INTO THE CUSTOMER'S HOUSE. THE EXCESS PRESSURE ESCAPED THROUGH A VALVEON THE WATER HEATER FILLING THE ATTIC WITH GAS. WHEN THE GAS IGNITED, THE CEILINGS WERE BLOWN DOW | 8000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
726 | 1988-02-12 | LA | other |  | LOUISIANA GAS SERVICE CO | BACKHOE BROKE 2" STUB TO ABANDONED SERVICE LINE OFF 6" MAIN.ELEMENTARY SCHOOL NEAR THE LEAK WAS EVACUATED. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
727 | 1988-02-03 | GA | other |  | ATLANTA GAS LIGHT CO | CREW WAS USING AIR HAMMER TO REMOVE CONCRETE FROM UNDERNEATH BELL TO REPAIR BELL JOINT LEAK ON 8" C.I. MAIN. THE AIR HAMMER BROKE THROUGH THE DUCT AND DAMAGED THE POWER CABLE. WHEN THE CABLE WAS RE-ENERGIZED BY THE POWER COMAPNY, AS IN HOLE FLASHED RESULT | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
728 | 1988-02-13 | WI | other | ASSOCIATED FLOW | WISCONSIN POWER & LIGHT CO | THIS WAS AN OLDER HOME WITH BASEMENT WALLS OF POURED CONCRETE BUT AN EARTH FLOOR. NO ONE WAS HOME AT THE TIME OF THE EXPLOSION. | 76000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
729 | 1988-02-26 | WI | other |  | WISCONSIN SOUTHERN GAS CO INC | A 3/4 INCH GALVANIZED STEEL GAS SERVICE PIPE PROVIDING GAS SERVICE TO THE RESIDENCE AT 2921 CIRCLE DRIVE FRACTURED TWO THIRDS OF THE CIRCUMFERENCE OF THE PIPE ON TH THREADED PORTION THAT WAS SCREWED INTO A STREET EL, WHICH WAS FITTED INTO A SADDLE TEE, TH | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
730 | 1988-02-15 | AL | other |  | DAPHNE UTILITY DEPT, CITY OF | LIT CIGARETTE IN MANHOLE NEAR GAS LEAK CAUSING FIRE AND BURNING MAN.HEAVY EQUIPMENT DRIVING OVER TAP POSSIBLY CAUSING TAP TO LEAK. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
731 | 1988-02-08 | ND | other |  | MONTANA - DAKOTA UTILITIES CO |  | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
732 | 1988-01-28 | CA | other |  | PACIFIC GAS & ELECTRIC CO | STRUCTURAL FAILURE OF BASEMENT WALL (CAUSE UNKNOWN) ALLOWED ENTIRE STRUCTURE TOCOLLAPSE. DEBRIS STRUCK SERVICE RISER, ALLOWING GAS TO EXCAPE TO ATMOSPHERE. BUILDINGS WERE EVACULATED AND TRAFFIC REROUTED. | 120100 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
733 | 1988-01-18 | TX | other | GRADE X42 | LONE STAR GAS CO | EXCAVATOR WAS USING LARGE FRONT-END LOADER TO REMOVE WING WALL AND STROM DRAIN. OUR 3" STEEL LINE LAY ON THE INSIDE OF THE WINGF WALL AND ON TOP OF THE DRAIN PIPE. THE FORCE AGAINST THE WING WALL AND THE 3" STEEL PIPE CAUSED A RAGGED HOLE TO BE TORN IN T | 15000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
734 | 1988-02-14 | TX | other | GENSCO | DEL RIO GAS SYSTEM, CITY OF | VEHICLE WENT OUT OF CONTROL KNOCKING DOWN FENCE AND HITTING THE GAS METER WHICHIGNITED A FIRE THAT DAMAGE A MOBILE HOME.DRIVER: RICARDO R. GOMEZ 710 W. 11TH ST. DEL RIO, TEXAS 78840 | 21700 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
735 | 1988-01-07 | VA | other |  | UNITED CITIES GAS CO | AT APPROXIMATELY 1845 HOURS OF JANUARY 7, 1988, WE INCURRED AN EXPLOSION WITHIN THE COMPRESSOR SHED DURING PEAK SHAVING OPERATIONS. SUBSEQUENT TO THE EXPLOSION, WE EXPERIENCED A NATURAL GAS FIRE EMITTING FROM A ONE-INCH STEEL LINE AT 90 PSIG. THIS STEEL | 60000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
736 | 1988-03-10 | MI | other | PHILLIPS | CONSUMERS POWER CO | AIRPLANE CRASHED INTO HOUSE AND HIT GAS SERVICE RISER. | 90000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
737 | 1988-02-28 | MO | other |  | UNION ELECTRIC CO | ABOUT 1:00 P.O., FEBRUARY 27, 1988, NATURAL GAS WAS TURNED ONTO A 5/8 INCH COPPER LINE THAT WAS OPEN INTO AN UNPROPERLY VENTED FIREPLACE.THE FIREPLACE VENTED INTO THE ATTIC SPACE BETWEEN THE CEILING AND ROOF ON A ONESTOREY DUPLEX, NOT THROUGH THE ROOF. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
738 | 1988-03-30 | OK | other | UNKNOWN (WOODWARD COUNTY) | OKLAHOMA NATURAL GAS CO | ON MARCH 30, 1988, AT APPROXIMATELY 2139 HOURS A VEHICLE DRIVEN BY MARION HUNTER OWENS IN WOODWARD, OKLAHOMA, STRUCK A NATURAL GAS DISTRIBUTION REGULATOR SETTING. MARION OWENS AND HIS WIFE, GLENDOLA OWENS, HAD BEEN SHOPPING AT THE FLEMING'S JACK N. JILL G | 20000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
739 | 1988-03-29 | AL | maintenance |  | CORDOVA, WATER WORKS & GAS BOARD FO THE CITY OF | THIS SERVICE WAS UNDER A LEAK HISTORY PROGRAM AND IN COMPLIANCE WITH 192.465E. | 75000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
740 | 1988-02-23 | TX | other |  | LONE STAR GAS CO | A CONTRACTOR INSTALLING A WATER MAIN HIT OUR STEEL SERVICE LINE AND BROKE A FITTING INSTALLED IN THE SERVICE BETWEEN THE STREET AND BUILDING STRUCTURE. POSSIBILITY OF GAS ACCUMULATION BEING IGNITED BY AN UNKNOWN SOURCE CAUSING THE EXPLOS | 55000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
741 | 1988-03-25 | TX | other | MUELLER | SOUTHERN UNION GAS CO | AT 12:00 P.M. MR. JESUS MAGALLANES IGNITED SOME DEAD WEEDS AND BRUSH ON HIS PROPERTY WHICH IS APPROXIMATELY 100 FEET EAST OF HIS HOME. THE FIRE RAPIDLY SPREADTO A SHACK ON THE PROPERTY AND DESTROYED A PORTION OF THE STRUCTURE.IN ADDITION, THE FIRE SPREAD | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
742 | 1988-03-19 | LA | other | UNKNOWN (JEFFERSON COUNTY) | LOUISIANA GAS SERVICE CO | PICKUP TRUCK HIT BRICK FENCE WHICH FELL ON METER INSTALLATION.ONLY ONE CUSTOMER WAS WITHOUT GAS, BUT FIRE DEPARTMENT EVACUATED 4 BLOCK AREA CONSISTING OF APPROXIMATELY 200 HOMES. | 1000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
743 | 1988-02-17 | TX | other |  | ROBSTOWN GAS SYSTEM, CITY OF | THEY WERE PREPARING TO REPLACE THE NEW LENGTH OF PIPE AND DISCOVERED THAT IT DID NOT FIT RIGHT, SO THAY USED THE TORCH TO HEAT THE PIPE SO THAT IT WOULD EXPANDAND FIT RIGHT INTO PLACE. THEY PLACED PRESSURE ON THE PIPE RUNNING NORTH AND SOUTH AND THE THREA | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
744 | 1988-02-24 | TX | other |  | ENERGAS CO | PAVING CONTRACTOR MADE AN EXCESSIVE CUT AND CUT INTO THE PIPELINE. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
745 | 1988-02-24 | TX | other |  | ENERGAS CO | FARMER PLOWED INTO GAS LINE. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
746 | 1988-02-03 | AL | technical failure |  | SOUTH ALABAMA UTILITIES | RICHARD BLANKINCHIP WAS WORKING IN A TAP HOLE USING A PROPANE TORCH TO HOT WRAPA TAP CONNECTION AFTER INSTALLING A SERVICE TO THE RESIDENCE OF B. E. DUNN. CHRIS HURD (CREW MAN) WAS GETTING READY TO INSTALL A UNION ON THE OUTLET SIDE OF THE HIGHPRESSURE RE | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
747 | 1988-01-29 | TX | other |  | LONE STAR GAS CO | FOUR TEENAGERS WERE SPEEDING IN A 1983 CHEV. CAMERO TRYING TO ELUDE THE CROWLEY, TX POLICE WHEN THEIR CAR CRASHED INTO THE METER INTALLATION AT 1800 W. SEMINARY DR. THE DAMAGE REISER BLEW GAS FOR APPROXIMATELY THREE MINUTES BEFORE IGNITING AND ENGULFING | 5000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
748 | 1988-02-29 | TN | other | .L. B. FOSTER | MEMPHIS LIGHT GAS & WATER DIVISION | CONTRACTOR WAS DRILLING HOLES FOR A STREET LIGHT AND HIT OUR 4" CWS MAIN AT APPROXIMATELY 9:15 A.M. HITTING THE LINE CAUSED AN EXPLOSION AND FIRE AND DAMAGED TWO LARGE VEHICLES OWNED BY CONTRACTOR. | 250000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
749 | 1988-02-16 | OH | other | UNKNOWN (FRANKLIN COUNTY) | COLUMBIA GAS OF OHIO INC | WATER LINE CONTRACTOR WAS EXCAVATING AND BROKE 1 1/4" STEEL GAS SERVICE LINE ATCURB VALVE. COMPANY CREW WAS IN PROCESS OF CUTTING LINE SO THAT THE FLOW OF GAS COULD BE CONTROLLED WHEN IGNITION OCCURRED. SUSPECTED SOURCE OF IGNITION WAS A GASOLINE DRIVEN | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
750 | 1988-01-18 | NC | other |  | PIEDMONT NATURAL GAS CO INC | THE INITIAL OFFICIAL CAUSE WAS DETERMINED BY THE INVESTIGATING WINSTON SALEM MECHANICAL INSPECTOR (IN CONCURRENCE WITH THE WINSTON SALEM FIRE DEPARTMENT) TO BEA BOILER EXPLOSION. DETERMINATION (BY THE ABOVE) WAS MADE THAT PIEDMONT NATURAL GAS CO. WAS NOT | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
751 | 1988-03-17 | NC | other |  | PIEDMONT NATURAL GAS CO INC | MINOR EXPLOSION AT RESIDENCE AND HOUSE DESTROYED BY FIRE. CUSTOMER HAD BEEN TURNED OFF IN FEBRUARY 1986 FOR UNAUTHORIZED USE OF GAS. THERE WAS A CONCERN THAT THE COSTOMER WAS AGAIN STEALING GAS BUT THIS WAS NOT THE CASE. THERE WAS NO METER PRESENT AND | 65000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
752 | 1988-03-21 | NC | other |  | PIEDMONT NATURAL GAS CO INC | CHEM-WAY EMPLOYEES MISHANDLED THE DISPOSITION OF CHEMICALS CAUSING FIRE. INITIALLY GAS WAS REPORTEDLY INVOLVED, BUT IT WAS NOT. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
753 | 1988-03-25 | NC | other |  | PIEDMONT NATURAL GAS CO INC | EXPLOSION IN COMMERCIAL NATURAL GAS OVEN OF EARTH GRAINS BAKERY. EXTINGUISHED ITSELF. FIVE PERSONS INJURED. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
754 | 1988-04-20 | TX | other | PLEXCO | GREY FOREST UTILITIES | GAS SERVICE LINE AND ELECTRIC CABLE WERE IN A COMMON TRENCH. LANDSCAPER DUG UPGAS AND ELECTRIC WITH A BACKHOE, COMPLETELY SEVERING BOTH LINES. THE ELECTRIC LINE IGNITED THE GAS. LANDSCAPER PUT OUT FIRE IMMEDIATELY. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
755 | 1988-04-01 | TX | other |  | ENERGAS CO | APPARENTLY THE FLOORING SUPPORTING THE WATER HEATER FAILED AND ALLOWED THE WATER HEATER TO FALL, BREAKING THE FLEXLINE SUPPLYING THE GAS. | 20000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
756 | 1988-03-16 | TX | other | DUPONT | ENTEX INC | CONTRACTOR APPARENTLY DAMAGED SERVICE LINE, THEN IGNITED THE EXCAPING GAS WHILEHEATING A NEARBY PIPE. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
757 | 1988-04-10 | TX | maintenance |  | ENERGAS CO | GAS HAD APPARENTLY ACCUMULATED UNDER AND WITHIN MOTEL. IT IGNITED IN ROOM 125,POSSIBLY FROM CIGARETTE BEING LIGHTED, CAUSING FIRE INTHIS ROOM AND SPREADING TO ATTIC OF MOTEL. EXPLOSION APPEARS TO HAVE SUBSEQUENTLY OCCURRED IN MOTEL ATTICOCCUPANTS OF ROO | 300000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
758 | 1988-04-07 | NY | other |  | CONSOLIDATED EDISON CO OF NEW YORK | MALFUNCTION OF THE CONTROLS ON A WATER HEATER ALLOWED GAS TO PASS THROUGH THE APPLIANCE WITHOUT BURNING. THE APPLIANCE FLUE WAS NOT VENTED TO A CHEMNEY NOR TOTHE OUTSIDE. THE GAS ESCAPED FROM THE FLUE INTO A BASEMENT AND WAS IGNITED BYAN UNKNOWN SOURCE | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
759 | 1988-03-10 | TX | other | DOMESTIC | GREY FOREST UTILITIES | THE GAS MAIN WAS DAMAGED BY A CONTRACTOR WHILE EXCAVATING FOR A ROAD WIDENING PROJECT. ALL GAS MAINS ARE SHOWN ON THE CONTRACTORS PLANS. | 20000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
760 | 1988-03-28 | MD | technical failure | PHILLIPS | EASTERN SHORE GAS CO | AN EASTERN SHORE GAS CO STREET CREW, CONSISTING OF JOESPH LONOGBARDI, CLIFF GLENN AND HOWARD TAYLOR WAS REMOVING A 2 INCH STEEL GAS MAIN TO MAKE WAY FOR A 24 INCH STORM SEWER. THEY HAD INSTALLED A 2 INCH MUELLER NO-BLOW FITTING ON THE SOUTHEND OF THE MAIN | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
761 | 1988-05-20 | CA | other | ALDYLA DUPONT | SOUTHERN CALIFORNIA GAS CO | STRUCTURE FIRE CAUSED BY ARSON AND FLAMMABLE LIQUID POURED ON FLOOR, BROKE GAS LINE. COLLAPSE OF STRUCTURE. | 120000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
762 | 1988-03-16 | TX | other |  | ENERGAS CO | EXPLOSION OF UNKNOWN ORIGIN DESTROYED THE HOUSE REQUIRING MEDICAL TREATMENT FORTHE FOUR OCUPANTS. | 30000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
763 | 1988-05-02 | TX | other |  | ENERGAS CO | MEASUREMENT STATION WS BY PASSED WITH INAPPROPRIATE REGUALTOR. EXCESS PRESSUREAT CUSTOMER APPLIENCES RESULTED IN EXPLOSION & FIRE. | 10000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
764 | 1988-04-14 | TX | other |  | ARKANSAS LOUISIANA GAS CO (ARKLA GAS CO) | FLEXIBLE CONNECTOR DISCONNECTED FROM WALL VALVE. VALVE WAS FOUND IN "ON" POSITION. | 30000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
765 | 1988-04-06 | TX | other |  | ARKANSAS LOUISIANA GAS CO (ARKLA GAS CO) | PRELIMINARY INVESTIGATION REVEALED USE OF RECREATIONAL VEHICLE BUTANE APPLIANCEINSIDE 10' X 12' CINDER BLOCK STRUCTURE. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
766 | 1988-04-14 | TX | other |  | ARKANSAS LOUISIANA GAS CO (ARKLA GAS CO) | PRELIMINARY INVESTIGATION BY LOCAL FIRE DEPARTMENT REVEALED VALVE IN CUSTOMER PIPING WAS LEAKING BEHIND OVEN. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
767 | 1988-03-15 | TX | other |  | RIO GRANDE VALLEY GAS CO | THE GAS RANGE SUPPLY VALVE WAS REPORTED TO BE IN THE OPEN POSITION WITH NEITHERRANGE CONNECTOR NOR RANGE CONNECTED. TEST REVEALED 360 CFH GAS ESCAPING WITH VALVE IN OPEN POSITION. HOUSE WAS TOTALLY DEMOLISHED BY A FIRE & EXPLOSION. THERE WER NO KNOWN O | 70000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
768 | 1988-04-11 | OH | maintenance |  | DAYTON POWER & LIGHT CO | THERE WERE TWO GAS MAINS IN THE EXCAVATION. A 6" COATED LINE WAS TO HAVE ADDITIONAL ANODES INSTALLED ON IT. THE OTHER LINE, A 4" BARE WROUGHT STEEL LINE, WAS LOCATED TO THE SIDE AND APPROXIMATELY 8" BELOW THE 6" PIPE. THE CREW MEMBER DIDNOT CHECK FOR CU | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
769 | 1988-04-26 | CO | other | UNKNOWN (LARIMER COUNTY) | PUBLIC SERVICE CO OF COLORADO | ON 4/20/88, A CONTRACTOR INSTALLING A 24" WATER LINE FOR THE CITY OF FT. COLLINS STRUCK A 2" PSC GAS LINE IN THE 1700 BLOCK ON E. HIGHWAY 14 FRONTAGE ROAD. THIS LINE HAD BEEN PREVIOUSLY INCORRECTLY LOCATED BY PSC. (DATE UNKNOWN). THE 2" GAS LINE WAS DENT | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
770 | 1988-04-25 | TX | technical failure | WALWORTH | LONE STAR GAS CO | EMPLOYEE FOR HAUGHT CONSTRUCTION COMPANY WAS CUTTING REINFORCEMENT RODS FROM SEWER PIPE USING A GASOLINE POWERED SAW. THERE WAS A SMALL CONCENTRATION OF NATURAL GAS THAT HAD BUILT UP IN THE STORM SEWER WHICH EXPLODED AS A RESULT FROM SPARKS CREATED FROM | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
771 | 1987-04-27 | NE | other |  | METROPOLITAN UTILITIES DISTRICT | ORIGIN & CAUSE OF GAS ESCAPE IS UNKNOWN AT THIS TIME. PERIMETER OF HUSE, GAS SERVICE & MAINS WERE HECKED BY BAR HOCING W/FLAME IONIZATION & "CGI" MACHINES. ALL READIGS WERE NEGTIVE. BASEMENT METER SET UNDAMAGED BY FIRE OR EXPLOSION. METER SECURED, GAS | 60000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
772 | 1988-06-01 | CO | other |  | PUBLIC SERVICE CO OF COLORADO | ON JUNE 1, 1988, GRIMM CONSTRUCTION PULLED AN 1 1/4" STEEL SERVICE OUT OF AN 1 1/4" OMPRESSION COUPLING AT THE TAP TO 1245 W. ALAMEDA AVENUE. THE CONTRACTOR WAS INSTALLLING A NEW WATER MAIN FOR THE DENVER WATER BOARD WHEN THE BACKHOE ENCOUNTERED THE STEE | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
773 | 1988-06-02 | KY | maintenance | UNKNOWN (MCCRACKEN COUNTY) | WESTERN KENTUCKY GAS CO | COOROSION LEAK ON 2" MAIN IGNITED BY UNKNOWN CAUSE. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
774 | 1988-05-18 | CA | other |  | PACIFIC GAS & ELECTRIC CO | FAULTY OPERATION OF GAS RANGE | 70000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
775 | 1988-03-21 | CA | other |  | PACIFIC GAS & ELECTRIC CO | CHILDREN PLAYING WITH WALL FURNACE IGNITED NEWSPAPER; RESULTING FIRE SPREAD TO STRUCTURE. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
776 | 1988-06-13 | TN | other | PHILLIPS DRISCOPIPE | MEMPHIS LIGHT GAS & WATER DIVISION | A CONTRACTOR, VILLAGE PLUMBING COMPANY, EXCAVATING WITH A BACKHOE TO INSTALL A SEWER LINE TO A NEW HOUSE UNDER CONSTRUCTION AT 4366 OLD FOREST RD. STRUCK AND RUPTURED A 2" POLYETHYLENE GAS MAIN. TWO EMPLOYEES OF THE PLUMBING COMPANY ENTERED THE EXCAVATIO | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
777 | 1988-06-01 | TX | other | DUPONT | ENTEX INC | HASSELL CONSTRUCTION WAS INSTALLING MANHOLE AND CUT 2" PLASTIC MAIN. | 300 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
778 | 1988-06-01 | TX | other | UNKNOWN (MONTGOMERY COUNTY) | ENTEX INC | OUTSIDE PARTY STRUCK 2" PLASTIC DISTRIBUTION MAIN WITH DOZER BLADE. GAS IGNITEE, RESULTING IN MINOR FACIAL BURNS TO BULLDOZER OPERATOR. THERE WAS NO DAMAGE TO EQUIPMENT OR PROPERTY OTHER THAN THE ACTUAL GAS MAIN BREAK. THE EQUIPMENT OPERATOR WAS TREATE | 300 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
779 | 1988-06-08 | IN | other | UNKNOWN (FULTON COUNTY) | NORTHERN INDIANA PUBLIC SERVICE CO | AN EXCAVATING CONTRACOR, WHO WAS USING A BACKHOE STRUCK AND PULLED APART THE COMPRESSION COUPLING OF THE 1 1/4 SERVICE LINE TO THE HOUSE AT 717 E. 9TH STREET CAUSING GAS TO BLOW BELOW GROUND AGAINST THE FOUNDATION. GAS ACCUMULATED WITHIN THE HOUSE AND SO | 80000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
780 | 1988-06-08 | CA | technical failure | UNKNOWN (ALAMEDA COUNTY) | PACIFIC GAS & ELECTRIC CO | AT APPROXIMATELY 1334 HOURS, JUNE 8, 1988 TWO PACIFIC GAS AND ELECTRIC COMPANY EMPLOYEES WERE BURNED AS A RESULT OF GAS IGNITION IN AN EXCAVATION IN WHICH THEYWERE WORKING. THE EMPLOYEES HAD BEEN IN THE PROCESS OF CUTTING A 3" STEEL SERVICE LINE WHEN GAS | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
781 | 1988-06-28 | MN | other |  | MINNEGASCO INC | WHILE PREPARING MAIN FOR CONNECTION TO A CONTINUING MAIN AND AFTER THE TAP HAD BEEN MADE,SUDDENLY THE END OF THE TAPPED MAIN IGNITED.CONTINUED BURNING UNTIL GAS SUPPLY IN MAIN WAS TURNED OFF. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
782 | 1988-04-17 | TX | other |  | DUMAS, CITY OF |  | 30000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
783 | 1988-06-24 | TX | other | UNKNOWN (BEXAR COUNTY) | SAN ANTONIO CITY PUBLIC SERVICE BOARD | PICK-UP TRUCK DRIVER LOST CONTROL OF VEHICLE. HIT METER, BROKE SERVICE RISER, GAS IGNITED. | 140000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
784 | 1988-07-08 | TX | other | DUPONT | ENTEX INC | DURWOOD GREEN WAS PUTTING IN NEW STREET & GOT INTO LINE WITH LIME MIXER MACHINE | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
785 | 1988-05-25 | TX | other | UNKNOWN ( COUNTY) | ENTEX INC | CONTRACTOR, WHILE INSTALLING A STROM SEWER LINE, HOOKED A 2" GAS SERVICE LINEAND PULLED IT APART FROM AN 8" MAIN LINE. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
786 | 1988-07-06 | FL | other |  | CITY GAS CO OF FLORIDA | DRIVER OF AUTO LOST CONTROL AND HIT RISER/METER SET AND HOUSE CAUSING EXTEN. DAMAGE. CALL WAS RECEIED FROMT EH FIRE DEPARTMENT THAT A CAR HAD HIT A RISER AND FIRE WAS INVOLVED AT 12:44 P.M. OUR UNITS RESPONDED AND MADE SAFE AT 1:22 P.M. BY PINCHING AND | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
787 | 1988-07-20 | WA | other | FISHER | WASHINGTON WATER POWER CO | TRUCK BACKED INTO METER SET ASSEMBLY WHICH BROKE THE GAS SERVICE REGULATOR ANDTHE BUILDING CAUGHT ON FIRE. | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
788 | 1988-07-14 | TN | other | POLY-ARK | FAYETTEVILLE GAS SYSTEM | JOHNSON & JOHNSON CONSTRUCTION COMPANY EMPLOYEES, DANIEL SMITH AND DEAN HILL, WERE IN THR PORCESS OF PURGING AIR FROM A RECENTLY INSTALLED 400 FOOT SECTION OF 2 INCH POLYETHYLENE PIPE. THE EMPLOYEES HAD INSTALLED A SQUEEZE-OFF TOOL APPROXIMATELY 3 FEET F | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
789 | 1988-06-24 | CO | technical failure |  | PUBLIC SERVICE CO OF COLORADO | NATURAL GAS FROM BROKEN SERVICE APPARENTLY MIGRATED THROUGH SOIL AND INTO BUILDING THROUGH CRACKED CONCRETE SLAB FLOOR. THE SOURCE OF IGNITION IS UNKNOWN AT THIS TIME. | 200000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
790 | 1988-07-09 | OH | other | UNKNOWN (STARK COUNTY) | COLUMBIA GAS OF OHIO INC | SHARP METAL OBJECT WHICH WAS BURIED IN THE BACKFILL OF CUSTOMER OWNED SERVICE LINE PENETRATED 1" P.E. PIPE WALL OVER A PERIOD OF TIME FROM ORIGINAL INSTALLATION DATE FORCE CAUSING PENETRATION UNDETERMINED. CUSTOMER OWNED SERVICE LINE HAD BEEN TESTED AT 9 | 35000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
791 | 1988-06-22 | TX | other |  | ENERGAS CO | A FIRE OF UNKNOWN ORIGIN DESTROYED HOUSE; OCCUPANT HAS 2ND/3RD DEGREE BURNS. | 85000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
792 | 1988-07-16 | TX | other |  | ENERGAS CO | PERCY EDWARDS, ENERGAS MANAGER AT FLOYDADA, RECEIVED A CALL FROM THE SHERIFF'S DEPARTMENT ABOUT AN EXPLOSION AT 216 WEST VIRGINIA. WHEN HE AND A SERVICEMAN ARRIVED AT THIS ADDRESS, AT 11:00 PM, THE GAS METER HAD ALREADY BEEN TURNED OFF.THE EXPLOSION HAD O | 20000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
793 | 1988-07-07 | TX | other | UNKNOWN (TRAVIS COUNTY) | SOUTHERN UNION GAS CO | SOUTHERN UNION GAS COMPANY LINE LOCATING PERSONNEL HAD RESPONDED TO CONTRACTOR'SREQUEST TO MARK GAS FACILITIES ON JUNE 15, 1988. MARK WAS PLACED ON PAVEMENT 4'1" FROM DAMAGE SITE. | 1 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
794 | 1988-07-13 | TX | other | UNKNOWN (TRAVIS COUNTY) | SOUTHERN UNION GAS CO | SWELLING OF CLAY SOIL BENEATH THE PIPE PUSHING UPWARD CAUSED STRESS FRACTURE. | 1000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
795 | 1988-06-17 | TX | other | UNKNOWN (TRAVIS COUNTY) | SOUTHERN UNION GAS CO | DELIVERY TRUCK BACKED OVER COMMERCIAL METER SET - CRACKING THE BIPASS LINE AND THE METER CASE. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
796 | 1988-05-26 | CA | other |  | PACIFIC GAS & ELECTRIC CO | ATTEMPTED SUICIDE INVOLVING THE ACCUMULATION OF NATURAL GAS IN THE ABOVE STRUCTURE RESULTED IN AN EXPLOSION. THIS INTENTIONAL RELEASE OF GAS ORIGINATED ON THECUSTOMER'S HOUSELINE. NEARBRY BUILDINGS WERE EVACUATED AS A PRECAUTION. | 4900 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
797 | 1988-06-27 | PA | other |  | PHILADELPHIA GAS WORKS | A RESIDENT OF 2461 SEPVIVA STREET IDENTIFIED AS MR. RICHARD LITOSTANSKY, ALLEGEDLY DESPONDENT OVER MARITAL PROBLEMS, CALLED POLICE TO HIS HOME AND WHEN THEY ARRIVED ON THE SCENE, HE WENT TO THE BASEMENT OF 2461 SEPVIVA AND REMOVED A 3/4/" ACREW PLUG FROM | 75000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
798 | 1988-07-19 | VA | technical failure | PLEXCO | LYNCHBURG GAS CO | THE NEW PLASTIC GAS PIPELINE TO ENGLISH'S SUBDIVISION IN HURT, VA. HAD BEEN COMPLETED. OUR CONTRACTOR, FALWELL CORP., HAD LOADED SOME GAS TO THE LINE IN PREPARATION TO PURGE THE LINE OF AIR. JEFF MYERS (CONTRACTOR) AND ROBERT STONE (LYNCHBURG GAS) WENT TO | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
799 | 1988-07-31 | CA | other | UNKNOWN (LOS ANGELES COUNTY) | SOUTHERN CALIFORNIA GAS CO | THE INCIDENT OCCURRED ON JULY 31, 1988 AT 1243 WEST 101ST STREET, LOS ANGELES,LOS ANGELES COUNTY. DUE TO EXTENSIVE DAMAGE TO A HOUSE RESULTING FROM AN EXPLOSION, A TELEPHONIC REPORT WAS MADE TO THE CALIFORNIA PUBLIC UTILITIES COMMISSION. A 3/4 INCH THRE | 40000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
800 | 1988-08-01 | CA | other | DUPONT | SOUTHERN CALIFORNIA GAS CO | THE INCIDENT THAT OCCURRED ON AUGUST 1, 1988, AT THE INTERSECTION OF MATIE ROADAND SPYGLASS DRIVE, PISMO BEACH, SAN LUIS OBISPO COUNTY. DUE TO EXTENSIVE DAMAGE TO THE EQUIPMENT OF A THIRD PARTY OPERATOR,A TELEPHONIC REPORT WAS MADE TO THE CALIFORNIA PUBL | 12850 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
801 | 1988-07-01 | TX | other | UNKNOWN (TRAVIS COUNTY) | SOUTHERN UNION GAS CO | CONTRACTOR DAMAGED SERVICE LINE WHILE BACKFILLING A DITCH THAT WAS CUT TO FACILITATE THE INSTALLATION OF A 66" WATER TRANSMISSION MAIN.HE BUILDING WAS OF DOUBLE BRICK WALL CONSTRUCTION WITH WOOD RAFTERS AND SHEETING, AND ASPHALT ROOF. THE BUILDING FIRE DA | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
802 | 1988-08-01 | NY | other |  | ROCHESTER GAS & ELECTRIC CORP | GENTLEMAN AT 105 JERSEY ST. CALLED HIS GIRLFRIEND AT KODAK WHERE SHE WORKED ANDSAID HE WAS GOING TO COMMIT SUICIDE. SHE CALLED KODAK SECURITY WHO THEN CALLED911. THE POLICE AND FIRE DEPARTMENTS RESPONDED AND THE FIRE DISPATCHER NOTIFIED R.G.&E. ALL OF | 300000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
803 | 1988-07-22 | VA | technical failure | EXTRON | UNITED CITIES GAS CO |  | 10000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
804 | 1988-07-22 | TX | ACCIDENTALLY CAUSED BY OPERATOR |  | ENERGAS CO | WHILE SERVICING DISTRICT REGULATOR STATION MAINTENANCE MAN INADVERTENTLY LEFT VALVE CLOSED RESULTING IN OUTAGE. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
805 | 1988-07-15 | CA | other | ROCKWELL | PACIFIC GAS & ELECTRIC CO | FIRE BEGAN IN A PILE OF CARDBOARD BOXES NEAR THE METER SET. THE HOUSE IGNITED, WHICH THEN IGNITED THE METER SET. | 85000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
806 | 1988-07-21 | SC | ACCIDENTALLY CAUSED BY OPERATOR |  | LANCASTER COUNTY NATURAL GAS AUTH | THEY HAD PUT A 2" X 1/2 IPS PLASTIC SADDLE ON 2" PLASTIC LINE. WHEN THEY HAD FOUND OUT IT WAS WRONG, THEY WERE GOING TO REPLACE IT WITH A 2" X 5/8" PLASTIC SADDLE. DURING THIS CHANGEOVER, SOMETHING CAUSED A FLASH FIRE AND BURNED THESE TWO MEN. THE FLAS | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
807 | 1988-08-01 | WI | other | COBRA METAL HOSE INC. | WISCONSIN SOUTHERN GAS CO INC | THE BRAZING/SOLDERING THAT CONNECTED AN END FITTING TO THE TUBING DETERIORATED AND THE FITTING SEPERATED FROM THE TUBING. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
808 | 1988-07-25 | KY | other | UNKNOWN (FLEMING COUNTY) | FLEMINGSBURG UTILITIES SYSTEM | GAS LINE NOT MARKED ON CONSTRUCTION MAP. CONTRACTORS DID NOT KNOW GAS LINE WASTHERE. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
809 | 1988-08-02 | PA | technical failure | PLEXCO | PEOPLES NATURAL GAS CO | A PIPELINE CONSTRUCTION CREW WAS TIEING-IN A NEWLY LAID PLASTIC LINE T THE EXISTING DISTRIBUTION SYSTEM USING A 2-INCH HIGH VOLUME TAPPING TEE. THE EXISTING LINE, ALSO PLASTIC, WAS OPERATING AT 35 PSIG. THE CREW, USING A MCELROY SIDEWINDER, WAS IN THE P | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
810 | 1988-08-12 | TX | other | UNKNOWN (RANDALL COUNTY) | ENERGAS CO | A SOUTHWESTERN PUBLIC SERVICE COMPANY CREW WAS INSTALLING A CUSTOMER SERVICE LINE DROP. THE LOCATION OF THEIR NEW POLE WAS IN A PUBLIC UTILITY EASEMENT WHERE AN ENERGAS MAIN WAS LOCATED. THEY DRILLED A HOLE IN THE MAIN. 42 CUSTOMERS WERE OUT OF GAS SER | 1000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
811 | 1988-08-06 | MI | other | FLAGG FITTING | CONSUMERS POWER CO | AN EXPLOSION AND FIRE OCCURRED AT AN ABANDONED BUILDING DUE TO A THIRD PARTY DAMAGE. AN EXCAVATING CONTRACTOR HIT AND DAMAGED A 3/4" STEEL GAS SERVICE WITH A BACKHOE BUCKET. THE GAS SERVICE BROKE AT A 3/4" STEEL STREET ELBOW LOCATED INSIDE THE BUILDING | 672000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
812 | 1988-07-14 | CA | other |  | PACIFIC GAS & ELECTRIC CO | ATTEMPTED SUIDICE BY THIRD PARTY OCCUPANT OF UNIT #8. EXTINGUISHED PILOTS ON GAS RANGE ALLOWING GAS TO ACCUMULATE IN THE APARTMENT. THE OCCUPANT IGNITED GAS WITH A CIGARETTE LIGHTER CAUSING STRUCTURAL DAMAGE TO THE BUILDING. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
813 | 1988-08-05 | TX | other | PLEXCO | MORAN UTILITIES CO | CONTRACTOR WAS INSTALLING WATER LINE AT #12 HAWTHORNE DRIVE WITH A SMALL WALK BEHIND TRENCHER AND CUT A TWO INCH POLY GAS MAIN. GAS IGNITED, OPEATOR REFUSE TREATMENT FOR 1ST DEGREE BURNS ON ARM AND FACE OFFERED BY FIRE DEPARTMENT. FIRE DESTROYED TRENCHE | 3000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
814 | 1988-08-16 | MI | other | AMERICAN | MICHIGAN CONSOLIDATED GAS CO (MICHCON) | LIGHTNING STRUCK DWELLING AND CAUSED A FAILURE AT AN OUTSIDE HARDCASE METER. LEAKING GAS THEN IGNITED. A TWO STORY DWELLING AND CONTENTS WERE DESTROYED. | 60000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
815 | 1988-09-26 | AZ | ACCIDENTALLY CAUSED BY OPERATOR |  | SOUTHERN UNION GAS CO | NORTHERN PIPELINE CONSTRUCTION CREW WAS WELDING A 12" X 1" EXTENSION. TOP OF RISER HAD BEEN BENT IN PREVIOUS ACCIDENT AND NORTHERN PIPELINE WAS HIRED TO REPAIR IT. A LEAVE-IN 1" LINE PLUG WAS PUT IN AND THE DAMAGED RISER WAS CUT - WHILE WELDING, THE PLU | 5000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
816 | 1988-09-23 | MI | other | PHILLIPS | CONSUMERS POWER CO | LIGHTNING HIT PLASTIC GAS SERVICE LOCATING WIRE CAUSING GAS LEAK. DAMAGE TO SINGLE FAMILY DWELLING DUE TO FIRE FROM LIGHTNING STRIKE AND LOW LEVEL EXPLOSION. | 95000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
817 | 1988-09-10 | TX | maintenance | UNKNOWN (HARRIS COUNTY) | ENTEX INC | PASSING TRAIN CAUSED SPARKS WHICH STARTED A SMALL GRASS FIRE. GRASS FIRE SPREAD OVER MAIN AND IGNITED GAS ESCAPING FROM ISOLATED CORROSION LEAK ON 18" MAIN. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
818 | 1988-09-14 | TX | other | UNKNOWN (RANDALL COUNTY) | ENERGAS CO | A TORNADO DAMAGED 68 RESIDENCES IN SOUTHWEST AMARILLO. THE ONLY ENERGAS DAMAGEWAS A RISER BROKEN BELOW THE STOP AT 8110 SANTA FE AND A BROKEN REGULATOR AT 4313 SCOTTY DRIVE. | 1000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
819 | 1988-04-24 | WI | other |  | WISCONSIN GAS CO | WISCONSIN GAS COMPANY FACILITIES WERE NOT A CAUSE OF THIS EXPLOSION AND FIRE. AN EXPLOSION AND FIRE BEGAN AT ABOUT 11:20 PM. ON SUNDAY NIGHT IN THE PAINT STORE AT 2324 NORTH FARWELL. THE FIRE SPREAD THROUGHOUT THIS BUILDING, 2334 AND 2340 NORTH FARWELL | 1500000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
820 | 1987-11-26 | NY | other | UNKNOWN (KINGS COUNTY) | BROOKLYN UNION GAS CO | A BROKEN 6" - C.I.B.S. MAIN WAS FOUND IN FRONT OF #44 EAST 57TH STREET O NOVEMBER 26, 1987. MOBILE LEAK SURVEY HAD BEEN PERFORMED ON NOVEMBER 6, 1987 BUT NO LEAK WAS DETECTED AT THAT TIME. CAUSE OF BROKEN MAIN UNKNOWN. | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
821 | 1988-08-31 | IL | ACCIDENTALLY CAUSED BY OPERATOR | PHILLIPS MFG. CO | NORTH SHORE GAS CO | COMPANY CREW PUNCTURED 4" PL/STL TRANSITION FITTING. WHILE EXCAVATING TO SHUT OFF LINE, BROKE A COMMONWEALTH EDISON COMPANY CABLE. IGNITION OCCURRED. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
822 | 1988-09-11 | OK | other |  | OKLAHOMA NATURAL GAS CO | THE INCIDENT OCCURRED AT APPROXIMATELY 16:55 HOURS ON SEPTEMBER 11, 1988, CRITICALLY INJURING THE EMPLOYEE. A LEAK REPORT WAS CALLED IN BY A REAL ESTATE SALESPERSON WHO WAS SHOWING A HOUSE NEXT DOOR TO THE HOUSE WHICH EXPLODED. THE CALLWAS RECEIVED AT 1 | 68000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
823 | 1988-09-18 | TX | other |  | ENERGAS CO | THE INCIDENT APPARENTLY OCCURRED ABOUT 10:45 PM ON SUNDAY, SEPTEMBER 18TH. WAYNE ELLISTON DID NOT LEARN OF ITS OCCURRENCE UNTIL THE NEXT MORNING. THE TULIA FIRE DEPARTMENT RESPONDED TO THE FIRE AND TURNED THE GAS METER OFF THAT SERVES THE BUILDING. BEC | 20000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
824 | 1988-09-21 | TX | other |  | ENERGAS CO | OUR DISPATCHER WAS CALLED AT 2:23 AM. THIS MORNING, SEPTEMBER 21ST BY SANDRA CODY OF THE SHALLOWATER POLICE DEPARTMENT REPORTING A FIRE. OUR SERVICEMAN IN TURN WAS DISPATCHED TO THE LOCATION AT 703 10TH STREET IN SHALLOWATER. HE FOUND THE STORAGE HOUSE | 3000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
825 | 1988-09-11 | NM | other | UNKNOWN (QUAY COUNTY) | GAS CO OF NEW MEXICO | ON SEPTEMBER 11,1988, AT APPROXIMATELY 2:20 A.M. A CAR HIT A RESIDENTIAL METER SET LOCATED AT 915 S. ADAMS STREET, TUCUMCARI, NEW MEXICO. THE ACCIDENT RESULTED IN THE FAILURE OF THE STEEL SERVICE LINE, IMMEDIATELY UPSTREAM OF THE INLET VALVE. THE CAR AN | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
826 | 1988-08-16 | TX | other |  | LONE STAR GAS CO |  | 35000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
827 | 1988-08-08 | TX | other | NIPAK | LONE STAR GAS CO | PIPELINE HAD BEEN EXPOSED BY PARTY CAUSING DAMAGE TO COMPLETE WORK ON PHONE CABLES. | 5000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
828 | 1988-07-01 | TX | other | LONE STAR | BRAZOS RIVER GAS CO | APPROXIMATELY AT THE DATE AND TIME INDICATED, A TRUCK OWNED AND OPERATED BY L-M-S POLE LINE CONSTRUCTION CO WAS SOUTHBOUND ON FM 1287 PULLING A LOADED POLE TRAILER. L-M-S WAS DOING SOME WORK IN THE BUNGER AREA FOR FORT BELKNAP ELECTRIC COOP. THE TRAILER C | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
829 | 1988-09-12 | TX | other | UNKNOWN (TRAVIS COUNTY) | SOUTHERN UNION GAS CO | CONTRACTOR INITIATED EXCAVATION THE AFTERNOON OF SEPTEMBER 12,1988 (SAME DAY ASINCIDENT) WITHOUT NOTIFYING LOCAL UTILITIES OF PROPOSED EXCAVATION EITHER BY PHONE OR THROUGH LOCAL ONE-CALL SYSTEM.CONTRACTOR WAS INITIATING EXCAVATION WITH TRACKHOE TO PLACE | 6000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
830 | 1988-09-14 | TX | other | UNKNOWN (TRAVIS COUNTY) | SOUTHERN UNION GAS CO | WHILE DRILLING TO REPLACE UTILITY POLE, CONTRACTOR DAMAGED A 6" WS GAS MAIN. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
831 | 1988-08-18 | TX | other | UNKNOWN (TRAVIS COUNTY) | SOUTHERN UNION GAS CO | EXCAVATOR WAS CUTTING BAR-DITCH FOR STATE HIGHWAY DEPT ROAD PROJECT USING A CATAPILLER 933 LOADER WHEN EQUIPMENT STRUCK AND PUNCTURED A 12" WS HIGH PRESSURE MAIN.IN MARCH, 1988, SOUTHERN UNION GAS COMPANY WAS NOTIFIED BY THE TEXAS STATE HIGHWAY DEPARTMENT | 130000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
832 | 1988-09-04 | LA | other |  | LOUISIANA GAS SERVICE CO | GAS SERVICEMAN TURNED ON GAS FOR NEW CUSTOMER AT 105 OLLIE DRIVE ON FRIDAY, SEPTEMBER 2, 1988. AT 0435 HOURS CDT, SEPTEMBER 4, 1988 THE PLAQUEMINES PARISH FIRE DEPARTMENT CALLED THE LOUISIANA GAS SERVICE COMPANY NIGHT DISPATCHER NOTIFYINGHIM OF AN EXPLOS | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
833 | 1988-09-28 | NY | other | UNKNOWN (BROOME COUNTY) | COLUMBIA GAS OF NEW YORK INC | A 1" COATED STEEL CUSTOMER-OWNED SERVICE LINE WAS BROKEN BY A CONTRACTOR DIGGING FOR A SEPTIC TANK. THE GAS MIGRATED INTO THE HOUSE AND WAS IGNITED BY AN UNKNOWN SOURCE. THE HOUSE EXPLODED AND BURNED. NO INJURIES OF FATALITIES OCCURRED. | 75000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
834 | 1988-09-29 | TX | other | UNKNOWN (TARRANT COUNTY) | LONE STAR GAS CO | CURRENTLY UNDER IVESTIGATION. | 30000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
835 | 1988-10-22 | TX | other | UNKNOWN (HUTCHINSON COUNTY) | ENERGAS CO | A FIRE OF UNKNOWN ORIGIN DESTROYED HOUSE. | 45000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
836 | 1988-10-06 | TX | other |  | ENTEX INC | FARMER CUTTING DRAINAGE DITCH PUNCTURED 8" PIPE LINE. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
837 | 1988-10-17 | TX | other | UNKNOWN (MOORE COUNTY) | SOUTHERN UNION GAS CO | AT A DISTANCE OF EIGHT FEET WEST OF TEH METER, A TRANSITION ( STEEL TO ABS PLASTIC) WAS CRACKED AND LEAKING. | 10000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
838 | 1988-09-28 | TX | other | NIPAK | LONE STAR GAS CO |  | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
839 | 1988-10-04 | TX | other | UNKNOWN (HARRIS COUNTY) | ENTEX INC | GAS LEAKING FROM OPEN HOUSE LINE IGNITED AND EXPLODED A VACANT HOUSE. TELEPHONIC REPORT MADE BECAUSE OF THE SIGNIFICANCE OF THE EVENT. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
840 | 1988-09-29 | TX | other | UNKNOWN (TRAVIS COUNTY) | SOUTHERN UNION GAS CO | SOIL SHRINKAGE DUE TO DRY WEAHER CAUSED STRESS FRACTURE IN CAST IRON MAIN. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
841 | 1988-10-04 | TX | other | DUPONT | ENTEX INC | CONTRACTOR WAS INSTALLING UNDERGROUND CABLE WITH SMALL TRENCHER AD CUT SERVICE LINE. GAS IGNITED, BURNING TRENCER AND BRICK WALL. ONE EMPLOYEE OF CONTRACTOR WAS TREATED FOR A MINOR BURN AND RELEASED. | 5000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
842 | 1988-09-30 | TX | technical failure | UNKNOWN (ECTOR COUNTY) | ENERGAS CO | LEAKING GAS ACCUMULATION IN WATER METER BOX. CUSTOMER IGNITED THE GAS WITH LIGHTER AND RECEIVED MINOR FLASH BURNS TO FACE. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
843 | 1988-09-11 | TX | other | NIPAK | LONE STAR GAS CO | A TRANSVERSE CRACK OCCURRED IN A 2" POLYETHYLENE MAIN, EXTENDING ABOUT ONE-HALFTHE CIRCUMFERENCE OF THE PIPE. IT WAS LOCATED AT THE BASE OF A SERVICE TAP. | 500 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
844 | 1988-09-17 | TX | other | UNKNOWN (BEXAR COUNTY) | SAN ANTONIO CITY PUBLIC SERVICE BOARD | LIGHTNING STRUCK RISER, ESCAPING GAS IGNITED. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
845 | 1988-09-11 | CA | other | NIPAC | SOUTHERN CALIFORNIA GAS CO |  | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
846 | 1988-09-20 | CA | other |  | PACIFIC GAS & ELECTRIC CO | A STRUCTURE FIRE OF AN UNKNOWN ORIGIN DESTROYED TWO GAS METERS, ALLOWING GAS TOESCAPE & IGNITE. BUILDINGS WERE EVACUATED & TRAFFIC REROUTED. | 1001000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
847 | 1988-10-31 | MA | other | UNKNOWN (MIDDLESEX COUNTY) | BOSTON GAS CO | CONTRACTOR DID NOT NOTIFY DIG SAFE AS REQUIRED BY MASSACHUSETTS LAW. CONTRACTOR EXCAVATING TO REPLACE SEPTIC TANK COVERS, PULLED AND BROKE A 3/4 INCH H.P. STEEL GAS SERVICE CAUSING FIRE AND EXPLOSION. | 200000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
848 | 1988-10-10 | OH | other | UNKNOWN (HURON COUNTY) | COLUMBIA GAS OF OHIO INC | EXPLOSION AND FIRE OCCURRED AT THIS ADDRESS. OCCUPANTS REPORTEDLY HAD SMELLED GAS. THE SON INVESTIGATED ODOR ABOUT 5:00 PM. AND THE FATHER ABOUT 7:00 PM. WHEN THE FATHER, RETURNING FROM THE BASEMENT, TURNED LIGHT OUT, THE EXPLOSION OCCURRED. INVESTIGA | 90000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
849 | 1988-10-25 | IL | other |  | NORTHERN ILLINOIS GAS CO | A CAR ENTERED THE DRIVEWAY OF THE COMMERCIAL BUILDING AT 124 SCHMALE RD, AND DROVE INTO THE SIDE OF THE STRUCTURE DAMAGING THE METER SET AND REGULATOR, CAUSINGFIRE AND WATER DAMGE. | 150000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
850 | 1988-10-21 | IL | other |  | NORTHERN ILLINOIS GAS CO | LOUIS RUFFOLO AND SONS, BOLINGBROOK , ILLINOIS, WERE INSTALLING WATER SERVICE STUBS ON MILL STREET. AT 11:52 AM. NI-GAS RECEIVED A REPORT OF A HIT GAS MAIN AT711 MILL STREET. AT 12:08 A NI-GAS EMPLOYEE ARRIVED AND MADE A LEAK INVESTIGATION. THE MAIN I | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
851 | 1988-10-18 | NY | maintenance | UNKNOWN (NASSAU COUNTY) | LONG ISLAND LIGHTING CO |  | 200000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
852 | 1988-11-03 | PA | other | DUPONT | PHILADELPHIA ELECTRIC CO | AT 06:14 ON NOVEMBER 3, 1988, AN EXPLOSION OCCURRED AT 1842 SHALLCROSS AVE. FOLCORFT. THE FORCE OF THE EXPLOSION PUSHED OUT THE FRONT FOUNDATION WALL, BENDINGTHE GAS SERVICE RISER SLEEVE AT THE SERVICE HEAD ADAPTER. THE METER ASSEMBLY WAS COVERED BY THE | 300000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
853 | 1988-11-04 | CA | other | POWELL | PACIFIC GAS & ELECTRIC CO | SUSPECTD ARSON, NATRUAL GAS EXPLOSION IN VACANT DUPLEX CAUSED WALL TO FALL ON RISER AND METER SET. | 65500 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
854 | 1988-11-03 | CA | other | UNKNOWN (ALAMEDA COUNTY) | PACIFIC GAS & ELECTRIC CO | INSUFFICIENT VENTALIATION OF THE CUSTOMER-OWNED GAS WASTER HEATER ALLOWED CUMBUSTION BYPORDUCTS TO COLLECT IN THE LIVING SPACE RESULTING IN CARBON MONIXIDE POISONING. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
855 | 1987-01-25 | NY | other | UNKNOWN (NASSAU COUNTY) | LONG ISLAND LIGHTING CO | PIPE FRACTURED DUE TO IMPROPER BACKFILLING DURING SERWER CONSTRUCTION. | 300000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
856 | 1987-02-17 | NY | other | DUPONT | LONG ISLAND LIGHTING CO | EXCAVATOR PROVIDED INCORRECT INFORMATION ON THE LOCATION RESULTING IN MARKOUT OF WRONG LOCATION. | 30000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
857 | 1988-03-04 | NV | other | UNKNOWN (CLARK COUNTY) | SOUTHWEST GAS CORP | A CRACKIN A 1/2" PVC SERVICE TO SPACE 37 WORLD WIDE MOBILE HOME PARK LEAKED ANDWAS APPARENTLY IGNITED BY THE WATER HEATER. THE MOBIL HOME ( SPACE 37) AND ITSCOTENTS WAS DESTROYED BY FIRE. THE SERVICE WAS ABANDONED. | 64685 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
858 | 1988-11-01 | TX | other | UNKNOWN (EL PASO COUNTY) | SOUTHERN UNION GAS CO | ON NOVEMBER 1, 1988 AT 12:48 PM. A CONTRACTOR WORKING FOR 3EL PASO ELECTRIC COMPANY DAMAGED OUR 4" H.P. PIPELINE WITH AN AUGER WHILE INSTALLING POWER POLES. THE ELECTRIC COMPANY HAD REQUESTED THAT OUR LINES BE SPOTTED ON SEPTEMBER 16, 1988, AT WHICH TIME | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
859 | 1988-10-09 | KS | other |  | K P L GAS SERVICE | CAUSE HAS BEEN LISTED AS INCENDIARY BY THE LOCAL FIRE DEPARTMENT. FOUND NO INDICATION OF GAS LEAKAGE ON ANY KPL GAS SERVICE FACILIITIES. INITIAL SHUTIN TESXTREVEALED LEAKAGE TOO SMALL TO ESTIMATE. | 41000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
860 | 1988-11-11 | TX | other |  | ENERGAS CO | A KITCHEN FIRE OCCURRED FOR REASONS UNKNOWN. FIRE DAMAGE TO KITCHEN AREA RESULTED. INCIDENT ON CUSTOMER'S PREMISES. | 20000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
861 | 1988-11-21 | TX | other |  | ENERGAS CO |  | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
862 | 1988-11-21 | TX | other |  | ENERGAS CO | OCCUPANT LIGHTED THE WALL FURNANCE AND IGNITED GAS ESCAPING A FAULTY CONNECTION. FIRE DAMAGE TO WALL RESULTED. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
863 | 1988-11-15 | TX | other | PHILLIPS | ENERGAS CO | A TEXAS HIGHWAY DEPARTMENT CREW REPLACING CULVERT HIT 2" GAS LINE. 28 CUSTOMERSWERE OUT OF GAS FOR 4 HOURS. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
864 | 1988-11-11 | TX | other |  | SOUTHERN UNION GAS CO | WHILE LIGHTNING AND CHECKING HEATING FURNACES, THE SCHOOL MAINTENANCE PERSONNELWERE PURGING THE LINE TO A FURNACE. THE BLOWER WAS RUNNING AND DREW THE PURGEDGAS INTO THE DUCT SYSTEM AND THEN WAS BLOWN INTO THE SCHOOL MAIN BUILDING. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
865 | 1988-10-19 | TX | other | PLEXCO | SOUTHERN UNION GAS CO | CONTRACTOR WAS USING PORTABLE ELECTRIC AUGER TO DRILL HOLES FOR PLACEMENT OF PARK BENCHES WHEN A 1" POLY SERVICE WAS STRUCK DAMAGED. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
866 | 1988-10-28 | TX | other | UNKNOWN (TRAVIS COUNTY) | SOUTHERN UNION GAS CO | SHIFT IN SOIL WITH HIGH CLAY CONTENT CAUSED CAST IRON MAIN TO SEPARATE. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
867 | 1988-09-20 | TX | other |  | SOUTHERN UNION GAS CO | APARTMENT OCCUPANT ALLEGELY AN INTENTIONALLY TURNED ON GAS WITHOUT PROVIDING FOR SAFE AND PROPER IGNITION. ESCAPING GAS WAS FROM OUTLET ON CUSTOMER PIPING. NO GAS ESCAPED FROM SYSTEM PRIOR TO THE METER. INCIDENT WAS REPORTED DUE TO NEWSMEDIA ATTENTION. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
868 | 1988-10-18 | TX | other |  | SOUTHERN UNION GAS CO |  | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
869 | 1988-10-06 | TX | other |  | SOUTHERN UNION GAS CO | EXCAVATOR HAD EXPOSED 1 1/4" STEEL PIPE AT DEPTH OF APPROX. 18" WHICH WAS WITHIN 18" OF GAS MARK. THE EXCAVATOR, THERE FORE, ASSUMED THIS PIPE WAS THE GAS SERVICE TO 2321 HARTFORD ROAD AND PROCEEEDED TO EXCAVATE PAST THE EXPOSED PIPE. EXCAVATOR STUCK AN | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
870 | 1988-10-30 | MO | other | UNKNOWN (COLE COUNTY) | UNION ELECTRIC CO | AT ABOUT 5:30 AM. (CST) ON SUNDAY, 10/30/88 AN EXPLOSION OCCURRED IN A TWO-STORY OFFICE BUILDING AT 410-412 JEFFERSON STREET, IN JEFFERSON CITY, MISSOURI. TWOADDITINAL BUILDINGS IN THE 400 BLOCK OF JEFFERSON STREET WERE ALSO DAMAGED. UNION ELECTRIC REPO | 400000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
871 | 1988-10-17 | TX | other |  | ENTEX INC | AUTO LEFT ROADWAY TO AVOID COLLISION WITH TRACTOR TRAILER RIG. AUTO STRUCK CYCLONE FENCE AND ENTEX REGULATOR STATION. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
872 | 1988-10-23 | TN | other |  | LEBANON GAS DEPT, CITY OF |  | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
873 | 1988-11-09 | TX | other |  | SOUTHERN UNION GAS CO |  | 40000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
874 | 1988-11-20 | CO | other | UNKNOWN (EAGLE COUNTY) | ROCKY MOUNTAIN NATURAL GAS CO | 1 1/4" MAIN CRACKED. PREVIOUS THIRD PARTY DAMAGE HAD NOT BEEN REPORTED. | 45000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
875 | 1988-11-06 | NM | other | REPUBLIC STEEL | GAS CO OF NEW MEXICO |  | 60000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
876 | 1988-11-19 | NY | other | UNKNOWN (SUFFOLK COUNTY) | LONG ISLAND LIGHTING CO | A CONCRETE CONTACTOR WHILE EXCAVATING FOR FOOTINGS WITH A BACKHOE AT THE BUILDING WALL, HIT A 3/4 INCH STEEL SERVICE PULLING AND BREAKING A FITTING ON HE INSIDE PIPING. THE EXCAPING GAS FILLED THE BASEMENT, SHICH ULTIMATELY AUSED AN EXPLOSION. IGNITION | 1000000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
877 | 1988-11-15 | NC | other | PHILLIPS DRISCOPIPE | PUBLIC SERVICE CO OF NORTH CAROLINA | GTE SERVICEMAN WAS REPAIRING A PHONE CABLE WITH A HEAT SHRINK SLEEVE WHEN HE SET HIS PROPANE TORCH DOWN AND BURNED THROUGH THE GAS SERVICE. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
878 | 1988-11-06 | NE | other | UNKNOWN (OTOE COUNTY) | NEBRASKA CITY UTILITIES | INCIDENT WAS A RESULT OF VEHICLE ACCIDENT. VEHICLE LEFT STREET AND RAN OVER DSTRIBUTION REGULATOR SET. SET WAS COMPLETELY REBUILT AFTER ACCIDENT. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
879 | 1988-10-15 | CA | other | UNKNOWN (ALAMEDA COUNTY) | PACIFIC GAS & ELECTRIC CO | AN ELECTRIC SURGE RESULTED WHEN DAMIEN P. LEE, THIRD PARTY, CLIMBED A 115 KV ELECTRIC TRANSMISSION TOWER AND TOUCHED THE CONDUCTOR. MR. LEE RECEIVED A SHOCK AND FELL APPROXIMATELY SIXTY (60) FEET. AS A RESULT OF INJURIES CAUSED BY THE SHOCK AND HIS FALL | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
880 | 1988-10-31 | CA | other | UNKNOWN (FRESNO COUNTY) | PACIFIC GAS & ELECTRIC CO | UNKNOWN PERSON ENTERED VACANT DUPLEX AT 851 W. ATCHINSON STREET, OPENED AN APPLIANCE VALVE, ALLOWING GAS TO ACCUMULATE IN THE BUILDING AND EXPLODE. THE SOURCEOF IGNITION IS BELIEVED TO BE AN APPLIANCE PILOT LIGHT. PACIFIC GAS AND ELECTRIC COMPANY FACILI | 65000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
881 | 1988-12-08 | LA | other | UNKNOWN (ST TAMMANY COUNTY) | LOUISIANA GAS SERVICE CO | TRACTOR STRUCK RISER AND CAUSED BLOWING GAS TO IGNITE. FIRE BURNED TRACTOR ANDCAUSED INJURY TO OPEATOR. | 5000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
882 | 1988-02-08 | OH | technical failure | UNKNOWN (LAKE COUNTY) | EAST OHIO GAS CO | A FILLET WELD ON THE TOP OF A PAD SADDLE CRACKED FROM ABOUT THE 10:30 O'CLOCK POSITION TO ABOUT THE 1:30 O'CLOCK POSITION. THE WELD WAS MADE BETWEEN JANUARY 19 AND 28, 1988 AS PART OF A NEW 4 INCH BY 20 INCH SIDE CONNECTION ON AN EXISTING20 INCH MAIN THA | 84000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
883 | 1988-11-04 | CA | other | POWELL | PACIFIC GAS & ELECTRIC CO | SUSPECTED ARSON RELATED NATURAL GAS EXPLOSION IN VACANT DUPLEX CUSED BUILDING WALL TO FALL ON METER SET AND RISER. | 65500 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
884 | 1988-09-16 | KS | other | UNKNOWN (JOHNSON COUNTY) | K P L GAS SERVICE | NTSB HAS A SECTION OF THE SERVICE LINE FOR LABORATORY ANALYSIS, PLUS THERE IS ONGOING INVESTIGATION OF PROBABLE CAUSE OF INCIDENT. | 300000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
885 | 1988-12-13 | NH | other | UNKNOWN (MERRIMACK COUNTY) | ENERGY NORTH NATURAL GAS INC |  | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
886 | 1988-12-22 | TX | other | DUPONT | ENTEX INC |  | 7000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
887 | 1988-12-19 | TX | other | UNKNOWN (TRAVIS COUNTY) | SOUTHERN UNION GAS CO |  | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
888 | 1989-01-09 | TX | other | UNKNOWN (BEXAR COUNTY) | SAN ANTONIO CITY PUBLIC SERVICE BOARD |  | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
889 | 1989-01-10 | TX | other | DOMESTIC | GREY FOREST UTILITIES | THE GAS MAIN WAS DAMAGED BY A CONTRACTOR WHILE BACKFILLING A SEWER MAIN. A CORNER OF A BACKHOE LOADER STRUCK THE PIPE. ALL GAS MAINS WERE SHOWN ON THE CONTRACTOR'S PLANS. OPERATORS PERSONNEL ATTENDED PRECONSTRUCTION MEETINGS. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
890 | 1988-08-12 | CA | other | UNKNOWN (FRESNO COUNTY) | PACIFIC GAS & ELECTRIC CO | A PG&E SERVICEMAN RESPONDED TO A NATURAL GAS LEAK INCIDENT T 214 W. ALAMOS ON OCTOBER 25, 1988. A TREE ROOT WAS FOUND TO HAVE DAMAGED A PLASTIC GAS MAIN, RESULTING IN TE ESCAPE OF GAS TO THE ATMOSPHERE. WHILE INVESTIGATING THE OCTOBER 25, 1988 INCIDENT, | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
891 | 1989-01-09 | MA | other | UNKNOWN ( COUNTY) | COMMONWEALTH GAS CO | THE CAMBRIDGE WATER DEPARTMENT STRUCK AND BROKE AN 8" LP CI GAS MAIN WHILE EXCAVATING FOR A WATER LEAK IN A LOCATION THAT WAS WELL MARKED WITH UNDERGROUND GASLOCATIONS. WATER ENTERED THE GAS MAN AND BEGAN CAUSING OUTAGES IN THE AREA. AT APPROXIMATELY | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
892 | 1989-01-04 | GA | technical failure | PHILLIPS | AUSTELL NATURAL GAS SYSTEM, CITY OF | POOR BONDING IN FUSION JOINT DUE TO SUSPECTED CONTAMINATION. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
893 | 1989-01-01 | UT | other | IPSCO | MOUNTAIN FUEL SUPPLY CO | DIKE ON QUAIL CREEK DAM OWNED BY WASHINGTON COUNTY WATER CONSERVANCY DISTRICT FAILED. THE ENSUING WATER RELEASE WASHED THE PIPELINE FROM THE TRENCH, CAUSING THE PIPE TO RUPTURE. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
894 | 1988-12-29 | MA | other |  | BAY STATE GAS CO | BUILDING CONTRACTOR WAS EXCAVATING FOR THE INSTALLATION OF A SEWER LINE TO THE HOUSE ADDITION WHEN HIS BACKHOE OPERATOR BROKE THE NATURAL GAS SERVICE PIPE TO THE EXISTING STRUCTURE COUSING NATURAL GAS TO BLOW INTO CELLAR AREA AND EVENTUALLY WAS IGNITED AN | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
895 | 1988-03-29 | IL | other | DUPONT | CONSUMERS GAS CO | B-1 : THE CAUSE OF THE INCIDENT HAS NOT BEEN DETERMINED. THE COLLAPSE OF A WALL, FALLING OF A ROOF AND /OR FALLING OF A KITCHEN RANGE ON THE METER SETTING ANDRISER EXERTED AND DAMAGING OUTSIDE FORCE. B-2: EXCAVATION BY THE OWNER AND ANOTHER PARTY. ATTA | 60000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
896 | 1988-12-29 | NV | other | PHILLIPS | SOUTHWEST GAS CORP | THE INCIDENT OCCURRED AT 7:45 AM. ON DECEMBER 29, 1988 AS MR. HATT BUTLER OF HICKEY CONSTRUCTION COMPANY, 1420 MAHOGANY DRIVE, MINDEN, DEVEADA 89423, WAS USINGA TORCH TO THAW OUT SOME FROZEN WATER LINES LYING NEAR THE NATURAL GAS SERVICE LINE STUBBED TO T | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
897 | 1988-12-31 | MS | maintenance | U.S. STEEL | MISSISSIPPI VALLEY GAS | THIS ACCIDENT IS STILL UNDER INVESTIGATION BUT IT APPEARS THAT GAS FROM A CORROSION LEAK ON A SERVICE LINE ENTERED THE SANITARY SEWER SYSTEM AND MIGRATED UNDERTHE SLAB FOUNDATION OF 2811 ARBOR HILL DRIVE BY A ROUTE AS YET UNDERTERMINED. GAS APPARETLY ENT | 75000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
898 | 1989-01-02 | LA | other | UNKNOWN (JEFFERSON COUNTY) | LOUISIANA GAS SERVICE CO | WHILE TIGHTENING BUSHING ON RISER, SERVICEMAN HEARD RISER CRACK AND START LEAKING BELOW GROUND. GAS BLEW FOR APPROXIMATELY ONE HOUR UNTIL GAS WAS TURNED OFF AT HOT TAP. UNKNOWN TO REPAIR CREW, GAS ACCUMULATED IN VOID UNDER HOUSE SLAB INTO AN EXPLOSIVE M | 20000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
899 | 1988-12-24 | LA | other | UNKNOWN (PLAQUEMINES COUNTY) | LOUISIANA GAS SERVICE CO | HOUSE TRAILER CAUGHT FIRE CAUSING METER INSTALLATION TO BURN. NATURAL GAS WAS FOUND TO BE ESCAPING FROM A BROKEN PLASTIC SERVICE LINE AT THE METER INSTALLATION. IT IS NOT KNOWN IF THE SERVICE LINE WAS LEAKING BEFOE OR AFTER THE FIRE START | 5000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
900 | 1988-12-15 | PA | other | UNKNOWN (MONROE COUNTY) | UNION GAS CO | GROUND SUBSIDENCE DUE TO SEWER CONSTRUCTION ACTIVITY. | 250000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
901 | 1988-12-07 | AL | other |  | ALABAMA GAS CORP | A 1/2" FUEL LINE VALVE (WITH NO APPLIANCE CONNECTED) WAS FOUND IN THE OPEN POSITION INSIDE THE HOUSE. THIS ALLOWED GAS TO ESCAPE INSIDE THE HOUSE CREATING AN EXPLOSIVE CONDITION. WE HAVE BEEN UNABLE TO DETERMINE THE REASON THE CUSTOMER WOULD HAVE REMOVE | 75600 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
902 | 1989-01-13 | OK | maintenance | UNKNOWN (GRADY COUNTY) | ARKANSAS LOUISIANA GAS CO (ARKLA GAS CO) | AT APPROXIMATELY 6:00 PM. ON FRIDAY, JANUARY 13, 1989, A LINDA SCOTT WHO RESIDES AT 926 SOUTH 15TH IN CHICKASHA SAYS SHE OPENED THE WATER METER VALVE BOX LOCATED NEXT TO THE STREET IN FRONT OF HER HOUSE, LIT A MATCH TO SEE INSIDE AND GOT FLASHED. SHE SAY | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
903 | 1989-01-14 | AL | other | UNKNOWN (JEFFERSON COUNTY) | PLEASANT GROVE MUNICIPAL GAS SYSTEM, CITY OF | DAMAGE CAUSED BY TREE ROOT GROWING AGAINST SERVICE LINE. TREE ROOT MOVED SERVICE LINE AT ELL CAUSING PIPE TO BREAK TO ELL.SUPPLEMENT : MR E J LITTLETON & MRS VIRGINIA LITTLETON DIES FRIDAY, FEBRUARY 17,1989. | 90000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
904 | 1988-12-08 | TX | other | DRISCOPE | LONE STAR GAS CO | 2" POLY SERVICE WAS PULLED OFF 8" WR ST IHP MAIN BY JIM BOWMAN COMPANY REPLACING CURBS UNDER CONTRACT FOR THE CITY OF DALLAS. THIS GAS WAS IGNITED BY A CAR WHICH BURNED UP IN THE 100 BLOCK OF HOUSTON STREET BETWEEN ELM AND MAIN STREET APPROXIMATELY 1 A 1 | 15000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
905 | 1989-01-12 | TX | other |  | ENERGAS CO | AT 1517 HOURS ON JANUARY 12, 1989 ENERGAS RECEIVED A GAS ODOR COMPLAINT FROM A PERSON LEVING AT 118 W. ALBERT. THE ORDER WAS DISPATCHED, AND OUR SRERVICEMAN ARRIVED AT 118 W. ALBERT AT 1525 HOURS. HE MET THE OCCUPANT AT THE DOOR WHERE HEWAS DIRECTED TO | 30000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
906 | 1989-01-12 | TX | other |  | ENERGAS CO | AT CREEK CROSSING PIECES OF BROKEN CONCRETE WERE DUMPED ON GAS LINE CAUSING A FRACTURE. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
907 | 1989-01-18 | IL | other | UNKNOWN (COOK COUNTY) | NORTHERN ILLINOIS GAS CO | OPERATOR OF VEHICLE LOST CONTROL AND RAN INTO METER & REG. AT 1914 S. 9TH AVE. IN MAYWOOD. THE SERVICE WAS BROKEN AND SET HOUSE ON FIRE. THE FIRE DEPARTMENT ON THE SCENE CONTROLLED THE FIRE UNTIL STREET CREW ARRIVED. STREET CREW EXTINGUISHED FIRE AND S | 30000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
908 | 1988-12-24 | CA | technical failure | DUPONT | SOUTHERN CALIFORNIA GAS CO |  | 140000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
909 | 1989-01-11 | MN | other | PLEXCO | NORTHERN STATES POWER CO | TWIN CITY TESTING DRILL TRUCK DRILLED THROUGH 3" IPS PLASTIC MAIN WITH AUGER. IGNITION OF ESCAPING GAS RESULTED, AND DRILL TRUCK WAS SET ABLAZE. DUE TO FIRE NO GAS LINE LOCATING MARKS WERE VISIBLE AT SITE OF DRILL HOLD BUT OTHER LOCATINGMARKS WERE WITHI | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
910 | 1988-12-27 | CO | other | UNKNOWN (DENVER COUNTY) | PUBLIC SERVICE CO OF COLORADO | PRELIMINARY INVESTIGATION OF THE EARTH AROUND THE 2" STEEL GAS MAIN IN THE 800 N. BLOCK OF WOLFF STREET AND PHYSICAL EXAMINATION OF THE SERVICE TAP TO 812 N.WOLFF STREET AND THE ADJACENT COUPLING ON THE 2" STEEL GAS MAIN INDICATED DAMAGE TO THESE FACILI | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
911 | 1989-02-10 | KY | other | UNKNOWN (GALLATIN COUNTY) | UNION LIGHT HEAT & POWER CO | WHILE EXCAVATING TO INSTALL A WATER LINE, CONTRACTOR DAMAGED GAS MAIN DIGGING PARRELL TO GAS MAIN. GAS MAIN IGNITED, FIRE DESTROYED CONTRACTOR'S EQUIPMENT | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
912 | 1989-01-31 | AR | other | UNKNOWN (GARLAND COUNTY) | ARKANSAS LOUISIANA GAS CO (ARKLA GAS CO) | 1" CROSS OVER LINE WAS ACCIDENTALLY STRUCK WHILE DIGGING, 1" LINE CRACKED ABOVETAP VALVE CAUSING LEAK. | 77168 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
913 | 1989-01-28 | CA | maintenance | UNKNOWN (SAN DIEGO COUNTY) | SAN DIEGO GAS & ELECTRIC CO | THE GAS IS BELIEVED TO HAVE MIGRATED FROM BENEATH A CONCRETE ALLEYWAY,TO THE FOUNDATION OF A GARAGE CONVERTED FOR USE AS AN APARTMENT. THE GAS ENTERED A WALL AT THE BEDROOM TO A MIXTURE APPROPRIATE FOR COMBUSTION. THE TENANT LIT A CIGARETTE CAUSING IGNI | 12500 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
914 | 1989-01-22 | MN | other | ORANGBURG | MIDWEST GAS CO | SERVICE LINES WERE INSTALLED IN MAY OF 1966. OTHER UTILITIES WERE INSTALLED IN1971. SERVICE LINES WERE CUT TO ACCOMODATE OTHER UTILITY DITCHES. CUT SERVICELINES WERE RECONNECTED USING A COMPRESSION COUPLING. IMPORPER TAMPING OF BACKFILL CAUSING SETTLE | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
915 | 1989-01-16 | OK | other | DUPONT | OKLAHOMA NATURAL GAS CO | AT APPROXIMATELY 0517 HOURS ON JANUARY 16,1989, AN EXPLOSION DEMOLISHED A CONCRETE BLOCK BUILDING NEAR THE INTERSECTION OF HIGHWAY 117 AND HIGHWAY 66, WEST OF SAPULPA, OKLAHOMA. THE BUILDING WAS BEING RENOVATED AND WAS TO OPEN SOMETIME IN THE SPRING AS A | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
916 | 1988-12-26 | TX | other | UNKNOWN (DALLAS COUNTY) | LONE STAR GAS CO | ON DECEMBER 26, 1988, 6:00 AM., THE CITY OF CARROLLTON WATER DEPARTMENT REQUESTED LINE LOCATION AT THE SUBJECT ADDRESS. LINE WAS MARKED BY FLAGS. THE CITY THEN CUT THE 2" POLY GAS MAIN AND A TV CABLE. BEFORE LONE STAR GAS ARRIVED ON THE SCENE, STORER | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
917 | 1988-09-28 | TX | technical failure | PLEXCO | TOMBALL GAS DEPT, CITY OF | THERE WERE 2-4" MAINS WITH CAPS IN DITCH THAT WE HAD DUG OUT FOR THE TIE IN. THE DITCH WAS 23' IN LENGTH AND 5' IN WIDTH AT POINT OF STIE IN. THE REMAINDER OF THE SQUEEZER ALREADY ON THE PIPE AND SQUEEZED OFF, WITH THE CAP REMOVED. THE STUB ON THE EAST | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
918 | 1989-01-10 | TX | other | UNKNOWN (BEXAR COUNTY) | SAN ANTONIO CITY PUBLIC SERVICE BOARD | HOLE DRILLING MACHINE OPERATOR DRILLING HOLES FOR PIERS DRILLED INTO 8" STEEL GA | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
919 | 1988-12-30 | TX | other | UNKNOWN (JIM WELLS COUNTY) | ENTEX INC | VEHICLE RAN OVER GAS METER IN ALLEY AND GAS IGNITED ON IMPACT. | 5000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
920 | 1988-12-17 | PA | other | UNKNOWN (DELAWARE COUNTY) | PHILADELPHIA ELECTRIC CO | AT 0455 AM. ON DECEMBER 17, 1988, AN EXPLOSION OF LOW MAGNITUDE OCCURRED AT 357HAWARDEN ROAD IN SPRINGFIELD, AND A SMALL FIRE WAS EXTINGUISHED. THE FORCE OF THE EXPLOSION DAMAGED THE STRUCTURE OF THE HOUSE BEYOND REPAIR, ALTHOUGH THE HOUSE REMAINED STAND | 200000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
921 | 1989-01-14 | IL | other | UNKNOWN (MCHENRY COUNTY) | NORTHERN ILLINOIS GAS CO | USE AT 1277 MULBERRY AND WAS IGNITED BY AN UNKNOWN SOURCE CAUSING AN EXPLOSION AND FIRE, THE STRUCTURE AT 1277 MULBERRY WAS COMPLETELY DESTROYED WITH MINOR DAMAGE TO THE HOMES AT 1271 AND 1281. | 200000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
922 | 1989-01-12 | IL | other | UNKNOWN (MCHENRY COUNTY) | NORTHERN ILLINOIS GAS CO | NATURAL GAS FROM A GAS MAIN DAMAGED BY EXCAVATION EQUIPMENT MIGRATED INTO THE HOUSE AT 293 MLLARD AND WAS IGNITED BY AN UNKNOWN SOURCE CAUSING AN EXPLOSION. THE STRUCTURE AT 293 MILLARD WAS COMPLETELY DESTROYED WITH MINOR DAMAGE TO THE HOUSES ON EITHER SI | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
923 | 1989-02-05 | NE | other | UNKNOWN (DOUGLAS COUNTY) | METROPOLITAN UTILITIES DISTRICT | BREAK CAUSED BY THE WEATHER. FROST CAUSED STREET TO HEAVE, BREAKING 3/4" DRIPSTEM. | 10000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
924 | 1989-02-06 | TN | other |  | MIDDLE TENNESSEE NATURAL GAS UTIL DIST | PIPE SPLIT LONGITUDINALLY FOR FULL LENGTH OF PIPE JOINT. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
925 | 1989-02-15 | CO | ACCIDENTALLY CAUSED BY OPERATOR | UNKNOWN ( COUNTY) | PUBLIC SERVICE CO OF COLORADO | DURING REGUALTOR CHANG-OUT, THREADS ON NIPPLE UPSTREAM OF SERVICE VALVE WERE CRACKED. TWENTY FIVE MINS. LATER GAS WAS IGNITED FROM UNKNOWN SOURCE. | 300000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
926 | 1989-02-01 | PA | other |  | EQUITABLE GAS CO | INVESTIGATION OF THE EXPLOSION INDICATES NO EVIDENCE FO COMBUSTIBLES OVER THE COMPANY'S SERVICE LINE OR AROUND PERIMETER OF THE BUILDING. CUSTOMER'S SERVICE LINE (CURB TO METER) WAS PRESSURE TESTED AT 13" WATER COLUMN AND FOUND TO BE NOT LEAKING. HOUSE | 300000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
927 | 1988-11-25 | MS | other |  | K P L GAS SERVICE | A CIRCUMFERAL CRACK IN A 1" SERVICE LINE WAS FOUND AT A 1" COLLAR. THIS PIPE WASTAKEN BY CLINT C TRORPE II, WITH NTSB. WHILE A SPECIFIC CAUSE FOR THE FRACTURE IS NOT READILY AVAILABLE, A PROBABLE CAUSE WOULD BE GROUND SHIFT AND SETTLEMENT,COMBINED WITH TR | 52000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
928 | 1989-02-10 | MS | other | UNKNOWN (JACKSON COUNTY) | KANSAS POWER & LIGHT CO | VISUAL INSPECTION OF THE SERVICE LINE REVEALED A CIRCUMFERENTIAL CRACK, APPROXIMATELY 20' - 6" EAST OF THE METER RISER. THE CRACK WAS APPROXIMATELY TWO-THIRDSAROUND THE DIAMETER OF THE PIPE, AND HAD AN OPENING ON THE BOTTOM SIDE OF A NOMINAL AMOUNT. THE | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
929 | 1989-02-08 | UT | other | STRAINERS INC. | MOUNTAIN FUEL SUPPLY CO | AN INLET STRAINER ON THE STATION OF A DEAD-END SYSTEM PLUGGED WITH GREASE CAUSING THE STATION WHICH FED THE TOWN OF SANTAQUIN, UTAH, TO SHUTDOWN. (659 METERS). | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
930 | 1989-03-10 | DC | other | UNKNOWN ( COUNTY) | WASHINGTON GAS LIGHT CO | UTILITY CONSTRUCTION,INC. WORKING FOR WASHNGTON GAS LIGHT COMPANY INSTALLING A VALVE GAUGE RISER ON A LIVE MAIN, HAD AN EMPLOYEE BURNED WHEN NATURAL GAS IGNITED. A CIVILIAN MOTORIST STOPPED AT A TRAFFIC SIGNAL ADJACENT TO THE WORK TRENCH,LIT A CIGARETTE | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
931 | 1989-03-14 | MN | other | DUPONT | INTERSTATE POWER CO | DRESSER FITING (STYLE 38); APPARENTY LOOSENED OVER THE YEARS. INSTALLED TO CONNECT TWO SECTIONS OF DUPONT ALDYL "A" IN A RELINING INSTALLATION IN 1973. PART3 - TIME AND CONSTANT FLEXONG OF THE PLASTIC PIPE. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
932 | 1989-03-04 | TX | other |  | ENERGAS CO | VEHICLE RAN OVER METER SETTING. ESCAPING GAS IGNITED, BURNING CAR & NEARBY FENCE | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
933 | 1989-02-18 | TX | other | DUPONT | ENTEX INC |  | 6000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
934 | 1989-03-02 | ND | other | ALDYL "A" | NORTHERN STATES POWER CO | THE FIRE AND SLIGHT EXPLOSION AT 845 COUNTRYSIDE TRAILER COURT SOUTH FARGE, ND, MARCH 2, 1989, WAS CAUSED BY A CUT IN THE 5/8" PE IDLE GAS SERVICE SERVING 847COUNTRYSIDE COURT SO., WHICH RUNS UNDER THE SOUTH EAST CORNER OF 845 CONTRYSIDECOURT SO. NSP WA | 7000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
935 | 1989-03-07 | CA | other | UNKNOWN (LOS ANGELES COUNTY) | SOUTHERN CALIFORNIA GAS CO | TREE TRIMMING RESULTED IN LIMB FALLING ON AND BREAKING METER SET FITTING. | 150000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
936 | 1989-04-02 | MO | maintenance | UNKNOWN (ST LOUIS COUNTY) | LACLEDE GAS CO |  | 150000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
937 | 1989-04-02 | MO | other |  | K P L GAS SERVICE | KPL GAS SERVICE WAS CALLED TO THE SCENE OF THE FIRE AT THIS APARTMENT BUILDING TO SHUT OFF THE FLOW OF GAS TO THE BUILDING. THERE WERE SEVEN METERS LOCATED INTHE BASEMENT OF THE BUILDING, WHICH APPARENTLY MELTED,DUE TO THE EXTENSIVE HEATOF THE FIRE, AND | 75000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
938 | 1989-03-08 | MO | other | UNKNOWN (JACKSON COUNTY) | K P L GAS SERVICE | WRITTEN REPORT WAS NOT SUBMITTED WITHIN THE 20 DAY TIME PERIOD, SINCE COMPANY WAS NOT AWARE THAT THE ACCUMULATED TOTAL COSTS WOULD EXCEED $5,000. DAMAGE OCCURRED OUTSIDE OF AREA OF LOCATES.THIRD PARTY WAS REMOVING DIRT WITH BULLDOZER AND STRUCK GAS MAIN. | 9400 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
939 | 1989-03-25 | TX | other |  | ENERGAS CO | SERVICE RISER WAS DAMAGED WHILE FIRE DEPT. ATTENDED TO NEARBY GRASS FIRE. EXCAPING GAS WAS IGNITED BY FIRE. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
940 | 1989-03-24 | TX | other | PLEXCO | SOUTHERN UNION GAS CO | WHILE EXCAVATING WITH CASE 480 BACKHOE TO INSTALL ELECTRIC CONDUCT AT NEW SHOPPING CENTER,CONTRACTOR DAMAGED 2" PE SERVICE LOCATED ON WEST SIDE OF PRIVATE PROPERTY. | 250 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
941 | 1988-11-13 | GA | other | PLOYETHYLENE PROD. | BAINBRIDGE GAS DEPT, CITY OF | EXPLOSION OCCURRED ON 11/13/88 IN LANDMARK APTS. - D16. AFTER GAS PERSONNEL WERE NOTIFIED AREA WAS MADE SAFE BY CHECKING FOR AREA OF POSSIBLE LEAK AND AFTER VERIFICATION OF A LEAK, THE MAIN VALVE SUPPLYING APARTMENTS WAS SHUT DOWN. NEXT, TELEPHONE CALLS | 15000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
942 | 1989-03-29 | KS | other | UNKNOWN (SHAWNEE COUNTY) | K P L GAS SERVICE | ON WEDNESDAY, MARCH 29, 1989, A COMPANY DISPATCHER RECEIVED A CALL FROM THE FIRE DEPARTMENT, INDICATING THAT AN EXPLOSION AND FIRE HAD OCCURRED AT 3030 KENTUCKY. COMPANY PERSONNEL RESPONDED, CONFIRMED THE DAMAGE, AND TOOK STEPS TO CONTROLTHE EMERGENCY. D | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
943 | 1989-03-27 | IA | other |  | PEOPLES NATURAL GAS | GAS SAMPLES WERE TAKEN AND ANALYZED AT STRATEGIC LOCATIONS IN THE PLANT. THE NATURAL GAS LINE FEEDING A FURNACE IN THE ROOM WHERE THE EXPLOSION TOOK PLACE HADNO LEAKS. THEREFORE, IT IS CURRENTLY BELIEVED THAT PROPANE WAS IGNITED. TWO VALVES ON THE PROP | 120000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
944 | 1989-03-22 | WI | technical failure | CONTINENTAL IND. | WISCONSIN GAS CO | ON MARCH 22, 1989 AT APPROXIMATELY 8:35 P.M. THERE WAS AN EXPLOSION AT 521 NORTH STREET, IN THE CITY OF NEKOOSA, WOOD COUNTY, WI. MR. GORDON KRUBSACK, DIED ASA RESULT OF THE EXPLOSION. OLGA KRUBSACK AND KATHY DAVIS SUFFERED SECOND AND THIRD DEGREE BURNE | 75000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
945 | 1989-03-18 | MD | other | AMERICAN METER | BALTIMORE GAS & ELECTRIC CO | AT APPROXIMATELY 1830 HOURS ON 3/18/89 BALTIMORE CITY FIRE DEPARTMENT RECEIVED A NOTIFICATION OF FIRE AT THE ABOVE ADDRESS. A BALTIMORE CITY POLICE OFFICER WAS THE FIRST TO ARRIVED ON THE SCENE. HE OBSERVED HEAVY FIRE COMING FROM FRONT BASEMENT WINDOW. | 150000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
946 | 1989-03-30 | AR | other |  | ARKANSAS LOUISIANA GAS CO (ARKLA GAS CO) | BACKHOE OPERATOR WAS INSTALLING SEWER SERVICE LINE. BACKHOE BUCKET HOOKED CUSTOMERS GAS SERVICE LINE. GAS LINE WAS PULLED AND BROKEN OUT OF 1" ELL AT BASE OF METER RISER NEXT TO HOUSE. | 85000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
947 | 1989-03-06 | AR | other | DRESSER | ARKANSAS LOUISIANA GAS CO (ARKLA GAS CO) | CUSTOMER ATTEMPTING TO READ HIS WATER METER LIT MATCH SO HE COULD SEE DOWN IN WATER METER BOX. NATURAL GAS HAD COLLECTED BENEATH WATER METER BOX LID. GAS IGNITED AND FLASH BURNED CUSTOMER. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
948 | 1989-03-01 | NV | other | KRALOY CONTROL | SOUTHWEST GAS CORP | 1/8" HOLE IN PVC PIPE NEXT TO COUPLING. CUSTOMER CONSTRUCTED ROOM ADDITIONOVER OPERATOR'S 1/2" PVC LINE. | 65000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
949 | 1989-03-09 | VT | other | DRESSER | VERMONT GAS SYSTEMS INC | FROST ACTION PULLED A 3/4" STEEL SERVICE FROM A COMPRESSION OUTLET SERVICE TEE. TOP OF MAIN WAS 2' 10" IN DEPTH AT THIS LOCATION. | 175000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
950 | 1989-02-21 | NC | other | ROCKWELL | PUBLIC SERVICE CO OF NORTH CAROLINA | A ROCKWELL 043 3/4"X1" RIGHT ANGLE BODY WITH IRV REGULATOR FAILED AT THE CUSTOMER'S METER SET ALLOWING 42 PSIG PRESSURE INTO THE HOUSE FUEL LINE, WITH A RESULTING FIRE. ESTIMATED DAMAGE TO HOUSE CAUSED BY FIRE IS $30,000.00. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
951 | 1989-06-05 | MD | other |  | BALTIMORE GAS & ELECTRIC CO | ORIGIN OF THE FIRE WAS LIGHTNING OR ELECTRICAL FAILURE IN 3618 EASTERN AVENUE.SUBSEQUENT FIRE DESTROYED 3618, 3614, 3612 EASTERN AVENUE AND DAMAGED 3610 EASTERN AVENUE. WHEN THE ROOF OF 3618 COLLAPSED, A HOUSE LINE WAS BROKEN ON THE SECOND FLOOR WHICH FU | 150000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
952 | 1989-05-25 | MN | other |  | NORTHERN STATES POWER CO | AS A RESULT OF SEWER WORK IN THIS AREA, A 4" CI MAIN WAS DAMAGED. NATURAL GAS MIGRATED FROM THE LOCATION OF THE DAMAGED PIPE AND FITTINGS, TO A MANHOLE. THE NATURAL GAS WAS IGNITED BY AN UNKNOWN SOURCE, SERIOUSLY BURNING A SEWER WORKER IN THE MANHOLE. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
953 | 1989-04-03 | TX | other |  | ENERGAS CO | A FIRE WAS REPORTED AT 1510 WEIDEL ON APRIL 3, 1989. ROBERT HOGUE OWNER OF THIS RENT HOUSE WAS DOING SOME REPAIR WORK UNDER THE HOUSE, WHEN HE THOUGHT HE SMELLED GAS AND THEN LIT A MATCH. HE DROVE HIMSELF TO THE HOSPITAL, AND THE FIRE WAS REPORTED FROM | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
954 | 1989-05-19 | TX | other | PLEXCO | SOUTHERN UNION GAS CO | CONTRACTOR TRENCHING WITH BACKHOE IN SCHOOL YARD FOR MODIFICATION TO SCHOOL BLDG. STRUCK AND DAMAGED 2" P.E. LINE SERVING IND. METER AT SCHOOL. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
955 | 1989-04-12 | TX | other | UNKNOWN (TRAVIS COUNTY) | SOUTHERN UNION GAS CO | RECEIVED ONE-CALL FROM CONTRACTOR ON 3/30/89 REQUESTING LOCATORS TO MEET WITH CONTRACTOR ON 4/3/89 AT 10 A.M. ON LOCATION. LOCATOR MET WITH CONTRACTOR AND PROVIDED LOCATIONS AS REQUESTED ON 4/3/89. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
956 | 1989-01-07 | MO | maintenance | UNKNOWN (CALLAWAY COUNTY) | FULTON BOARD OF PUBLIC WORKS |  | 21000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
957 | 1989-05-17 | SC | other | PLEXCO | SOUTH CAROLINA ELECTRIC & GAS CO |  | 500 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
958 | 1989-04-09 | MT | other |  | MONTANA - DAKOTA UTILITIES CO | EXPLOSION & FIRE OCCURRED AT SUPER 8 LODGE, 5400 SOUTHGATE DR., BILLINGS, MT, AT APPROXIMATELY 1:11 A.M., 4/9/89. AFTER THOROUGH INVESTIGATION, THE BILLINGS FIRE DEPARTMENT DETERMINED NATURAL GAS EXPLOSION OCCURRED IN BUILDING LAUNDRY ROOM AS A RESULT OF | 1000000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
959 | 1989-03-01 | CA | other |  | PACIFIC GAS & ELECTRIC CO | RV CAUGHT FIRE, SETTING THE HOUSE ON FIRE. OUR METER CAUGHT ON FIRE AFTER THE HOUSE WAS ALMOST COMPLETELY BURNED. THE FIREMEN WERE UNABLE TO TURN OFF THE GASAT THE METER BECAUSE THE SERVICE VALVE BROKE. THE METER FIRE OCCURRED AFTER THE HOUSE WAS ALMOS | 100500 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
960 | 1989-05-09 | LA | other | UNKNOWN (ST TAMMANY COUNTY) | LOUISIANA GAS SERVICE CO | CONTRACTOR BROKE 2" HOT TAP OFF 4" STEEL MAIN WHILE DIGGING A DRAINAGE DITCH. OPERATOR'S EMPLOYEE HAD PREVIOUSLY BEEN ON SITE AND MARKED THE SITE WITH STAKES. STAKES WERE IN PLACE AT TIME OF BREAK. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
961 | 1988-11-17 | NY | other | UNKNOWN (QUEENS COUNTY) | BROOKLYN UNION GAS CO | TWO PEOPLE WERE INJURED WHEN VAPORS FROM GLUE IGNITED IN THE BASEMENT OF 8908 -103RD AVENUE, QUEENS, NEW YORK ON NOVEMBER 17, 1988. NATURAL GAS READINGS WEREPRESENT AT THE FRONT WALL OF THE BASEMENT. A BROKEN 6" C.I.B.S. LP GAS MAIN WAS FOUND ON 103RD A | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
962 | 1989-05-20 | OH | other |  | HAMILTON GAS DEPT, CITY OF | A 1" VALVE IN THE KITCHEN OF THE DOWNSTAIRS APARTMENT WAS OPENED BY TENANT IN AN ATTEMPT TO COMMIT SUICIDE. EXPLOSION WAS CAUSED BY TENANT LIGHTING CIGARETTE. | 60000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
963 | 1989-02-24 | IA | other | UNKNOWN (STORY COUNTY) | IOWA ELECTRIC LIGHT & POWER CO | WHEN OUR CREWS ARRIVED ON THE SCENE THEY WERE UNABLE TO DETECT ANY GAS IN THE GROUND. IT WAS OVER AN HOUR LATER THAT ANY GAS WAS DETECTED AND THE SEARCH FOR A LEAK WAS THEN INITIATED. THE CUSTOMER HAD BEEN HAVING FURNACE TROUBLE DURING THE DAY, AND THERE | 75000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
964 | 1989-03-25 | CA | technical failure | DUPONT | SOUTHERN CALIFORNIA GAS CO | INCIDENT WAS THE RESULT OF IMPORPER ALIGNMENT AND POOR FUSION OF A 2" BRANCHINGSADDLE CONNECTION TO A 2" POLYETHYLENE PLASTIC MAIN. | 150000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
965 | 1989-03-28 | NY | ACCIDENTALLY CAUSED BY OPERATOR | UNKNOWN ( COUNTY) | CONSOLIDATED EDISON CO OF NEW YORK | GAS IGNITION CAUSED NO DAMAGE TO COMPANY OR OUTSIDE PARTY PROPERTY. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
966 | 1989-06-17 | TX | other |  | SOUTHERN UNION GAS CO | GAS ESCAPING FROM DISCONNECTED SPACE HEATER SUPPLY LINE AND TWO (2) OPEN RANGE BURNER VALVES APPARENTLY ACCUMULATED INSIDE THE PRIVATE RESIDENCE RESULTING IN AN EXPLOSION WHICH DESTROYED APPROXIMATELY 75% OF THE STRUCTURE. AUTHORITIES SUSPECT THE INCIDEN | 35000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
967 | 1989-03-27 | TX | other |  | ENERGAS CO | FIRE OF UNKNOWN ORIGIN RESULTING IN ONE FATALITY. SUBSEQUENTLY, FIRE MARSHALL DETERMINED FIRE WAS CAUSED BY COMBUSTIBLES PLACED NEAR SPACE HEATER. | 20000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
968 | 1989-04-18 | TX | ACCIDENTALLY CAUSED BY OPERATOR | UNKNOWN | ENERGAS CO | AN UNDERGROUND VALVE SERVED TWO CHECK METERS. THE EMPLOYEE WAS UNAWARE OF THIS AND THOUGHT THIS VALVE TURNED OFF THE BYPASS FOR ONLY THE METER HE WAS TESTING. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
969 | 1989-01-26 | TX | other |  | ENERGAS CO | A FLASH FIRE OF UNKNOWN ORIGIN CAUSED MAJOR DAMAGE TO HOME. A MAN AND WOMANOCCUPING HOUSE WERE BURNED. A SHUT IN OF CUSTOMER PIPING AFTER INCIDENT SHOWED LEAK OF 3 CFH. | 2000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
970 | 1989-01-20 | TX | other |  | ENERGAS CO | A FIRE OF UNKNOWN ORIGIN STARTED IN BASEMENT OF VACANT WAREHOUSE. THE GAS METER HAD BEEN REMOVED IN JUNE 1986. | 30000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
971 | 1989-01-20 | TX | other |  | ENERGAS CO | THE FIRE HAD ORIGINATED IN THE HOT WATER HEATER CLOSET. DEBRIS WAS FOUND ONTHE FLOOR AROUND THE HOT WATER HEATER. IT HAD APPARENTLY CAUGHT FIRE CAUSING THE HOUSE TO CATCH FIRE. THE FIRE HAD MELTED THE ALUMINUM TUBING ATTACHED TO THE HOT WATER HEATER AN | 10000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
972 | 1988-11-12 | TX | other |  | COLEMAN NATURAL GAS CO | CAR BACKED OVER METER, REG. SET & MAIN LINE. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
973 | 1988-06-13 | TX | other | UNKNOWN (GRIMES COUNTY) | COLEMAN NATURAL GAS CO | MOWING GRASS WITH TRACTOR, TAIL WHEEL WENT THROUGH METER PIN BROKE OFF REGULA | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
974 | 1988-10-27 | TX | other | UNKNOWN (HARRIS COUNTY) | COLEMAN NATURAL GAS CO | CUT TREES DOWN, DOWN ON MAIN LINE TAP, BROKE OFF METER & REG . SET ON MAIN LINE TAP. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
975 | 1988-11-03 | TX | other |  | COLEMAN NATURAL GAS CO | DOGS PLAYING IN BACKYARD BROKE OFF RISER GOING TO BAR-Q PIT. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
976 | 1988-09-17 | TX | other |  | COLEMAN NATURAL GAS CO | MOVING TRUCK BACKED OVER METER, REG SET & MAIN. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
977 | 1989-04-26 | TX | other | UNKNOWN | ENERGAS CO | A CONTRACTOR DRILLING POST HOLES HIT THE GAS MAIN. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
978 | 1989-04-27 | TX | other |  | ENERGAS CO | RANGER CONSTRUCTION CO. RUPTURED GAS LINE WHILE DIGGING DITCH FOR TELEPHONE LINE. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
979 | 1989-04-11 | TX | other | DUPONT | ENTEX - DIVISION OF ARKLA INC | TELEPHONE COMPANY CUT PLASTIC SERVICE LINE WITH TRENCHER WHILE INSTALLING DROP. GAS IGNITED & DESTROYED MACHINE. NO INJURIES. | 4000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
980 | 1989-04-14 | TX | other | UNKNOWN (BEXAR COUNTY) | SAN ANTONIO CITY PUBLIC SERVICE BOARD | VEHICLE RAN INTO GAS METER, ESCAPING GAS IGNITED. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
981 | 1989-04-24 | CA | other | UNKNOWN (MARIN COUNTY) | PACIFIC GAS & ELECTRIC CO | CAUSE OF FIRE BELIEVED TO BE WOOD BURNING STOVE OR WALL HEATER WITH INSUFFICIENT CLEARANCE. | 150000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
982 | 1989-06-15 | LA | other | UNKNOWN ( COUNTY) | NEW ORLEANS PUBLIC SERVICE INC | ON THURSDAY, JUNE 15, 1989 AT APPROXIMATELY 12:33 AM., THERE WAS AN EXPLOSION APPARENTLY CAUSED BY THE ACCUMULATION AND SUBSEQUENT IGNITION OF NATURAL GAS IN THE MULTI-FAMILY DWELLING AT 1233 SOUTH TELEMACHUS STREET IN NEW ORLEANS, LOUISIANA. THE EXPLOSI | 80000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
983 | 1989-04-02 | MO | other | UNKNOWN (JASPER COUNTY) | KANSAS POWER & LIGHT CO | DARRYL G. JONES LOST CONTROL OF HIS 1976 JEEP CJ-5, ALONG MURPHY BLVD, TRAVELING AIRBORNE INTO DISTRICT REGULATOR STATION #45 AT 1930 MURPHY BLVD. STATION PIPING AND BARRICADE WERE DESTROYED, AND THE JEEP LANDED ON ITS TOP, PINING MR JONES. HE SUSTAINED | 16000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
984 | 1989-03-28 | TX | other | JET STREAM | SOUTH RUSK COUNTY GAS CO | TERRIBLE STORM AND HIGH WATER WASHED OUT A CREEK CROSSING. | 10172 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
985 | 1989-05-17 | TX | other | UNKNOWN (EL PASO COUNTY) | SOUTHERN UNION GAS CO | FAILURE OF CUSTOMER'S EQUIPMENT RESULTED IN FIRE THAT DESTROYED A PRIVATE RESIDENCE. GAS COMPANY'S INVOLVEMENT WAS STRICTLY ASSISTING FIRE MARSHALL IN THE INVESTIGATION. | 24000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
986 | 1989-05-12 | TX | other | UNKNOWN (FORT BEND COUNTY) | ENTEX - DIVISION OF ARKLA INC | A CAR HIT A VACANT RISER CAUSING A LEAK AND IGNITION OF GAS. THE CAR BURNED. | 6500 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
987 | 1989-06-11 | MD | other | UNKNOWN (MONTGOMERY COUNTY) | WASHINGTON GAS LIGHT CO | THE CUSTOMER SMELLED SMOKE FROM HIS BASEMENT AND INVESTIGATED. HE FOUND THEGAS METER,IN AN ENCLOSED METER CABINET, ON FIRE. HE CALLED THE FIRE DEPARTMENT WHO CALLED WGL AND GAS WAS TURNED OFF OUTSIDE. THE FIRE MARSHALL'S INVESTIGATION COULD NOT DETERMI | 55000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
988 | 1989-07-01 | FL | other | UNKNOWN (BROWARD COUNTY) | ALL PRO GAS CO |  | 20000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
989 | 1989-04-27 | MA | other | UNKNOWN (MIDDLESEX COUNTY) | COMMONWEALTH GAS CO |  | 200000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
990 | 1989-06-07 | IN | other |  | TERRE HAUTE GAS CORP | AUTOMOBILE HIT GAS METER AND BROKE RISER ELBOW BELOW GROUND LEVEL, ALLOWING GAS TO ESCAPE ADJACENT TO HOUSE BELOW GRADE. | 25000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
991 | 1989-05-22 | TX | other | UNKNOWN (WALKER COUNTY) | ENTEX - DIVISION OF ARKLA INC | A TRUCK WAS LEFT UNATTENDED IN A SERVICE STATION PARKING LOT. THE TRUCK ROLLED OUT OF THE PARKING LOT, ACROSS A HIGHWAY, DOWN AN EMBANKMENT, AND STRUCK A RELIEF VALVE RISER. THE RISER WAS BROKEN OFF RESULTING IN GAS ESCAPING AND IGNITION OF GAS. THE TRU | 47500 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
992 | 1989-04-28 | TX | other | UNKNOWN (HARRIS COUNTY) | ENTEX - DIVISION OF ARKLA INC | PRIVATE CONTRACTOR PULLED 3/4" STEEL SERVICE TAP FROM 4" STEEL MAIN. INDIANSHORES DRIVE WAS BLOCKED OFF AD ONE HOUSE EVACUATED AS A SAFETY PRECAUTION. | 100 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
993 | 1989-06-14 | TX | other |  | ENERGAS CO | DRIVER LOST CONTROL OF VEHICLE AND RAN OVER A METER SETTING INTERRUPTING SERVICE TO ABOUT 22 HOUSES. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
994 | 1989-05-03 | TX | other | DUPONT | ENTEX - DIVISION OF ARKLA INC | LIGHTNING STRUCK A UTILITY POLE AND FOLLOWED THE BROUNG WIRE TO THE GROUND ROD BURNING A HOLE IN A 2" PLASTIC MAIN AND RESULTING IN IGNITION OF NATURAL GAS. | 400 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
995 | 1989-05-22 | TX | ACCIDENTALLY CAUSED BY OPERATOR | UNKNOWN (NUECES COUNTY) | CORPUS CHRISTI, CITY OF - GAS DIV | GAS CREW, WHILE REPAIRING A SMALL GAS LEAK ON THE WELD OF A 1" TAP TEE ON A 2" WRAPPED STEEL MAIN, HAD SET A PUNCH INTO THE TAP TEE TO STOP THE FLOW OF GAS. THE CAP OF THE TAP TEE HAD BEEN REMOVED AND THE PUNCH SET INTO THE TAP OF THE GAS MAIN. WHILE TH | 5000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
996 | 1989-05-05 | TX | other | UNKNOWN (GREGG COUNTY) | ENTEX - DIVISION OF ARKLA INC | DURING A STORM A LARGE TREE FELL ON A REGULATOR STATION RUPTURING A 2" RISER, RESULTING IN THE LOSS OF GAS SERVICE TO 150 CUSTOMER. | 2150 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
997 | 1989-06-26 | TX | technical failure |  | ENERGAS CO | AN EXTENSION WAS BEING INSTALLED ON AN EXISTING VALVE TO ALLOW FOR EASIER ACCESS TO GREASE TO VALVE. AS THE EXTENSION WAS BEING THREADED ONTO THE VALVE THE COMPANY EMPLOYEE CONTINUE TO TURN THE EXTENSION UNTIL IT BEGAN TO CLOSE THE VALVE. THIS PROCEDURE | 2000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
998 | 1989-07-10 | LA | other | PLEXCO | LOUISIANA GAS SERVICE CO | CONTRACTOR'S BACKHOE SEVERED GAS MAIN. APPROXIMATELY 40 CUSTOMERS WERE WITHOUT GAS FOR A 5 HOUR PERIOD. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
999 | 1989-07-05 | SD | other |  | MIDWEST GAS CO | OPERATOR WAS NOT CALLED FOR LOCATION OF FACILITIES. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1000 | 1989-07-11 | MO | other | UNKNOWN (ST LOUIS COUNTY) | LACLEDE GAS CO |  | 125000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1001 | 1989-07-08 | MO | other | UNKNOWN (JACKSON COUNTY) | KANSAS POWER & LIGHT CO | PICKUP TRUCK HIT & BROKE OUTLET PIPE TO REGULATOR STATION. | 5000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1002 | 1989-06-03 | AZ | other | UNKNOWN (COCONINO COUNTY) | SOUTHERN UNION GAS CO | HOUSE SETTLED DOWN ONTO HOUSEPIPING BREAKING PIPE UNDER HOUSE. BREAK WAS DOWNSTREAM OF OPERATORS METER. | 10000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1003 | 1989-07-21 | TX | other | UNKNOWN (TRAVIS COUNTY) | SOUTHERN UNION GAS CO | GROUND SURROUNDING STORM DRAIN HAD SETTLED CAUSING CI MAIN TO BREAK. | 500 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1004 | 1989-07-26 | TX | technical failure | UNKNOWN (MIDLAND COUNTY) | ENERGAS CO | MAINTENANCE CREW UNCOVERED A LEAKING DRESSER COUPLING. PIPE SLIPPED OUT OF DRESSER. SERVICE LOSS TO 78 HOUSES. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1005 | 1989-07-14 | TX | other | UNKNOWN (ECTOR COUNTY) | ENERGAS CO | EMPLOYEE OF CUSTOMER ATTEMPTED TO LOCATE YARD LINE LEAK WITH CIGARETTE LIGHTER AND IGNITED GAS. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1006 | 1989-07-22 | NY | other | DUPONT | LONG ISLAND LIGHTING CO | UNDER THE DIRECTION OF THE ARSON SQUAD,GAS C&M PERSONNEL UNEARTHED A FAULTEDSECONDARY ELECTRIC CABLE (INSTALLED BY AN ELECTICIAN) WHICH HAD BURNED THE PLASTIC GAS SERVICE AT THE BUILDING. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1007 | 1989-07-31 | KS | other | UNKNOWN ( COUNTY) | PRODUCERS GAS EQUITIES INC |  | 2676 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1008 | 1989-07-24 | WV | other |  | HOPE GAS INC | THIS WAS THE THIRD OF THREE (3) LINE BREAKS CAUSED BY THE SAME THIRD PARTY WHILE LAYING 1,000 FT OF NEW WATER LINE. MAY 31, 1989, JULY 12, 1989, AND JULY 24, 1989. HOPE WAS INFORMED THEY WOULD NOT BE DIGGING ON THE SIDE OF THE ROAD OF THIS LAST DIG-IN. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1009 | 1989-07-28 | AK | other | PHILLIPS DRISCOPIPE INC. | ENSTAR NATURAL GAS CO | TAB ELECTRIC EMPLOYEES DAMAGED A 4" PLASTIC GAS MAIN WITH POST HOLE AUGER. THE ESCAPING GAS IGNITED AND THREE OF THEIR EMPLOYEES WERE INJURED (ONE WAS AMINOR BURN). THE TAB CREW WAS USING AN ELECTRIC DRILL NEAR THE DAMAGED, THIS SEEMS TO BE THE APPARENT | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1010 | 1989-08-01 | WI | other | DRESSER | WISCONSIN GAS CO | ON TUESDAY, AUGUST 1, A CONTRUCTION WORKER FOR MAINLINE SEWER & WATER, INC. WAS ON A SEWER MANHOLE WHICH WAS UNDER CONSTRUCTION. HE LIT A LIGHTER TO SMOKE A CIGARETTE. THE LIGHTER IGNITED AN EXPLOSIVE NATURAL GAS AND AIR MIXTUREAT THE MANHOLE. THE WORK | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1011 | 1989-07-28 | NY | other |  | CONSOLIDATED EDISON CO OF NEW YORK | A TRASH FIRE UNDERNEATH A GAS METER MELTED THE SOLDER THAT SEALED THE METER. THIS ACTION ALLOWED GAS TO ESCAPE WHICH WAS THEN IGNITED BY THE FIRE. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1012 | 1989-07-15 | NY | other |  | CONSOLIDATED EDISON CO OF NEW YORK | THE PROBABLE CAUSE OF THE EXPLOSION WAS GAS LEAKING THROUGH AN OPEN-ENDED PIPE, ESCAPING THROUGHOUT THE HOUSE, AND BEING IGNITED BY AN UNKNOWN SOURCE. | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1013 | 1989-02-05 | TX | other |  | LONE STAR GAS CO |  | 5200 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1014 | 1989-07-13 | CA | other |  | PACIFIC GAS & ELECTRIC CO | SMALL GAS STOVE TOPPLED ON INFANT CAUSING THIRD-PARTY FATALITY. THE OTHER OCCUPANTS WERE OVERCOME BY GAS AND WERE TREATED AT A LOCAL HOSPITAL. NO IGNITION OR EXPLOSION, AND BUILDING WAS EVACUATED. GAS ESCAPED FROM BROKEN FLEX LINE, CAUSED BY FALLING STOVE | 500 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1015 | 1989-07-27 | CA | other | UNKNOWN (ALAMEDA COUNTY) | PACIFIC GAS & ELECTRIC CO | AN OUT OF CONTROL VEHICLE STRUCK AND DAMAGED THE SERVICE RISER AT THE ABOVE ADDRESS, ALLOWING GAS TO ESCAPE TO THE ATMOSPHERE. NEARBY BUILDINGS WERE EVACUATED AS A PRECAUTION. | 25800 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1016 | 1989-08-18 | NJ | other | UNKNOWN (ESSEX COUNTY) | PUBLIC SERVICE ELECTRIC & GAS CO | ON AUGUST 18, 1989, AT APPROXIMATELY 12:50 P.M., WILLIAM ELMER, STREET MECHANIC, WAS WORKING ON A GAS SERVICE REPLACEMENT. WHILE PULLING A 2" PLUG ON A SADDLE OFF A 6" CAST IRON UTILIZATION PRESSURE MAIN, AN IGNITION OCCURRED FROM AN UNKNOWN SOURCE. W. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1017 | 1989-07-27 | TX | other |  | RIO GRANDE VALLEY GAS CO | THE JULY 27 INCIDENT WAS THE RESULT OF A TRUCK RUNNING OVER OUR METER. THE METER SET ASSEMBLY WAS REPLACED THE SAME DAY OF THE INCIDENT. | 1000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1018 | 1989-07-23 | NV | other | UNKNOWN (CLARK COUNTY) | SOUTHWEST GAS CORP | A 1/2" PVC SERVICE WAS APPARENTLY SQUEEZED BY A LARGE TREE ROOT RESULTING INA LEAK, EXPLOSION, AND FIRE TO THE HOUSE. | 75000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1019 | 1989-08-24 | MN | technical failure | UNKNOWN ( COUNTY) | MINNEGASCO INC | CONTRACTOR DIGGING WHILE WORKING ON STATE HWY PROJECT WAS UNCOVERING NATURALGAS TRANSMISSION LINE WHEN HE CAUGHT THE LINE ON ITS PARTS WITH HIS BUCKET CAUSING A HOLE OR BREAK. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1020 | 1989-08-20 | IL | maintenance |  | NORTHERN ILLINOIS GAS CO | CUSTOMER AT 21694 ELM ST. IN LAKE VILLA CONSTRUCTED A GARAGE OVER OUR GAS SERVICE. N.I. GAS WAS NOT CALLED TO RELOCATE SERVICE. CORROSION OCCURRED ON COPPER SERVICE UNDER CEMENT FLOOR OF GARAGE WHICH CAUSED FAILURE. THE GARAGE WASBADLY DAMAGED WHEN IGNIT | 30000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1021 | 1989-09-02 | AR | other | POLY ARK | ARKANSAS LOUISIANA GAS CO (ARKLA GAS CO) | RESIDENTS REPORTED LIGHTENING STRIKE IN IMMEDIATE AREA. IT APPEARS THAT CURRENT FROM ELECTRICAL STORM ENTERED THE LOCATOR WIRE. THE CURRENT TRAVELED ALONG THE LOCATOR WIRE TO AN AREA WHERE THE INSULATION ON THE LOCATOR WIRE HAD AVOID. AT THIS POINT, TH | 150000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1022 | 1989-07-13 | MI | other |  | MICHIGAN GAS UTILITIES CO | PRIOR TO 7:55 AM. ON THURSDAY, JULY 13, 1989, A CONTRACTOR USING A BACKHOE BEGAN EXCAVATION FOR SEWER LINES IN CLOSE PROXIMITY TO THE BACK OF THE TASTEE FREEZ BUILDING. DURING EXCAVATION THE BACKHOE BUCKETT STRUCK AND PULLED A 3/4" STEEL NATURAL GAS SERV | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1023 | 1989-09-25 | MD | ACCIDENTALLY CAUSED BY OPERATOR | UNKNOWN ( COUNTY) | BALTIMORE GAS & ELECTRIC CO | OVEN OF GAS RANGE WAS TURNED ON AND PASSING GAS FOR AN EXTENDED PERIOD OF TIME. WHEN A NEIGBOR COMPLAINED ABOUT THE ODOR OF GAS, OCCUPANT TRIED TO LIGHTTHE OVEN. AN EXPLOSION AND FIRE RESULTED. | 20000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1024 | 1989-09-07 | IA | other | UNKNOWN (POLK COUNTY) | PEOPLES NATURAL GAS | ON AUGUST 30, 1989, PEOPLES NATURAL GAS LOCATED GAS TRANSMISSION LINES AT 209 N. 3RD STREET, GRIMES, IOWA, IN PREPARATION FOR THE CITY'S INSTALLATION OF SEWER LINES. ON SEPTEMBER 7, 1989, AFTER INSTALLATION OF THE SEWER LINES, VANCE MARSH, AN EMPLOYEE OF | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1025 | 1989-09-08 | NJ | other | DUPONT | SOUTH JERSEY GAS CO | WHILE PURGING AIR FROM THE END OF A NEW 2" PLASTIC MAIN, THE GAS-AIR MIXTUREIGNITED, BURNING THE ARM, BACK AND FACE OF AN EMPLOYEE WORKING IN THE HOLE ATTHE TIME. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1026 | 1989-08-28 | MI | other | SUPERIOR | MICHIGAN CONSOLIDATED GAS CO (MICHCON) | A BULLET FIRED BY AN UNKNOWN PERSON PIERCED THE INSIDE METER. LEAKING GAS, IGNITED BY AN UNKNOWN SOURCE, CAUSED AN EXPLOSION. THE DWELLING AND CONTENTSWERE DAMAGED. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1027 | 1989-09-22 | LA | other | PLEXCO | LOUISIANA GAS SERVICE CO | SOUTH CENTRAL BELL EMPLOYEE WAS REPAIRING TELEPHONE CABLE IN A BELL HOLE AT 3230 BAYOU ROAD, TOCA, LOUISIANA. SOUTH CENTRAL BELL EMPLOYEE LIT PROPANE TORCH TO REMOVE THERMO PLASTIC SHEATHING FROM THE TELEPHONE CABLE. WHILE USINGTHE TORCH, EMPLOYEE BURNE | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1028 | 1989-09-30 | TN | other | REPUBLIC STEEL | ADAMSVILLE GAS DEPT, TOWN OF | THE BANK TO SHIFT ADD EXERT PRESSURE AGAINST LINE. | 5000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1029 | 1989-10-01 | TN | other | REPUBLIC STEEL | ADAMSVILLE GAS DEPT, TOWN OF | DUE TO HEAVY RAINFALL, THE SLOPE OF FILL DIRT WAS UNDERMINED BY WATER CAUSING THE BANK TO SHIFT AND EXERT PRESSURE AGAINST LINE. | 2000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1030 | 1989-09-11 | MO | other | UNKNOWN (JACKSON COUNTY) | KANSAS POWER & LIGHT CO | FIRE OF UNKNOWN ORIGIN IN BASEMENT, MELTED SOLDER ON METER, AND IGNITION OCCURRED. | 125000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1031 | 1989-10-02 | NY | other | UNKNOWN (ONTARIO COUNTY) | NEW YORK STATE ELECTRIC & GAS CORP | THIS INCIDENT OCCURRED ON CUSTOMER-OWNED FACILITIES. THE INJURED PARTY TURNED ON AN ELECTRICAL SWITCH WHICH WAS FOLLOWED BY AN EXPLOSION AND FIRE. SUBSEQUENT INVESTIGATION DETERMINED THAT A GAS LINE INSIDE THE CUSTOMER'S BUILDING HAD BEEN DISCONNECTED F | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1032 | 1989-09-14 | CA | other | PHILLIPS DRISCO | SOUTHERN CALIFORNIA GAS CO | KENNEDY PIPELINE CO. EMPLOYEE, USING PROPANE TORCH TO MAKE WELDED REPAIR TO 2 INCH COPPER WATER LINE, MELTED 1/2 INCH PLASTIC GAS SERVICE. GAS LINE WAS EXPOSED IN THE EXCAVATION AT THE TIME OF THE INCIDENT. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1033 | 1989-10-09 | WA | other | UNKNOWN | WASHINGTON NATURAL GAS CO | NATURAL GAS ESCAPED THROUGH A PINHOLE LEAK IN A 5/8" PLASTIC GAS SERVICE LYING ADJACENT TO THE HOUSE. GAS MIGRATED INTO THE GARAGE WHERE IT WAS IGNITED.THE RESULTING EXPLOSION AND FIRE RESULTED IN DAMAGED ESTIMATED TO EXCEED $50,000. THE CAUSE OF THE LE | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1034 | 1989-10-03 | LA | other | UNKNOWN (ST TAMMANY COUNTY) | LOUISIANA GAS SERVICE CO | CUSTOMER DISCONNECTED COPPER TUBING FROM 1/2" GALVANIZED LINE SUPPLYING WALLHEATHER IN AN APPARENT SUICIDE ATTEMPT. NATURAL GAS FILLED HOUSE CAUSING AN EXPLOSION AND FIRE. SOURCE OF IGNITION IS UNKNOWN. | 40000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1035 | 1989-10-09 | NE | other | UNKNOWN (SARPY COUNTY) | PEOPLES NATURAL GAS | A SUBCONTRACTOR, WORKING FOR THE DEPARTMENT OF ROADS, STRUCK THE OPERATOR'S LINE WITH A BULLDOZER. THE RESULTING LOSS OF PRESSURE TEMPORARILY AFFECTED GAS SERVICE TO PORTIONS OF THE CITY OF BELLEVUE, NEBRASKA. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1036 | 1989-09-28 | AL | other | NIPAK TR418 | ALABAMA GAS CORP (EX. MARENGO CORP PROPERTY) | AT 8:45 AM. ON SEPTEMBER 28, 1989, TALLADEGA POLICE REPORTED A GAS MAIN BREAK AND FIRE AT THE INTERSECTION OF WESTERN BY-PASS (HIGHWAY 275) AND ALABAMA HIGHWAY 21 SOUTH. AN ALAGASCO SERVICEMAN ARRIVED ON THE SCENE AT 8:53 A.M. THE FOLLOWING INFORMATION | 110000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1037 | 1989-10-19 | MN | other | PLEXCO | MINNEGASCO INC | NORTHERN STATES POWER COMPANY (UTILITY) WHILE DIGGING, HIT MINNEGASCO, INC. (UTILITY) NATURAL GAS MAIN, CUTTING THE LINE. NORTHERN STATES POWER CALLED FOR LOCATION OVER A MONTH PRIOR, BUT NEVER SHOWED UP TO DIG UNTIL A MONTH LATER, WITHOUT CALLING FOR REL | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1038 | 1989-09-29 | OH | other | UNKNOWN | WEST OHIO GAS CO | WEST OHIO GAS COMPANY'S 8" HIGH PRESSURE DISTRIBUTION PIPELINE WAS HIT BY A CONTRACTORS EARTH GRADING FOR A NEW STREET, BRIARCLIFF DRIVE, IN A NEW SUBDIVISION, ROLLING HILLS ESTATES IN ST. MARYS, OHIO. THE HOLE IN THE DAMAGED PIPERESULTED IN THE LOSS OF S | 350000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1039 | 1989-10-19 | AL | other | TBV INC. | DE KALB - CHEROKEE COUNTY GAS DEPT | LEAK AROUND CRYOGENIC VALVE STEM PACKING. LEAK REPAIRED BY ADJUSTING PACKINGSTEM NUT.ON OCTOBER 19,1989, EMPLOYEE MR. JOE DOVER WAS OPERATING THE LNG SATELLITE FACILITY. AT APPROCIMATELY 5:45 P.M. LOCAL TIME, THE OPERATOR RECEIVED, THROUGH THE CONTROL PA | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1040 | 1989-10-14 | TX | other |  | ENERGAS CO | OUR DISPATCHER RECEIVED A CALL FROM THE PLAINVIEW FIRE DEPARTMENT SATURDAY AT 6:41 P.M. THEY REPORTED THAT A CAR HAD HIT ONE OF OUR GAS METERS, WITH ENSUING FIRE ON THE METER SETTING AND ON THE CAR. BRAD HERRINGTON OF THE FIRE DEPT. CALLED ENERGAS'S DI | 2200 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1041 | 1989-11-02 | VA | ACCIDENTALLY CAUSED BY OPERATOR | UNKNOWN ( COUNTY) | CHARLOTTESVILLE, CITY OF | A NEW GAS SERVICE LINE WAS BEING INSTALLED BY A CONTRACTOR WORKING FOR THE CITY OF CHARLOTTESVILLE. THE BACKHOE BUCKET SNAGGED THE EXISTING SERVICES LINEAND PULLED THE SERVICE LINE FROM A THREADED TEE IN THE BASEMENT OF THE HOUSE. THE BASEMENT FILLED WITH | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1042 | 1989-10-27 | MS | other | AMERICAN | WILLMUT GAS & OIL CO - MAIN OFFICE | OPERATOR WAS PURGING A LINE INCLUSIVE OF METER THROUGH AN OPEN 2" VALVE. METER LOCKED UP, PRESSURE ONLY FILLED ON SIDE OF THE METER PUTTING EXCESSIVE PRESSURE DIFFERENTIAL ACROSS THE INNER WALL OF THE METER. THE INTERNAL WALL FAILED, IMPACTED INTERNAL P | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1043 | 1989-10-23 | TX | other | UNKNOWN (BEXAR COUNTY) | GREY FOREST UTILITIES | DAMAGE WAS CAUSED BY A LARGE EXCAVATOR. | 5000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1044 | 1989-10-13 | IN | maintenance | UNKNOWN (LAKE COUNTY) | NORTHERN INDIANA PUBLIC SERVICE CO | ON OCTOBER 13, 1989 AT APPROXIMATELY 4:30 A.M. THERE WAS AN EXPLOSION WHICH DESTROYED THE GARAGE AT THE ABOVE LOCATION. THE EXPLOSION ALSO CAUSED DAMAGE TO SEVERAL ADJACENT STRUCTURES. INVESTIGATION INDICATED THAT GAS LEAKING FROM THE 2" DISTRIBUTION MA | 65000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1045 | 1989-10-20 | CA | technical failure | PHILLIPS-DRISCO PIPE | PACIFIC GAS & ELECTRIC CO | WHILE THE CREW WAS BACKFILLING A TRENCH, FUSION JOINT FAILED, GAS IGNITED, AND BURNED ONE EMPLOYEE. STATIC ELECTRICITY IS SUSPECTED AS SOURCE OF IGNITION | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1046 | 1989-10-21 | CA | other | UNKNOWN (KERN COUNTY) | PACIFIC GAS & ELECTRIC CO | OCCUPANT ACCIDENTALLY TURNED ON STOVE WITHOUT PILOT LIGHTS, ALLOWING GAS TO ACCUMULATE IN THE BUILDING. SOURCE OF IGNITION IS SUSPECTED TO BE A CIGARETTE LIGHTER. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1047 | 1989-10-17 | CA | other | UNKNOWN (MONTEREY COUNTY) | PACIFIC GAS & ELECTRIC CO | OVERTURNED TRACTOR TRAILER DAMAGED REGULATOR SET, ALLOWING GAS TO ESCAPE TO THE ATMOSPHERE. TRAFFIC WAS REROUTED. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1048 | 1989-10-17 | CA | other | UNKNOWN ( COUNTY) | PACIFIC GAS & ELECTRIC CO | PROPERTY OWNER DROVE STAKE INTO 1/2-INCH PLASTIC LINE AND LEAKING GAS ENTERED BUILDING, CAUSING AN EXPLOSION. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1049 | 1989-11-01 | IL | ACCIDENTALLY CAUSED BY OPERATOR | UNKNOWN (SANGAMON COUNTY) | CENTRAL ILLINOIS LIGHT CO | OPERATOR CONNECTED A 40 P.S.I.G. SERVICE TO A SERVICE WITH 6" W.C. WITHOUT FIRST TURNING OFF GAS COCK AT METER. GAS ENTERED CUSTOMERS FUEL LINE. | 45000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1050 | 1989-11-17 | KY | technical failure | PHILLIPS DRISCOPIPE | DELTA NATURAL GAS CO INC | AT APPROXIMATELY 4:58 AM NOVEMBER 17, 1989, THE LAUREL COUNTY DISPATCH CENTER RECEIVED A CALL FROM AN EMPLOYEE AT THE MCDONALDS RESTAURANT LOCATED ON NORTH MAIN ST REPORTING A STRONG GAS ODOR OUTSIDE. THE DISPATCH CENTER NOTIFIED THE LAUREL COUTY FIRE DEP | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1051 | 1989-11-27 | MA | other | UNKNOWN (MIDDLESEX COUNTY) | COMMONWEALTH GAS CO | A FIRE DESTROYED A SINGLE FAMILY HOME AT 100 GOODALE ROAD, MALBORO, MASS. THE FIRE IS BELIEVED TO HAVE STARTED IN OR NEAR THE BOILER ROOM IN THE CELLAR.NODETERMINATION HAS BEEN MADE AS TO THE CAUSE OF THE FIRE. AN INVESTIGATION BY THE TOWN FIRE DEPARTME | 275000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1052 | 1989-10-30 | TX | other | UNKNOWN (MORRIS COUNTY) | ARKANSAS LOUISIANA GAS CO (ARKLA GAS CO) | CUSTOMER HAD UNCAPPED LINE IN BATHROOM DURING REMODELING. | 10000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1053 | 1989-10-10 | TX | ACCIDENTALLY CAUSED BY OPERATOR | NIPAK | LONE STAR GAS CO |  | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1054 | 1989-11-30 | MN | other | UNKNOWN (LE SUEUR COUNTY) | MINNEGASCO INC | FROM OUR INVESTIGATION OF THE INCIDENT AT THIS TIME AND DATE, WE BELEIVE THELINE INDICATES BEING SCRAPED OR HIT BY A PIECE OF CONSTRUCTION EQUIPMENT ANDCOVERED UP BY GROUND. | 45000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1055 | 1989-11-24 | LA | technical failure | UNKNOWN | LOUISIANA GAS SERVICE CO | WHILE REMOVING A 3" HIGH PRESSURE STEEL MAIN CANAL CROSSING TO FACILITATE A DRAINAGE PROJECT, IT WAS NECESSARY TO CLOSE NINE VALVES. UPON COMPLETION OF CUTTING OUT THE SECTION OF PIPE OVER THE CANAL AND CAPPING THE MAIN FROM THE NORTH SIDE, THE CREW LEAD | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1056 | 1989-12-14 | MD | other |  | BALTIMORE GAS & ELECTRIC CO | FIRE STARTED AT OR AROUND THE FURNACE AREA. NATURAL GAS FURNACE BECAME INVOLVED AND CONTRIBUTED TO THE FIRE. INTERIOR OF THE HOUSE WAS DESTROYED. CAUSE OF THE FIRE WAS NOT DETERMINED. | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1057 | 1989-12-11 | PA | other | UNKNOWN (PHILADELPHIA COUNTY) | PHILADELPHIA GAS WORKS | CAST IRON GAS MAIN FRACTURED AFTER ITS SUPPORT WAS DISTURBED BY OUTSIDE FORCES AND THE FAILURE OF OPERATOR'S PERSONNEL TO FOLLOW PROPER PROCEDURES DURINGLEAK INVESTIGATION. | 60000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1058 | 1989-12-23 | NJ | other | INNERTITE | ELIZABETHTOWN GAS CO | THE GAS COMPANY WAS WORKING ON A GAS LEAK AND IN THE PROCES OF EXCAVATING BROKE A WATER MAIN. THE WATER MAIN HAD TO BE REPAIRED AND TO DO SO A PUMP WAS BEING USED TO CLEAR THE WATER FROM THE HOLE. THE PUMP BACKFIRED CAUSING IGNITION TO THE LEAKING GAS. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1059 | 1989-12-29 | NJ | other | U.S. PIPE FOUNDRY | ELIZABETHTOWN GAS CO | ESCAPE OF GAS RESULTING FROM CRACK IN MAIN APPARENTLY CAUSED BY PRESSURE FROM TREE ROOT FROM LARGE SYCAMORE TREE LOCATED NEARBY. | 200000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1060 | 1989-12-03 | PA | other | UNKNOWN (MONTGOMERY COUNTY) | PHILADELPHIA ELECTRIC CO | RESIDENTS AND TOWNSHIP OFFICIALS HAD BEEN COMPLAINING TO NEARBY QUARRY ABOUTHEAVY BLASTING, ESPECIALLY ON FRIDAYS. THE INJURED PARTY IS ONE OF THOSE TOWNSHIP OFFICIALS. SUDDEN CIRCUMFERENTIAL BREAK IN A 4-INCH MECHANICAL JOINT CAST IRON MAIN APPARENTLY | 211000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1061 | 1989-12-12 | NJ | other | UNKNOWN | PUBLIC SERVICE ELECTRIC & GAS CO | ON DECEMBER 12, 1989 AT 3:16 PM A LEAK ORDER WAS RECEIVED AT THE PLAINFIELD GAS DISTRICT DISPATCH OFFICE REGARDING A GAS ODOR OUTSIDE OF NUMBER 436 GARRETSON RD., BRIDGEWATER TWP., NJ. A SERVICE SPECIALIST WAS DISPATCHED AND ARRIVED ON THE SCENE AT 4:10 | 160000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1062 | 1989-11-29 | TX | other | N/ | ENERGAS CO | AN OPEN FLAME GAS HEATER SITUATED TOO CLOSE TO A WALL CAUGHT WALL ON FIRE. | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1063 | 1989-12-13 | MD | other | UNKNOWN (PRINCE GEORGES COUNTY) | WASHINGTON GAS LIGHT CO | AT 1329 HOURS ON 12/13/89 WASHINGTON GAS WAS NOTIFIED OF NATURAL GAS ODOR NEAR 519 ELM AVENUE BY A PASSERBY. A PRIORITY 3 CODE ORDER WAS DISPATCHED AT 1350 HOURS AND THE LEAK INVESTIGATOR ARRIVED AT 1420 HOURS. HE CHECKED INSIDETHE HOUSES IN THE IMMEDIA | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1064 | 1989-12-25 | GA | other | SINGER | ATLANTA GAS LIGHT CO | APPARENT INCING OF REGULATOR CAUSING OVERPRSSURE AT FURNACE. SAFETY DEVICE AT FURNACE DID NOT SHUT OFF GAS. | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1065 | 1989-12-25 | NJ | other | UNKNOWN (CUMBERLAND COUNTY) | SOUTH JERSEY GAS CO | HOUSE FIRE AND EXPLOSION WITH BUILDING AND CONTENTS TOTALLY DESTROYED. NO INJURIES. FOUND 2" BARE STEEL MAIN THREADS CRACKED AT COUPLING. GROUND FROZEN TO MAIN DEPTH OF 33 INCHES. REPAIRED WITH 2" 54C CLAMP. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1066 | 1989-12-20 | NY | other | UNKNOWN ( COUNTY) | CONSOLIDATED EDISON CO OF NEW YORK | A CRACKED 6" CAST IRON GAS MAIN LEAKED GAS INTO BASEMENT OF TWO-FAMILY HOUSEAT 2329 ELLIS AVENUE. EXTENSIVE DAMAGE WAS CAUSED WHEN GAS IGNITED. ONE PERSON RECEIVED FACIAL BURNS AND WAS ADMITTED TO HOSPITAL. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1067 | 1989-12-27 | WI | other | UNKNOWN (MANITOWOC COUNTY) | WISCONSIN PUBLIC SERVICE CORP | THREE PEOPLE WERE INJURED IN A FIRE & EXPLOSION AT 1018 31ST STREET, TWO RIVERS, WI. A 2" WRAPPED STEEL GAS MAIN WAS LEAKING IN FRONT OF THE HOUSE. | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1068 | 1989-12-22 | PA | other | UNKNOWN (ALLEGHENY COUNTY) | COLUMBIA GAS OF PENNSYLVANIA | WE BELIEVE THAT OUR PIPELINE WAS DAMAGED BY A THIRD PARTY AT SOME TIME IN THEPAST, PROBABLY LAST SUMMER. THIS DAMAGE WAS THE CAUSE OF A CRACK IN THE PIPELINE WHEN INFLUENCED BY THE EXTREME WEATHER CONDITIONS AT THE TIME OF THE INCIDENT, AND THE PIPE FAIL | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1069 | 1989-12-21 | TN | ACCIDENTALLY CAUSED BY OPERATOR | PLEXCO | UNITED CITIES GAS CO | THE MAIN IS PART OF A REINFORCEMENT PROJECT WHICH JOINED TWO BRANCHES OF A 25 PSIG DISTRIBUTION SYSTEM. THE PROJECT INVOLVED THE CONTRACT INSTALLATION OF 282' OF 4" P.E. PIPE AND 707' OF 2" P.E. PIPE WHICH JOINED A 2" P.E. MAIN TO A 2" COATED STEEL MAIN. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1070 | 1989-12-29 | OH | other | OIL CREEK | COLUMBIA GAS OF OHIO INC | CONTRACTOR DIGGING A TRENCH TO INSTALL A BURIED ELECTRICAL SERVICE FOR THE MOBILE HOME ON LOT 13 STRUCK THE CUSTOMER-OWNED SERVICE LINE. GAS IGNITED ANDCOMPLETELY DESTROYED THE TRENCHING MACHINE AND THE NEW UNOCCUPIED MOBILE HOME | 64000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1071 | 1989-12-19 | IL | other |  | NORTHERN ILLINOIS GAS CO | EXPLOSION AND FIRE DESTROYED THE RESIDENCE CAUSING INJURIES TO TWO OCCUPANTS, ONE FATAL. WILL COUNTY SHERIFF'S POLICE REPORT INDICATES FURNACE AS A PROBLEM. | 75000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1072 | 1989-12-19 | MO | other |  | MISSOURI PUBLIC SERVICE CO |  | 25000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1073 | 1989-12-24 | LA | other |  | GULF STATES UTILITIES CO | EXPLOSION WITH-IN EXXON REFINERY BATON ROUGE CAUSED THIS 12" AERIAL CROSSINGTO RUPTURE. FIRE WITH-IN REFINERY WAS BROUGHT UNDER CONTROL THE NEXT DAY. | 25000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1074 | 1989-12-31 | OH | other | WALWORTH | DAYTON POWER & LIGHT CO | A 4" GRAY IRON LUBIRCATED PLUG VALVE WAS FOUND TO HAVE A CRACK IN THE BODY. | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1075 | 1990-01-19 | TX | other |  | ENERGAS CO | OUR DISPATCHER RECEIVED A CALL AT 8:12 AM. THIS MORNING, JANUARY 19TH. THEYREPORTED A FIRE AT THE HOME OF CLINT ROBERSON 1/2 MILE WEST AND 1/2 MILE SOUTH OF DRESS. OUR SERVICEMAN WAS DISPATCHED TO THE SCENE. THE SERVICEMAN FOUND THAT THE SERVICE REGULA | 700 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1076 | 1989-12-15 | TX | other |  | DEL RIO GAS SYSTEM, CITY OF | ON 12/16/89 AT APPROXIMATELY 1:05 PM OFFICERS RUBID AND SANTELLANES WERE DISPATCHED TO 610 W. CONTINAS IN REFERENCE TO A DECEASED VICTIM. UPON ARRIVAL AND FURTHER INVESTIGATION SUBTAINED FROM EMS ADVISED OFFICERS RUBID AND SANTELLANES THAT THERE WAS A ST | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1077 | 1989-12-21 | IN | other |  | NORTHERN INDIANA PUBLIC SERVICE CO | ON DECEMBER 21,1989, AT APPROXIMATELY 8:30 PM., AN OFFICE TRAILER LOCATED AT3900 MICHIGAN AVENUE, EAST CHICAGO, INDIANA, CAUGHT FIRE AND MR. KEVIN REYESSUFFERED BURNS AND WAS HOSPITALIZED. ALTHOUGH THERE WAS NO GAS SERVICE TO THE TRAILER, GAS LEAKING FRO | 10000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1078 | 1989-12-29 | IL | other | UNKNOWN (COOK COUNTY) | PEOPLES GAS LIGHT & COKE CO | CUSTOMER OF RECORD FOR INCIDENT LOCATION REMOVED A SECTION OF INTERIOR SERVICE PIPE IN THE KITCHEN AREA. THIS ALLOWED GAS TO ESCAPE INTO THE BUILDING AND IT IGNITED FROM AN UNKNONW SOURCE. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1079 | 1989-12-25 | AL | other | UNKNOWN (MOBILE COUNTY) | MOBILE GAS SERVICE CORP | SERVICEMAN A. CAMPBELL WAS DISPATCHED TO 805 WILLJOHN STREET AT 9:00 AM. ON DECEMBER 25, 1989 TO INVESTIGATE A GAS ODOR. UPON ARRIVAL AT 9:14 AM., CAMPBELL DETECTED S STRONG GAS ODOR ON THE NORTHEAST CORNER OF WILLJOHN AND CLARENCE STREETS. HE CHECKED T | 5000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1080 | 1990-01-06 | AL | other | UNKNOWN (BUTLER COUNTY) | SOUTHEAST ALABAMA GAS DISTRICT | WE FOUND THAT THE SERVICE LINE HAD BEEN HIT BY EQUIPMENT ON THE OPPOSITE SIDE OF THE STREET FROM THE MAIN. THE BLOW HAD CAUSED A HAIRLINE CRACK IN THE THREADS WHERE IT WAS SCREWED INTO AN ELL NEAR THE TAP ON THE MAIN, CAUSING A GAS LEAK. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1081 | 1990-01-09 | TX | other | UNKNOWN (TRAVIS COUNTY) | SOUTHERN UNION GAS CO | ON THE EVENING OF JANUARY 9, 1990, A MAINTENANCE CREW FOR THE CITY OF AUSTINWATER/WASTEWATER DEPARTMENT WAS EXCAVATING TO EXPOSE A LEAKING WATER MAIN TAP LOCATED UNDER THE PAVEMENT IN FRONT FOF 4602 CANDLETREE LANE. WHILE EXCAVAITING WITHIN THE ROADWAY, | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1082 | 1989-12-11 | TX | other |  | ARKANSAS LOUISIANA GAS CO (ARKLA GAS CO) | HOT WATER CIRCULATING BOILER EXPLODED. | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1083 | 1989-12-19 | OH | other | PHILLIPS DRISCOPE | EAST OHIO GAS CO | WHILE MAKING REPAIRS TO AN ELECTRIC SERVICE LINE IN FRONT OF 97 FOX HALL DRIVE AN ELECTRIC UTILITY EMPLOYEE BURNED THROUGH A 5/8-INCH PLASTIC SERVICE LINE CAUSING A FLASH FIRE, INJURING HIMSELF AND DAMAGING THE SERVICE LINE. THEAREA WAS MADE SAFE IMMEDIA | 300 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1084 | 1990-01-04 | PA | other | UNKNOWN (PHILADELPHIA COUNTY) | PHILADELPHIA GAS WORKS |  | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1085 | 1990-02-06 | LA | other | UNKNOWN ( COUNTY) | EUNICE GAS DEPT, CITY OF | DAMAGE DONE BY 3RD PARTY CONTRACTOR FOR UNION PACIFIC. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1086 | 1990-01-11 | PA | other | UNKNOWN (YORK COUNTY) | COLUMBIA GAS OF PENNSYLVANIA | SUSBEQUENT INVESTIGATION OF THE FAILUE TO OUR 2" STEEL PIPELINE REVEALED THAT THE PIPELINE WAS SNAGGED AND DAMAGED BY A BACKHOE BUCKET, MOST LIKELY DURING PREVIOUS CONSTRUCTION OF A SEWER LINE, BY A SEWER CONTRACTOR. THE PRIOR DAMAGE EVENTUALLY RESULTED | 150000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1087 | 1990-02-10 | GA | other | VARIES | AUSTELL NATURAL GAS SYSTEM, CITY OF | HIGH WINDS AND POSSIBLE MULTIPLE TORNADOES STRUCK JUST AFTER 5:00 AM. ON SATURDAY MORNING, FEBRUARY 10,1990. GAS SERVICE LINES WERE DAMAGED WHEN TREES WERE TOPPLED TEARING LINES FROM GROUND, WHEN HOUSES WERE DEMOLISHED AND WHEN MOBILE HOMES WERE BLOWN FR | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1088 | 1989-12-20 | NC | other |  | PUBLIC SERVICE CO OF NORTH CAROLINA | AFTER FURTHER CONSIDERATION AND INVESTIGATION OF THE INCIDENT, IT APPEARS THAT THIS MIGHT BE A NON-REPORTABLE ACCIDENT. IT APPEARS THAT THERE WAS A MALFUNCTION OF THE SERVICE REGULATOR WHICH CAUSED OVERPRESSURING OF THE FUEL LINE. WE NOW SUSPECT THAT TH | 200000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1089 | 1989-12-16 | MT | other | DUPONT | MONTANA - DAKOTA UTILITIES CO | CUSTOMER HAD DUG A WELL PIT ALONG SIDE OF HIS HOUSE WHICH REQUIRED RELOCATION OF THE GAS SERVICE LINE AND METER SETTING. THE CUSTOMER HAD THE WELL PIT EXCAVATED AND WAS PREPARING TO BUILD THE WELL HOUSE. RATHER THAN TRENCH AROUND THE WELL PIT AND A LARG | 100 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1090 | 1990-02-01 | IA | other | UNKNOWN (FLOYD COUNTY) | INTERSTATE POWER CO | UPON EXCAVATION, IT WAS DISCOVERED THAT A 6" LONG STAINLESS STEEL LEAK REPAIR CLAMP HAD BEEN INSTALLED AROUND A SECTION OF 2" STEEL GAS MAIN THAT HAD BEEN HIT BY A BACKHOE TOOTH. THE PIPE WAS DEFORMED AND WELL OUT OF ROUND AND WAS NOT LEAKING AT THE TIME | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1091 | 1990-01-24 | IL | other | UNKNOWN (COOK COUNTY) | PEOPLES GAS LIGHT & COKE CO | A 6" CAST IRON LOW PRESSURE MAIN LOCATED IN THE PARKWAY OPPOSITE A WATER METER VAULT WAS DAMAGED BY FROST. GAS FROM THE DAMAGED MAIN MIGRATED ALONG THE WATER SERVICE INTO THE VAULT AND IGNITED WHEN A WATER D | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1092 | 1990-02-13 | CA | other | DUPONT | SOUTHERN CALIFORNIA GAS CO | MASONRY CONTRACTOR EXCAVATED TO EXPOSE SUBTERRANEAN WALL TO DRY AND WATERPROOF IT. A 2 INCH PLASTIC SERVICE WAS ALSO UNCOVERED. A PROPANE HEATER USED IN THE DRYING PROCESS WAS LEFT UNATTENDED, MELTING THE SERVICE, IGNITING THE GAS. THREE APARTMENT UNIT | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1093 | 1989-01-15 | TX | other |  | LONE STAR GAS CO | METER LOOP HIT BY VEHICLE BREAKING INLET RISER. GAS IN\GNITED CAUSING VEHICLE TO BURN. VEHICLE DESTROYED. NO ONE WAS INJURED. SERVICE WAS INTERRUPTEDTO ONE COMMERCIAL CUSTOMER. | 5000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1094 | 1989-01-19 | TX | other | UNKNOWN (HARRIS COUNTY) | ENTEX - DIVISION OF ARKLA INC | RISER APPARENTLY STRUCK BY UNKNOWN FORCE, POSSIBLY AUTOMOBILE, CAUSING BREAKIN THREADS AT COUPLING. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1095 | 1990-02-13 | PA | technical failure | UNKNOWN (PHILADELPHIA COUNTY) | PHILADELPHIA GAS WORKS | WHILE REBUILDING METER CONNECTION TO 249 S. 56TH ST., OPERATOR'S EMPLOYEE BROKE OFF 1-1/4" STEEL SERVICE BEYOND THE FRONT FOUNDATION WALL, CAUSING NATURAL GAS TO LEAK INTO THE BASEMENT OF 251 S. 56TH ST. | 75000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1096 | 1990-01-31 | CA | ACCIDENTALLY CAUSED BY OPERATOR |  | SOUTHERN CALIFORNIA GAS CO | CONTRACTOR EMPLOYEE, ON SERVICE REPLACEMENT PROJECT, FAILED TO COMPLETELY CLOSE SERVICE RISER VALVE PRIOR TO REMOVING METER. ESCAPING GAS MIGRATED UP THROUGH KITCHEN FLOOR AND WAS IGNITED BY GAS RANGE. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1097 | 1990-01-19 | WA | other |  | WASHINGTON NATURAL GAS CO | VEHICLE DRIVEN BY INTOXICATED DRIVER LEFT THE ROAD AND STRUCK A POWER POLE WHICH FELL TO THE GROUND. COMMERCIAL POWER SHORTED THROUGH GROUND TO 8" STEELGAS LINE. POWER DISCHARGED IN CONTROL ROOM AT DIERINGER GATE (N. TACOMA) STATION, STARTING FIRE WHICH | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1098 | 1990-03-01 | AL | other | LTV | ALABAMA GAS CORP (EX. MARENGO CORP PROPERTY) | A CONTRACTOR, W.S. NEWELL, WAS UTILIZING A CATERPILLAR ROTOFLEX TO TILL AND COMPACT THE SOIL IN AND AROUND THE AREA OF A FOUR-INCH HIGH PRESSURE MAIN IN PREPARATION FOR THE CONSTRUCTION OF A RAILROAD SPUR. THE MACHINE STRUCK THE FOUR-INCH MAIN DURING THE | 183076 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1099 | 1990-02-09 | TX | other |  | BRAZOS RIVER GAS CO |  | 5000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1100 | 1989-12-24 | TX | other | LONE STAR STEEL | LONE STAR GAS CO |  | 7400 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1101 | 1990-03-09 | LA | other |  | LOUISIANA GAS SERVICE CO | POLICE REROUTED TRAFFIC AND EVACUATED APPROXIMATELY SIX HOUSES. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1102 | 1990-03-08 | NH | other | UNKNOWN | ENERGY NORTH NATURAL GAS INC | THE CONTRACTOR WHILE DRILLING SOIL SAMPLES BORED THROUGH A 6" STEEL GAS MAINOPERATING A 58 PSIG. THE ONE CALL SYSTEM WAS NOTIFIED AND THE GAS MAIN WAS M | 85000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1103 | 1990-01-18 | PA | other | UNKNOWN | ALLIED GAS CO | CIRCUMFERENTIAL CRACK ON 6" CAST IRON MAIN. UNSURE AT THIS TIME OF ACTUAL CAUSE OF CRACK. POSSIBILITY THAT CRACK COULD HAVE OCCURRED DUE TO FORCE OF EXPLOSION THAT OCCURRED WITHIN HOUSE # 101 CENTRE STREET, ASHLAND PA. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1104 | 1989-11-11 | TX | other |  | ENTEX - DIVISION OF ARKLA INC | SERVICE RISER WAS BROKEN OFF AT THREADS DUE TO TRUCK DRIVING INTO IT. ESCAPING GAS WAS IGNITED. TRUCK WAS BURNED. NO INJURIES. | 8000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1105 | 1990-02-21 | TX | other | UNKNOWN | ENTEX - DIVISION OF ARKLA INC | LARGE TRUCK DROVE OFF PAVEMENT ONTO SOFT DIRT. WEIGHT OF TRUCK CAUSED SERVICE LINE TO CRACK IN THREADED JOINT. FIRE DEPARTMENT BLOCKED TRAFFIC AND EVACUATED TWO SMALL BUSINESSES UNTIL SITUATION MADE SAFE. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1106 | 1990-02-25 | TX | other | PLEXCO | LONE STAR GAS CO | LINE BELIEVED TO BE DAMAGED BY LANSCAPER WHILE INSTALLING A TREE. | 5000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1107 | 1987-01-05 | MA | other | UNKNOWN (HAMPDEN COUNTY) | BAY STATE GAS CO | A SEWER REPAIR CREW WAS EXCAVATING IN FRONT OF THE HOUSE WHEN THEY DAMAGED AGAS SERVICE PIPE. THERE WAS NO SMELL OUTSIDE, BUT THE PIPE WAS PULLED INTO THE WALL CAUSING THE FITTINGS INSIDE TO BREAK OFF. THIS LEAD TO GAS GOING INTO THE HOUSE AND EVENTUALL | 75000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1108 | 1990-03-07 | NJ | other |  | SOUTH JERSEY GAS CO | GAS SERVICE BROKE NEAR THE HOUSE FOUNDATION, RESULTING IN HIGH PRESSURE GAS ENTERING THE HOUSE. GAS WAS ACCIDENTALLY IGNITED INSIDE THE HOUSE CAUSING ANEXPLOSION AND AN ENSUING HOUSE FIRE. HOUSE AND CONTENTS WERE TOTALLY DESTROY | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1109 | 1990-03-08 | MN | other | PLEXCO | NORTHERN STATES POWER CO | AS A RESULT OF A 1/4" HOLE BY A POSSIBLE RODENT IN NSP'S 5/8" P.E. GAS LINE,AN EXPLOSION OCCURRED AT 3833 RICHTER AVE. A DEAD RODENT WAS DISCOVERED ADJACENT TO 5/8" P.E. PIPE. | 90000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1110 | 1990-02-23 | NY | other |  | CONSOLIDATED EDISON CO OF NEW YORK | A CONTRACTOR INSTALLED A NEW METER BAR AND CONTROL VALVE UNDER LIVE CONDITIONS. AS A RESULT, GAS BUILT UP IN UNVENTILATED ROOM. THE CONTRACTOR IGNITED THE GAS WITH A SPARCK FROM HIS ELECTRIC JACKHAMMER. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1111 | 1990-03-28 | TX | other | GIBCO PIPE CO. | FORT STOCKTON MUNICIPAL SYSTEM, CITY OF | THIRD PARTY RAN INTO NORTH GATE AFTER RUNNING STOP SIGN, AND KNOCKING DOWN 2" GAUGE PIPE. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1112 | 1990-03-12 | CO | other | UNKNOWN (GUNNISON COUNTY) | SALGAS INC OF CRESTED BUTTE | ON MARCH 6, 1990 AT 08:55 HRS., THE CRESTED BUTTE STATE BANK WAS LEVELED BY AN EXPLOSION. THE CAUSE OF THE EXPLOSION IS AN UNKNOWN GAS. 3 PEOPLE WERE KILLED, 14 INJURED. THE BUILDING WAS DESTROYED. ON MARCH 12, 1990 AT 16:30 HRS., THIS OFFICE WAS NOTI | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1113 | 1990-02-16 | MO | other | UNKNOWN (BOONE COUNTY) | UNION ELECTRIC CO | CIRCUMFERENTIAL FRACTURE OF CAST IRON PIPE. NO READILY RECOGNIZABLE CAUSE. | 30000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1114 | 1990-03-13 | KY | other | UNKNOWN | UNION LIGHT HEAT & POWER CO |  | 70000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1115 | 1990-03-22 | IN | other | UNKNOWN (ADAMS COUNTY) | NORTHERN INDIANA PUBLIC SERVICE CO | CONSTRUCTION EQUIPMENT BEING UTILIZED BY JOHNSON BROTHERS CONSTRUCTION OF YORKTOWN, INDIANA, STRUCK AND PULLED OUR A 3/4" STEEL SERVICE FROM THE COMPRESSION COUPLING OF THE 4" DISTRIBUTION MAIN OPERATING AT 45 PSIG. THIS LINE SERVED A BUILDING AT 109 EAS | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1116 | 1990-03-12 | IA | other | UNKNOWN (WORTH COUNTY) | INTERSTATE POWER CO |  | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1117 | 1990-03-26 | TN | other |  | UNITED CITIES GAS CO | ON MONDAY, MARCH 26, 1990 AT APPROXIMATELY 9:00 PM. A HOUSE EXPLOSION AND FIRE WAS REPORTED AT THE CORNER OF WEST SEVIER AVENUE AND BROAD STREET IN KINGSPORT, TENNESSEE. THE SITE WAS LATER IDENTIFIED AS 110 WEST SEVIER AVENUE, ANUNOCCUPIED TWO-STORY, FRA | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1118 | 1989-12-07 | TX | other | DUPONT | ENTEX - DIVISION OF ARKLA INC | OPERATOR HAD SQUEEZED OFF AND REMOVED A LEAKING SECTION OF 2" PLASTIC MAIN IN A BELL HOLE. WHILE MAKING PERMANENT REPAIRS, THE PIPE SQUEEZING TOOL WAS ADJUSTED, AND SEBSEQUENTLY, GAS FILLED THE BELL HOLE. THE GAS WAS IGNITED BY A NEARBY PORTABLE ELECTRI | 1000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1119 | 1990-04-26 | MN | other | UNKNOWN (HENNEPIN COUNTY) | MINNEGASCO INC | SERVICE LINE WAS HIT BY A THIRD PARTY EXCAVATOR CAUSING A COUPLING PULL-OUT. | 250000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1120 | 1990-04-26 | NJ | ACCIDENTALLY CAUSED BY OPERATOR |  | ELIZABETHTOWN GAS CO | OPERATOR DIGGING TO REPAIR MINOR LEAK DAMAGED THE MAIN, CAUSING LARGE LEAK WHICH IGNITED BY UNKNOWN SOURCE, CAUSING FIRE WHICH DAMAGED ADJACENT DWELLINGS. | 300000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1121 | 1990-05-21 | FL | other |  | CENTRAL FLORIDA GAS CORP | FGT INTRODUCED AIR INTO ITS TRANSMISSION LINE SERVING ST. CLOUD. THE AIR GOT INTO THE ST. CLOUD DISTRIBUTION SYSTEM CAUSING SEVERAL CUSTOMERS TO LOSE SERVICE. THE GAS WAS SHUT OFF TO THE TOWN BY THE GAS DISTRIBUTION COMPANY FOR SAFETY PURPOSES. THREE HU | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1122 | 1990-05-16 | PA | other |  | U G I CORP | THE GAS SERVICE TO 2027 ASTER ROAD WAS AFFECTED BY A SUBSIDENCE OF UNKNOWN ORIGIN WHICH RESULTED IN THE FRACTURE OF THE 0.75 INCH PIPE AT A THREADED SOCKET COUPLING AND THE PARTIAL PULLOUT OF A 0.75-INCH STEEL SERVICE FROM A COMPRESSION TEE. THE ESCAPING | 200000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1123 | 1990-05-19 | NJ | other | GRINNELL | PUBLIC SERVICE ELECTRIC & GAS CO | THE INITIAL INVESTIGATION REVEALS AN IGNITION OF ACCUMULATED NATURAL GAS RESULTING IN AN EXPLOSION & ENSUING FIRE. THE ORIGINAL DELAYED IGNITION OCCURRED ON THE SECOND FLOOR LEVEL ABOVE THE BASEMENT UTILITY ROOMS. THE SOURCE OFACCUMULATING GAS AND THE | 1000000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1124 | 1990-05-17 | CA | other | UNKNOWN (FRESNO COUNTY) | PACIFIC GAS & ELECTRIC CO | DRIVER LOST CONTROL OF VEHICLE AND HIT THE FENCE, THE GAS METER SET AND THE BUILDING. | 20350 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1125 | 1990-06-19 | LA | technical failure |  | LOUISIANA GAS SERVICE CO | TRANSMISSION COMPANY FAILED TO OPEN ALL VALVES ON CROSS OVER LINE WHILE TAKING ONE OF TWO PIPELINES OUT OF SERVICE FOR MAINTENANCE. A TOTAL OF 161 CUSTOMERS WERE WITHOUT GAS. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1126 | 1990-06-21 | PA | other | DUPONT | PENNSYLVANIA GAS & WATER CO |  | 113000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1127 | 1990-06-25 | CA | other | UNKNOWN (SACRAMENTO COUNTY) | PACIFIC GAS & ELECTRIC CO | CONTRACTOR EXCAVATING WITH BACKHOE STRUCK MAIN, CAUSING GAS TO ESCAPE. COMPANY EMPLOYEE IN ATTEMPT TO GAIN ACCESS TO A VALVE TO SHUT OFF THE GAS STARTEDUP BACKHOE AND MOVED THE BUCKET OUT OF THE EXCAVATION. AN UNKNOWN SOURCE IGNITED THE GAS. THE COMPAN | 82500 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1128 | 1990-06-26 | MO | other | PHILLIPS PET | LACLEDE GAS CO | DURING THE REPAIR OF THE DAMAGE THAT RESULTED FROM ACTION BY OUTSIDE PARTY/THIRD PARTY THERE WAS AN IGNITION FROM AN UNKNOWN SOURCE. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1129 | 1990-07-13 | MA | other | UNKNOWN ( COUNTY) | BAY STATE GAS CO | THREE CONSTRUCTION WORKERS, EMPLOYED BY RAVOLI CONSTRUCTION (NORTH READING MASS) WERE INVOLVED IN INSTALLATION OF NEW SEWER FACILITIES. ONE PERSON APPARENTLY WAS IN A NEW SEWER MANHOLE, HE REPORTEDLY IGNITED A "BIC" TYPE CIGARETTE LIGHTER AND CAUSED IGNI | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1130 | 1990-07-02 | MO | ACCIDENTALLY CAUSED BY OPERATOR |  | K P L GAS SERVICE | IN CONJUNCTION WITH A MAIN INSTALLATION PROJECT FOR SYSTEM REINFORCEMENT, THE EXISTING SERVICE LINE TO 128 WEST 5TH WAS REPLACED WITH A NEW SERVICE LINE. DURING THE PROCESS OF TRANSFERRING SERVICE FROM THE OLD SERVICE LINE TOTHE NEW SERVCIE LINE, THE O | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1131 | 1990-06-28 | OK | other | DRISCO | OKLAHOMA NATURAL GAS CO | JEFF JONES WAS DIGGING POSTHOLES FOR A FENCE AT 3824 SIMS AND HIT A 2-INCH PLASTIC MAIN. THIS RESULTED IN A GAS LEAK WHICH WAS IGNITED BY A GASOLINE ENGINE FIVE FEET FROM POINT OF RUPTURE. | 1500 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1132 | 1990-07-13 | CA | other |  | PACIFIC GAS & ELECTRIC CO | FIRE FROM UNKNOWN SOURCE DAMAGED HOME. | 55150 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1133 | 1990-07-02 | MT | other | UNKNOWN | MONTANA - DAKOTA UTILITIES CO | THE OPERATOR OF A MOTOR HOME STRUCK A METER SET CAUSING RISER TO BREAK AT STOP, RESULTING IN A FIRE WHICH DESTROYED THE MOTOR HOME. | 47000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1134 | 1990-05-15 | MO | maintenance | UNKNOWN (ST LOUIS COUNTY) | LACLEDE GAS CO | NO READINGS FOR NATURAL GAS BECAME EVIDENT UNTIL 5/19/90. THE ACTUAL CORROSION LEAK WAS ISOLATED ON 5/20/90 AND THE APPROPRIATE REPAIRS WERE COMPLETED AT THAT TIME. | 60000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1135 | 1990-07-12 | MD | other | DUPONT | WASHINGTON GAS LIGHT CO | TWO EMPLOYEES WORKING FOR THE FREDERICK FENCE COMPANY INSTALLING FENCE POSTSWITH A GASOLINE AUGER, STRUCK AND DAMAGED A 1 1/4" PLASTIC HIGH PRESSURE NATURAL GAS LINE. THE ESCAPING NATURAL GAS IGNITED, INJURING BOTH WORKERS, WHO SUSTAINED FIRST, SECOND AN | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1136 | 1990-07-10 | CA | other | UNKNOWN | PACIFIC GAS & ELECTRIC CO | INITIALLY REPORTED AS A GAS EXPLOSION; INVESTIGATION REVEALED HOUSE COLLAPSED DUE TO DRYROT DAMAGING SERVICE LINE. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1137 | 1990-06-18 | NY | other |  | CONSOLIDATED EDISON CO OF NEW YORK | CONSTRUCTION WORK ON FRONT STOOP OF RESIDENCE RUPTURED UNUSED THREE-INCH SERVICE. IGNITION OF GAS OCCURRED, POSSIBLY CAUSED BY WELDING EQUIPMENT. REPORT OF TWO PERSONS HOSPITALIZED LATER PROVED TO BE ERRONEOUS. INVESTIGATION PROVED THAT INCIDENT DID NO | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1138 | 1990-07-27 | TX | technical failure | PLEXCO | LONE STAR GAS CO | A PROBLEM WITH THE TAPPING EQUIPMENT WHILE ATTEMPING TO CONNECT A 3-" POLYETHYLENE LINE TO AN 6" PLOYETHYLENE GAS MAIN. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1139 | 1990-08-02 | OK | other | UNKNOWN (CLEVELAND COUNTY) | OKLAHOMA NATURAL GAS CO | ATLAS PAVING (CONTRACTOR FOR CITY OF OKLAHOMA CITY) WAS EXCAVATING WITH A PULVERIZER IN PREPARATION OF A LIME STABILIZED SUBBASE FOR AN OKLAHOMA CITY STREET IMPROVEMENT PROJECT ON SOUTHWEST 104TH STREET. THE PULVERIZER CONTACTED A 2 3/8-INCH OD HIGH-PRES | 169200 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1140 | 1990-07-20 | CA | other |  | PACIFIC GAS & ELECTRIC CO | STRUCTURE FIRE SPREAD TO GAS METER LOCATION. | 100150 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1141 | 1990-08-02 | NC | other | PHILLIPS | PIEDMONT NATURAL GAS CO INC | ON THURSDAY, 080290, 3 PERSONS WERE BURNED AS A RESULT OF A DIG-IN TO A PIEDMONT NATURAL GAS SERVICE LINE. THE INCIDENT OCCURRED AT WEST CHARLOTTE SENOIRHIGH SCHOOL, 2219 SENIOR DR, CHARLOTTE, NC. WILLIAMS ELECTRIC CO WAS TRENCHING IN ORDER TO INSTALL UND | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1142 | 1990-08-25 | WI | other | LACLEDE | WISCONSIN PUBLIC SERVICE CORP | AN ABOVE GROUND REGULATORY FACILITY WAS STRUCK BY A PICK-UP TRUCK WHICH CROSSED A MEDIAN, TWO OPPOSING TRAFFIC LANES, WENT THROUGH A DITCH, AND 200 FEET THROUGH A FIELD. A 2" RISER PIPE WAS SEVERED UPON IMPACT. THE ESCAPING GAS IGNITED AND THE TRUCK WAS | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1143 | 1990-08-22 | NJ | other |  | PUBLIC SERVICE ELECTRIC & GAS CO | PRELIMINARY INVESTIGATIONS INDICATES THAT THE CUSTOMER'S RANGE APPLIANCE MAYHAVE BEEN FAULTY CAUSING GAS TO ESCAPE UNDETECTED WHICH RESULTED IN THIS INCIDENT. CUSTOMER WAS ON VACATION AND UPON RETURN DETECTED A STRONG ODOR. WHILE IN THE PROCESS OF OPENI | 80000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1144 | 1990-08-14 | CA | other | UNKNOWN (SAN MATEO COUNTY) | PACIFIC GAS & ELECTRIC CO | CUSTOMER'S GAS APPLIANCE IGNITED NEARBY GASOLINE FUMES RESULTING IN STRUCTURE FIRE WHICH SPREAD TO AND IGNITED THE GAS REGULATORY. | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1145 | 1990-08-13 | CA | other |  | PACIFIC GAS & ELECTRIC CO | VEHICLE STRUCK CUSTOMER HOUSELINE. ONE RESIDENT WASOVERCOME BY THE SMELL OFTHE NATURAL GAS, WAS TAKEN TO THE HOSPITAL. | 1800 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1146 | 1990-08-13 | CA | technical failure | DRISCO | PACIFIC GAS & ELECTRIC CO | EMPLOYEE WAS CUTTING A SQUEEZED OFF 2-INCH PLASTIC DEAD END MAIN WITH A PLASTIC PIPE CUTTER WHEN PIPE END BLEW OFF AND ESCAPING GAS WAS IGNITED BY ADJACENT CREW TRUCK'S GENERATOR. EMPLOYEE RECEIVED 2ND DEGREE BURNS ABOUT HANDS AND FACE. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1147 | 1990-08-15 | CA | other | AMERICAN | PACIFIC GAS & ELECTRIC CO | STRUCTURE FIRE OF UNKNOWN SOURCE CAUSED GAS METER TO MELT AND IGNITE. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1148 | 1990-08-21 | CO | other | UNKNOWN (JEFFERSON COUNTY) | PUBLIC SERVICE CO OF COLORADO | A SEWER CONTRACTOR USING A LINK BACKHOE TO EXCAVATE A TRENCH TO INSTALL A NEW SEWER LINE HIT AND PULLED A 2" MW MAIN OUT OF A COMPRESSION COUPLING. DURING THE PROCESS OF EMERGENCY CREWS ATTEMPTING TO EXPOSE THE SECTION OF LINE THAT HAD BEEN PULLED, AN UN | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1149 | 1990-08-30 | WA | technical failure |  | WASHINGTON NATURAL GAS CO | DURING WITHDRAWAL OF A RUBBER STOPPER AFTER A HOT TAP OPERATION, THE RUBBER WAS TORN FROM THE TAPPING MACHINE SHAFT, PREVENTING CLOSURE OF THE GATE VALVE. EMPLOYEE OF OPERATOR'S SUB-CONTRACTOR REMOVED THE BARREL ALLOWING GAS TO ESCAPE AND IGNITE FROM AN | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1150 | 1990-08-18 | TX | other |  | LONE STAR GAS CO | CAR HIT METER INSTALLATION. | 5000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1151 | 1990-09-09 | MD | other | UNKNOWN (HARFORD COUNTY) | BALTIMORE GAS & ELECTRIC CO | FIRE AT LOG CABIN CREATED PARTIAL COLLAPSE OF FRONT WALL. TIMBER FELL ON OUTSIDE METER/REGULATOR INSTALLATION CAUSING A RELEASE OF GAS AND ADDITIONAL FIRE. BEL AIR FIRE DEPARTMENT TURNED OFF VALVE AT OUTSIDE SERVICE RISER. AFTERTHE FIRE DEPARTMENT SHUT | 60000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1152 | 1990-08-22 | CA | other |  | PACIFIC GAS & ELECTRIC CO | FAILURE OF SERVICE PIPE ALLOWED GAS TO MIGRATE INTO BUILDING. WALL HEATER IN APARTMENT 6 IS ATTRIBUTED AS THE LIKELY SOURCE OF IGNITION. STRUCTURE FIREENSUED, CAUSING STRUCTURAL DAMAGE. BUILDINGS WERE EVACUATED AND TRAFFIC REROUTED. | 165000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1153 | 1990-09-17 | UT | other | UNKNOWN (WEBER COUNTY) | MOUNTAIN FUEL SUPPLY CO | ON SATURDAY, SEPTEMBER 15TH, THE HOMEOWNER OF 2282 WEST 4400 SOUTH IN ROY, UTAH CONSTRUCTED A MAKESHIFT AWNING OVER HIS CAMPER USING PINE POLES, CANVAS AND ROPE. THE POLES WERE POSITIONED SUCH THAT THEY WERE LEANING UP AGAINST THE HOUSE AND WERE HELD INP | 60000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1154 | 1990-08-29 | PA | other |  | U G I CORP | AT 5:10 AM. ON AUGUST 29, 1990, A CALL WAS RECEIVED REPORTING AN EXPLOSION AND FIRE AT 423 AND 425 N. 5TH ST., ALLENTOWN. UPON INVESTIGATION, AN AREA OFSUBSIDENCE APROXIMATELY 10' BY 36' WAS DISCOVERED AROUND THE MAIN BREAK. THE AREA OF SUBSIDENCE WAS O | 300000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1155 | 1990-08-30 | OK | technical failure | PLEXCO | OKLAHOMA NATURAL GAS CO | EMPLOYEES OF A & L UNDERGROUND, A PIPELINE CONTRACTOR, HAVE BEEN INVOLVED INA DGETR 7UTION REBUILD PROJECT FOR OKLAHOMA NATURAL GAS COMPANY (ONG). ON THURSDAY, AUGUST 30, 1990, THE CONTRACTOR HAD A CREW WORKING AT 526 EAST LATIMER COURT. THEY WERE CLAMP | 500 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1156 | 1990-08-13 | CA | other | FISHER | SOUTHERN CALIFORNIA GAS CO | SHORTED ELECTRIC FUSES AT AN INDUSTRIAL COMPLEX CAUSED A GAS HOUSELINE SOLENOID VALVE TO CLOSE. GAS RELIEVING THROUGH A RELIEF VALVE IN THE MSA WAS IGNITED BY FLYING SPARKS. TWO INDUSTRIAL METER SETS WERE DESTROYED. | 15300 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1157 | 1990-08-29 | CA | other |  | SOUTHERN CALIFORNIA GAS CO | THE D.W. BURHOE CONSTRUCTION CO., GRADING FOR STREET IMPROVEMENT FOR THE CITY OF PALMDALE, STRUCK AND DAMAGED A 6 INCH HIGH PRESSURE MAIN, CAUSING GAS TOESCAPE. | 39400 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1158 | 1990-09-05 | CA | ACCIDENTALLY CAUSED BY OPERATOR |  | PACIFIC GAS & ELECTRIC CO | EMPLOYEE ACCIDENTALLY STEPPED ON 1 1/4 INCH STUB SERVICE CAUSING GAS SERVICETO CRACK AND LEAK. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1159 | 1990-09-27 | AR | other | PHILIPS-DRISCOPIPE | ARKANSAS LOUISIANA GAS CO (ARKLA GAS CO) | ARKLA CREW WAS IN THE PROCESS OF INSERTING A 2" PLS GAS MAIN IN AN EXISTING 4" STEEL MAIN. ALL ASPECTS OF THE JOB HAD BEEN COMPLETED WHEN THE SQUEEZE OFF WAS RELEASED, BLEEDING THE AIR OUT OF THE LINE FOR THE FINAL CONNECTION. WHILE BLEEDING THE LINE, T | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1160 | 1990-10-08 | WV | maintenance |  | MOUNTAINEER GAS CO | TWO EMPLOYEES OF ROVER CONSTRUCTION COMPANY REMOVED THE LID FROM A MAN HOLE COVER TO ENTER A SEWER LINE UNDER CONSTRUCTION. THEY WERE USING A BATTERY POWERED LAZER BEAM WHICH SPARKED AND IGNITED GAS THAT HAD ACCUMULATED. ONE EMPLOYEE, JOHN PRINGLE WAS T | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1161 | 1990-10-05 | MO | other |  | K P L GAS SERVICE | REGARDING PIPELINE LOCATION MARKERS:CITY REQUESTED MAIN LOCATION DATA BY TELEPHONE (EMERGENCY LOCATE) AT 10:15.KANSAS CITY WATER AND POLLUTION CONTROL DEPT. BROKE A DRIP POT LOOSE FROM 24"CAST IRON MAIN WHILE EXCAVATING A SEWER LINE. | 7000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1162 | 1990-09-24 | KY | ACCIDENTALLY CAUSED BY OPERATOR | WATTS FLUID POWER | CARROLLTON GAS DISTRICT SYSTEM, CITY OF | THE UTILITY WAS IN THE PROCESS OF UP-RATING A SIX INCH (6") STEEL NATURAL GAS PIPELINE TO A MAOP OF FOUR HUNDRED AND TWENTY FIVE POUNDS PER SQUARE INCH(425 PSIG). THE UTILITY'S PROPANE-AIR PEAK SHAVING PLANT IS CONNECTED TO THIS PIPELINE THROUGH APPROXIM | 49000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1163 | 1990-10-12 | WI | other | DRESSER INDUSTRIES | WISCONSIN GAS CO | SERVICE PIPE WAS PULLED APART AT A COUPLING BECAUSE OF SETTLEMENT OF SOIL INTHE TRENCH OF A NEW SEWER.ON OCTOBER 12, 1990 AT 1:42 P.M. A GAS EXPLOSION OCCURED AT W67 N396 GRANT AVENUE IN CEDARBURG, WI. A SEWER CONTRACTOR WAS FLUSHING A SEWER TRENCH WITH | 80000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1164 | 1990-10-15 | WI | other |  | WISCONSIN GAS CO | CUSTOMER'S BOILER OVER FLOW TANK FELL AND BROKE HOUSEPIPE WHICH LEAKED AND IGNITED ON A PILOT LIGHT.ON OCTOBER 15, 1990 AT 5:12 P.M. A GAS EXPLOSION OCCURRED AT 1406 N. 23RD STREET, AN APARTMENT BUILDING OF 10 UNITS. A HEAVY TANK USED FOR OVERFLOW OF HOT | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1165 | 1990-10-01 | NY | maintenance |  | CONSOLIDATED EDISON CO OF NEW YORK | MECHANIC WAS LOOSENING BOLTS ON A 6" STEEL COUPLING IN EXCAVATION WHEN FIRE ERUPTED.CONSTRUCTION CREW WAS PERFORMING A GAS MAIN CUT-OUT WHEN A FIRE ERUPTED IN THE EXCAVATION. A MECHANIC WAS LOOSENING BOLTS ON A 6" STEEL COUPLING WHEN INCIDENT OCCURRED. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1166 | 1990-10-05 | MO | technical failure |  | LACLEDE GAS CO | DURING THE PROCESS OF PURGING A PROPANE GAS MAIN FOR THE CONVERSION TO NATURAL GAS, A FITTING USED IN THE TEMPORARY PURGE PIPING FAILED. IT APPEARS THATTHE NATURAL GAS WAS IGNITED BY STATIC ELECTRICITY. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1167 | 1990-10-13 | LA | other | UNKNOWN | NEW ORLEANS PUBLIC SERVICE INC | GIRTH WELD FAILED AS A RESULT OF EXTERNAL STRESS. CAUSE OF FAILURE IS UNDER INVESTIGATION | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1168 | 1990-10-16 | NC | other |  | PUBLIC SERVICE CO OF NORTH CAROLINA | A CONTRACTOR INSTALLING A WATER LINE AT RESIDENCE PULLED THE GAS SERVICE OUTOF A MECHANICAL COUPLING CAUSING A GAS LEAK. THE LEAK WAS UNREPORTED AND WAS LATER IGNITED BY A PLUMBING WORKER WHO WAS LIGHTING A CIGARETTE. THE PLUMBING WORKER WAS BURNED AROU | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1169 | 1990-10-02 | MA | other |  | BOSTON GAS CO | THE TOWN OF WINTHROP MAINTAINED A BRICK DRAIN MANHOLE ON GRANDVIEW AVENUE ATBILLOWS STREET. THE MANHOLE HAD A 15" DRAIN OUTFALL RUNNING INTO WINTHROP HARBOR WHICH WAS AFFECTED BY THE OPERATION OF THE TIDES. TIDAL WATER ENTERED THE MANHOLE THROUGH THE 15 | 950000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1170 | 1990-10-15 | OH | other | UNKNOWN (LAKE COUNTY) | EAST OHIO GAS CO | THE HOME OWNER, WHILE ATTEMPTING TO BY-PASS HIS NATURAL GAS METER, SAYS HE REMOVED A 1" SCREW PLUG FROM A 1" X 1" SCREW TEE UPSTREAM OF HIS SERVICE REGULATOR AND LOCATED UNDERGROUND NEAR HIS NATURAL GAS METER MANIFOLD. HE REMOVEDTHE 1" SCREW PLUG FROM TH | 102414 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1171 | 1990-10-15 | CA | other | SPRAGUE | PACIFIC GAS & ELECTRIC CO | STRUCTURE FIRE DAMAGED METER AND REGULATOR. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1172 | 1990-10-26 | MN | other | UNKNOWN (RAMSEY COUNTY) | NORTHERN STATES POWER CO | CONTRACTOR STRUCK 8" STEEL MAIN CROSSING INTERSTATE FREEWAY, CAUSING TRAFFICTO BE STOPPED FOR 40 MINUTES. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1173 | 1990-10-09 | NY | other |  | CONSOLIDATED EDISON CO OF NEW YORK | WHILE DRILLING HOLES IN THE PROCESS OF REPLACING A CORRODED GAS RISER LEADING TO A GAS HEATER, A GENERAL CONTRACTOR CAUSED THE RISER TO LEAK. THIS ACTIONPRECIPITATED A GAS EXPLOSION BY AN UNKNOWN IGNITION SOURCE. TWO PERSONS WERE TAKEN TO THE HOSPITAL. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1174 | 1990-11-15 | CA | other | ALDYL A | PACIFIC GAS & ELECTRIC CO | DURING THE INVESTIGATION, PACIFIC GAS AND ELECTRIC COMPANY AND THE PARADISE FIRE DEPARTMENT FOUND THAT THE GAS SERVICE HAD BEEN PREVIOUSLY SEVERED BY AN UNKNOWN THIRD-PARTY. THE DAMAGED SERVICE WAS REPAIRED WITH HOSE CLAMPS AND APIECE OF AUTOMOBILE HEATE | 125000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1175 | 1990-11-02 | IL | other | UNKNOWN | NORTHERN ILLINOIS GAS CO | A SERVICE TEE WAS KNOCKED OFF A 6-INCH, 150 PSI MAIN BY THE CUSTOMER WHO WASGRADING IN A DITCH. NI-GAS PERSONNEL WERE CALLED AND RESPONDED TO STOP THE ESCAPING GAS AND MAKE REPAIRS. WHILE REPAIRS WERE UNDER WAY, ESCAPING GAS WAS IGNITED, RESULTING IN IN | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1176 | 1990-11-29 | GA | other | DRISCO | ATLANTA GAS LIGHT CO | CONTRACTOR MAKING A 30" BORE STRUCK AND DAMAGED 4" GAS MAIN LOCATED IN RIGHT-OF-WAY OF INDIAN TRAIL ROAD. FLOW OF NATURAL GAS BACK THROUGH CASING WAS IGNITED BY BORING RIG, RESULTING IN DAMAGE TO THE BORING RIG EQUIPMENT. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1177 | 1990-11-14 | PA | other |  | PEOPLES NATURAL GAS CO | CONTRACTOR HIT P-1156 WITH BULLDOZER. LINE HAD BEEN LOCATED & MARKED BY PNG. | 180000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1178 | 1990-11-13 | MN | other | AMERICAN METER | NORTHERN MINNESOTA UTILITIES | THE TIME THAT THE PRESSURE EXCEEDED THE MAOP IS UNDEFINED. IT IS SUSPECTED THAT THE EXCESS PRESSURE MAY HAVE BEEN INITIATED ON TUESDAY, NOVEMBER 13TH. THE PRESSURE WAS REDUCED TO WITHIN MAOP BY 1055 HOURS, NOVMEMBER 15, 1990. PRESSURE IS JUDGED TO HAVE | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1179 | 1990-11-27 | IN | other | DUPONT | NORTHERN INDIANA PUBLIC SERVICE CO | ON NOVEMBER 27, 1990, AT APPROXIMATELY 1330 HRS., THE HOUSE IN QUESTION EXPLODED AND WAS GUTTED BY THE ENSUING FIRE. MS. ANN HORVATH, AGE 78 YEARS, WAS HOSPITALIZED DUE TO INJURIES CAUSED BY FALLING DEBRIS. THE CAUSE OF THE INCIDENT IS ABGRIBUTED TO LEA | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1180 | 1990-12-04 | NY | other |  | BROOKLYN UNION GAS CO | A N.Y.C. CONTRACTOR EMPLOYEE WAS INJURED WHILE WORKING IN A SEWER MANHOLE ONEAST 72ND. STREET BETWEEN AVENUE L AND AVENUE M. A BROOKLYN UNION CHEMIST CONFIRMED THE PRESENCE OF NATURAL GAS IN THE SEWER MANHOLE. UPON INVESTIGATION BY LEAK SURVEILLANCE CR | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1181 | 1990-11-17 | NY | other |  | CONSOLIDATED EDISON CO OF NEW YORK | PERSON WAS USING COMMERCIAL BAKING OVEN WHEN AN EXPLOSION OCCURRED. | 1000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1182 | 1990-12-04 | CA | other |  | PACIFIC GAS & ELECTRIC CO | GAS METER SET IN GARBAGE COLLECTION AREA CAUGHT ON FIRE. | 25000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1183 | 1990-12-06 | OH | other | PHILLIPS DRISCOPIPE INC | EAST OHIO GAS CO | TEMPORARY LOCATION MARKING WAS INACCURATE. ANOTHER UTILITY HIT A 4-INCH PLASTIC LOW PRESSURE MAIN WITH A BORING DEVICE. GAS MIGRATED 17 FEET THROUGH SOIL TO A HOUSE. THE HOUSE EXPLODED. THERE WERE NO INJURIES OR FATALITIES. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1184 | 1990-12-15 | LA | maintenance | UNKNOWN (ORLEANS COUNTY) | NEW ORLEANS PUBLIC SERVICE INC | GAS ESCAPING FROM A RUSTED OUT 1 1/2 INCH CONCRETE COATED LOW PRESSURE SERVICE LINE TO 4512-14 BANKS ACCUMULATED IN THE FRONT WALL OF THE BUILDING AND MAY HAVE BEEN IGNITED BY A LIGHT SWITCH OR DOOR BELL. A SMALL AMOUNT OF SIDINGWAS BLOWN OFF THE FRONT W | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1185 | 1990-12-14 | LA | other | UNKNOWN (ORLEANS COUNTY) | NEW ORLEANS PUBLIC SERVICE INC | GAS ESCAPING FROM A BROKEN 6 INCH LOW PRESURE CAST IRON GAS MAIN LEAKED INTOTHE SEWER LINE LEADING TO 3409 11 SHORT STREET. GAS THEN ESCAPED THROUGH BROKEN SEWER PIPES UNDER 3411 SHORT, ENTERED THE BATHROOM AND WAS IGNITED BY A WATER HEATER. MS. LEOLIA | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1186 | 1990-12-20 | LA | technical failure | UNKNOWN | LOUISIANA GAS SERVICE CO | A COMPANY CONSTRUCTION CREW WAS ATTEMPTING TO REWORK AND GREASE A 4" PLUG VALVE AT THE CORNER OF MERAUX LANE AND EAST JUDGE PEREZ DRIVE. THE VALVE WAS STUCK IN THE OFF POSITION. WHEN THE CONSTRUCTION WORKER LOOSENED THE BONNET RETAINING BOLTS, THE VALVE | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1187 | 1990-12-31 | CO | other |  | PUBLIC SERVICE CO OF COLORADO | CAB PLASTIC SERVICE WAS INSERTED INSIDE 1 1/4" STEEL SERVICE IN 1965. CAB PLASTIC PULLED OUT OF THE COMPRESSION COUPLING AT THE WALL OF THE STRUCTURE AT4940 LOWEL BLVD. THE ESCAPING GAS WAS IGNITED BY SOME UNKNOWN SOURCE, RESULTNG IN A STRUCTURE FIRE. | 30000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1188 | 1990-12-15 | TN | other | UNKNOWN | UNITED CITIES GAS CO | ABOUT 12:05 PM. ON SATURDAY, DECEMBER 15, 1990, THE RESIDENCE AT 908 EAST MARKET STREET EXPLODED AND BURNED. THERE WERE TWO RESIDENTS AND A LANDSCAPE CONTRACTOR WITH HELPER AT THE HOME. THE CONTRACTOR AND HIS HELPER WERE NOT INJURED, HOWEVER, ONE RESIDE | 35000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1189 | 1990-12-18 | VA | other | DUPONT | COMMONWEALTH GAS SERVICES INC | AN EXPLOSION OCCURRED IN A BUILDING UNDER CONSTRUCTION THAT DID NOT HAVE NATURAL GAS SERVICE, INJURING FOUR CONSTRUCTION WORKERS, TWO OF WHOM WERE HOSPITALIZED. ALTHOUGH THE SOURCE AND NATURE OF THE COMBUSTIBLE MATERIAL HAS NOT BEEN DETERMINED, NATURAL G | 75000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1190 | 1990-12-05 | ME | other |  | NORTHERN UTILITIES INC (ME) | THE CONTRACTOR PULLED A 1 1/4" STEEL CAUSING THAT HAD 1" PLASTIC MAIN INSIDE THIS, IN TURN, BROKE A 3/4" MALLEABLE TEE WHERE IT WAS THREADED INTO A 1 1/4 X 3/4 TEE WITH A POSI-LOCK ADAPTOR WHERE A TRANSITION HAD BEEN MADE FROM PLASTIC TO STEEL TO JOIN TO | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1191 | 1990-12-07 | NY | other |  | CONSOLIDATED EDISON CO OF NEW YORK | HOSE CONNECTION MELTED AT CUSTOMER'S BARBECUE GRILL. GAS RELEASED FROM MELTED HOSE IGNITED AND THE FIRE SPREAD TO THE HOUSE. | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1192 | 1990-12-28 | LA | other | UNKNOWN | LOUISIANA GAS SERVICE CO | DUMP TRUCK LOADED WITH SAND ROLLED OVER VALVE BOX CAUSING VALVE NIPPLE TO CRACK IN THREADS. | 75000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1193 | 1991-01-05 | LA | other |  | LOUISIANA GAS SERVICE CO | 2" GAS MAIN WAS RUPTURED BY A BACKHOE THAT WAS ATTEMPTING TO DIG UP AND REMOVE A PAVED STREET. | 4000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1194 | 1991-01-02 | MI | other | US STEEL | CONSUMERS POWER CO | CONTRACTOR AUGERING FOR WATER LINE HIT AND DAMAGED GAS MAIN. GAS IGNITED DURING REPAIR. | 75000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1195 | 1991-01-02 | OH | other | UNKNOWN | COLUMBIA GAS OF OHIO INC | PAUL CYGAN, CUSTOMER AND PROPERTY OWNER, WAS ATTEMPTING TO REPAIR A GAS LEAKON A BRASS METER VALVE IN HIS BASEMENT WHEN THE VALVE CORE BLEW OUT. ESCAPING GAS WAS IGNITED BY A BURNING PROPANE TORCH THAT MR. CYGAN HAD IN THE BASEMENT WITH HIM. THE FIRE CA | 3000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1196 | 1991-01-15 | NY | other |  | BROOKLYN UNION GAS CO | N.Y.C. FIRE DEPARTMENT REPORTED THAT NATURAL GAS WAS FUELING A FIVE ALARM BLAZE INVOLVING SEVERAL LARGE INDUSTRIAL BUILDINGS WITHIN ONE SQUARE BLOCK. INVESTIGATION AS TO THE CAUSE OF THE FIRE IS STILL BEING CONDUCTED. AS PER FEDERAL REGULATION 49-CFR-19 | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1197 | 1991-01-08 | MD | other |  | BALTIMORE GAS & ELECTRIC CO | AT 1040, BALTIMORE CITY FIRE DEPARTMENT REQUESTED SERVICE ON WORKING TWO ALARM FIRE AT 4004 FREDERICK AVENUE. ARRIVING AT 1045 THE FIRST BALTIMORE GAS AND ELECTRIC REPRESENTATIVE REPORTED TO THE BATTALION CHIEF. THE BATTALION CHEIF #4 STATED "FIRE WAS N | 275000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1198 | 1990-12-29 | AR | other | UNKNOWN (GARLAND COUNTY) | ARKANSAS LOUISIANA GAS CO (ARKLA GAS CO) | 4" CAST IRON COLD BREAK. | 150000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1199 | 1990-12-21 | CA | other |  | PACIFIC GAS & ELECTRIC CO | EXPLOSION AND IGNITION OF ESCAPING GAS DAMAGED STRUCTURE AT ABOVE ADDRESS. SOURCE OF THE ESCAPING GAS IS STILL UNDER INVESTIGATION. NEARBY BUILDINGS WERE EVACUATED & TRAFFIC REROUTED. THE METER WAS REMOVED & THE SERVICE PIPE WAS CAPPED. | 465000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1200 | 1991-01-07 | MO | other | UNKNOWN (ST FRANCOIS COUNTY) | LACLEDE GAS CO | DURING REPAIR OF WATER MAIN, WATER COMPANY'S BACKHOE PUSH/PULLED STEEL GAS SERVICE TO THIS ADDRESS, CAUSING FITTING TO PULL APART, RESULTING IN EXPLOSION AND FIRE. | 95000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1201 | 1991-01-13 | MN | other |  | GREAT PLAINS NATURAL GAS CO | THIS REPORT IS A FOLLOW-UP TO THE TELEPHONIC REPORT. EXTENSIVE TESTING INDICATES THAT THERE WAS NO RELEASE OF GAS FROM THE PIPELINE. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1202 | 1991-01-06 | OR | other | UNKNOWN | NORTHWEST NATURAL GAS CO | BASEMENT FIRE AT THE RESIDENCE INVOLVED ONE FATALITY AND MELTDOWN OF A BASEMENT METER SET. FREEZING RAIN, ICY STREETS, AND TRAFFIC SNARLS CONTRIBUTED TOTHE TWO-HOUR RESPONSE TIME. INVESTIGATION BY CITY FIRE MARSHALL, STATE UTILITY COMMISSION AND NATIONA | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1203 | 1991-01-14 | MO | other | UNKNOWN | MISSOURI PUBLIC SERVICE CO |  | 60000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1204 | 1990-12-23 | WY | other | DUPONT | JACKSON VANGAS INC | 12/23/89 2:00 PM. (APPROX). A CALL WAS PLACED TO JOHN NORBY IN RUPERT IDAHOBY JOHN SLOAN, SUBURBAN PROPANE EMPLOYEE, STATING THAT THERE HAD BEEN AN EXPLOSION AT THE CORNER OF FLAT CREEK & KARNS ACROSS FROM THE RADEO GROUNDS. JOHN SLOAN ON 2-WAY MOBILE P | 125000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1205 | 1991-01-09 | MO | other | UNKNOWN | K P L GAS SERVICE | A FIRE AT 2121 ST. JOHN MAY HAVE RESULTED FROM AN IGNITION OF GAS WHICH COULD HAVE MIGRATED FROM A CRACK IN A 4" CAST IRON MAIN IN THIS VICINITY. THE CRECK MAY HAVE BEEN CAUSED BY EARTH MOVEMENT POSSIBLY DUE TO FROST CONDITIONS IN THE SOIL. THE POINT OF | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1206 | 1990-09-21 | NJ | other | INNER-TITE | PUBLIC SERVICE ELECTRIC & GAS CO | ON SEPTEMBER 21, 1990, AT 5:07 AM., A TELEPHONE CALL WAS RECEIVED BY THE COMPANY FROM BRIDGEWATER FIRE COMPANY TO REPORT A GAS LEAK ON FINDERNE AVENUE, BRIDGEWATER, IN THE VICINITY OF 3RD AVENUE. A SERVICEMAN FROM PLAINFIELD DISTRICT WAS DISPATCHED AND A | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1207 | 1991-01-31 | MA | other |  | COMMONWEALTH GAS CO | TWO PERSONS WERE REMOVED FROM THE BUILDING PER ORDER OF THE NATICK FIREDEPARTMENT. BOTH PERSONS WERE ADMITTED AND TESTED FOR CARBON MONOXIDEEXPOSURE AT LEONARD MORSE HOSPITAL, FRAMINGHAM, MA. RESULTS OF THESE TESTSWERE NOT KNOWN AT THE TIME OF THE TELEP | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1208 | 1991-01-17 | MO | other | UNKNOWN (ST LOUIS COUNTY) | LACLEDE GAS CO | EXTERNAL STRESSES ON A 6 INCH LOW PRESSURE CAST IRON MAIN CAUSED A COMPLETE CIRCUMFERENCE BREAK. | 75000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1209 | 1991-02-05 | NY | other | UNKNOWN ( COUNTY) | CONSOLIDATED EDISON CO OF NEW YORK | CONSTUCTION CREW PERFORMING GAS MAIN TIE-IN WHEN FIRE ERUPTED IN THE EXCAVATION. THEY WERE MANIFOLDING TWO 4" PIPES FROM A 20" MAIN TO A 6" MAIN WHEN INCIDENT OCCURRED. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1210 | 1991-01-06 | NY | other |  | CONSOLIDATED EDISON CO OF NEW YORK | NO NATURAL GAS INVOLVED. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1211 | 1991-01-30 | NY | other |  | CONSOLIDATED EDISON CO OF NEW YORK | A CRACKED WELD ON A 6" MEDIUM PRESSURE STEEL MAIN CAUSED NATURAL GAS TO MIGRATE OVER 300 FEET UNDER THE GROUND AND SEWER SYSTEM. AN EXPLOSION OCCURRED AND THIS HOUSE DUE TO THE BUILD UP OF GAS IN THE HOME. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1212 | 1991-01-26 | IL | other | PLEXCO | ILLINOIS POWER CO | ON JANUARY 26, 1991, AT APPROXIMATELY 10:20 AM., AN EXPLOSION AND RESULTING FLASH WAS REPORTED TO THE LOCAL FIRE DEPARTMENT AT 123 N. MAIN STREET IN CHERRY. A SEVEN YEAR OLD BOY, STANDING OUTSIDE OF THE GARAGE INVOLVED, WAS HOSPITALIZED DUE TO BURNS. TH | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1213 | 1991-01-24 | WI | other | UNKNOWN | WISCONSIN NATURAL GAS CO | WALL AT DWELLING COLLAPSED, DUE TO FIRE, THEREBY BREAKING RISER PIPE UPSTREAM OF METER ASSEMBLY. | 65000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1214 | 1991-01-26 | PA | other |  | U G I CORP | ACCORDING TO THE HARRISBURG BUREAU OF FIRE INCIDENT REPORT, THE LEAK AND SUBSEQUENT IGNITION APPEARED TO ORIGINATE FROMTHE FURNACE TO HOUSE NO.2251 KENSINGTON STREET, HARRISBURG. THERE WAS NO APPARENT INVOLVEMENT WITH UGI FACILITIES AS TO CAUSE. HOWEVER | 225000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1215 | 1991-01-31 | CA | other | ROCKWELL | PACIFIC GAS & ELECTRIC CO | STRUCTURE FIRE OF UNKNOWN ORIGIN SPREAD TO METER/REGULATOR, ALLOWING GAS TOESCAPE AND IGNITE. ONE THIRD-PARTY INJURY REQUIRED ADMITTANCE TO LOCALHOSPITAL. SUPPLEMENTAL REPORT 8/26/94 INDICATES A REVISION IN INCIDENT CAUSE.STRUCTURE FIRE. | 75500 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1216 | 1991-02-19 | NJ | other |  | ELIZABETHTOWN GAS CO | UNION COUNTY ARSON INVESTIGATION UNIT HAS RULED THE EXPLOSION AS STILL UNDERINVESTIGATION AS OF FEBRUARY 21, 1991. | 300000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1217 | 1991-02-03 | NY | other | UNKNOWN (MONROE COUNTY) | ROCHESTER GAS & ELECTRIC CORP | CATCH BASIN RECENTLY RECONSTRUCTED IN JULY 1990, WAS DISCOVERED RESTING ON THE CAST IRON MAIN APPROXIMATELY 5' FROM WHERE THE BREAK OCCURRED IN THE MAIN. | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1218 | 1991-02-21 | IN | technical failure |  | OHIO VALLEY GAS CORP | APPROXIMATELY 7:30 AM., FEBRUARY 21,1991, A 2' GAS LINE BECAME DISCONNECTED,WHICH CAUSED RAW GAS TO GO INTO THE PLANT. THIS WAS IN CONJUCTION WITH HOT WORKS REMOVING BURNERS FROM THE TANK HEAT-UP. TWO ANCHOR GLASS EMPLOYEES, KENNY MCCOY AND JACK PHILLIP | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1219 | 1991-02-06 | CT | other |  | SOUTHERN CONNECTICUT GAS CO | ON JANUARY 17, 1991, WHILE ON ROUTINE LEAK SURVEY, A MAIN BREAK WAS DETECTEDADJACENT TO A NEWLY INSTALLED MANHOLE NEAR 74 DWIGHT STREET, NEW HAVEN. THESPREAD OF THE GAS LEAK WAS APPROXIMATELY 100 FT. IN EACH DIRECTION, WITHIN THE STREET, FROM THE BREAK. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1220 | 1991-02-05 | WI | other | UNKNOWN (MILWAUKEE COUNTY) | WISCONSIN NATURAL GAS CO | THE LOCATION OF SERVICE LINE WAS REASONABLY MARKED AT THE TIME OF THE INCIDENT. | 200000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1221 | 1991-02-14 | PA | other |  | PEOPLES NATURAL GAS CO | ED HERNANDEZ'S CAR LEFT THE HIGHWAY AND SHEARED OFF THE NATURAL GAS METER AGAINST THE GEORGE HOME, STARTING A FIRE THAT DESTROYED THE RESIDENCE. | 60000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1222 | 1991-02-19 | PA | other |  | U G I CORP | AT 1011 HOURS ON FEBRUARY 19, 1991 UGI RECEIVED NOTIFICATION VIA TELEPHONE THROUGH ITS CUSTOMER INFORMATION CENTER THAT A CONTRACTOR HAD HIT A GAL LINE AT 314-316 N. WATER STREET IN LITITZ BOROUGH. TWO UGI EMPLOYEES RESPONDED, VENTILATED ONE DUPLEX TYPE | 500000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1223 | 1991-02-02 | NM | other | UNKNOWN | GAS CO OF NEW MEXICO | ON SATURDAY, FEBRUARY 2, 1991, THE ALBUQUERQUE FIRE DEPARTMENT (APD) CALLED THE GAS COMPANY OF NEW MEXICO (GCNM) DISPATCH OFFICE AT 2:16 PM TO REPORT A CAR HIT METER WITH A BLOWING GAS LINE AT 1111 AMHERST SE. THE AFD REQUESTED GCNM'S ASSISTANCE. GENERA | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1224 | 1991-03-14 | CO | other | UNKNOWN (KIT CARSON COUNTY) | PEOPLES NATURAL GAS | FARMER OPERATING EXCAVATING EQUIPMENT STRUCK LINE WITHOUT FIRST MAKING LINE LOCATE REQUEST. | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1225 | 1991-03-20 | OR | other | UNKNOWN | NORTHWEST NATURAL GAS CO | CONTRACTOR DOING ENVIRONMENTAL DRILLING TO TEST FOR GASOLINE CONTAMINATION OF SOIL STRUCK AN INACTIVE CURB SERVICE ON RIVER ROAD AT THE REAR OF 19625 MCLOUGHLIN. CONTRACTOR PERSONNEL STATED THAT THEY SMELLED GAS, BUT THOUGHT THATGASOLINE VAPORS WERE COMI | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1226 | 1991-04-02 | NJ | other | DUPONT | SOUTH JERSEY GAS CO | ON APRIL 2, 1991, AT APPROXIMATELY 14:30 HOURS, SOUTH JERSEY GAS COMPANY RECEIVED A CALL FROM A CONTRACTOR REPORTING THAT A GAS MAIN HAD BEEN STRUCK AND WAS BLOWING. A SERVICEMAN WAS DISPATCHED AT 14:33 HOURS. HE ARRIVED AT 14:45 HOURS AND REQUESTED A S | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1227 | 1991-03-13 | LA | other | UNKNOWN | NEW ORLEANS PUBLIC SERVICE INC | AN EXPLOSION AND FIRE OCCURRED AT 1301-03 S. SARATOGA DESTROYING THE BUILDING AND DAMAGED THE SERVICE RISER BELOW THE VALVE. THE SERVICE WAS IGNITED BY THE FIRE AND WAS CUT-OFF AT THE MAIN. THE EXPLOSION WAS INVESTIGATED BY AF&TAND ARSON DIVISION OF NEW | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1228 | 1991-03-01 | GA | other |  | ATLANTA GAS LIGHT CO | AT 1:46 PM. ON 3/1/91, ATLANTA GAS LIGHT'S SERVICE DISPATCH OFFICE NOTIFIED ATLANTA DISTRIBUTION DISPATCH OF AN EXPLOSION AT 1224 WESTMONT ROAD. UPON ARRIVING AT THE SCENE ATLANTA GAS LIGHT COMPANY WAS UNABLE TO COMPLETELY SURVEYTHE GAS FACILITIES DUE TO | 65000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1229 | 1991-03-25 | TX | other | DUPONT, ALDYL A | ENTEX - DIVISION OF ARKLA INC | A HOUSTON LIGHTING AND POWER COMPANY CONSTRUCTION CREW CUT A 3/4" PLASTIC NATURAL GAS SERVICE LINE WHILE INSTALLING AN ELECTRIC POWER POLE. AN ENTEX EMPLOYEE ATTEMPTING TO REPAIR THE LINE WAS OVERCOME BY GAS AND LOST CONSCIOUSNESS. THE EMPLOYEE WAS HOSP | 150 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1230 | 1991-04-03 | MD | other | UNKNOWN | BALTIMORE GAS & ELECTRIC CO | AT APPROXIMATELY 0715 ON APRIL 3, 1991, MR. HART LIT A KEROSINE HEATER. TO WARM HOUSE. HEATER CAUGHT FIRE AND DESTROYED UNFINISHED ADDITION TO HOUSE. DURING THE FIRE SOMETHING FELL ON METER AND INSTALLATION AND GAS SERVICE, SEVERING 3/8" PLASTIC SERVIC | 125000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1231 | 1991-05-17 | MA | other |  | FITCHBURG GAS & ELECTRIC LIGHT CO | CONTRACTOR HIT EXPOSED PIPE STUB. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1232 | 1991-05-07 | MN | ACCIDENTALLY CAUSED BY OPERATOR |  | NORTHERN STATES POWER CO | PART 3 (DESCRIPTION): A CONTRACT EMPLOYEE, WHILE ATTEMPTING TO RELIGHT AN OLD STYLE ("OCTOPUS TYPE") GRAVITY FURNACE, RECEIVED FIRST-DEGREE BURNS TO FACE AND SECOND-DEGREE BURNS TO ONE HAND. THE INJURED EMPLOYEE MISTAKENLY PRESSED THE MANUAL BUTTON WHIC | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1233 | 1991-04-24 | PA | other | UNKNOWN | PENNSYLVANIA GAS & WATER CO |  | 250000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1234 | 1991-04-11 | OR | other | UNKNOWN | NORTHWEST NATURAL GAS CO | PART 2A&B MARKING AND MONITORING IS ONGOING AND FREQUENT BY THE GAS COMPANYFOR THIS MAJOR SEWER PROJECT. THE SERVICE WAS EXPOSED SATISFACTORILY DURING EXCAVATION AND APPARENTLY WAS DAMAGED IN THE BACKFILL PROCESS. SEWER CONTRACTOR PULLED THE SERVICE TO | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1235 | 1991-03-30 | NY | other |  | CONSOLIDATED EDISON CO OF NEW YORK | GAS BLOWING FROM 1" CONTROL LINE FOR REGULATOR STATION. STRONG ODOR OF GASIN AREA. FIRE DEPARTMENT EVACUATES BUILDING AND CLOSES OFF COLUMBUS AVENUE TO TRAFFIC. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1236 | 1991-05-04 | AR | other | TEXTUBE | ARKANSAS LOUISIANA GAS CO (ARKLA GAS CO) | VERY HEAVY RAIN-FALL THIS YEAR CAUSED THE BAYOU TO REMAIN AT A HIGH LEVEL FOR A LONG TIME. HIGH WATER WASHED AWAY THE PIPE COVER AT THE BANK, LETTING THE PIPE MOVE AND CAUSING THE FAILURE. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1237 | 1991-05-03 | NM | other | UNKNOWN (SANTA FE COUNTY) | GAS CO OF NEW MEXICO |  | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1238 | 1991-05-20 | MA | other |  | BOSTON GAS CO | EMPLOYEE WAS THREADING SERVICE TEE INTO 4" C.I. MAIN WHEN GAS ESCAPIING FROMTAP HOLE IGNITED. EMPLOYEE EXITED OPENING WITH ASSISTANCE FROM CREW MEMBERS. HE WAS BURNED ON BOTH HIS ARMS AND FACE. FIRE WAS EXTINGUISHED APPROXIMATELY 5 MINUTES AFTER IGNITI | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1239 | 1991-05-08 | AR | other | PLEXCO | ARKANSAS LOUISIANA GAS CO (ARKLA GAS CO) | WE HAD JUST INSERTED THE 2" STEEL GAS MAIN WITH 1 1/4" PLASTIC PIPE. A 1/2"E11 HAD BEEN FUSED TO A SERVICE "T" ON THE MAIN TO TIE IN THE LAST SERVICE.THE SERVICE MEN WERE WAITING FOR THE LAST FUSION TO COOL, BEFORE TYING IN THE 1/2" PLASTIC SERVICE. THE | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1240 | 1991-05-21 | AK | other | PHILLIPS | ENSTAR NATURAL GAS CO | RESIDENTIAL STRUCTURE FIRE MELTED THE GAS METER AND REGULATOR. PRELIMINARY FIRE INVESTIGATION DETERMINED THE FIRE STARTED INSIDE THE STRUCTURE FROM A BURNING CIGARETTE IN THE CARPET OR FURNITURE. | 60000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1241 | 1991-05-30 | VA | other |  | WASHINGTON GAS LIGHT CO | SHORTLY BEFORE 1038 HOURS ON MAY 30, 1991, THE K&M ROAD BORING COMPANY STRUCK A 6" WRAPPED STEEL H.P. GAS MAIN PUSHING IT OUT OF A STRIPPED COMPRESSION COUPLING UNDERGROUND. WGL PERSONNEL RESPONDED AND FOUND ZERO PRESSURE READINGS DOWNSTREAM OF THE BREA | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1242 | 1991-05-14 | SD | other | DUPONT | NORTHWESTERN PUBLIC SERVICE CO |  | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1243 | 1991-05-19 | GA | other | DRESSER | ATLANTA GAS LIGHT CO | ON MAY 19, 1991, AT APPROXIMATELY 12:40 P.M., AN AIRPLANE DEPARTING FROM PEACHTREE DEKALB AIRPORT STRUCK AND SEVERED AN ELECTRICAL POWER LINE. THE ELECTRICITY FROM THE DOWNED POWER LINE APPARENTLY TRAVELED THROUGH THE GROUND AND ALONG THE SERVICE LINE OF | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1244 | 1991-05-08 | TN | ACCIDENTALLY CAUSED BY OPERATOR | CLOW & SONS | KNOXVILLE UTILITIES BOARD | KNOXVILLE UTILITIES BOARD BUREAU OF GAS CREW HAD REMOVED SECTION OF CAST IRONPIPE TO PLACE A DROP IN THE LINE TO ALLOW FOR CONSTRUCTION OF SEWER LINE. THE DROP WAS CONSTRUCTED AND LEAK TESTED ACCORDING TO ESTABLISHED PROCEDURES.WHILE CREW WAS WRAPPING ME | 25000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1245 | 1991-06-07 | NJ | other | UNKNOWN | NEW JERSEY NATURAL GAS CO | ON FRIDAY JUNE 7, 1991, SANITARY CONSTRUCTION COMPANY WAS INSTALLING AN 8" CAST IRON WATER MAIN ON SUNSET LANE AT CARLTON PLACE IN THE SOUTH MANTOLOKING BEACH SECTION OF BRICK TOWNSHIP. SOMETIME BEFORE 12:18 PM. THE CONTRACTOR STRUCK THE 3/4" SERVICE TO | 150000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1246 | 1991-05-16 | VA | maintenance | DRESSER | COMMONWEALTH GAS SERVICES INC | GAS COMING FROM A CORROSION LEAK IN THE BARREL OF A 4" BOLTED COUPLING CONNECTING THE RISER OF THE MEASUREMENT & REGULATION (M&R) SETTING TO A 4" PLASTICMAIN WAS IGNITED FROM AN UNDETERMINED SOURCE. THE RESULTING FIRE AT THE M&R STATION OUT SIDE A BRICK | 200000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1247 | 1991-05-19 | NY | ACCIDENTALLY CAUSED BY OPERATOR |  | CONSOLIDATED EDISON CO OF NEW YORK | WELDING SLAG FROM RECENTLY INSTALLED STEEL TRAFFIC PLATES OVER EXCAVATION DROPPED DOWN ON PLASTIC GAS MAIN BELOW AND GAS FIRE ENSUED. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1248 | 1991-06-10 | NJ | other |  | SOUTH JERSEY GAS CO | TWO, FIVE-GALLON FUEL CANS CONTAINING SOME TYPE OF LIQUID ACCELERANT WAS PLACED IN FRONT OF THE GAS STOVE WHICH HAD STANDING PILOT LIGHTS. THE VAPORS FROMTHE ACCELERANT GATHERED NEAR THE FLOOR AND, AFTER REACHING THE HEIGHT OF 11 INCHES, CAUSED AN EXPLOSI | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1249 | 1991-06-22 | MA | other |  | COMMONWEALTH GAS CO | THE DRIVER OF A MOTORCYCLE WAS FATALLY INJURED WHEN HIS VEHICLE LEFT THE TRAVELED WAY AND STRUCK AN OUTSIDE METER ASSEMBLY AT 25 SMITH PLACE, CAMBRIDGE, MASS. A 1 1/4" I.P. SERVICE WAS BROKEN FROM THE IMPACT. PERMANENT REPAIRS WERE MADE TO THE PIPING AT | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1250 | 1991-06-24 | NV | other | R.W. LYALL & CO. | SOUTHWEST GAS CORP | SERVICE RISER WAS BROKEN OFF IN THREADS AT STOP COCK WHILE ATTEMPTING TO LOOSEN METER CONNECTION. | 80000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1251 | 1991-06-27 | TN | other |  | GALLAWAY GAS DEPT, CITY OF | WHILE MAKING REPAIRS TO AN EXISTING FIRE HYDRANT, MEMPHIS LIGHT GAS & WATER -- WATER MAINTENANCE CREW, CUT THE 4" POLY GAS MAIN ON MILLINGTON-ARLINGTON ROAD APPROXIMATELY 3 MILES NORTH OF ARLINGTON, TN. THE ABOVE CREW DID NOT REQUEST INFORMATION REGARDIN | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1252 | 1991-06-18 | AZ | other | UNKNOWN | SOUTHWEST GAS CORP | LEONARD WAHLQUIST, FOREMAN FOR AMERICAN UNDERGROUND CONSTRUCTION, WAS BORINGWITH A 2' AUGER, WHILE PUSHING A 30" CASING, WHEN HE HIT OUR 4" DISTRIBUTON GAS MAIN | 6500 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1253 | 1991-06-19 | IL | ACCIDENTALLY CAUSED BY OPERATOR |  | NORTHERN ILLINOIS GAS CO | ACCIDENT WAS CAUSED BY A MISUNDERSTANDING BETWEEN A NI-GAS SUB-CONTRACTOR'S SUPERVISOR AND LABORER. A PURGE PROCEDURE FOR A PIPE CONTAINING A GAS/AIR MISTURE WAS STARTED BEFORE A HOT WRAPPING OPERATION WAS COMPLETED. THE RESULTING FLASH FIRE CAUSED FIRS | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1254 | 1991-07-15 | NE | technical failure |  | METROPOLITAN UTILITIES DISTRICT | NEW MAIN INSTALLED AND WAS BEING CONNECTED TO EXISTING MAIN W/CLOSURE PIECE WHICH WAS ISOLATED FROM NEW AND EXISTING MAINS BY "BAG-OFF". CLOSURE PIECE WAS BEING PURGED. OPERATOR'S EMPLOYEE HAD FILLED "BURN BAG" FROM VENT ON PURGE CONNCECTION AND ATTEMPT | 1000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1255 | 1991-04-28 | MN | other |  | NORTHERN STATES POWER CO | PART 1 (#5 ELAPSED TIME) - SOMETIME AFTER THE WATER MAIN BROKE AT AROUND 3:00 AM. THE LOW PRESSURE GAS MAIN FILLED WITH WATER, CUTTING OFF THE FLOW OF GAS. FIRST MADE AWARE THAT THERE WAS A PROBLEM WHEN NOTIFIED AT 6:09 AM. BY A CUSTOMER "NO GAS" CALL.PA | 56000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1256 | 1991-06-18 | IN | other |  | INDIANA GAS CO INC | RESIDENT MOVING SINK BROKE OFF FUEL LINE TO RANGE, CAUSING GAS LEAK; RESIDENT OVERCOME BY FUMES, TREATED AND RELEASED. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1257 | 1991-07-17 | LA | other |  | GULF STATES UTILITIES CO | FOLLOWING A SAFETY CHECK ON HOUSEPIPING AND APPLIANCES, OUR SERVICEMAN TURNED THE GAS ON AND CHECK FOR LEAKAGE USING THE GAS METER TEST DIAL. NO LEAKAGEFOUND. SERVICEMAN LIT THE STOVE AND WATER HEATER AND LEFT SITE OK. APPROXIMATELY TWO (2) HOURS LATER | 5000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1258 | 1991-06-17 | TX | other |  | BRAZOS RIVER GAS CO |  | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1259 | 1991-07-21 | NY | other |  | CONSOLIDATED EDISON CO OF NEW YORK | CONTRACTOR UNDER CONTRACT TO CON EDISON DAMAGED 1 1/4 INCH PLASTIC HIHG PRESSURE SERVICE. NEWS MEDIA WAS PRESENT. THIS INCIDENT IS NOT REPORTABLE. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1260 | 1991-08-05 | MN | maintenance |  | CENEX LIQUID PETROLEUM GAS PLANT | EXPLOSION AND SMALL FIRE IN BASEMENT OF UPTOWN MEATS. VICTIM WAS TRAPPED AND CAUGHT UNDER DEBRIS IN BASEMENT. EXPLOSION WAS BELIEVED TO BE CAUSED BY LEAKING PROPANE GAS FROM OUR SERVICE LINE LOCATED OUTSIDE THE BUILDING. THIS WAS DETERMINED BY THE MN S | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1261 | 1991-07-16 | IL | technical failure | UNKNOWN | CENTRAL ILLINOIS LIGHT CO | WHILE REPAIRING A GRADE 2 LEAK, A BURIED MECHANICAL JOINT FAILED, ALLOWING A 6" C.I. MAIN TO BECOM DISCONNECTED FROM THE COMPRESSION FITTING. | 10000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1262 | 1991-07-24 | AR | other | UNKNOWN | ARKANSAS LOUISIANA GAS CO (ARKLA GAS CO) | AN ASPHALT STRIPPING MACHINE REMOVING THREE INCHES OF ASPHALT STRUCK A 4" CAST IRON GAS MAIN, RUPTURING THE MAIN. THE ESCAPING NATURAL GAS IGNITED, DESTROYING THE ASPHALT REMOVING EQUIPMENT. | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1263 | 1991-07-23 | CO | other | UNKNOWN | PUBLIC SERVICE CO OF COLORADO | WHILE THE CREW WAS COMPLETING THE FINAL TIE-IN BAG HOLE (3 BAG STOPS REQUIRED), THE GAS IGNITED FROM AN UNKNOWN SOURCE. THE IGNITION TOOK PLACE AS THE FINAL BAG WAS BEING REMOVED. FOUR PEOPLE (1 GAS COMPANY, 3 CONTRACTOR MEMBERS) WERE TREATED AND RELEAS | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1264 | 1991-07-05 | OK | other | FISHER | OKLAHOMA NATURAL GAS CO | THIRD PARTY HAD BEEN PERFORMING LANDSCAPE SERVICE SODDING YARD. NO MATERIALDEFECT WAS APPARENT. HOWEVER, THE REGULATORY HAS NOT BEEN DISASSEMBLED PENDING AND INVESTIGATION BY NTSB. REGULATOR VENT PORT WAS PLUGGED WITH DIRT. RESIDENTIAL FIRE RESULTED W | 400000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1265 | 1991-07-25 | AZ | technical failure | DUPONT | SOUTHWEST GAS CORP | ON JULY 25, 1991, AT APPROXIMATELY 1750 HOURS, A SOUTHWEST GAS CUSTOMER SERVICE SUPERVISOR HEARD A NEWS REPORT OF AN EXPLOSION AND FIRE IN THE 5000 BLOCKOF NORTH FIRST AVENUE ON HIS F.M. RADIO. THE SUPERVISOR REPORTED THIS TO HIS HAS DISPATCHER AND PROCE | 200000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1266 | 1991-07-07 | NY | other |  | CONSOLIDATED EDISON CO OF NEW YORK | IT WOULD APPEAR THAT AN EXPLOSION CAUSED THE COLLAPSE OF A BUILDING. ALTHOUGH THE INCIDENT IS STILL UNDER INVESTIGATION, GAS DOES NOT APPEAR TO HAVE BEEN INVOLVED. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1267 | 1991-07-30 | TX | other | UNKNOWN | LONE STAR GAS CO | CREW WAS REPAIRING LEAK ON RISER AND THE GAS WAS IGNITED AND BURNED APARTMENT BUILDING. | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1268 | 1990-11-12 | KS | maintenance | UNKNOWN (MONTGOMERY COUNTY) | UNITED CITIES GAS CO |  | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1269 | 1991-01-15 | KS | other | UNKNOWN (JOHNSON COUNTY) | UNITED CITIES GAS CO |  | 80000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1270 | 1991-08-05 | FL | other | POLYETHYLENE PRODUCTS, INC. | CLEARWATER GAS DIV, CITY OF | APPROXIMATELY 9:40 AM, AN EMPLOYEE (MIKE RITTER) OF VISK CONSTRUCTION RUPTURED A NATURAL GAS MAIN, WHILE USING A POWER DITCH DIGGER. THE RUPTURED GAS MAIN CAUGHT FIRE AND BURNED THE EMPLOYEE RIDING THE DITCHER. CLEARWATER FIRE DEPARTMENT RESPONDED TO TH | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1271 | 1991-08-16 | TX | other |  | IRAAN UTILITY SYSTEMS, CITY OF |  | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1272 | 1991-08-22 | VA | other |  | VIRGINIA NATURAL GAS | AUGER STRUCK GAS PIPELINE WHILE INSTALLING SOUND BARRIERS ALONG INTERSTATE. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1273 | 1991-08-22 | MO | other | UNKNOWN (JACKSON COUNTY) | K P L GAS SERVICE | VEHICLE WENT OUT OF CONTROL - HIT GAS LINE AND HOUSE, IGNITING GAS. DAMAGE TO CAR AND HOUSE. HOUSE SET 45' FROM STREET. | 63000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1274 | 1991-08-14 | MO | other | AMERICAN | K P L GAS SERVICE | A FIRE, OF UNKNOWN ORIGIN, AT THIS RESIDENCE, DAMAGED THE GAS METER ASSEMBLY, RESULTING IN THE IGNITION OF GAS. | 250000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1275 | 1991-09-24 | LA | other |  | GULF STATES UTILITIES CO | VEHICLE HIT METER SET BREAKING RISER BELOW VALVE. | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1276 | 1991-09-19 | LA | other |  | GULF STATES UTILITIES CO | CONTRACTOR CUTTING A CONCRETE STREET CUT THE TOP OF A 4" STEEL LINE. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1277 | 1991-08-31 | MA | other |  | BERKSHIRE GAS CO | TESTING OF THE SERVICE LINE, METERS AND COMPANY INSTALLED PIPING FROM THE METER TO THE CUSTOMER OWNED PIPING HAS SHOWN THAT THESE WERE NOT FACTORS IN THIS INCIDENT. THE STATE FIRE MARSHALL HAS NOT YET CONCLUDED HIS INVESTIGATION AS TO THE FUEL OR THE IGN | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1278 | 1991-07-16 | TX | maintenance |  | ENERGAS CO | A CALL WAS RECEIVED AT THE SERVICE CENTER AT APPROXIMATELY 9:40 AM ON TUESDAY, JULY 16TH, REPORTING AND EXPLOSION IN THE VICINITY OF 34TH STREET AND SOUTH MONROE. CHARLES WALLER, SERVICEMAN, WAS DISPATCHED TO THE SCENE. WHEN HE ARRIVED ATH THE SCENE, HE | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1279 | 1991-09-01 | CA | other |  | PACIFIC GAS & ELECTRIC CO | CUSTOMER TAMPERED WITH AND DAMAGED SERVICE VALVE, ALLOWING GAS TO ESCAPE, ENTER THE HOUSE, EXPLODE AND IGNITE FROM UNKNOWN SOURCE OF IGNITION. | 160350 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1280 | 1991-08-29 | MO | other | KRALOY/CHEM & ROL | MADISON GAS DEPT, CITY OF |  | 45000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1281 | 1991-01-21 | TX | other | UNKNOWN | LONE STAR GAS CO |  | 6000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1282 | 1991-09-24 | MA | other |  | BOSTON GAS CO | BOSTON GAS COMPANY RESPONDED TO A REPORT OF SERVICE ON FIRE IN BASEMENT. UPON ARRIVAL, A BOSTON GAS EMPLOYEE NOTICED A FLAME ABOVE THE PIPE AND SHUT OFFA 4" WHEEL VALVE AND EXTINGUISHED THE FLAME. THE CALL WAS MADE BY A WELDER DOING RENOVATION WORK IN T | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1283 | 1991-04-07 | TX | other |  | SOUTHERN UNION GAS CO | CAR RUN OVER THE METER. | 2000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1284 | 1991-03-12 | TX | other | DOMESTIC ORIGIN | GREY FOREST UTILITIES |  | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1285 | 1991-03-11 | TX | ACCIDENTALLY CAUSED BY OPERATOR | DOMESTIC ORIGIN | GREY FOREST UTILITIES | GREY FOREST UTILITIES EMPLOYES VASSAR JONES & KEITH SCHNEIDER HAD DRILLED HOLES THROUGH PAVEMENT AND WERE PROBING TO PINPOINT AN UNDERGROUND LEAK. WHEN THE PROBE BAR CAME IN CONTACT WITH THE STEEL MAIN, THEY PRESUMED THEY WERE IN CONTACT WITH A ROCK. THE | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1286 | 1991-03-07 | TX | other |  | SOUTHERN UNION GAS CO | THIS LINE WAS DAMAGED BY CONTRACTORS EXCAVATING IN A LOCATION AHEAD OF SCHEDULE. OUR REPRESENTATIVES HAD MET WITH EXCAVATOR ON NUMEROUS OCCASIONS AND "EXPOSED" GAS FACILITIES ACCORDING TO A SCHEDULE AGREED TO BY SUG AND EXCAVATOR. | 1000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1287 | 1991-03-06 | TX | other |  | LONE STAR GAS CO | HIGH PRESSURE MAIN WAS HIT BY SUB CONTRACTOR FOR TP L WHILE BORING HOLE. E | 12000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1288 | 1991-03-06 | TX | technical failure |  | ENTEX - DIVISION OF ARKLA INC | OPERATOR'S CONTRACTOR HAD PLUGGED AN EXTENSION FITTING AND WAS PREPARING TO WELD WHEN PLUG FAILED. ESCAPING GAS IGNITED. STREET WAS BLOCKED. E | 1365 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1289 | 1991-01-20 | TX | other |  | SOUTHERN UNION GAS CO | AUTOMOBILE STRCUK UTILITY POLE ABOVE GROUND CAUSING DAMAGE BELOW GROUND TO OPERATORS FACILITY. | 7340 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1290 | 1991-10-01 | NY | other |  | BROOKLYN UNION GAS CO | ON OCTOBER 1, 1991, A N.Y.C. CONTRACTOR EMPLOYEE WAS INJURED WHILE WORKINGIN A SEWER MANHOLE ON PERKIOMEN AVENUE BETWEEN WAINWRIGHT AVE AND DEAD END.A BROOKLYN UNION CHEMIST CONFIRMED THE PRESENCE OF NATURAL GAS IN THE SEWER MANHOLE. THE SOURCE OF NATURA | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1291 | 1991-09-29 | NY | maintenance |  | NATIONAL FUEL GAS DISTRIBUTION CORP - NEW YORK | EMPLOYEES ATTEMPTING TO BAND CLAMP 7/8" X 1 5/8" CORROSION LEAK. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1292 | 1991-07-17 | MI | technical failure | DRESSER | CONSUMERS POWER CO | INACCURATE RECORDS. FACILITY RECORDS DID NOT SHOW IN-LINE COMPRESSIONFITTING ADJACENT TO PIPE SEGMENT BEING REPLACED. FITTING PULLED OUT WHEN PIPEWAS SEVERED DOWNSTREAM OF FITTING. SUPPLEMENTAL REPORT 3/10/95 INDICATESCHANGE IN PART 2 TO "C" - FROM OTHER | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1293 | 1991-10-08 | MS | other |  | ENTEX INC |  | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1294 | 1991-09-25 | GA | other |  | DALTON WATER LIGHT & SINKING FUND COMMISSION | SERVICE COMPANY PERSONNEL WERE WORKING ON HEAT UNITS. CAUSE STILL UNDER INVESTIGATION. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1295 | 1991-09-30 | WA | other |  | WASHINGTON NATURAL GAS CO | TWO CITY UNTILITY WORKERS WERE BURNED WHEN THEIR ACTIVITIES INSIDE A POWER VAULT IGNITED NATURAL GAS THAT HAD ACCUMULATED IN THE VAULT. THERE ARE NO GASFACILITIES IN THE VAULT. THE GAS SOURCE IS POSSIBLY A CRACKED 6" CAST IRON LOW PRESSURE GAS MAIN FOUN | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1296 | 1991-09-12 | CA | other |  | PACIFIC GAS & ELECTRIC CO | STRUCTURE FIRE DAMAGED METER AND REGULATOR | 75200 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1297 | 1991-09-18 | IL | ACCIDENTALLY CAUSED BY OPERATOR |  | UNITED CITIES GAS CO | REMOVING ORFICE PLATE FROM PIPE & BLOWING TRASH OUT OF 4" NATURAL GAS PIPE WITH NATURAL GAS PRESSURE - GAS IGNITED FROM PILOT LIGHT ON THE WATER BATH HEATER. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1298 | 1991-10-11 | CA | other |  | PACIFIC GAS & ELECTRIC CO | BRUSH FIRE GOT OUT OF CONTROL IN HILLS EAST OF OAKLAND AND BERKELEY. BRUSH FIRE LEAD TO BURNING OF APPROXIMATELY 4,000 DWELLING UNITS, DESTROYING OVER 2000 GAS SERVICES AND OVER 3000 GAS METERS, | 15000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1299 | 1991-10-22 | VA | technical failure | MUELLER | COMMONWEALTH GAS SERVICES INC | COMPANY PERSONNEL, WHILE IN THE PROCESS OF PLACING APPROXIMATE 700' OF RELOCATED 6" WELDED TREATED MAIN IN-SERVICE, INSTALLED A LINE STOPPER AT THE UNSTREAM TIE-IN BEFORE THE DOWNSTREAM FITTING WAS TAPPED. THE RESULTING EFFECT WAS LOSS OF SERVICE TO APPR | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1300 | 1991-10-09 | AL | other |  | JACKSONVILLE WATER WORK, GAS & SEWER BOARD | ABOUT 5 OR MIN TO NOON, WED 18-9-91, I GOT A CALL ON THE RADIO TO GO TO 711 E FRANCIS ST. SOMEONE WAS CUTTING A TREE AND BROKE THE GAS LINE. I WAS TOLD THIS ON THE RADIO BEFOR I WENT OVER THERE. I GOT OVER THERE AND I SAW THE ONE INCH SERVICE LINE WAS B | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1301 | 1991-10-03 | NY | technical failure |  | CONSOLIDATED EDISON CO OF NEW YORK | A CONTRACTOR DAMAGED A ONE-INCH MEDIUM PRESSURE GAS SERVICE. MEDIA WERE PRESENT. THERE WERE NO FATALITIES, INJURIES, OR PROPERTY DAMAGE. THIS INCIDENTSHOULD BE REMOVED FROM THE LIST OF INCIDENTS. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1302 | 1991-10-07 | MI | other |  | MICHIGAN CONSOLIDATED GAS CO (MICHCON) | CONTRACTOR FAILED TO CALL MISS DIG, STRUCK AND PULLED SERVICE LINE OUT OF COMPRESSION FITTING BELOW GRADE. | 125000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1303 | 1991-10-08 | NJ | other | UNKNOWN (BERGEN COUNTY) | PUBLIC SERVICE ELECTRIC & GAS CO | ON TUESDAY 10/8/91 AT APPROXIMATELY 2:40 P.M., WHILE PROCEEDING TO UPRATE A 120 PSI DESIGN GAS MAIN FROM 100 PSI TO 120PSI, MULTIPLE FAILURES OCCURED IN THE AREA OF THE METER SET AT THE GARDEN STATE PAPER CO., #141 LANZA AVE., GARFIELD. THE ESCAPING GAS | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1304 | 1991-05-09 | TX | other | DUPONT | ENTEX - DIVISION OF ARKLA INC | LINE WAS MARKED FOR PRIME CABLE THE PREVIOUS WEEK. COASTAL CONDUIT DID NOT REQUEST. HAS CUT 2" MAIN - AIR COMPRESSOR 6' FROM CUT - GAS IGNIGHTED. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1305 | 1991-05-16 | TX | other | DUPONT "AA" | ENTEX - DIVISION OF ARKLA INC | WE RECEIVED CALL FROM BRUCE SMITH OF PERRY HOMES AT 9:07 A.M. REPORTING CUT LINE AND FIRE, WE DISPATCHED TO SERVICEMAN & CONSTRUCTION CREW AT 9:07 A.M.WE ARRIVED ON SCENE AT 9:15 A.M. LINE WAS SQUEEZED AT 9:45 A.M. LINE WAS CUT BY PAUL BATES WITH E&M P | 25000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1306 | 1991-05-24 | TX | other | UNKNOWN (DALLAS COUNTY) | LONE STAR GAS CO | RUSHING AND RISING WATER IN FIVE MILE CREEK WASHED OUT AND BROKE 4" LP WRAPPED STEEL MAIN. | 9000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1307 | 1991-05-30 | TX | other | DUPONT | ENTEX - DIVISION OF ARKLA INC | CONTRACTOR BROKE PLASTIC MAIN WHILE INSTALLING DRAINAGE SYSTEM. TRAFFIC WASREROUTED UNTIL AREA WAS MADE SAFE. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1308 | 1991-06-12 | TX | other | DUPONT | ENTEX - DIVISION OF ARKLA INC | PIPE WAS INCORRECTLY LOCATED. CONTRACTOR CUT PLASTIC MAON WITH A CORING AUGUR. FIRE DEPARTMENT EVACUATED NEARBY APARTMENT COMPLEX UNTIL AREA WAS MADE SAFE. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1309 | 1991-06-15 | TX | other | UNKNOWN (TRAVIS COUNTY) | SOUTHERN UNION GAS CO | WHILE EXCAVATING WITH KOMATSU D355A DOZER FOR COMMERCIAL DRIVEWAY APPROACH, CONTRACTOR PULLED 4" WS MAIN APART WITH RIPPER BLADE. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1310 | 1991-06-20 | TX | other | DUPONT | ENTEX - DIVISION OF ARKLA INC | TRAFFIC MAINTENANCE CUT 4", TRAFFIC RE-ROUTED AND POLICE DEPARTMENT EVACUATEDAN OFFICE BUILDING. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1311 | 1991-06-23 | TX | other |  | ENERGAS CO | AUTOMOBILE WAS STOLEN BY UNKNOWN PARTY. OUR NOTIFICATION WAS BY THE MIDLANDPOLICE DEPARTMENT. DRIVER OF VEHICLE FLED SCENE AFTER ACCIDENT. DRIVER L;OST CONTROL OF VEHICLE AND RAN INTO METER SETTING. SUBSEQUENT FIRE DESTROYED CAR AND METER SETTING. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1312 | 1991-06-28 | TX | other |  | SAN ANTONIO,CITY PUBLIC SERVICE BOARD OF |  | 30372 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1313 | 1991-07-03 | TX | other | PLEXCO | SOUTHERN UNION GAS CO | POLYETHYLENE YARDLINE DID HAVE WARNING TAPE IN DITCH. PLUMBER WORKING ON SPRINKLER SYSTEM DAMAGED SERVICE AND IGNITED GAS. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1314 | 1991-07-13 | TX | other |  | SOUTHERN UNION GAS CO | BACKHOE POERATOR DAMAGE THE GAS SERVICE LINE. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1315 | 1991-07-23 | TX | other |  | LONE STAR GAS CO | MRS. COOPER BACKED INTO OUR METER AND REGULATOR PULLING THE REGULATOR FROM THE BASE. | 10000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1316 | 1991-07-23 | TX | other | UNKNOWN (TRAVIS COUNTY) | SOUTHERN UNION GAS CO | LOCATIONS PROVIDED 5/23/91 AND JOB MONITORED PERIODICALLY. WHILE TRENCHING TO INSTALL TELEPHONE CABLE, CONTRACTOR CUT 1 1/4" GAS SERVICE. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1317 | 1991-07-25 | TX | other |  | ENTEX - DIVISION OF ARKLA INC | PAVING CONTRACTOR CUT STEEL MAIN WHILE EXCAVATING. NO IGNITION | 30794 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1318 | 1991-08-01 | TX | other |  | ENTEX - DIVISION OF ARKLA INC | CITY WATER CO. KNOCKED TAP OFF A 16" MAIN. 4500 GRIGGS BLOCKED BOTH DIRECTIONS. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1319 | 1991-08-13 | TX | technical failure |  | BRACKETTVILLE, CITY OF, HOUSING AUTH OF | AT APPROXIMATLY 9:35 A.M. MR. JAY HAM, SUPERINTENDENT OF THE RIEMER CALHOUN,JR'S NEW SENOIR CITIZENS PROJECT CAME INTO MY OFFICE AND INFORMED ME THAT C.P.L. HAD DRILLED INTO THE MAIN DISTRIBUTION LINE COMING INTO BRACKETTVILLE FRLOM THE VALERO SUB-STATION | 1828 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1320 | 1991-08-21 | TX | other |  | ENTEX - DIVISION OF ARKLA INC | CAR HIT GAS METER - ESCAPING GAS INGNITED - DAMAGE TO METER ABD REGULATOR, CAR AND BUILDING. | 25000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1321 | 1991-08-22 | TX | technical failure |  | ROMA GAS DEPT, CITY OF | MOVEMENT OF DIRT BY PREVIOUS CONSTRUCTION IN VICINITY OF GAS MAIN. WATER LINE WAS INSTALLED NEXT TO GAS MAIN, A BORE ACROSS HIGHWAY 83 WAS DONE, AT THIS POINT WAS WHERE THE EARTH SETTLE AND BROKE GAS MAIN. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1322 | 1991-08-30 | TX | other |  | BRAZOS RIVER GAS CO | UNKNOWN AUTOMOBILE RAN THROUGH BARRACADE DESTROYING AN INTERMEDIATE PRESSURETO LOW PRESSURE REGULATOR STATION. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1323 | 1991-09-16 | TX | other |  | SOUTHERN UNION GAS CO | 4" CAST IRON MAIN CRACKED UNDER ROADWAY. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1324 | 1991-09-23 | TX | other | DUPONT | ENTEX - DIVISION OF ARKLA INC | OUTSIDE CONTRACTOR CUT 2" PLASTIC MAIN RESULTING IN THE LOSS OF 72 ACTIVE SERVICES. MARKED LINES ON 8-1-91, CHECKED ON 8-2-91-STILL MARKED. RE-MARKED LINES ON 8-6-91, CHECKED ON 8-8-91 - STILL MARKED. | 1404 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1325 | 1991-09-24 | TX | other |  | ENERGAS CO |  | 15000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1326 | 1991-10-04 | TX | other |  | ENTEX - DIVISION OF ARKLA INC | CAR HIT GAS METER, ESCAPING GAS INITED, DAMAGE TO CAR, GAS METER & REGULATOR. | 16150 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1327 | 1991-05-05 | TX | other | SINGER | GULFSIDE GAS CO | RECIEVED CALL @ 6:30 AM 5-5-91 FROM BEXAR CO. FIRE ALARM I.E. VEHICLE ON FIRE @ 10305 MAIN ST MACDONA RX. ARRIVED 7:10 AM. AFTER A BRIEF INSPECTION OF SITUATION, IT WAS DETREMINED BEST COURSE OF ACTION WAS TO TURN GAS OFF@ MACDONA REGULATOR STATION. THE | 3745 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1328 | 1991-05-03 | TX | other | DUPONT | ENTEX - DIVISION OF ARKLA INC | A WORKER FOR C-JO WAS OPERATING A DITCHING MACHINE AND CUT A 3/4" SERVICE LINE. THE GAS IGNITED CAUSING IT TO BURN THE DITCHING MACHINE AND A COUPLE OF HUSHES IN THE YARD. | 10000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1329 | 1991-04-26 | TX | other |  | SOUTHERN UNION GAS CO | CONTRACTOR DEMOLISHING A STRUCTURE AT 505 S. KANSAS CAUSED A WALL TO COLLAPSE. THE WEIGHT OF THE DEBRIS FALLING ON A 1 1/4" GAS RISER RESULTED IN THE FAILURE OF THE ELL ON THE BOTTOM OF THE RISER. | 1500 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1330 | 1991-04-24 | TX | other | DUPONT | ENTEX - DIVISION OF ARKLA INC | CONTACTOR TOLD OPERATOR THAT HE WOULD NOT BE WORKING NEAR THIS MAIN AND WOULD NOT NEED IT MARKED UNTIL LATER IN THE WEEK, THEN HE HIT IT. | 5350 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1331 | 1991-04-12 | TX | other |  | ENERGAS CO | A COMPANY CREW WAS REMOVING AN OLD CLAMP-ON SERVICE SADDLE TAP ON A LOW PRESSURE (APPROXIMATLEY 0.5 PSI) MAIN. THE SADDLE HAD BEEN REMOVED AND A TEMPORARY CLAMP HAD BEEN INSTALLED. THE OPERATOR IN THE EXCAVATION WAS CLEANING THEMAIN WITH AN ELECTRIC GRI | 200 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1332 | 1991-10-26 | IN | other |  | NORTHERN INDIANA PUBLIC SERVICE CO |  | 80000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1333 | 1991-10-29 | AR | maintenance |  | ARKANSAS LOUISIANA GAS CO (ARKLA GAS CO) | A HOLE WAS DISCOVERED IN THE 2" CAST IRON MAIN APPROXIMATELY 93' AWAY FROM THE HOUSE. THE MAIN WAS ON THE STREET FROM THE HOUSE. THE INVESTIGATION IS STILL ON GOING TO DETERMINE IF NATURAL GAS MIGRATED ACROSS THE STREET AND YARDTO TYHE HOUSE. | 75000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1334 | 1991-11-21 | WY | other |  | PETROLANE WYOMING GAS SERVICE |  | 16000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1335 | 1991-11-01 | AL | technical failure | PLEXCO | MOBILE GAS SERVICE CORP | WHILE PURGING AIR FROM APPROXIMATLEY 300' OF NEW 4" PLASTIC GAS MAIN WITH GAS, AN IGNITION OCCURRED WHICH LASTED LESS THAN 30 SECOUNDS. AS A RESULT OF THE IGNITION, THREE EMPLOYEES WERE BURNED. THE COMPANY'S OPERATIONS AND MAINTENANCE MANUAL CONTAINS SP | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1336 | 1991-10-28 | TX | other |  | LONE STAR GAS CO | FIRE AND APPARENT EXPLOSION OCCURRED AT RESIDENCE. HEAVY RAIN AND LIGHTNINGWAS OCCURRING AT TIME OF INCIDENT. HOME WAS TOTALLY DESTROYED, GARAGE AND AUTOMOBILES WERE DAMAGED. TWO PERSONS WERE INJURED WITH FIRST AND SECOND DEGREE BURNS. INITIAL LEAK TE | 125000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1337 | 1991-11-09 | MI | other |  | MICHIGAN CONSOLIDATED GAS CO (MICHCON) | WHILE MAKING AN INSPECTION OF AN ORIFICE FITTING, EMPLOYES INADVERTENTLY OPENED AN INTERNAL VALVE IN THE ORIFICE FITTING CAUSING A RELEASE OF GAS. | 300000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1338 | 1991-11-25 | LA | other |  | LOUISIANA GAS SERVICE CO | A DENT IN THE PIPE WAS SUSTAINED IN THE SUMMER OF 1991 AND CAUSED A CRACK INTHE PIPE ON 11-25-91. DAMAGE WAS DONE BY AN OUTSIDE PARTY DIGGING WITH A BACK HOE. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1339 | 1991-11-20 | MS | other |  | MISSISSIPPI VALLEY GAS | ON NOVEMBER 20, 1991 AT APPROXIMATELY 4:30 A.M. C.S.T., TORNADO STRUCK THE TOWN OF BROOKSVILLE. MISSISSIPI AND DESTROYED OR HEAVILY DAMAGED APPROXIMATELY30 BUILDINGS. MISSISSIPPI VALLEY GAS HAS A RESIDENT MANAGE IN THE AREA AND HE IMMEDIATELY TURNED OFF | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1340 | 1991-11-22 | TX | other |  | SOUTHERN UNION GAS CO | ALL DUE TO THE WATER LEAKING FROM THE KITCHEN SINK ONTO A 1/2" GASLINE THAT EVIDENTLY CAUSED THE PIPE TO CORRODE TO THE POINT WHERE A GAS LEAK DEVELOPED UNDER THE CRAWL SPACE OF THE BUILDING. THE PILOT LIGHT ON THE WATER HEATER IN THE KITCHEN MOST LIKELY | 55000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1341 | 1991-10-20 | NY | other |  | CONSOLIDATED EDISON CO OF NEW YORK | NATURAL GAS WAS NOT INVOLVED. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1342 | 1991-11-14 | LA | other | PLEXCO | ARKANSAS LOUISIANA GAS CO (ARKLA GAS CO) | ARKLA'S AGENT WAS IN THE PROCESS OF TAPING OUT AN 8" X 3/4" TAP TEE. THE CONTRACTOR HAD TROUGLE WITH THE CUTTER IN THE 8" X 3/4" TAP TEE BECAUSE IT WOULD NOT PENETRATE THE 8" PLASTIC MAIN. THEY, THEN, ATTEMPTED TO DRILL THE TAP HOLE OUT IN ORDER TO REMO | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1343 | 1991-12-06 | WA | other |  | WASHINGTON NATURAL GAS CO | EXPLOSION AND RESULTING FIRE DESTROYED RESIDENTIAL TRIPLEX, INJURED TWO OCCUPANTS OF ONE UNIT. SUSPECTED SOURCE OF NATURAL GAS IS A 3/4" STEEL SERVICE BROKEN AT THE MAIN IN THE ALLEY BEHIND 802 N PEARL ST. THE BREAK APPARENTLY OCCURRED DUE TO POOR COMPA | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1344 | 1991-12-02 | MA | other |  | BOSTON GAS CO | G IN BURNS TO ONE EMPLOYEE'S FACE AND BURNS TO A SECOND EMPLOYEE'S FACE AND WRIST. THE TRENCH WAS IN CLOSE PROXIMITY TO AN ELECTRIC COMPANY DUCT LINE, CONTAINING BARE WIRES. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1345 | 1991-11-27 | CO | other |  | COLORADO SPRINGS, CITY OF | A RESIDENCE AND ITS CONTENTS WERE DESTROYED BY AN EXPLOSION AND FIRE RESULTING IN MINOR INJURIES TO TWO ELDERLY OCCUPANTS. THE APPARENT CAUSE OF THE ACCIDENT WAS GAS LEAKING FROM A METALLURGICAK FRACTURE IN A 1-1/4" STEEL GAS SERVICE. THE SERVICE LINE W | 73000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1346 | 1991-11-16 | PA | maintenance |  | COLUMBIA GAS OF PENNSYLVANIA | INITIAL INFORMATION SUGGESTED A RESIDENT AT REFERENCED ADDRESS WAS OVERCOME BY NATURAL GAS. INVESTIGATION REVEALED THAT THERE WAS A SMALL LEAK ON THE CUSTOMER'S HOUSE LINE PIPING AND A SOMEWHAT LARGER LEAK ON CUSTOMER'S SERVICE LINE. RESIDENT, WHO WAS H | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1347 | 1991-11-25 | MO | other |  | K P L GAS SERVICE | AN APPARENT IGNITION OF GAS WHICH OCCURRED AT 3704 E. 72ND STREET MAY HAVE RESULTED FROM A CRACK DISCOVERED ON A 6" CAST IRON MAIN IN THIS VICINITY. THECAUSE OF THE BREAK IS UNDETERMINED AT THIS TIME. GAS POSSIBLY INFILTRATED THROUGH A CLAY TILE SEWER I | 35000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1348 | 1991-12-03 | OH | other |  | COLUMBIA GAS OF OHIO INC | EXPLOSION & FIRE TOTALLY DESTROYED INSIDE FAMILY RESIDENCE (NO INJURIES ORFATALITIES). AN INSTRUMENT LEAK SURVEY OF THE SURROUNNDING AREA DID NOT REVEAL ANY LEAKAGE ON MAIN OR COMPANY SERVICE LINES. A FOLLOW-UP PRESSURE DROP TEST ON THE CUSTOMER SERVICE | 75000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1349 | 1991-12-07 | PA | other |  | PHILADELPHIA ELECTRIC CO |  | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1350 | 1991-12-27 | MA | other | GLENWOOD | COMMONWEALTH GAS CO |  | 70000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1351 | 1991-12-08 | CA | other |  | PACIFIC GAS & ELECTRIC CO |  | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1352 | 1991-12-20 | TX | other | NIPAK | LONE STAR GAS CO |  | 75000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1353 | 1991-12-01 | MA | other |  | BOSTON GAS CO |  | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1354 | 1991-12-28 | CA | other | AMP | PACIFIC GAS & ELECTRIC CO | LOCATION WAS FIRST MARKED ON APRIL 22, 1991. MARKS WERE VERIFIED/RENEWED ATTWO WEEK INTERVALS FROM 4/22 TO 10/14/1991. AT APPROXIMATELY 0426 HOURS ONSAT., DECEMBER 28, 1991, A FIRE BROKE OUT IN AN EIGHT UNIT APARTMENT COMPLEXLOCATED AT 631 SPENCER STREET | 500000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1355 | 1991-12-20 | LA | other |  | LOUISIANA GAS SERVICE CO | CAR LEFT HIGHWAY HITTING 1 INCH STEEL RISER. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1356 | 1991-12-20 | LA | other | PLEXCO | LOUISIANA GAS SERVICE CO | HWY DEPT. WORK CREW DRILLING PAST HOLE CUT 3/4 INCH PLASTIC SERVICE LINE. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1357 | 1992-01-12 | AL | other |  | ALABAMA GAS CORP |  | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1358 | 1992-01-02 | NY | other |  | ROCHESTER GAS & ELECTRIC CORP |  | 1000000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1359 | 1992-01-26 | AZ | other |  | CITIZENS UTILITY CO |  | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1360 | 1992-01-11 | ND | other |  | MONTANA - DAKOTA UTILITIES CO | DRIVER LOST CONTROL OF SNOWMOBILE WHEN THROTTLE STRUCK AND HIT THE METER SETALONGSIDE THE MOBILE HOME BREAKING A PIPE NIPPLE IN THE METER SETTING ANDCAUSING A RELEASE OF NATURAL GAS. MONTANA-DAKOTA UTIL. CO GAVE TELEPHONICREPORT UNDER 49CFR, PART 191, SUB | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1361 | 1991-08-10 | NV | other | KRALOY | SOUTHWEST GAS CORP | SOUTHWEST GAS HAD TEMPORARILY REMOVED A SECTION OF 2" PVC DISTRIBUTIONPIPELINE TO ACCOMMODATE THE INSTALLATION OF A LARGE DIAMETR WAS WATER PIPELINEPROJECT FOR THE CITY OF ELKO. THE GAS FLOW WAS CURTAILED BY THE INSTALLATIONOF TWO 2" SHORTSTOP FITTINGS. | 250000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1362 | 1992-01-06 | FL | other |  | PEOPLES GAS SYSTEM INC | DAMAGE CAUSED BY UNKNOWN OUTSIDE FORCES. UNDERWATER PIPELINE ON BOTTOM OF 54FT. DEEP CHANNEL AT BRIDGE WAS HIT BY UNKNOWN OUTSIDE FORCE CAUSING LEAK.AFTER UNSUCCESSFUL ATTEMPT TO REPAIR LINE, IT WAS TAKEN OUT OF SERVICE ANDWILL HAVE TO BE REPLACED. WRITTE | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1363 | 1992-02-03 | NJ | other |  | PUBLIC SERVICE ELECTRIC & GAS CO | ON FEBRUARY 3, 1992 AT APPROXIMATELY 2:22 P.M. AN EXPLOSION OCCURRED AT TOMMY'S DINER IN WALLINGTON (245 PATERSON AVE.) CAUSING EXTENSIVE PROPERTY DAMAGEAND INJURY TO 5 FIREFIGHTERS. THE AREA WAS VENTILATED AND INVESTIGATION REVEALED A CIRCUMFERENTIAL CR | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1364 | 1992-01-28 | NH | other |  | ENERGY NORTH NATURAL GAS INC | 6" CAST ITON MAIN CRACKED AS A RESULT OF FROST CONDITIONS.6" CAST IRON MAIN CRACKED AS A RESULT OF FROST CONDITIONS. | 75000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1365 | 1992-01-23 | MA | other |  | BOSTON GAS CO | A FIRE OCCURRED IN A RESIDENCE AT #155 SHARON STREET, MEDFORD, MASSACHUSETTS. A LEAK INVESTIGATION WAS CONDUCTED AND A 4" LOW PRESSURE CAST IRON CIRCUMFERENTIAL BREAK WAS FOUND ON A MAIN LOCATED IN THE STREET WITH APPROXIMATELY 11 1/2' OF FROST. AN ON-G | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1366 | 1991-12-30 | MA | other |  | BOSTON GAS CO | WHILE WORKING IN A TRENCH INSTALLING A SLEEVE, THERE WAS AN IGNITION RESULTING IN BURNS TO AN EMPLOYEE'S FACE AND HANDS. A PORTABLE HALOGEN LIGHT WAS BEING USED TO LIGHT THE JOB SITE AND WAS DETERMINED TO BE THE SOURCE OF IGNITION | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1367 | 1992-01-17 | IN | other | REPUBLIC | BATESVILLE GAS UTILITY | MAIN WAS 6-7 INCHES BELOW CURB SURFACE. STREET HAD BEEN RECURBED SINCE PIPEINSTALLATION. | 200000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1368 | 1992-01-30 | MS | other |  | MISSISSIPPI VALLEY GAS | A PRELIMINARY CHECK FOUND NO EVIDENCE OF GAS LEAKAGE FROM MISSISSIPPI VALLEYGAS FACILITIES; BUT THE EXACT CAUSE OF THE EXPLOSION AND FIRE WAS NOT DETERMINED. A TELEPHONE REPORT WAS MADE FOR THE ABOVE REASON. SUBSEQUENT INVESTIGATION PROVED THAT NO GAS LE | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1369 | 1992-01-21 | SC | other | DUPONT | SOUTH CAROLINA ELECTRIC & GAS CO | EMPLOYEES FOR JAMES ISLAND PUBLIC SERVICE DISTRICT (JIPSD) WERE PERFORMING ASEWERTAP FOR A NEW HOME AT 1766 MOHOWK STREET WHEN A 2" POLYETHYLENE (PLASTIC) GAS MAIN WAS DAMAGED. A BACKHOE OPERATOR FOR JIPSD DAMAGED THE 2" GAS LINE DUIRING EXCAVATION. JIP | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1370 | 1992-01-21 | KY | technical failure |  | WESTERN KENTUCKY GAS CO | WHILE WORKING ON A REGULATOR CONTROL LINE, GAS ESCAPED AND APPEARED TO BE IGNITED BY A NEARBY HEATER. TWO EMPLOYEES RECEIVED FLASH BURNS. ONE WAS HOSPITALIZED OVERNIGHT FOR OBSERVATION. BOTH EMPLOYEES HAVE SINCE RETURNED TO WORK | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1371 | 1992-02-21 | FL | other |  | PEOPLES GAS SYSTEM INC | A SMALL AMOUNT GAS LEAKING THROUGH SANDY SOIL WAS IGNITED BY AN UNKNOWN SOURCE. A "4" P.E. SERVICE LINE WAS LEAKING AS A RESULT OF MATERIAL FAILURE IMMEDIATELY ADJACENT TO A 4" SOCKET FUSION COUPLING. THE CUSTOMER WHO WAS BEING SERVED BY THE LINE REPORTE | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1372 | 1992-03-04 | NY | other |  | NIAGARA MOHAWK POWER CORP | GAS MIGRATED FROM 8" CRACKED CAST IRON MAIN (MECHANICAL POINT) INTO HOUSE AT1413 EAST PARK ROAD. AN UNKOWN SOURCE OF IGNITION CAUSED EXPLOSION AND FIRE. BOTH RESIDENTS DIED. ACTION TAKEN: GAS SERVICE TO 1413 EAST PARK RD WAS RETIRED AS HEADER WAS BROK | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1373 | 1992-03-16 | RI | other | MUELLER H-11071 | PROVIDENCE GAS CO | COMPOSITE NARRATIVE: BACKHOE OPERATOR MICHEAL SILVEIRA WAS EXCAVATING FOR FOOTINGS TO BE INSTALLED UNDER THE FRON PORCH OF 84 SOWANS ROAD, WHICH IS THE REAR HOUS OF 82 SOWANS ROAD (THE REPORTED ADDRESS) AND IS PART OF PROPERTY OWNED BY SILVEIRA'S FATHER | 125000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1374 | 1992-02-04 | TX | other |  | CORPUS CHRISTI, CITY OF - GAS DIV | STORMWATER CREW USING A GRADE-ALL TO CLEAN DRAINAGE DITCHES, HIT A 2" GAS MAIN, DAMAGING THE MAIN AND PULLING ONE END OUT OF A VALVE. IN THE PROCESS OF PUMPING WATER OUT OF THE DITCH WHERE DAMAGE OCCURRED, THE ESCAPING GAS WAS IGNITED. ONE EMPLOYEE RECE | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1375 | 1991-12-30 | TX | other |  | LONE STAR GAS CO | HALL CONSTRUCTION COMPANY WAS IN PORCESS OF REMOVING CONCRETE FROM THE WALL OTHE NORTH SIDE OF MARY'S CREEK WHEN THEY HIT AN 8" IP STEEL MAIN. THEY HOOKED A TOOTH IN THE 8" MAIN AT A 45 DEGREE ELL WITH A 235 CAT TRACKHOE. THE GAS HAD TO BE CUT OFF. SER | 12000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1376 | 1992-02-07 | TX | other |  | SAN ANTONIO,CITY PUBLIC SERVICE BOARD OF | EN EXPLOSION OCCURRED INSIDE A HOUSE LOCATED AT 1619 BASSE ROAD. AT THE TIMEOF THE EXPLOSION THERE WERE THREE OCCUPANTS INSIDE THE HOUSE AND ONE OCCUPANT SUSTAINED INJURIES WHICH REQUIRED IN-PATIENT HOSPITALIZATION TREATMENT | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1377 | 1992-02-21 | TX | other |  | GULFSIDE INDUSTRIES LTD | TWO INCH (2") GAS MAIN HIT BY SOMERSET CITY EMPLOYEE WHILE INSTALLING FLAG POLE. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1378 | 1992-02-21 | MO | other |  | K P L GAS SERVICE | A VEHICLE LEFT THE ROADWAY AND STRUCK THE METER SETTING ADJACENT TO THE HOUSE LOCATED AT 400 RICHWOOD, DAMAGING THE METER SETTING. GAS WAS SUBSEQUENTLY IGNITED, RESULTING IN DAMAGE TO THE VEHICLE AND THE HOUSE. | 80000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1379 | 1992-02-20 | CA | other |  | SOUTHERN CALIFORNIA GAS CO | THIS REPORT IS SUBMITTED UNDER 191.9, INCIDENT REPORTING, PER 191.3(3). NO OPERATOR FACILITY WAS INVOLVED. INVESTIGATION REVEALED CUSTOMER HOUSELINE LEAKED, CAUSING A SUBSEQUENT EXPLOSION AND FIRE THAT ATTRACTED SIGNIFICANT MEDIA ATTENTION. ALL OPERATO | 15000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1380 | 1992-02-11 | NM | other |  | RATON GAS TRANSMISSION CO | FEBRUARY 11, 1992: AT ABOUT 2:10 P.M., DONNA MUNDEN, ADVISED ME OF A REPORTED DAMAGED GAS LINE AT 925 OAK STREET. I ARRIVED AT THE LOCATION APPROXIMATELY 2:15P.M. AND FOUNS THAT THE 2" P.V.C. GAS MAIN HAD BEEN HIT BY A BACK HOE. LINE WAS CUT IN TWO. INS | 60000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1381 | 1992-02-08 | CA | maintenance |  | PACIFIC GAS & ELECTRIC CO |  | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1382 | 1992-01-18 | TX | maintenance |  | LONE STAR GAS CO | GAS LEAK IN THE MAIN IN THE ALLEY MIGRATED TO BACK WALL OF HOUSE. | 20000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1383 | 1992-01-26 | AZ | other |  | CITIZENS UTILITY CO | AT APPROXIMATELY 02:37 AM. ON 1.26/92 A VACANT RENTAL HOME AT 1212 1/2 WEST SECOND STREET IN WINSLOW, ARIZONA EXPLODED AND COUGHT FIRE. AFTER THE FIRE WAS OUT, EXCAVATION WAS BEGUN TO DISCOVER THE SOURCE OF THE LEAKING GAS. AFTER EXCAVATION, IT WAS DISC | 60000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1384 | 1992-02-20 | WI | other | PLEXCO | NORTHERN STATES POWER CO | AT APPROXIMATELY 12:30 -1:00 AM THE UPSTAIRS BUILDING TENANTS CAME HOME AND DROVE CAR INTO DOUBLE METER SET LOCATED ON THE SIDE OT THE DUPLEX. THE METERSET WAS SEPARATED FROM THE PARKING AREA BY APPROXIMATELY 10 FEET OF GRASS COVERED AREA. THE FORCE OF | 20000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1385 | 1992-03-25 | CA | other |  | PETROLANE GAS SERVICE LP | COUNTY BACK HOE DUG UP 3/4" YARD LINE WHILE EXCAVATING IN ROADWAY. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1386 | 1992-03-12 | VT | other | AMERICAN METER | VERMONT GAS SYSTEMS INC | RAIN FREEZING ON REGULATOR. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1387 | 1992-03-16 | NJ | other | DUPONT | SOUTH JERSEY GAS CO | MARKOUT REQUEST WAS MADE ON THIS DATE BY A SUBCONTRACTOR DOING WORK NEAR THIS LOCATION. THE CITY OF SEA ISLE DID NOT REQUEST A MARKOUT PRIOR TO WORKING ON 3-16-92. SEA ISLE CITY WORKMAN, WHILE PERFORMING WATER MAIN MAINTENANCE, PUNCTURED A 2-INCH PLASTI | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1388 | 1992-03-16 | MI | technical failure |  | MICHIGAN CONSOLIDATED GAS CO (MICHCON) | UNEXPECTED EXCESS LIQUIDS ENTERED STATION PIPING HYDRAULIC HAMMER RESULTING IN SUBSEQUENT GASKET FAILURE. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1389 | 1992-04-08 | CA | other | DRISCO | SOUTHERN CALIFORNIA GAS CO | A BACKHOE OPERATOR, WORKING FOR LBS PIPELINE CONTRACTORS, WHILE EXCAVATING TO INSTALL A WATER LINE, STRUCK AND DAMAGED A 2" PLASTIC MAIN. THE ESCAPING GAS IGNITED AND THE BACKHOE WAS COMPLETELY DESTROYED. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1390 | 1992-03-24 | KS | other | ROCKWELL | UNITED CITIES GAS CO | WATER LINE CONTRACTOR ALLOWED A 42 INCH CONCRETE CONDUIT TO ROLL INTO A METER SETTING. CONDUIT DAMAGED S 202 REGULATOR ALLOWING EXCESS GAS PRESSURE TO ENTER BUILDING. IGNITION OCCURRED DAMAGING INTERIOR OF BUILDING. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1391 | 1992-03-23 | AZ | other | ASO PIPE | CITIZENS UTILITY CO | WHILE REPLACING SERVICE LINE, SHOVEL CUT PLASTIC PIPE CAUSING GAS TO ESCAPE AND IGNITE. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1392 | 1992-04-01 | LA | other |  | LOUISIANA GAS SERVICE CO | EQUIPMENT OPERATOR FOR LOUISIANA HIGHWAY DEPARTMENT CYT STELL MAIN WHILE REMOVING DIRT FROM A CULVERT CROSSING FORSYTHE AVENUE. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1393 | 1992-05-02 | WY | other |  | NORTHERN GAS OF WYOMING - DIV OF KN ENERGY INC | CAR HIT METER LOOP AND MOBILE HOME. A CAR CAR DRIVEN BY AN 18YR OLD LADY, WHICH WAS LATER CHARGED WITH DWI, LEFT THE STREET, PROCEEDED DOWN AN ALLEY, THEN BETWEEN TWO TRAILERS, RUNNING OVER A FENCE, THE ELECTRICAL BOX, TELEPHONE BOX, AND OVER THE GAS | 48000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1394 | 1992-04-08 | IL | other |  | NORTHERN ILLINOIS GAS CO | N1-GAS LOCATOR ATTEMPTED TO LOCATE THE SERVICE BY CONTACTING THE CUSTOMER. THE CUSTOMER TOLD HIM SHE HAD NO GAS SERVICE. THE LOCATOR THEN CONTACTED HISHEADQUARTERS AND DETERMINED THAT THE CUSTOMER WAS A NONUSER OF NATURAL GAS. 3RD PARTY DAMAGED AN UN-MA | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1395 | 1992-02-16 | TX | other |  | ENTEX - DIVISION OF ARKLA INC | LEAK ON CUSTOMER LINE | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1396 | 1992-04-11 | CO | other |  | COLORADO SPRINGS, CITY OF | AN EXPLOSION SUSPECTED TO BE CAUSED BY NATURAL GAS BLEW OUT SEVERAL PORTIONSOF WALL ON BOTH STORIES OF THE BUILDING. THE EXPLOSION CAUSED A BRICK WALL TO COLLAPSE ONTO THE GAS METER, BREAKING THE INLET PIPING UPSTREAM OF THE REGULATOR. THE RUPTURED GAS | 500000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1397 | 1992-05-12 | MI | other | HEXAGRAM | MICHIGAN CONSOLIDATED GAS CO (MICHCON) | METER ASSEMBLY FAILURE DUE TO EXCESS EXPOSURE TO HIGH LEVEL OF WATER AND SEWAGE. A NATURAL GAS EXPLOSION RESULTED FROM A LEAK ASSOCIATED WITH AN AUTOMATIC METER READING DEVICE (SENSOR). THE SENSOR DISLOGED FROM THE METER DIAL GLASS, THUS ALLOWING THE ES | 35000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1398 | 1992-06-14 | MA | other |  | BOSTON GAS CO | A SPEEDING CAR HIT A UTILITY POLE THAT HAD A HIGH VOLTAGE ELECTRIC TRANSFORMER ATTACHED TO IT. THE POLE FELL TO THE GROUND AND THE LIVE WIRES ARCED THROUGH THE PAVEMENT AND SOIL. THE STEEL GAS MAIN WAS IN CONTACT WITH A DRAINAGECATCH BASIN. THE ARCING | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1399 | 1992-06-06 | CT | technical failure |  | SOUTHERN CONNECTICUT GAS CO | VENTING GAS FROM REGULATOR VAULT IGNITED DURING STARTUP OF GASOLINE ENGINE PUMP INJURING TWO EMPLOYEES AND DAMAGING TRUCK PARKED NEARBY. | 15000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1400 | 1992-05-31 | CA | other |  | PACIFIC GAS & ELECTRIC CO | CAR VEERED OFF PRIVATE DRIVE & STRUCK GAS 10 METER MANIFOLD. FIRE ENSUED, DAMAGING CAR AND BUILDING. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1401 | 1992-05-20 | MI | other | CHICAGO | CONSUMERS POWER CO | CONTRACTOR EXCAVATING FOR TREE PLANTING HIT GAS SERVICE LINE AND PULLED COMPRESSION FITTING APART ALLOWING GAS TO MIGRATE INTO BUILDING RESULTING IN EXPLO | 700000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1402 | 1992-05-14 | CA | other |  | PACIFIC GAS & ELECTRIC CO | HOUSE WAS VACANT. FIRE STARTED BY AN ARSONIST. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1403 | 1992-05-18 | MD | technical failure |  | BALTIMORE GAS & ELECTRIC CO | TECHNICIANS ON SITE DID NOT PROPERLY DEPRESSURIZE THE GAS FILTER BEFORE SERVICING IT. THE GAS FILTER WAS ISOLATED BETWEEN TWO VALVES BUT WAS STILL PRESSURIZED WIHT 90 PSIG BETWEEN THE REGULATOR AND UPSTREAM VALVES. AS THE TECHNICIAN ATTEMPTED TO REMOVE | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1404 | 1992-05-25 | NY | other |  | BROOKLYN UNION GAS CO | ON MARCH 25, 1992 AT 03:42 HOURS, BROOKLYN UNION GAS RECEIVED NOTIFICATION FROM THE N.Y.C. FIRE DEPARTMENT THAT A FIRE A WAS IN PROGRESS AT 1575 FLATBUSH AVENUE, BROOKLYN, N.Y. AT 05:45 HOURS THE GAS SERVICE CURB VALVES TO THISADDRESS AND THE TWO ADJACE | 400000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1405 | 1992-04-09 | LA | other |  | TERREBONNE PARISH CONSOLIDATED GOVERNMENT | WE WERE LOOKING IN THE AREA TO PINPOINT THIS LEAK WHEN THE FIRE OCCURRED. FIRE APPARENTLY STARTED IN THE BACK AREA OF THE RESIDENCE. INITIAL THRUST FROM THE SPREADING FIRE APPARENTLY WAS THE REASON FOR THE GAS LEAK CATCHING IN FIRE. THERE IS NO EVIDENC | 40000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1406 | 1992-05-29 | VA | other | PLEXCO | COMMONWEALTH GAS SERVICES INC | ON MAY 29, 1992 AT APPROXIMATELY 11:04 A.M. A BORING CONTRACTOR WORKING AT THE INTERSECTION OF U.S. ROUTE 360 AND SOUTHSHORE DRIVE, MIDLOTHIAN, VIRGINIA BORED INTO A 8" PLASTIC MEDIUM PRESSURE GAS MAIN LINE. THE RESULTING NATURALGAS LEAK WAS APPARENTLY I | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1407 | 1992-05-14 | OH | other |  | DAYTON POWER & LIGHT CO | A 3-MAN CREW WAS REPLACING A 1" STEEL GAS SERVICE WITH A 1" PLASTIC PIPE. WHILE ONE EMPLOYEE WAS REMOVING THE SCREWED CAP FROM THE COUPLING TO INSERT THE TRANSFITTING TO CONNECT THE SERVICE, THE GAS IGNITED IN THE EXCAVATED TRENCH. BOTH EMPLOYEES JUMPED | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1408 | 1992-05-24 | AK | other | PHILLIPS | ENSTAR NATURAL GAS CO | RESIDENTAIL STRUCTURE FIRE MELTED THE GAS METER/REGULATOR ASSEMBLY. THE INITAIL FIRE INVESTIGATION DETERMINED THE FIRE STARTED INSIDE THE STRUCTURE FROMFAULTY HOUSE PIPING AND/OR A GAS APPLIANCE. | 80000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1409 | 1992-06-09 | CA | other |  | PACIFIC GAS & ELECTRIC CO | GAS ESCAPING FROM AN UNCAPPED GAS CONNECTION IN A LAUNDRY ROOM EXPLODED, SEVERLY DAMAGING A BUILDING. THE CUSTOMER-OWNED BRANCH LINE TO THE CONNECTION CONTAINED A CUSTOMER-OWNED VALVE. IT IS NOT KNOWN IF THE VALVE HAD BEEN OPENED OR WAS LEAKING. SUBSEQ | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1410 | 1992-06-16 | IA | other |  | IOWA SOUTHERN UTILITIES CO | AT APPROXIMATELY 4:00 A.M. ON JUNE 16, BRAIN NELSEN, WHO IS THE OPERATOR OF THE TRUCK STOP, WAS APPARENTLY HOSING OUT A PICKUP TRUCK WHICH WAS LOCATED INTHE PIT AREA OF ONE OF THE SERVICE BAYS. AT THIS TIME THE EXPLOSION OCCURRED. MR. NELSEN HAS BEEN IN | 200000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1411 | 1992-06-19 | CA | other |  | SOUTHERN CALIFORNIA GAS CO | AUTOMOBILE OPERATOR LOST CONTROL OF THE VEHICLE ALLOWING IT TO TRAVEL OVER CONCRETE WHEEL BUMPERS, THROUGH TWO 4" CONCRETE-FILLED STEEL METER GUARDS AND INTO METER SET ASSEMBLY (MSA). ESCAPING GAS FROM THE DAMAGED MSA IGINITED ANDTHE RESULTING FIRE DAMAGE | 250000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1412 | 1992-07-06 | CA | other |  | PACIFIC GAS & ELECTRIC CO | CUSTOMER'S GRAVITY FURNACE "BLEW OUT" CAUSING BUILDING FIRE. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1413 | 1992-07-14 | CA | other |  | PACIFIC GAS & ELECTRIC CO | A FIRE OCCURRED IN THE BUILDING AND THE GAS SERVICE RISER WAS FOUND TO HAVE BEEN CUT NEAR THE RISER VALVE. THE ESCAPING GAS IGNITED. | 355000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1414 | 1992-07-09 | WI | other |  | WISCONSIN GAS CO | THE DRIVER OF A CAR PULLING INTO A PARKING SPACE AT THE BUDGET SOUTHGATE MOTEL AT 4300 SOUTH 27TH STREET, MILWAUKEE APPARENTLY DROVE TOO FAR FORWARD. THE CAR EITHER HIT OR PUSHED A WHEEL BARROW INTO THE GAS METER SET. THE SERVICE RISER PIPE BROKE RELEAS | 51000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1415 | 1992-06-27 | FL | maintenance |  | VISION ENERGY JACKSONVILLE BEACH DIV | THIS MAIN WAS DISCONTINUED FROM SERVICE COMPLETELY (SMALL SECTION) SERVICED ONLY ONE CUSTOMER. COMPLAINTS OF ODOR LED US TO LEAK IN 2" DIST. MAIN (AERATION REQUIRED). | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1416 | 1992-07-11 | MN | other | CENTURY | PEOPLES NATURAL GAS |  | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1417 | 1992-07-30 | OK | other | PHILLIPS | OKLAHOMA NATURAL GAS CO | CONTRATOR WORKING ON AN ELECTRICAL SERVICE LINE CUT A 2" PLASTIC LINE WITH AKUBATO DITCHING MACHINE. A SMALL LEAK OCCURRED WHICH THE CONTRACTOR ATTEMPTED TO REPAIR WITH PLASTIC TAPE. THE SAME LEAK WAS IGNITED BY A PROPANE TORCHUSED BY THE CONTRACTOR. T | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1418 | 1992-07-28 | TX | other | DUPONT | ENTEX INC | THIS LINE WAS LOCATED AT 8:00 A.M. JULY 28, 1992, BY PAINT. THE THIRD PARTY HAND DUG AND EXPOSED THE LINE AND TELEPHONE CABLE IN CONSTRUCTION DITCH. AFTER SPLICING, THE TELEPHONE REPAIRMAN USED A TORCH TO PLACE SHRINK HEAT SLEEVES ON SPLICE AND LET TH | 1600 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1419 | 1992-08-06 | IN | technical failure | L B FOSTER | CITIZENS GAS & COKE UTILITY | THE CAUSE OF THE ACCIDENT HAD BEEN DETERMINED TO BE A MISAPPLICATION OF THE HOT TAPPING PROCEDURE, ALLOW GAS TO ESCAPE INTO THE EXCAVATION WHICH ULTIMATELY WAS IGNITED, BY AN UNKNOWN SOURCE, INFLICTING BURN INJURIES TO FOUR OF THECORBITT AND SONS CONSTRUC | 25000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1420 | 1992-08-11 | MT | ACCIDENTALLY CAUSED BY OPERATOR |  | SHELBY GAS ASSOCIATION | A SHELBY GAS ASSOCIATION CREW CONSISTING OF A FOREMAN AND TWO SERVICEMEN WERE REPLACING A 600 FT SECTION OF 2" STEEL DISTRIBUTION MAIN WITH 2" ALDYL A PEPIPE. THE DISTRIBUTION SYSTEM WAS BEING OPERATED AT 12 PSIG AND THE TRANSITION FROM STYEEL TO P E PIP | 100 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1421 | 1992-07-27 | LA | other | AMERICAN METER | LOUISIANA GAS SERVICE CO | THE PRIMARY REGULATOR AT THE LACOMBE TOWN BORDER STATION APPARENTLY MALFUNCTIONED CAUSING AN OVERPRESSURE CONDITION ON THE METER. THE LARGE POSITIVE DISPLACEMENT METER SHATTERED CAUSING INJURY TO ONE EMPLOYEE. THE CAUSE OF THE ACCIDENT IS STILL UNDER IN | 5000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1422 | 1992-07-30 | NY | other |  | LONG ISLAND LIGHTING COMPANY | CONTRACTOR WAS INSTALLING OIL TANK AT 120 ROUNDHILL ROAD IN EAST HILLS. WHILE EXCAVATING, CONTRACTOR PULLED 3/4" STEEL GAS SERVICE . THE PULLING ACTION CAUSED A FITTING INSIDE THE HOUSE TO BREAK, ALLOWING GAS TO ESCAPE. CONTRACTOR CLOSED THE HEAD OF SERV | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1423 | 1992-08-03 | CO | other |  | PUBLIC SERVICE CO OF COLORADO | WHILE EMPLOYEE WAS INSTALLING A CLAMP ON A LEAKING GAS MAIN IT CAUGHT FIRE INJURING THE EMPLOYEE. THE SOURCE OF THE IGNITION IS PENDING INVESTIGATION. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1424 | 1992-08-18 | CO | other |  | PUBLIC SERVICE CO OF COLORADO | MATT FITZGERALD, A BACKHOE OPERATOR FOR KEHN CONSTR. CO OF 6322 SO. COLLEGE AVE. - FT. COLLINS, DUG INTO AN 1 1/4" PE GAS MAIN & BROKE THE MAIN AT AN 1 1/4 " STEEL TO PE TRANSITION FITTING. ESCAPING GAS FROM THE BROKEN MAIN BLEW DEBRIS FROM THE EXCAVAT | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1425 | 1992-08-18 | VA | other | DUPONT | WASHINGTON GAS LIGHT CO | CONTRACTOR WILLIAM HAZEL INC. WAS DRILLING FOR A ROADWAY PROJECT, WHEN THEY DRILLED THROUGH A 12" STEEL CASING AND THE INSERTED 8" PLASTIC MAIN. THE MAIN WAS PROPERLY MARKED WITH PAINT AND WOODEN STAKES. | 75000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1426 | 1992-08-12 | MI | other |  | MICHIGAN CONSOLIDATED GAS CO (MICHCON) | WORKER OVERCOME BY GAS WHILE ATTEMPTING TO CHANGE A 3/4" TEST TUBE VALVE IN A VAULT ON A 100 PSIG 8" MAIN VALVE. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1427 | 1992-08-26 | LA | other |  | LOUISIANA GAS SERVICE CO | POWER LINES FELL DURING HURRICANE FORCE WINDS AND CONTACTED THE GAS SYSTEM AT AN UNKNOWN LOCATION. A HOLE BLEW THROUGH THE MAIN DUE TO HIGH VOLTAGE, THEGAS INGNITED AND 25 HOMES WERE EVACUATED UNTIL THE GAS LEAK COULD BE CONTROLL | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1428 | 1992-08-21 | MA | technical failure | UPONOR ALDYL CO. | BOSTON GAS CO | NATURAL GAS WAS BEING INTRODUCED INTO A NEWLY INSTALLED PLASTIC MAIN. IGNITION WAS CAUSED BY STATIC ELECTRICITY AT THE PERGING POINT, RESULTING IN BURNSTO ONE COMPANY EMPLOYEE AND TWO CONTRACTOR EMPLOYEES. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1429 | 1992-07-21 | NE | technical failure |  | HASTINGS UTILITIES | THE ACCIDENT OCCURRED WHEN THE CONSTRUCTION CREW WAS REMOVING AN OLD ABANDONED SERVICE TAP FROM THE MAIN IN ACCORDANCE WITH STANDARD GAS DEPARTMENT PROCEDURES AS GIVEN IN OUR OPERATIONS AND MAINTENANCE MANUAL CHAPTER XIII. IN ACCORDANCE WITH GAS DEPARTMEN | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1430 | 1992-09-22 | CO | other | PLEXCO | PUBLIC SERVICE CO OF COLORADO | FENCE COMPNAY RUPTURES A 3" PE NATURAL GAS LINE WHICH IGNITED AFTER ANGERINGINTO THE LINE WITH A TRACTOR MOUNTED POST HOLE DIGGER, OPERATOR WAS BURNED AND TRANSPORTED TO HOSPITAL. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1431 | 1992-09-23 | OH | maintenance |  | EAST OHIO GAS CO | LEAK FROM CORROSION PIT MIGRATED INTO BUILDING. EXPLOSION AND FIRE WERE IGNITED WHEN OCCUPANT LIT A CIGARETTE. | 300000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1432 | 1992-09-14 | WI | other | PHILLIPS DRISCO PIPE | WISCONSIN NATURAL GAS CO | AN ELECTRIC UTILITY EMPLOYEE, WHILE REPORTEDLY SPLICING AN ELECTRIC CABLE WITH A PROPANE TORCH, ACCIDENTALLY DAMAGED A NEARBY GAS SERVICE PIPE. THE LOCATION OF THE SERVICE LINE WAS REASONABLY MARKED BEFORE THE ACCIDENT AND THE SERVICE WAS EXPOSED AND VI | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1433 | 1992-09-17 | DC | technical failure | DUPONT | WASHINGTON GAS LIGHT CO | BYERS ENGINEERING WORKING AS A CONTRACT LOCATOR FOR WASHINGTON GAS LIGHT COMPANY FAILED TO ADEQUATELY MARK A 2" PLASTIC GAS SERVICE IN THE AREA OF CONSTRUCTION. CONTRACTOR BADGER DRILLING INC. DRILLED THROUGH A 2" PLASTIC GAS SERVICE. IN THE INTEREST OF | 3000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1434 | 1992-09-10 | MN | other | PLEXCO | TWO HARBORS CITY MUNICIPAL GAS DEPT | ON THE MORNING OF SEPTEMBER 10, 1992 OUR ELECTRIC DEPARTMENT ASKED US TO MARK GAS SERVIDE FOR THE RELOCATION OF A POLE. WE MARKED THE GAS LINE OUT TO THE MAIN AND LEFT. AT ABOUT 11:00 A.M. THEY HIT THE SERVICE AND IMMEDIATELY CALLED OUR SERVICEMAN ON T | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1435 | 1992-09-24 | CA | other | DUPONT | SOUTHERN CALIFORNIA GAS CO | TWO EMPLOYEES OF TIERRA CONSTRUCTION WERE USING A PROPANE BURNER TORCH WHILEINSTALLING TELEPHONE CONDUIT IN THE SAME EXCAVATION WIHT EXPOSED 2" AND 1/2"PLASTIC GAS LINES. ONE EMPLOYEE WAS LIFTING THE PLASTIC GAS LINE WHILE THE OTHE WAS APPARENTLY APPLYIN | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1436 | 1992-10-03 | NY | other |  | LONG ISLAND LIGHTING COMPANY | THE STRUCTURE AT 263 WEST MAIN STREET WAS AN APARTMENT BUILDING THAT WAS UNDERGOING RENOVATIONS ON OCTOBER 3, 1992. A FIRE STARTED IN THE REAR OF THE BUILDING AND CAUSED A COLLAPSE OF THE STRUCTURE WHICH BROKE A LOW PRESSURE GAS SERVICE HOUSELINE. THE T | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1437 | 1992-10-26 | TX | other |  | SOUTHERN UNION GAS CO | VEHICLE STRUCK BUILDING AND METER SET. THE IMPACT CRACKED THE STRAINER WHICHPRODUCER HAD ABANDONED PRODUCTION FROM HIGH ISLAND 206 AND MADE NEW CONNECTIO IGNITED.N TO SAME TRANSCO UWTV ASSEMBLY FROM HIGH ISLAND 207. PRODUCER HAD COMPLETED DISASSEMBLING | 35000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1438 | 1992-11-02 | AR | technical failure |  | ARKANSAS LOUISIANA GAS CO (ARKLA GAS CO) | THE ONE INCH SERVICE LINE HAD A STRESS FRACTURE UNDER THE STREET. THE SERVICE LINE APPEARED TO HAVE BEEN BENT UPWARD TO ACCOMODATE THE PASSAGE OF A SEWER LINE BENEATH THE SERVICE. THE SEWER LINE HAD BEEN INSTALLED AS LONG AS FIFTEEN YEARS BEFORE THE INC | 25000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1439 | 1992-09-29 | AL | other | PLEXCO | ALABAMA GAS CORP | ON TUESDAY, SEPTEMBER 29, 1992, LANGFORD PATTON, LABORER - BENTON/MARKS, INCWAS INSTALLING A 3/4" SERVICE LINE TO 1928 CLOVER DRIVE FOR ALABAMA GAS CORPORATION. AFTER HE PRESSURE TESTED THE NEW SERVICE LINE, PATTON TAPPED THE TOW INCH PLASTIC MAIN USING | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1440 | 1992-11-25 | AL | other | PLEXCO | ONEONTA GAS DEPT | THE ACCIDENT OCCURRED ABOUT 2:30 P.M. AT THE HERITAGE GREEN SUB-DIVISION LOCATED IN ONEONTA, ALABAMA. (BLOUNT COUNTY) WE RECEIVED A CALL FROM THE OFFICE OF THE DEVELOPER STATING THAT ONE OF THEIR MEN HAD CUT OUR GAS LINE AND THAT IT WAS ON FIRE. THE CALL | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1441 | 1992-11-11 | OK | other |  | ARKANSAS LOUISIANA GAS CO (ARKLA GAS CO) | LEAK FOUND ON FURNACE CONNECTION AND COOK STOVE INSIDE DWELLING AND ON YARD LINE UNDER HOUSE SLAB. WOULD NOT HOLD PRESSURE TEST. CAUSE OF YARD LINE LEAK IS NOT KNOWN. | 20000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1442 | 1992-11-06 | NY | other |  | CENTRAL HUDSON GAS & ELECTRIC CORP | ON NOVEMBER 6, 1992 AT 7:52 PM AN EXPLOSION OCCURRED IN A TWO STORY WOOD FRAME RESIDENCE AT 26 LIBERTY STREET IN THE VILLAGE OF CATSKILL, NY. TWO PEOPLEWERE IN THE RESIDENCE AT THE TIME OF THE EXPLOSION. THE OWNER, AN 87 YEAR OLD FEMALE, DIED AND HER DA | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1443 | 1992-10-24 | TX | other | NIPAK | LONE STAR GAS CO | PERSON DROPPED CIGARETTE ON DYING GRASS. GRASS IGNITED CAUSING LEAKING NATURAL GAS TO IGNITE. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1444 | 1992-10-16 | TX | other |  | GULFSIDE GAS CO | SOUTHWESTERN BELL TELEPHONE EMPLOYEE WAS WORKING A "SPLICE PIT" MAKING A "SPLICE CLOSURE" WITH A "MID GAS FLAME TORCH" WHEN NATURAL GAS IGNITED FROM A 2"PVE GAS DISTRIBUTION LINE APPROXIMATELY 3"-12" BELOW THE WORK BEING PERFORMED BY THE SOUTHWESTERN BELL | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1445 | 1992-11-13 | IL | other |  | CENTRAL ILLINOIS PUBLIC SERVICE | STATION FAILED AT 4 PLACES: 2 SCREW FITTINGS, A WELD, AND AT A CAST IRON VALVE. CHEVROLET BLAZER STRUCK REGULATOR STATION AFTER MAKING A TURN AND SLIDING ON GRAVEL. | 30000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1446 | 1992-12-09 | DE | other | PLEXCO | CHESAPEAKE UTILITY CORP | ON TUESDAY, DECEMBER 9, 1992, AT APPROXIMATELY 11:30 A.M., A GAS IGNITION OCCURRED AT 208 EAGLES NEST DRIVE, DOVER, DELAWARE WHEN A GASOLINE MOTOR-DRIVENFENCE POST HOLE AUGER STRUCK AND BROKE A 3/4" PLASTIC GAS SERVICE. A SERVICEMAN AND STREET CREW WERE | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1447 | 1992-11-14 | MO | other | DONLEY PIPE | LACLEDE GAS CO | THERE WAS A COMPLETE CIRCUMFERENCE BREAK OF A 1/2 INCH COPPER SERVICE THAT HAD BEEN INSERTED INTO 3/4 INCH STEEL. THE BREAK WAS FOUND APPROXIMATELY 8 TO9 INCHES WITHIN THE FOUNDATION WALL. | 225000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1448 | 1992-11-02 | IA | other |  | MIDWEST GAS - DIV OF IOWA PUBLIC SERVICE CO | ONE RESIDENCE EXPLODED. THE CAUSE OF THE EXPLOSION IS STILL UNDER INVESTIGAT | 55000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1449 | 1992-11-12 | VA | other | AMERICAN METER/AMERICAN METER | ROANOKE GAS CO | APPARENT CAUSE: EXCESSIVE HEAT FROM A FIRE. THE FIRE MARSHALL SUSPECTS ANDIS INVESTIGATING ARSON.11:21AM CENTRAL DISPATCH CENTER RECEIVED CALL FROM ROANOKE COUNTY FIRE DEPARTMENT REPORTING A STRUCTURE FIRE AT 2926 TREE SWALLOW ROAD, SW. 11:23 A.M.: DI | 250000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1450 | 1992-11-18 | CT | other |  | YANKEE GAS SERVICES CO | INVESTIGATORS FROM THE WATERBURY FIRE MARSHALL'S OFFICE DETERMINED THAT GAS ESCAPING FROM AN OPEN METER COCK WAS IGNITED BY AB UNDETERMINED SOURCE, CAUSING AN EXPLOSION AND FIRE. THE METER HAD BEEN REMOVED IN NOVEMBER 1990. THEY CONCLUDED THAT THE OPEN | 150000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1451 | 1992-11-18 | LA | ACCIDENTALLY CAUSED BY OPERATOR | PLEXCO | VILLE PLATTE GAS SYSTEM, TOWN OF | WAS WORKING TO RELOCATE A 2" GAS LINE & WHEN THEY SQUEEZE IT OFF & STARTED TO CUT THE 2" LINE, SOMETHING IGNITED THE GAS COMING OUT OF THE 2" PIPE AND MELTED THE 4" LINE A FEW MINUTES LATER WE WENT AND CUT THE 4" VALVE. THE LINE WAS REPAIRED AND TURN BAC | 3200 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1452 | 1992-12-04 | IL | other | NI-PACK | CENTRAL ILLINOIS LIGHT CO | 4" CAST IRON LINE WAS LOCATED, CONTROL LINE APPROXIMATELY 1" ABOVE AND PARELLEL TO 4" CAST IRON MAIN. ----- CONTRACTOR HIT A REGULATOR STATION PLASTIC BURIED CONTROL LINE WHICH THEN CAUSED THE LOW PRESSURE SYSTEM TO BECOME OVERPRESSURED. | 80000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1453 | 1992-12-04 | TN | ACCIDENTALLY CAUSED BY OPERATOR | PHILLIPS DRISCOPIPE | MEMPHIS LIGHT GAS & WATER DIVISION | THE OPERATOR'S CREW ACCIDENTLY STRUCK AND RUPTURED A 2" PE GAS MAIN WHILE EXCAVATING WITH A BACKHOE TO ABANDON THE GAS SERVICE TO 749 MONTGOMERY ST. THE FORCE OF THE ESCAPING NATURAL GAS BURLED SPOIL FROM THE EXCAVATION (DIRT, ROCKS, BROKEN PAVEMENT, ET | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1454 | 1992-12-09 | TX | technical failure |  | LONE STAR GAS CO | CREW MEMBER FAILED TO PROPERLY INSTALL COMPLETION PLUG IN 4" SHORT STOP TEE. HE REMOVED COMPLETION TOOL AND OPENED SHORT CUT VALVE COMPLETION BLEW OUT. SHORT CUT VALVE WAS CLOSED STOPPING FLOW OF GAS. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1455 | 1992-12-25 | WV | other |  | WEST VIRGINIA POWER GAS SERVICE | A VEHICLE TRAVELING ON STATE ROUTE 6, LOST CONTROL DUE TO SNOW AND ICY CONDITIONS, STRIKING NATURAL GAS METER ASSEMBLY. THE FORCE OF THE VEHICLE CAUSED NATURAL GAS LEAKAGE TO IGNITE. THE DRIVER OF THE VEHICLE RECEIVED BURNS ON THE FACE, LEG AND FOOT ARE | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1456 | 1992-12-24 | MO | other | MUELLER | LACLEDE GAS CO | LACLEDE GAS COMPANY SERVICEMAN WAS ATTEMPTING TO TURN OFF SHUT OFF VALVE AT INSIDE BASEMENT WALL TO REPAIR MINOR GAS LEAKS ON COMPANY PIPING WHEN SHUT OFF VAVLE FAILED RESULTING IN INTERMEDIATE PRESSURE GAS BEING RELEASED INSIDE STRUCTURE. SERVICEMAN THE | 200000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1457 | 1992-12-23 | OH | other | DUPONT | CINCINNATI GAS & ELECTRIC CO | THE USE OF AN OPEN FLAME IN AN UNDERGROUND PIT BY THE WATER METER READER. FAILURE OF A PLASTIC SERVICE TEE ALLOWED GAS TO SEEP INTO WATER METER PIT. NOFURTHER ACTION REQUIRED. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1458 | 1992-12-23 | IN | other | UPONOR | INDIANA GAS CO INC | OPERATORS EMPLOYEES WERE ATTEMPTING TO INSTALL A BY-PASS AROUND DAMAGED MAINWHEN IGNITION OCCURRED. | 5000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1459 | 1993-01-02 | VA | other | DUPONT | WASHINGTON GAS LIGHT CO | CONTRACTOR S&N COMMUNICATIONS WAS INSTALLING FIBER OPTIC CABLE WITH A TRENCHING MACHINE WHEN THEY STRUCK AND BROKE A 4" PLASTIC NATURAL GAS LINE. THE LINE WAS NOT MARKED DUE TO THE FAILURE OF THE CONTRACTOR TO UTILIZE THE MISS UTILITY SYSTEM. THIS ACTIO | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1460 | 1993-01-22 | MT | other | DUPONT | GREAT FALLS GAS CO | 1/2 IN. CTS PLASTIC BROKE IN TRANSION FITTING. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1461 | 1993-01-05 | OH | other | PHILLIPS | DAYTON POWER & LIGHT CO | APPARENC CAUSE: THE ESCAPE OF GAS CAUSED BY AN EARLIER ELECTRICAL DUCT FIRETHAT CAUSED AN INSERTED PLASTIC GAS PIPE TO MELT.ON JANUARY 4, 1993, AN ELECTRICAL CABLE, INSIDE A FIBER CONDUIT, SHORTED OUTCAUSING AN ELECTRICAL FIRE IN A VAULT. A 6 INCH PLAST | 6000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1462 | 1992-12-30 | IN | other |  | NORTHERN INDIANA PUBLIC SERVICE CO | IN 1989, THE HOMEOWNER ENGAGED A CONTRACTOR TO MAKE REPAIRS TO THE FOUNDATION OF THE BUILDING. THE SERVICE LINE WAS HIT AND DAMAGED BY CONTRACTOR'S EQUIPMENT. THIS DAMAGE SUBSEQUENTLY LED TO THE GAS LEAKING AND MIGRATING INTO THE BUILDING WHERE IT SOMEH | 60000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1463 | 1993-01-01 | AK | other | PHILLIPS | ENSTAR NATURAL GAS CO | THE OWNER OF LOT 1 BLOCK 4, WILDERNESS ACRES WAS WORKING ON A VEHICLE IN HISGARAGE. WHILE REMOVING THE FUEL PUMP SPILLED GASOLINE ON THE FLOOR. A BATTERY CHARGER WAS HOOKED UP TO CAR AND APPARENTLY IGNITED THE SPILLED GASOLINE. THE RESULTING FIRE BURNED | 80000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1464 | 1992-12-23 | TN | other |  | MEMPHIS LIGHT GAS & WATER DIVISION | ON WEDNESDAY, DECEMBER 23, 1992, WORKERS EMPLOYED BY INDUSTRIAL MECHANICAL CONTRACTORS WERE PERFORMING WORK ON NATURAL GAS FUEL LINES OWNED AND OPERATED BY THE HUMKO CHEMICAL DIVISION OF THE WITCO CORPORATION AT 1238 POPE STREET IN MEMPHIS. TO PREVENT SE | 85600 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1465 | 1993-01-20 | WA | other |  | WASHINGTON NATURAL GAS CO | INCIDENT STILL UNDER INVESTIGATION. SUSPECTED CAUSE - DURING SEVERE STORM, POWER OUTAGES AND DOWNED WIRES CAUSED ELECTRICAL CURRENTO TO ENERGIZE STEEL GAS SYSTEM. ARC JUMPED TO ADJACENT WATER LINE AND BURN THROUGH ON GAS SERVICE RESULTED. GAS MIGRATED UN | 250000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1466 | 1993-01-20 | RI | other |  | PROVIDENCE GAS CO | D'AMBRA CONSTRUCTION WAS INSTALLING SANITARY SEWERS AT THE INTERSECTION OF CLEARWATER AND FAIR STREETS IN WARWICK, RI. THIS PERPENDICULAR EXCAVATION EXPOIN THE TRENCH OF A 14 FOOT DEEP EXCAVATION. A 10 INCH VITRIFIED CLAY TILE DRAIN RUNNING PARALLEL TO | 300000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1467 | 1993-01-21 | NM | other | ROCKWELL | GAS CO OF NEW MEXICO | CUSTOMER METER SET, SERVICE REGULATOR VENT PRESUMEDLY BLOCKED BY ICE FORMATION. ALLEDGEDLY CONTRIBUTED TO REGULATOR MALFUNCTION, ALLOWING HIGHER THAN NORMAL .25 PSIG DELIVERY PRESSURE TO ENTER CUSTOMER HOUSEPIPING SYSTEM.. ELEVATED GAS PRESSURE EXTINGUIS | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1468 | 1993-01-21 | IN | maintenance |  | MONTEZUMA MUNICIPAL GAS UTILITIES DEPT |  | 78000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1469 | 1993-01-23 | MD | other | AMERICAN MTR | BALTIMORE GAS & ELECTRIC CO | ON JANUARY 23, 1993 AT 0245 HOURS, OPERATIONS RECEIVED A CALL FROM ANNE ARUNDEL FIRE HDGTS, OF A DWELLING FIRE AT 213 POPLAR AVENUE, RES A. AT 0305 HOURS, SERVICEMAN REPORTED A GAS LINE WAS ON FIRE AND WAS FEEDING FIRE. CENTRAL DISTRIBUTION WAS NOTIFIED | 80000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1470 | 1993-01-27 | PA | ACCIDENTALLY CAUSED BY OPERATOR |  | NATIONAL FUEL GAS DISTRIBUTION CORP | TWO BELL HOLE EXCAVATIONS, APPROXIMATELY 28 FEET APART, HAD BEEN PREPARED PRIOR TO A 10 INCH, LOW PRESSURE MAINLINE REPLACEMENT BY INSERTION. IN BELL HOLE #1, THE GAS FLOW HAD BEEN STOPPED BY USE OF A SINGLE GAS BAG INSERTED IN THE MAINLINE. A 5 FOOT SE | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1471 | 1993-02-09 | AZ | other | ROCKWELL | SOUTHWEST GAS CORP | SOUTHWEST GAS PERSONNEL RESPONDED TO A HOUSE FIRE AT 5102 WEST OSBORN ROAD IN PHOENIX. A TWO-INCH (2") ROCKWELL FIGURE 143 PLUG VALVE SHOWED A CIRCUMFERENTIAL CRACK OF APPROXIMATELY THREE INCHES (3") IN LENGTH NEAR THE FLANGED PORTION OF THE VALVE. | 85000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1472 | 1993-02-02 | WI | other | EXTRON | NORTHERN STATES POWER CO | THE MATERIAL FAILURE WHICH LED TO THE INCIDENT MENTIONED ABOVE, OCCURRED ON THE BODY OF THE PIPE, IMMEDIATELY ADJACENT TO A SOCKET FUSION ON A 3"X3"X3" TEE. THE FAILURE IS BELIEVED TO HAVE BEEN CAUSED BY A COMBINATION OF FACTORSTHE PIPE IN QUESTION WAS I | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1473 | 1993-02-08 | NJ | other | WARREN FOUNDRY & PIPE PHILLIPSBURG | ELIZABETHTOWN GAS CO | ESCAPE OF GAS RESULTING FROM CRACK IN MAIN APPARENTLY CAUSED BY WEATHER. | 90000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1474 | 1993-02-18 | LA | other |  | LOUISIANA GAS SERVICE CO | A BACKHOE OPERATED BY A CONTRACTOR PULLED A 2" GAS MAIN OUT OF A DRESSER COUPLING. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1475 | 1993-01-20 | CA | other |  | KIRKWOOD GAS AND ELECTRIC CO | HEAVY ACCUMULATION OF SNOWFALL. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1476 | 1993-02-25 | PA | other |  | PHILADELPHIA GAS WORKS | THE MATERIAL DEFECT WAS A "HARDSPOT" ON THE PIPE DUE TO THE MANUFACTURE'S PROCESS. THE "HARDSPOT" WAS PREVIOUSLY INDENTIFIED AND REINFORCED WITH A SLEEVE. THE REINFORCING SLEEVE CONTAINED THE DEFECT. | 86000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1477 | 1993-02-09 | OH | technical failure |  | COLUMBIA GAS OF OHIO INC | CREW WAS REPLACING A SERVICE LINE. THE OLD SERVICE WAS CUT AND PLUGGED WITHAN EXPANSION PLUG. THE EXPANSION PLUG WAS INSERTED 2-1/2 " INTO THE 6" SERVICE STUB LEFT ON THE MAIN BEFORE THE STUB WAS CAPPED WITH A COMPRESSION END CAP. EMPLOYEE FOUND A PIN | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1478 | 1993-02-05 | CO | other |  | IGNACIO MUNICIPAL GAS | SUPPLIER (EL PASO NATURAL GAS) ALLOWED SURGE OF WATER TO ENTER CITY GATE. WATER RENDERED MAIN SYSTEM REGULATORS INOPERABLE. WATER SURGE ALSO CAUSED PRESSURE RELIEF VALVE TO NOT RESET WHEN WATER SURGE CAUSED PRESSURE RELIEF VALVETO VENT INTO ATMOSPHERE. | 4950 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1479 | 1993-01-27 | AL | other |  | CHILTON COUNTY GAS DIST | ALLIED LIME CO. BULLDOZIER OPERATOR CARRYING OUT SUPERVISOR INSTRUCTIONS, HIT AND TORE LOOSE 53 FEET OF 3 INCH MAIN CAUSING OUTRAGE OF COMPLETE CHILTON COUNTY GAS SYSTEM. | 40000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1480 | 1992-10-04 | FL | other |  | SAWYER GAS OF JACKSONVILLE INC | SARAH ROBBINS' DEATH WAS REPORTED ON 11-05-92 TO WR BUER (DETECTIVE - ID# 5967) BY THE GAINSVILLE MEDICAL EXAMINERS OFFICE. | 40000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1481 | 1993-01-29 | MI | other |  | CONSUMERS POWER CO | PIPE FAILED AT THREADED JOINT. SEWER CONTRACTOR DAMAGED MAIN NEAR FAILED POINT ON 5/21/91. STRESS FROM DAMAGE CONTRIBUTED TO JOINT FAILURE. | 80000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1482 | 1993-02-21 | CA | other |  | SOUTHWEST GAS CORP | LACER COUNTY SHERIFF'S DEPARTMENT OF AN APPARENT NATURAL GAS EXPLOSION AT 3135ON FEBRUARY 21, 1993 AT 6:05 A.M., SOUTHWEST GAS RECEIVED A REPORT FROM THE P POLARIS. ON FEBRUARY 21, 1993, PRELIMINARY INVESTIGATION REVEALED THAT THE IGNITION OF NATURAL GA | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1483 | 1993-02-10 | AK | other |  | NORTH CROSSETT GAS & WATER | EXPLOSION AT RESIDENCE ACROSS ROAD FROM PIPELINE. THE EXACT CAUSE OF THE HOUSE FIRE AND THE PIPELINE RUPTURE ARE STILL UNDER INVESTIGATION. WHEN DETERMINED, A SUPLEMENTAL REPORT WILL BE ISSUED. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1484 | 1993-02-22 | MA | other |  | BOSTON GAS CO | THERE WAS A FIRE INSIDE THE HOUSE AT 54 AUTUMN STREET, MALDEN. AFTER REPORTED EXPLOSIONS, THE HOUSE WAS LEVELED. INVESTIGATION AND EXCAVATION REVEALED A FRESH CRACK IN THE SERVICE PIPE AT THE THREADED CONNECTION TO A COUPLING. SOURCE OF IGNITION FOR TH | 75000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1485 | 1993-02-08 | CT | other |  | YANKEE GAS SERVICES CO | NOMINAL PIPE SIZE (1) 1.25, (2) 0.75. WALL THICKNESS (1) .140, (2) 0.113.YEAR INSTALLED (1) 1979, (2) 1976. REGULATOR/METER MANIFOLDS WERE STRUCK BY FALLING DEBRIS WHICH RESULTED FROM FIRE. 3/4" PIPE NIPLE AT OUTLET OF RISER COCK AND 1 1/4" NIPPLE AT | 1000000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1486 | 1993-03-26 | MD | other |  | BALTIMORE GAS & ELECTRIC CO | VENT LINE FROM 3/4 REG. NOT VENTED TO OUTSIDE. REMODELING DONE TO HOUSE, POSSIBLY DISCOUNTED BY CUSTOMER AT THIS TIME. HOUSE AND CONTENTS DESTROYED BY FIRE OF SUSPICIOUS ORIGIN. ELECTRICITY HAD BEEN DENIED FOR NON-PAYMENT ON 2/10/93. FIRE DEPARTMENT | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1487 | 1993-03-02 | SD | other | UNKNOWN | MONTANA - DAKOTA UTILITIES CO | AT APPROXIMATELY 8:24 P.M., 3/02/93, THE HOUSE AT 512 INDIANA STREET, RAPID CITY, SD, EXPLODED. SUBSEQUENT INVESTIGATION FOUND THE CAUSE TO BE A CRACKEDNATURAL GAS MAIN. THE CRACK WAS IN THE 2 INCH GAS MAIN WHICH PARALLELED A CARPORT 7 FEET AWAY AND NEA | 125000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1488 | 1993-03-04 | PA | maintenance | UNKNOWN | PHILADELPHIA ELECTRIC CO | TWO LEAKING GAS SERVICES IMMEDIATELY NEXT DOOR AND DOWN HILL FROM THE INCIDENT SCENE CAUSED GAS TO MIGRATE UNDER THE PAVEMENT INTHE SANITARY SEWER MAIN TRENCH AND ALSO IN THE WATER MAIN TRENCH OUTSIDE OF PAVING. THE MIGRATING GASTHEN FOLLOWED THE WATER S | 55000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1489 | 1993-03-17 | WY | other |  | JACKSON VANGAS INC | AS OF 3/24/93, IT IS MY OPINION ALL INVESTIGATIONS ARE INCONCLUSIVE. THE CAUSE OF THE FIRE IS STILL UNDER INVESTIGATION. IN MY OPINION, THERE IS NO SUBSTANTIAL PROOF OF THE SOURCE OF IGNITION AT THIS TIME. SO FAR THERE IS NO EVIDENCE OF AN EXPLOSION. ON | 60000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1490 | 1993-02-22 | NY | other | UNAVAILABLE | NEW YORK STATE ELECTRIC & GAS CORP | ON INDICATES THERE WAS EXCAVATION ACTIVITY IN THE VICINITY OF THE DAMAGED MAIN SEVERAL TIMES SINCE THE MAIN WAS INSTALLED. | 150000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1491 | 1993-03-03 | OK | other | YOUNGSTOWN | OKLAHOMA NATURAL GAS CO | A CONTRACTOR, WORKING FOR THE CITY OF TULSA, HIT OUR LINE WHILE MAKING A BORE FOR THE INSTALLATION OF A SEWER LINE. THE FIRST REQUEST TO LOCATED OUR FACILITIES WAS MADE ON SEPTEMBER 23, 1992, AND CONVERED WORK TO BE PERFORMED AT VARIOUS LOCATIONS IN A 20 | 114000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1492 | 1993-03-04 | IN | maintenance |  | JASONVILLE GAS UTILITY | APPROXIMATELY 5 FEET WEST IF SERVICE TAP, FRACTURE CRACK OCCURRED AROUND ENTURE OUTSIDE DIAMETER OF 2" CAST IRON MAIN. NO CAPTAN ODOR HAD BEEN NOTICED BY TONY 0R DANE HALITON, OR ANYONE ELSE IN THAT NEIGHBOURHOOD. ALSO, A HEAVY SNOW WAS ON THE GROUND JU | 10000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1493 | 1993-04-07 | KS | other |  | K P L GAS SERVICE | ERSECTION OF 311TH AND HEDGE ROAD IN PAOLA, KANSAS. UPON IMPACT THE VEHICLEWERE DIVERTED FROM THE ROADWAY AND DAMAGED A BARRICADED DISTRICT REGULATOR STATION. AS A RESULT, THE STATION WAS TOTALLY DESTROYED AND ONE (1) OF THE PARTYS INVOLVED WAS HOSPITAL | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1494 | 1993-04-01 | PA | other |  | T W PHILLIPS GAS & OIL CO | LIGHTNING STRIKE AT OR NEAR REGULATOR STATION CREATED AN ENORMOUS SURGE OF ELECTRIC CURRENT WHICH ARCED ACROSS AN INSULATED FLANGE ON THE INLET SIDE OF THE MONITOR REGULATOR CAUSING THE GASKET TO BLOW OUT AND IGNITED ESCAPING GAS. THE INTENSE HEAT FROM TH | 200000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1495 | 1993-04-01 | LA | technical failure |  | ARKANSAS LOUISIANA GAS CO (ARKLA GAS CO) | I RESPONDED TO 601 TEXAS STREET, WHICH IS THE ADDRESS OF THE ROLEX CLUB LOCATED ON THE CORNER OF TEXAS AND MCNEILL. I RESPONDED TO A BUILDING FIRE, WHICH WAS REPORTED TO HAVE HAD A BURN VICTIM INVOLVED. UPON MY ARRIVAL, FIRE FIGHTERS SHOWED ME WHERE THE | 1000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1496 | 1993-04-03 | FL | other |  | PEOPLES GAS SYSTEM INC | SUB-CONTRACTOR WORKING FOR CITY OF LAKELAND OPERATING A ROAD MIXER STRUCK A4" STEEL GAS MAIN CITY OF LAKELAND HAD REQUESTED A LOCATE IN JANUARY, AND COMPANY PERSONNEL LOCATED THE 4" STEEL MAIN. SUB-CONTRACTOR HAD NOT REQUESTED A LOCATE AT TIME OF INCIDEN | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1497 | 1993-04-07 | IL | ACCIDENTALLY CAUSED BY OPERATOR | DUPONT | CENTRAL ILLINOIS PUBLIC SERVICE | CREW WAS COMPLETING TEMPORARY BYPASS WHEN ESCAPING GAS IGNITED.SUPPLEMENTALREPORT 9/13/94 INDICATES THAT JULIE NOTICE FOR THIS LOCATION WAS CALLED IN11:02 AM ON 4/5/93 LOCATED AND MARKED 4/6/93. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1498 | 1993-03-29 | NV | other | CELANESE | SOUTHWEST GAS CORP | OPERATOR LOCATIONS MARKS WERE VERY ACCURATE. | 400000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1499 | 1993-02-05 | CA | other | FISHER | SOUTHERN CALIFORNIA GAS CO | A TRUCK DRIVER DROVE HIS VEHICLE UP ONTO A SIDEWALK TO PREVENT A COLLISION WITH ANOTHER VEHICLE. THE TRUCK RAN OVER A CURB METER BOX LOCATED IN THE SIDEWALK. THE WEIGHT OF THE TRUCK CRUSHED THE METER BOX AND DAMAGED THE METER SET ASSEMBLY INSIDE. THE D | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1500 | 1993-03-14 | NY | other |  | NEW YORK STATE ELECTRIC & GAS CORP | APPARENT OUTSIDE FORCE DAMAGED PIPE, DATE OF CONTACT UNKNOWN, OUR INVESTIGATION INDICATES THERE WAS EXCAVATION ACTIVITY IN THE VICINITY OF THE DAMAGED SCREW COLLAR IN THE FALL OF 1992 WHEN A SEWER LATERAL WAS INSTALLED TO 31 CARMICHAEL RD. | 75000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1501 | 1993-03-20 | CT | other |  | CONNECTICUT NATURAL GAS CORP | THE PIPE THAT FAILED WAS APPROXIMATELY 7 FEET UNDER THE SURFACE. THE PIPE WAS LOACTED IN THE VICINITY OF A SWIMMING POOL, RETAINING WALL AND A SUBSTANTIAL BACK FILL, MOST OF WHICH APPARENTLY WAS ADDED WITHIN THE LAST 3 YEARS. ITPRESENTLY APPEARS THAT TH | 400000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1502 | 1993-03-14 | KY | other |  | WESTERN KENTUCKY GAS CO | ON 3/14/1993, WESTERN KENTUCKY GAS COMPANY (WKG) RECEIVED A CALL FROM THE MCCRACKEN COUNTY SHERIFF'S DEPARTMENT. THE SHERIFF'S DEPARTMENT DISPATCHER STATED THAT A CAR HAD STRUCK SOMETHING AND THERE WAS A GAS LEAK AT THE CORNER OFTHIRD STREET AND JACKSON | 160000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1503 | 1992-10-06 | MI | other |  | MICHIGAN CONSOLIDATED GAS CO (MICHCON) |  | 125000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1504 | 1993-04-14 | PA | other | ROCKWELL | NORTH PENN GAS CO | INCIDENT INVOVLED A STRUCTURE FIRE OF UNKNOWN ORIGIN AT THE JOHN WASHINSKI RESIDENCE, LOCATED IN A RURAL AREA NEAR WHITNEYVILLE IN THE WELLSBORO DISTRICT, CHARLESTON TOWNSHIP, TIOGA COUNTY. NO ONE WAS HOME AT THE TIME AND THERE WERE NO FATALITIES OR REPO | 80000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1505 | 1993-05-13 | MD | technical failure |  | BALTIMORE GAS & ELECTRIC CO | AT APPOXIMATELY 0935, THURSDAY, MAY 13, 1993, DURING PLANNED WORK BY BG&E PELEAK ON CUSTOMER OWNED FUEL LINE INSIDE HOUSE.RSONNEL, A RELEASE OF GSS FROM A HIGH PRESSURE SERVICE RISER INTO THE UTILITYROOM AT THE REAR OF 9623 BASKET RING RD IN COLUMBIA, MAR | 500000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1506 | 1993-04-28 | LA | other |  | LOUISIANA GAS SERVICE CO | CONTRACTOR INSTALLING SEWER LINE BROKE 2" GAS MAIN VALVE WITH BACKHOE. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1507 | 1993-04-23 | CA | other | DUPONT | SOUTHERN CALIFORNIA GAS CO | A BACKHOE OPERATOR WAS EXCAVATING A TRENCH TO INSTALL ELECTRICAL CONDUIT. THE BACKHOE BUCKET HIT AND RUPTURED THE PLASTIC MAIN, CAUSING GAS TO ESCAPE. APPROXIMATELY TWO MINUTES LATER, STATIC ELECTRICITY FROM OVERHEAD ELECTRICAL LINES, IGNITED THE ESCAPI | 70000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1508 | 1993-04-18 | KY | other |  | WESTERN KENTUCKY GAS CO | THE INCIDENT APPEARS TO HAVE OCCURRED WHEN A CAR, THAT WAS BEING PURSUED BY POLICE, LEFT THE ROAD AND STRUCK A 6-INCH STEEL PIPE BARRICADE FILLED WITH CONCRETE AND SET IN CONCRETE THAT WAS PROTECTING A DISTRICT REGULATOR STATION. AFTER STRIKING THE BARRIC | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1509 | 1993-04-20 | LA | other | PLEXCO PE 3408 | LOUISIANA GAS SERVICE CO | CONTRACTOR DAMAGED PLASTIC GAS MAIN WHILE REMOVING STUMPS WITH TRACKHOE.THE LOCATE WAS INCORRECT DUE TO A TELEPHONE CABLE CROSSING THE GAS MAIN. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1510 | 1993-04-20 | LA | other |  | LOUISIANA GAS SERVICE CO | WHILE LAYING DRAIN LINES, CONTRACTOR PULLED GAS MAIN AND BROKE IT IN A WELD. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1511 | 1993-06-10 | PA | technical failure |  | PENNSYLVANIA GAS & WATER CO | B" LEAK ON EXISTING FOUR-INCH (4") STEEL GAS MAIN. TWO (2) APPARENT LEAKS WERE VISIBLE AFTER EXCAVATION; 90 DEGREES ELBOW GOING FROM THE SERVICE TEE, AND THE OTHER, A PINHOLE AT 4:00 ON THE BOTTOM OF THE PIPE. CONTRACTOR WAS CLEANING WITH POWER CLEANER | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1512 | 1993-05-27 | AL | other | PHILLIPS DRISCOPIPE | ENSTAR NATURAL GAS CO | A STRUCTURE FIRE OF UNKNOWN ORIGIN SEVERLY DAMAGED THE HOUSE, GARAGE AND A VEHICLE PARK INSIDE THE GARAGE AT 22626 NORTH SHORE DRIVE, CHUGIAK, ALASKA. THE HOUSE WAS SERVED WITH NATURAL GAS THROUGH A 5/8" NPS, POLYETHYLENE SERVICELINE OPERATING AT APPROXI | 250000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1513 | 1993-05-21 | AK | other | PHILLIPS DRISCOPIPE | ENSTAR NATURAL GAS CO | A FIRE, CLASSIFIED AS ARSON BY THE ANCHORAGE FIRE DEPARTMENT, WAS STARTED INA DUMPSTER DIRECTLY ADJACENT TO ENSTAR'S METER SET ASSEMBLY (MSA). THE MSA WAS FED BY 55 PSIG GAS THROUGH A 7/8" NPS, POLYETHYLENE SERVICE LINE. WHERE THE SERVICE LINE CAME ABOV | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1514 | 1993-05-03 | MI | technical failure |  | MICHIGAN CONSOLIDATED GAS CO (MICHCON) | SUPPLY TO LARGE INDUSTRIAL CUSTOMER WAS INTERRUPTED DURING A SUPPLY CHANGE-OVER PROCEDURE. HUMAN ERRORS IN DEVELOPING AND EXECUTING THE CHANGE-OVER CAUSED THE SUPPLY INTERRUPTION. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1515 | 1993-06-12 | WI | other |  | WISCONSIN NATURAL GAS CO | METER SET ASSEMBLY WAS STRUCK BY MOTOR VEHICLE. LEAK OCCURRED AT OR NEAR DAMAGED PIPE NIPPLE. FIRE STARTED IMMEDIATELY AND INVOLVED ENTIRE BUILDING WITHIN SEVERAL MINUTES. | 1000000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1516 | 1993-06-15 | MD | other | DUPONT | WASHINGTON GAS LIGHT CO | UNKNOWN ARSONIST STARTED A FIRE UNDER THE 2" NONCORRODIBLE RISER TO 19211 WATKINS MILL ROAD. THE FIRE CREATED SUFFICIENT HEAT TO MELT THE FACTORY INSERTED PLASTIC PIPE CREATING A HIGH PRESSURE LEAK UNDERGROUND. UNDER THE SURFACETHERE WAS AN OPEN PIPE CH | 1000000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1517 | 1993-06-09 | OK | other | CENTRAL | OKLAHOMA NATURAL GAS CO | STRAY ELECTRICAL CURRENT CAUSED ADJOINING HOLES IN THE MEDIUM-PRESSURE METERRISER AND THE CUSTOMER'S LOW-PRESSURE SERVICE LINE AT THE CUSTOMER'S PROPERTY LINE. GAS LINES ARE USUALLY SEPARATED BY A DISTANCE OF AT LEAST ONE FOOT; HOWEVER, IN THIS INCIDENT | 150000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1518 | 1993-06-17 | AK | other | PHILLIPS DRISCOPIPE | ENSTAR NATURAL GAS CO | A STRUCTURE FIRE, CLASSIFIED AS ARSON BY THE ANCHORAGE FIRE DEPARTMENT, SEVERLY DAMAGED THE HOUSE LOCATED AT 901 W. 53RD AVE, ANCHORAGE, ALASKA. THE HOUSE WAS SERVED WITH NATURAL GAS THROUGH A 5/8" NPS, POLYETHYLENE SERVICE LINE OPERATING AT APPROXIMATEL | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1519 | 1993-05-22 | OH | other |  | EAST OHIO GAS CO | AN UNDERAGED JUVENILE USED ANOTHER PERSON'S AUTOMOBILE AND LEFT THE PREMISESAT 96 CUYAHOGA STREET IN AKRON, OHIO. UPON ENTERING CUYAHOGA STREET, THIS PERSON MADE A LEFT HAND TUNR BUT NEVER PULLED OUT OF THE TURN. THIS MOVEMENT BROUGHT HIM BACK TO A CONC | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1520 | 1993-06-17 | IN | other |  | NORTHERN INDIANA PUBLIC SERVICE CO | AN EXCAVATOR STRUCK A MARKED RESIDENTIAL SERVICE LINE, PULLING APART A COMPRESSION FITTING, WHICH ALLOWED THE UNDERGROUND RELEASE OF NATURAL GAS. THIS GAS MIGRATED INTO THE RESIDENCE, WHCIH WAS ULTIMATELY DAMAGE. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1521 | 1993-06-28 | PA | other |  | PENNSYLVANIA GAS & WATER CO | IN RESPONSE TO A CUSTOMER'S REQUEST TO RAISE A WATER VALVE BOX LOCATED IN PARKING LOT THAT WAS SCHEDULED FOR REPAVING, PENNSYLVANIA GAS AND WATER COMPANYDISPATCHED A CREW TO 18 MARKET STREET, NANTICOKE, ON MONDAY, JUNE 28, 1993.THE CREW LOCATED THE WATER | 500000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1522 | 1993-06-27 | FL | other |  | FLORIDA PUBLIC UTILITIES CO | INVESTIGATION TO DATE REVEALS THAT A THREE INCH, THREE PHASE ELECTRICAL CONDUIT SERVING THIS RESIDENCE WAS INSTALLED DIAGONALLY ACROSS AND IN DIRECT CONTACT WITH THE TOP OF AN EXISTING ONE INCH GAS SERVICE LINE. A HIGH VOLTAGE ELECTRICAL SURGE, EITHER FRO | 1500000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1523 | 1993-06-28 | IA | other |  | MIDWEST GAS - DIV OF IOWA PUBLIC SERVICE CO |  | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1524 | 1993-07-15 | AZ | maintenance |  | SOUTHWEST GAS CORP | AN EIGHT INCH (8") X .250" W.T. STEEL MAIN WAS BEING UPRATED TO SUPPLY ADDITIONAL SYSTEM CAPACITY. ON THE FINAL STEP OF THE URATING (55 PSIG), A CORROSION PIT FAILED, CAUSING TWO BUILDINGS TO BE EVACUTATED. THE MAIN WAS REPLACED BY INSERTION OF A FOUR INC | 50600 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1525 | 1993-07-22 | MN | other | DUPONT | NORTHERN STATES POWER CO | ON THURSDAY, JULY 22, 1993, AN EXPLOSION AND FIRE OCCURRED AT THE SUBJECT ADDRESS. NSP REPORTED THIS INCIDENT TO YOUR OFFICE ( MR. BRUYERE) THIS SAME DAY.THE EXPLOSION AND ENSUING FIRE INVOLVED NATURAL GAS AND RESULTED IN FATALITIES, IN-PATIENT HOSPITALIZ | 1000000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1526 | 1993-07-15 | PA | other |  | PHILADELPHIA GAS WORKS |  | 14405 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1527 | 1993-07-28 | TX | other | NIPAK | LONE STAR GAS CO |  | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1528 | 1993-08-08 | IN | other |  | CITIZENS GAS & COKE UTILITY | ON AUGHUST 8, 1993 WE RECEIVED A CALL FROM INDIANAPOLIS FIRE DEPARTMENT AT 7:53 AM REPORTING A WORKING FIRE AND EXPLOSION AT 5218 NORWALDO AVENUE. WHEN WE ARRIVED ON THE SCENE THE HOUSE AT 5243 NORWALDO AVENUE HAS BEEN DESTROYED. MS. LESLEY WILLIAMS, AGE | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1529 | 1993-07-02 | TX | other |  | SOUTHERN UNION GAS CO | SOUTHERN UNION GAS COMPANY'S INVOLVEMENT WAS STRICTLY T ASSIST THE FIRE MARSHALL WITH THE INVESTIGATION. NO DETERMINATION HAS BEEN MADE AS TO THE LOCATION OF THE GAS ACCUMULATION OR THE SOURCE OR IGNITION. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1530 | 1993-06-28 | DC | maintenance | UNKNOWN | WASHINGTON GAS LIGHT CO | ON JUNE 28,1993, AT APPROXIMATELY 1649 HOURS, A 12" CAST IRON MAIN FAILED DUE TO GRAPHITIZATION AT THE INTERSECTION OF PENNSYLVANIA AVENUE AT 30TH STREET, SE, WASHINGTON. THE ESCAPING GAS FOUND AN IGNITION SOURCE AND ENGULFED THEINTERSECTION IN FIRE, INJ | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1531 | 1993-07-20 | LA | other |  | GULF STATES UTILITIES CO | THE CITY OF BATON ROUGE INITIATED A MAJOR STREET RE-BUILDING PROGRAM IN 1990.TO DATE, THERE HAS BEEN MAJOR RE-WORK OF 409 MILES OF CITY STREETS. THE WORKIS BEING PERFORMED BY MULTIPLE CONTRACTORS AND PROJECTS ARE SCATTERED THROUGHOUT THE CITY. AT 8:30 A.M | 250000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1532 | 1993-07-23 | NV | other | LINK | SOUTHWEST GAS CORP | ON JULY 23, 1993, AT APPROXIMATELY 0416 HOURS, SOUTHWEST GAS CORPORATION (SOUTHWEST) WAS NOTIFIED BY THE NORTH LAS VEGAS FIRE DEPARTMENT OF A FIRE AT A MOBILE HOME COMMUNITY AT 2067 NORTH LAS VEGAS BOULEVARD. SOUTHWEST IMMEDIATELYDISPATCHED EMERGENCY CREW | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1533 | 1993-08-05 | AZ | other |  | SOUTHWEST GAS CORP | A LONGITUDINAL CRACK OF APPROXIMATELY 1-1/2" IN LENGTH PROPOGATED FROM THE VICINITY OF A COMPRESSION COUPLING.A LONGITUDIHAL CACK IN THE 3/4" 3306 PE SERVICE ALLOWED NATURAL GAS TO ENTER A BUILDING. THE SUBSEQUENT EXPLOSION INJURED FOUR PERSONS WHO REQUIR | 800000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1534 | 1993-03-11 | MD | other | UNKNOWN | BALTIMORE GAS & ELECTRIC CO | THE EMPLOYEE WAS TIGHTENING AL LOOSE FITTING ON AN OUTSIDE METER REGULATOR INSTALLATION. THE SERVICE WAS 3/8" PLASTIC, WITH THE ABOVE GROND PORTION BEING3/8" COPPER. A COMPRESSION NUT ON THE COPPER PORTION WAS BEING TIGHTENED WHEN IT CRACKED. THE EMPLOYEE | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1535 | 1993-08-24 | MO | other |  | WESTERN RESOURCES INC | THE CAUSE OF THE DAMAGE TO THE APARTMENT COMPLEX WS APPAENTLY DUE TO VEHICULAR DAMAGE TO THE APARTMENT METER SET. THE SERVICE RISER BROKE AT A LOCATION BELOW THE SERVICE REGULATOR AND WAS BENT SO AS TO ALLOW GAS TO ENTER A WINDOW WHICH WAS ALSO DAMAGED DU | 500000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1536 | 1993-08-18 | IN | other | PLEXCO | CITIZENS GAS & COKE UTILITY | WE RECEIVED A CALL FROM PERRY TOWNSHIP FIRE DEPARTMENT THAT OUR MAIN HAD BEEN HIT. WHEN WE ARRIVED OUR MAIN WAS ON FIRE. A VAN DRIVEN BY EDWARD ESKEW HADLEFT THE ROADWAY AND STRUCK A UTILITY POLE ON THE NORTHWEST CORNER OF MERIDIAN STREET AND DAHLIA LANE. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1537 | 1993-09-02 | TN | ACCIDENTALLY CAUSED BY OPERATOR | UNKNOWN | HUMBOLDT UTILITIES - GAS DEPT | MARK WAS IN A HOLE EXCAVATED TO EXPOSE A NATURAL GAS PIPE WHICH WAS LEAKING.DURING THE EXCAVATING PROCESS A SERVICE TAPPING TEE WAS HIT AND TORE LOOSE FROM THE MAIN GAS PIPELINE. A RUBBER EXPANSION PLUG WAS PUT IN THE HOLE LEFT AFTER THE TAPPING TEE WAS R | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1538 | 1993-09-07 | NY | technical failure | PLEXCO | NIAGARA MOHAWK POWER CORP | WHILE COMPLETING A 6" PLASTIC TIE-IN ON SEPTEMBER 7, 1993 AT APPROXIMATELY2:00 PM, A FAILURE OCCURRED RESULTING IN GAS ESCAPING AT 22 PSI. THE GASIGNIGHTED FROM AN APPARENT STATIC BUILD UP CAUSING VARIOUS LEVELS OF DAMAGE TOCOMPANY-OWNED EQUIPMENT AND PR | 150000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1539 | 1993-09-27 | WV | other | DUPONT | MOUNTAINEER GAS CO |  | 150000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1540 | 1993-08-29 | MT | other |  | MONTANA - DAKOTA UTILITIES CO |  | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1541 | 1993-09-01 | GA | technical failure | AMERICAN/SINGER | COVINGTON MUNICIPAL GAS SYSTEM, CITY OF | PART 3 NARRATIVE - SMALL INTERNAL CORROSION PIN HOLE LEAK, AT 5:00 POITION ON PIPE, WAS REPAIRED WITH PLIDCO CLAMP. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1542 | 1993-09-17 | NM | other | UNKNOWN | GAS CO OF NEW MEXICO | PART 3 NARRATIVE - SPECULATE THAT FISHING NET SNAG BROKE 1" PLEECO BLEEDER VALVE ON BLIND FANGE ON SUB-SEA VALVE SETTING. | 5000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1543 | 1993-10-22 | MS | maintenance |  | MISSISSIPPI VALLEY GAS | PART A - CORROSION - THE LEAKAGE OCCURED AT TWO (2) SMALL CORROSION PIT HOLES LOCATED IN A 1" LONG DENT IN THE PIPE WALL. VISUAL INSPECTION DID NOT INDICATE RECENT CORROSIVE ACTIVITY AND THE PIPE -TO-SOIL POTENTIAL READING WAS -1.0VOLT AT THE TIME OF THE | 1500 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1544 | 1993-08-26 | PA | other | PLEXCO | NORTH PENN GAS CO | PART B #3. OPERATOR GAVE NOTICE T0 A ONE CALL SYSTEM ON AUGUST 19,1993. PART1 GENERAL REPORT INFORMATION - THIS INCIDENT BECAME REPORTABLE UNDER PART 191.3 ONE DAY AFTER THE ACTUAL ACCIDENT WHEN THE INJURED EMPLOYEE SOUGHT A SECOND APPRAISAL OF HIS CONDIT | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1545 | 1993-08-23 | MD | other | BETHEHEM STEEL | WASHINGTON GAS LIGHT CO | AN ELECTRIC ARC FROM AN EXTENSION CORD THAT SEPARATED WHILE NATURAL GAS WAS BEING RELEASED.WHILE WORKING TO REMOVE A 3/4" STEEL RISER FROM A 2" STEEL MAIN, A 3/4" STREET ELL FAILED. WHILE THE CREW LEADER WAS ATTEMPTING TO PLACE A WOODEN PLUG INTHE BROKEN | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1546 | 1993-09-23 | AK | other | PHILLIPS DRISCOPIPE | ENSTAR NATURAL GAS CO | A STRUCTURE FIRE, CLASSIFIED AS SUSPICIOUS ORIGIN BY THE ANCHORAGE FIRE DEPARTMENT, SEVERELY DAMAGED THE COMMERICAL BUILDING AT THE CORNER OF THE OLD GLENN HWY AND HANSON STREET IN EAGLE RIVER, ALASKA. THE INTENSE HEAT FROM THE FIRE MELTED THE 5/8" PLASTI | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1547 | 1993-08-31 | NY | other |  | LONG ISLAND LIGHTING COMPANY | ON AUGUST 31, 1993, A.J. ANTONINO WHILE EXCAVATING TO INSTALL A SEWER LINE, STRUCK AND PULLED A 1 1/4 INCH STEEL GAS SERVICE FROM A COMPRESSION COUPLING RESULTING IN A LEAK AND SUBSEQUENT EVACUATION OF 100 PEOPLE FROM A BUILDING.THE EVACUATION WAS PERFOR | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1548 | 1993-09-09 | IA | other |  | MIDWEST GAS - DIV OF IOWA PUBLIC SERVICE CO |  | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1549 | 1993-09-30 | MO | other |  | HERMANN CITY NATURAL GAS SYSTEM | PART 2 - FLASH FIRE FROM GAS POCKET IN DAMAGED 6" STEEL GAS LINE FORCED OUT DUE TO FLOOD WATER FLOW AT OPEN END. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1550 | 1993-10-18 | NJ | other |  | PUBLIC SERVICE ELECTRIC & GAS CO | AN INVESTIGATION REVEALED THIS HOUSE WAS IN THE PROCESS OF BEING SOLD AND NOONE WAS LIVING IN THE HOUSE AT THE PRESENT TIME. THE OWNER'S BROTHER, SHU-HONG SHIEL, WAS CHECKING THE HOUSE PERIODICALLY. ON 10/18/1993 AT APPROXIMATELY12:00 NOON, MR SHIEL TURNE | 115000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1551 | 1993-09-20 | TX | ACCIDENTALLY CAUSED BY OPERATOR |  | SOUTHERN UNION GAS CO | WHILE REPLACING MAIN LINE WAS MISLOCATED AND HIT WITH ROCK SAW OPERATED BY COMPANY EMPLOYEES.MISLOCATE OF COMPANY FACILITIES AND 6" MAIN HIT WITH ROCKSAW. | 117000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1552 | 1993-08-22 | TX | other |  | LONE STAR GAS CO | THE BUILDING HOUSING THE LAKE DALLAS CAFE, TIMBERLINE TAXIDERMY AND A VACANTHARDWARE STORE AND LUMBERYARD CAUGHT FIRE. THE HEAT FROM THE FIRE MELTED THEGAS METER AND THE REGULATOR. | 200 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1553 | 1993-09-15 | SC | other | DRISCOPIPE | LAURENS COMMISSION OF PUBLIC WORKS | ON SEPTEMBER 15,1993, THE LAURENS COMMISSION OF PUBLIC WORKS (CPW) WAS CALLEDBY THE FIRE DEPARTMENT FOR ASSISTANCE IN REFERENCE TO A NATURAL GAS FIRE AT THE GARLINGTON STREET TRAILER PARK. WHEN CPW PERSONNEL ARRIVED AT THE SCENE, THE FIRE DEPARTMENT HAD P | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1554 | 1993-10-22 | SD | technical failure | PHILLIPS DRISCO | MONTANA - DAKOTA UTILITIES CO | PART 3 NARRATIVE - SADDLE FUSION AREA ON THE PIPE WAS OVERHEATED AND BLEW OUT - IGNITION SOURCE UNKOWN. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1555 | 1993-10-12 | CA | other | DUPONT | SAN DIEGO GAS & ELECTRIC CO | A 3" OOLYETHYLENE TEE FAILED. BENDING STRESS ON THE TEE AND PIPE ASSEMBLY INITIATED A SLOW GROWTH CRACK IN THE RUN PORTION OF THE TEE. OVER THE LAST FEW YEARS SEVERAL EXCAVATIONS HAVE OCCURRED IN CLOSE PROXIMITY TO THE INCIDENT LOCATION. WE BELIEVE ONE OF | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1556 | 1993-10-27 | WI | ACCIDENTALLY CAUSED BY OPERATOR | PLEXCO | WISCONSIN SOUTHERN GAS CO INC |  | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1557 | 1993-10-13 | NY | other |  | LONG ISLAND LIGHTING COMPANY | THE LONG ISLAND LIGHTING COMPANY PLACED A TELEPHONIC NOTIFICATION TO THE DEPARTMENT OF TRANSPORTATION BASED UPON THE PRELIMINARY INFORMATION RECEIVED FROM THE FIELD AT THE TIME OF THE INCIDENT. THIS INFORMATION INDICATED THAT A FIRE FIGHTER WAS TRANSPORTE | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1558 | 1993-10-20 | MN | other | ALDYLA | PEOPLES NATURAL GAS | LINE WAS STRUCK BY CONTRACTOR. LINE WAS MARKED BUT MAY NOT HAVE BEEN MARKED WHERE HIT. 148 JUNIOR HIGH STUDENTS EXAMINED BY MEDICAL PERSONNEL AT AREA CLINICS. | 5000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1559 | 1993-10-15 | ID | other |  | WASHINGTON WATER POWER CO | PART 3 CUSTOMER EQUIPMENT FAILURE AND LACK OF PROPER VENTILATION ALLOWED ACCUMULATIONOF GAS RESULTING IN EXPLOSION AND SMALL FIRE. SEE COVER LETTER FOR MORE DETAIL. DURING A PLANNED CONSTRUCTION PROJECT TO REPLACE THE BONNERS FERRY DISTRICT REGULATOR STA | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1560 | 1993-10-20 | MT | other |  | MONTANA POWER CO | A CONTRACTOR INSTALLING A NEW SEWER LINE STRUCK AND DAMAGED AN INACTIVE NATURAL GAS SERVICE LINE. SINCE THE LINE WAS NOT MARKED, AND LOCATIONS HAD BEEN REQUESTED, THE PERSON OPERATING THE EXCAVATOR DID NOT NOTIFY ANYONE THAT A LINE, HE CONSIDERED TO BE AB | 56000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1561 | 1993-11-11 | AK | other | PHILLIPS DRISCOPIPE | ENSTAR NATURAL GAS CO | A STRUCTURE FIRE, CLASSIFIED AS "ORIGIN UNKNOWN" BY THE PETERS CREEK FIRE DEPARTMENT, SEVERELY DAMAGED A SINGLE FAMILY HOME THAT WAS UNDER CONSTRUCTION. THE BUILDING WAS LOCATED AT LOT 2, BLK 1 SAMPSON ESTATES, PETERS CREEK, ALASKA. THE BUILDING WAS SERVE | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1562 | 1993-10-31 | PA | other | AMP. SPECIAL INDUSTRIES. | PENNSYLVANIA GAS & WATER CO | A DEFECTIVE AMP. FITTING DISTURBED DURING BACKFILLING AND /OR COMPACTION LEDTO THE SEPARATION OF THE TWO-INCH PLASTIC GAS MAIN FROM THE FITTING WHICH RESULTED IN THE ESCAPE OF GAS.PART 2 APPARENT CAUSE- OTHER - DEFECTIVE FITTING. | 115000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1563 | 1993-10-30 | IN | ACCIDENTALLY CAUSED BY OPERATOR | FISHER | CITIZENS GAS & COKE UTILITY | A 1" RELIEF VALVE BLEW BECAUSE OF A PROCEDURAL ERROR WHILE ATTEMPTING TO ISOLATE 23M-125 METER FOR REMOVAL. GAS IGNITED FROM UNKNOWN SOURCE AS EMPLOYEES WERE ATTEMPTING TO TURN OFF AT 2" 1/4 TURN PLUG VALVE. PART 4 - ORIGIN OF THEINCIDENT - GAS ESCAPED FR | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1564 | 1993-11-02 | CO | other | DRISCO/PLEXCO | PUBLIC SERVICE CO OF COLORADO | TCS CABLE, INC. DID HAVE LOCATES AND LOCATES WERE CORRECT. BACKHOE OPERATOR HIT 2" MAIN, WHEN LOOKING FOR PIPE LINE. CAUSE OF IGNITION OF GAS FIRE IS UNKNOWN. | 75000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1565 | 1993-11-15 | NJ | other |  | PUBLIC SERVICE ELECTRIC & GAS CO | ON 11/15/93, AT APPROXIMATELY 10:05 AM, AN EXPLOSION AND FIRE OCCURRED AT 13-15 WILLIAMS STREET, BLOOMINGDALE, CAUSING EXPTENSIVE PROPERY DAMAGE AND MINOR FACIAL INJYURY TO ONE RESIDENT INVESTIGATION DISCLOSEC A BACKHOE OPERATED BY N. FARRO CONSTRUCTION C | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1566 | 1993-11-04 | MO | other |  | LACLEDE GAS CO | THE INVESTIGATION IS CONTINUING AS TO THE CAUSE OF THE WELD FAILURE ON THE 8- INCH S.I.P. MAIN. THE FAILURE WAS APPROXIMATELY 280 DEGREES AND THE SEPARATION APPROXIMATELY 1/2 TO 5/8 INCHES. THERE WARE APPARENTLY TWO SEPARATE EXPLOSIONS IN THE INCIDENT. AT | 500000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1567 | 1993-11-05 | IN | other |  | NORTHERN INDIANA PUBLIC SERVICE CO | AN EXCAVATOR STRUCK A MARKED RESIDENTIAL SERVICE LINE, PULLING IT AND CAUSING AN ELBOW AT THE RISER TO BREAK, WHICH ALLOWED THE UNDERGROUND RELEASE OF NATURAL GAS. THIS GAS MIGRATED INTO THE RESIDENCE, WHERE IT BECAME IGNITED, CAUSING PROPERTY DAMAGE. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1568 | 1993-10-11 | TX | other | ROCKWELL | ENTEX - DIVISION OF ARKLA INC | PART B- ADDITIONAL INFORMATION - CUSTOMER OPENED REGULATOR BYPASS, ALLOWING UPSTREAM HIGH PRESSURE TO ENTER METER, OVERPRESSURING AND BURSTING METER CASE. FLYING DEBRIS CAUSED INJURY. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1569 | 1993-11-04 | NJ | other |  | NEW JERSEY NATURAL GAS CO | ON THURSDAY, NOVEMBER 4, 1993, A REPORT OF A "CAR FIRE-POSSIBLE BROKEN LINE"AT 201 DRUMMOND AVENUE WAS RECEIVED BY NEW JERSEY NATURAL GAS COMPANY (NJNG)AT 2:58 P.M. BOTH A DISTRIBUTION CREW AND AN APPLIANCE SERVICEPERSON WERE DISPATCHED TO THE SITE. THEY | 400000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1570 | 1993-11-15 | NJ | other |  | NEW JERSEY NATURAL GAS CO | DAMAGE CAUSED BY ARC FROM DOWNED OVERHEAD ELECTRIC LINE. PART 3 NARRATIVE- AT APPROXIMATELY 9:00 A.M. ON NOVEMBER 15, 1993, RESIDENTS OF DOVER ROAD, S. TOMS RIVER, NEW JERSEY REPORTED AN OVERHEAD ELECTRIC LINE WAS CRACKLING AND ARCING. AT 9:22 A.M. , NEW | 20000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1571 | 1993-12-16 | NY | ACCIDENTALLY CAUSED BY OPERATOR | DRESSER | LONG ISLAND LIGHTING COMPANY | ON DECEMBER 15, 1993, AN INSULATED DRESSER COUPLING WAS INSTALLED ON A TEN (10) FOOT SECTION OF EIGHT (8) INCH GAS MAIN BETWEEN TWO VALVES. THE VALVES WERE CLOSED, HOWEVER, ONE OF THE GAS VALVES WAS NOT TIGHTLY SEALED. THE DRESSERCOUPLING WAS TORQUED, TES | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1572 | 1994-01-14 | NE | other |  | PEOPLES NATURAL GAS | POWER SURGE CAUSED OVERHEAD ELECTRICAL DISTRIBUTION WIRE TO FALL ON METER SETALLOWING ELECTRICAL CURRENT ON GAS SERVICE LINE TO ARC ACROSS AN INSULATOR, THEREBY MELTING A HOLE IN THE SERVICE LINE AND ALLOWING GAS TO ESCAPE INTO HOUSE AND IGNITE. PART 3 - | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1573 | 1993-12-13 | CA | ACCIDENTALLY CAUSED BY OPERATOR | PLEXCO | SOUTHERN CALIFORNIA GAS CO | A SOUTHERN CALIFORNIA GAS COMPANY CREW WAS MAKING PREPARATIONS TO TIE IN ANEWLY INSTALLED 3" POLYETHYLENE PLASTIC MAIN TO AN EXISTING 3" POLYETHYLENEPLASTIC MAIN. TO ACCOMMODATE THE TIE-IN, THE EXISTING MAIN WAS PINCHEDAPPROXIMATELY 3 FEET FROM ITS END. T | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1574 | 1993-12-01 | CA | other | UNKNOWN | PACIFIC GAS & ELECTRIC CO | PART 3 - A SYAR INDUSTRIES EMPLOYEE STRUCK AND DMAGED A 24-INCH STEEL TRANSMISSION LINE 210 WHILE GRADING A ROAD WITH A BULLDOZER. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1575 | 1993-11-25 | CA | other |  | PACIFIC GAS & ELECTRIC CO | PART 3- BROKEN FLEX LINE AT RANGE, ESCAPING GAS IGNITED AT FURNACE. STRUCTURE FIRE RESULTED. PART D - FLEX CONNECTOR AT RANGE WAS PARTIALLY SEVERED. THE CAUSE IS UNKNOWN. ESCAPING GAS IGNITED AT A FORCED AIR FURNACE RESULTING IN AFIRE WHICH DESTROYED THE | 60000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1576 | 1993-12-16 | OH | ACCIDENTALLY CAUSED BY OPERATOR | DRISCO #6500 | COLUMBIA GAS OF OHIO INC | ON THURSDAY, DECEMBER 16, 1993, AT APPROXIMATELY 9:00 A.M., COLUMBIA GAS OF OHIO, INC. (COLUMBIA) DISPATCHED AN EMPLOYEE TO A NORTH RIDGEVILLE CITY STORMSEWER CONSTRUCTION SITE TO LOCATE AND MONITOR SEWER CONSTRUCTION. WHILE THERE HE RELOCATED A 1-INCH D | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1577 | 1994-01-09 | NJ | other |  | PUBLIC SERVICE ELECTRIC & GAS CO | ON JANUARY 9, 1994, AT APPROXIMATELY 11:05 P.M. AND EXPLOSION OCCURRED AT VANHOUTEN AUTO PARTS #890 VAN HOUTEN AVENUE CLIFTON,CAUSING EXTENSIVE PROERTY DMAGE TO #890 VAN HOUTEN AVENUE AND ADDITIONAL DMAGE TO FOUR SURROUNDING BUILDINGS AND PARKED VEHICLES. | 500000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1578 | 1993-11-22 | WV | other |  | WEST VIRGINIA POWER GAS SERVICE | A RALIEGH COUNTY PUBLIC SERVICE DISTRICT EMPLOYEE ENTERED A 4' X 8' UNDERGROUND VAULT TO RECORD WATER METER READINGS. INFORMATION GATHERED LEAD US TO BELIEVE THE EMPLOYEE LIT A CIGERETTE LIGHTER TO PROVIDE LIGHT TO READ THE LARGE CAPACITY TRANSFER POINT S | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1579 | 1994-01-14 | MA | other |  | BOSTON GAS CO | AT APPROXIMATELY 2,100 HOURS THE OWNER/OCCUPANT OF 787 FELLSWAY WEST WENT TOHIS BASEMENT TO INVESTIGATE A GAS ODOR. HE THEN RETURNED TO HIS LIVING QUARTERS. AT APPROXIMATELY 2236 HOURS HE HEARD A "THUD". HE THEN OBSERVED FLAMES ON THE LEFT SIDE OF HIS HOU | 75000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1580 | 1994-01-03 | CA | other |  | SAN DIEGO GAS & ELECTRIC CO | A 3/4 INCH GS RISER WAS BROKEN OFF BELOW THE STOP COCK BY A HIT AND RUN VEHICLE CONTACT. THE GAS WAS BLOWING INTO THE REAR DOORWAY OF THE BUILDING. THE RISER WAS APPROXIMATELY THREE FEET FROM THE DOORWAY. THE GAS WAS IGNITED BY ANUNKNOWN IGNITION SOURCE W | 800000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1581 | 1994-01-10 | PA | other |  | PHILADELPHIA GAS WORKS | THE FOLLOWING IS A DESCRIPTION OF THE FACTORS BELIEVED TO HAVE CONTRIBUTED TO THIS INCIDENT BASED UPON INITIAL ON-SITE FINDINGS.THE INITIAL REPORT TO PGWFROM THE PHILADELPHIA FIRE DEPARTMENT WAS A BUILDING COLLAPSED AT 1522 ON JANUARY 10, 1994. UPON ARRIV | 120000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1582 | 1994-01-12 | AL | other | PHILLIPS DRISCOPIPE | ALABAMA GAS CORP | A VACANT BUILDING WASUNDER RENOVATION WHEN GAS APPARENTLY ENTERED THE BUILDING AND WAS IGNITED. TWO PERSON WERE INJURED IN THE INCIDENT AND WERE HOSPITALIZED WITH BURN INJURIES. THE SERVICE LINE TO THE BUILDING WAS TESTED FOR LEAKAGE BUT NONE WAS FOUND. A | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1583 | 1993-12-16 | NJ | maintenance |  | NEW JERSEY NATURAL GAS CO | AT APPROXIMATELY 8:17 A.M. ON THURSDAY DECEMBER 16, 1993, NEW JERSEY NATURALGAS COMPANY'S (NJNG) DISPATCH CENTER RECEIVED A TELEPHONE REPORT OF A "MANHOLE EXPLOSION WITH A BURN VICTIM" FROM THE NEPTUNE POLICE. THE NJNG CONSTRUCTION AND REPAIR CRREW ARRIV | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1584 | 1994-01-25 | AK | other | PHILLIPS DRISCOPIPE | ENSTAR NATURAL GAS CO | A STRUCTURE FIRE WHICH STARTED IN THE KITCHEN, SEVERELY DAMAGED A SINGLE FAMILY HOME LOCATED AT LOT 4, BLK1 MIDWAY ESTATES , WASILLA, ALASKA. THE BUILDING WAS SERVED WITH NATURAL GAS THROUGH A 5/8" NPS, POLYETHYLENE SERVICE LINE OPERATING AT APPROXIMATELY | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1585 | 1994-01-25 | PA | other |  | PHILADELPHIA GAS WORKS |  | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1586 | 1994-02-07 | NJ | other |  | PUBLIC SERVICE ELECTRIC & GAS CO | ON FEBRUARY 7, 1994, AT APPROXIMATELY 6:29 AM A FIRE WAS REPORTED AT #63 ROUTE 46 (WINANT AVE), RIDGEFIELD PARK, N.J. ONCE THE GAS SERVICE WAS CUT-OFF, AN ADDITIONAL INVESTIGATION REVEALED A CIRCUMFERENTIAL CRACK ON A 4" CAST IRONUTILIZATION PRESSURE MAIN | 250000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1587 | 1994-01-23 | MI | other |  | MICHIGAN CONSOLIDATED GAS CO (MICHCON) | EMPLOYEE, USING AIR HAMMER DUE TO FROST, HIT PUBLIC LIGHTING CABLE, WHICH WAS NOT STAKED PROPERLY, EVEN AFTER SECOND CALL WAS PLACED FOR STAKING. EMPLOYEE WAS FLASHED WHEN SPARK FROM CABLE IGNITED LEAKING GAS FROM MAIN. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1588 | 1994-02-12 | NY | other |  | CENTRAL HUDSON GAS & ELECTRIC CORP | ON FEBRUARY 12, 1994, AT 7:19 A.M. A FIRE AND EXPLOSION OCCURRED IN A TWOSTORY WOOD FRAME RESIDENCE AT 14 FRANKLIN STREET IN THE VILLAGE OF WAPPINGERSFALLS, N.Y. ONE PERSON, A 50 YEAR OLD MALE, WAS IN THE RESIDENCE AT THE TIMEOF THE EXPLOSION AND HE SUSTA | 800000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1589 | 1994-01-31 | IL | other |  | NORTHERN ILLINOIS GAS CO |  | 150000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1590 | 1994-02-10 | IL | other |  | NORTHERN ILLINOIS GAS CO |  | 80000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1591 | 1994-02-11 | MI | other | US STEEL | CONSUMERS POWER CO | PART 3 - PIPE FAILED AT THIRD-PARTY DAMAGE. GAS MIGRATED INTO HOUSE CAUSING AN EXPLOSION AND FIRE. | 90000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1592 | 1994-02-13 | MI | other |  | MICHIGAN CONSOLIDATED GAS CO (MICHCON) | GROUND FROST OF APPROXIMATELY 38" TO 40" INCHES RESULTED IN A CIRCUMFERENTIAL FRACTURE OF THE 4" C.I. MAIN. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1593 | 1994-01-21 | MD | other | DUPOUNT | WASHINGTON GAS LIGHT CO | UNKNOWN CONTRACTOR DROVE A 1.5" X 1.5" WOODEN SQUARE STAKE THROUGH A 2" PLASTIC GAS LINE. DURING THE RECENT COLD WEATHER, THE GROUND FROZE CAUSING IT TO HEAVE, PULLING THE STAKE UP AND OUT OF THE HOLE IN THE MAIN. THE LEAKAGE TRAPPED BY THE FROZEN CAP OF | 400000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1594 | 1994-02-13 | DC | other | STOCKHAM | WASHINGTON GAS LIGHT CO | THE FACTORS CONTRIBUTING TO THE INCIDENT WERE THE UNUSUALLY COLD WEATHER IN THIS AREA, WHICH CAUSE THE FROST LINE IN THE GROUND TO GO DEEPER THAN NORMAL WHICH CAUSED EXTREME PRESSURE TO BE EXERTED ON THE BOY OF THE 12" VALVE. THISPRESSURE CAUSED THE BODY | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1595 | 1994-01-28 | NJ | maintenance |  | PUBLIC SERVICE ELECTRIC & GAS CO | A FIRE AND EXPLOSION WAS REPORTED AT A STRIP MALL ON PARK AVE, SOUTH PLAINFIELD. SERVICEMEN AND STREET CREWS RESPONDED TO SHUT OFF THE TWO GAS SERVICES TO THE MALL. A LEAK SURVEY OF THE SURROUNDING AREA WAS PERFORMED WITH NO SIGNIFICANT LEAKAGE FOUND. THE | 3000000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1596 | 1994-01-26 | NY | other |  | CONSOLIDATED EDISON CO OF NEW YORK | CREWS RESPONDED TO A REPORT OF AN EXPLOSION AND FOUND HIGH GAS READINGS ALONG 38TH AVENUE BETWEEN 21ST AND 22ND STREETS. AFTER CUTTING AND CAPPING A 12 INCH LOW PRESSURE CAST IRON GAS MAIN, GAS READINGS DISSIPATED. EXCAVATION OF THE GAS MAIN REVEALED A SI | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1597 | 1994-01-20 | NY | other |  | LONG ISLAND LIGHTING COMPANY | THE PIPE APPEARS TO HAVE BEEN PHYSICALLY DAMAGED BY AN UNKNOWN PARTY, POSSIBLY DURING A PREVIOUSLY COMPLETED SEWER CONNECTION. THE COMBINATION OF THE DAMAGED PIPE AND SEVERE WEATHER CONDITIONS APPARENTLY CONTRIBUTED TO THE INCIDENTPART B - DAMAGE BY OUTSI | 500000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1598 | 1994-01-28 | PA | other |  | U G I CORP | IT APPEARS NATURAL GAS ESCAPING FROM A CRACK IN A FOUR INCH CAST IRON MAIN LOCATED ALONG THE 900 BLOCK OF WYOMING STREET IN ALLENTOWN, PENNSYLVANIA MIGRATED INTO HOUSE 925 WYOMING STREET. THE GAS WAS SUBSEQUENTLY IGNITED BY AN UNKNOWN SOURCE CAUSING AND E | 300000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1599 | 1994-02-05 | MA | other |  | FITCHBURG GAS & ELECTRIC LIGHT CO |  | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1600 | 1994-01-18 | IL | other |  | PEOPLES GAS LIGHT & COKE CO | PART 3- A CRACK IN AN 8" STEEL CATHODICALLY PROTECTED MEDIUM PRESSURE PIPE LEAKED, CAUSING GAS TO MIGRATE UNDERGROUND. OUR INVESTIGATION CONTINUES AS TO THE CAUSE OF THIS INCIDENT. PART B.3- THE PIPE WAS PREVIOUSLY DENTED AT THE POINT WHERE THE CRACK OCCU | 600000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1601 | 1994-01-23 | PA | other |  | PHILADELPHIA GAS WORKS | CIRCUMFERENTIAL BREAK ON A LOW PRESSURE 6" CAST IRON GAS MAIN IN FRONT OF 3724 "M" STREET, 63" NORTH OF THE NORTH CURB LINE OF AIRDRIE STREET, 3'6" EAST OF THE WEST CURB OF "M" STREET. | 110000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1602 | 1994-01-19 | KY | other |  | WESTERN KENTUCKY GAS CO | ON THE ABOVE DATE AND TIME, WKG RECEIVED NOTIFICATION FROM THE BOWLING GREENFIRE DEPARTMENT THAT A HOUSE AT 239 W. 15TH STREET IN BOWLING GREEN WAS ON FIRE. WKG PERSONNEL WERE DISPATCHED IMMEDIATELY TO THE SCENE AND SOON AFTER ARRIVING, THE THREE HOUSES A | 250000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1603 | 1994-02-04 | CT | other | MERCO | YANKEE GAS SERVICES CO | FIRE FIGHTERS WERE CALLED TO RESPOND TO AN ODOR OF GAS AND FIRE AT THE SITE OF A BRICK AND WOOD FRAME TENANT HOUSE. YANKEE GAS RESPONDED WHEN CALLED FOR AND LOCATED AND CLOSED THE SERVICE CURB VALVE. YANKEE GAS CREWS CONTINUED INVESTIGATING FOR THE LEAK A | 350000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1604 | 1994-01-09 | NJ | other |  | NEW JERSEY NATURAL GAS CO | AT APPROXIMATELY 2:33 A.M. ON SUNDAY, JANUARY 9, 1994, NEW JERSEY NATURAL GAS COMPANY (NJNG) RECEIVED A REPORT OF A HOUSE FIRE AT 3 FAIRWAY W., COLTS NECK. THE NJNG APPLIANCE SERVICEMAN ARRIVED AT 2:57 A.M. AND FOUND THAT THE UNOCCUPIED HOUSE WAS ON FIRE | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1605 | 1994-01-25 | MA | other |  | BOSTON GAS CO | THE OCCUPANT ARRIVED HOME FROM WORK AT 6:OO A.M. AND NOTICED AN ODOR OF GAS IN HIS BASEMENT APARTMENT. HE INVESTIGATED THE ODOR IN EACH ROOM OF THE APARTMENT AND THE UTILITY AREA. SHORTLY BEFORE 8:30 A.M. HE SAT DOWN AND LIT A CIGARETTE. THERE WAS AN IMME | 25000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1606 | 1994-01-05 | NY | other |  | LONG ISLAND LIGHTING COMPANY | A THIRD PARTY CONTRACTOR DRILLED THROUGH AN 8" GAS MAIN WHILE PERFORMING TEST BORING OPERATIONS. THE LONG ISLAND LIGHTING COMPANY PLACED A TELEPHONIC NOTIFICATION OT THE DEPARTMENT OF TRANSPORTATION BASED UPON THE PRELIMINARY INFORMATION RECEIVED FROM THE | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1607 | 1994-01-19 | PA | other |  | U G I CORP | DUE TO OUTSIDE FORCES, CAUSED EITHER BY AN EARTHQUAKE FIVE DAYS PREVIOUSLY OR BY FROST RESULTING FROM ESTREMELY COLD WEATHER, A NOMINAL FOUR INCH CAST IRON GAS MAIN WAS BROKEN. THE MAIN WAS LOCATED UNDER THE STREET PAVEMENT ALONG THE 300 BLOCK OF NORTH SE | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1608 | 1993-12-11 | TX | other |  | ENERGAS CO | EXPLOSION DUE TO GAS ACCUMLATION FROM OPEN OUTLET WHERE A GAS DRYER PREVIOULSLY HAD BEEN CONNECTED | 17000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1609 | 1994-01-23 | NJ | maintenance |  | SOUTH JERSEY GAS CO | EXPLOSION AND FIRE OCCURRED AT A RESIDENTIAL HOME INJURING THE HOMEOWNER ANDREQUIRING HOSPITALIZATION. UPON ARRIVAL, NATURAL GAS WAS DETECTED AT THE FOUNDATION. TWO CORROSION LEAKS WERE DISCOVERED ON THE MAIN IN FRONT OF THE PROPERTY AND REPAIRED. CURR | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1610 | 1994-01-19 | TX | other |  | LONE STAR GAS CO | 4" POLY MAIN BROKEN AND ON FIRE AFTER BEING STRUCK BY BACKHOE WHILE DIGGING DITCH FOR NEW ELECTRIC CABLE. | 20000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1611 | 1994-01-07 | AL | ACCIDENTALLY CAUSED BY OPERATOR |  | HARTSELLE UTILITIES BOARD | OUR WASTE WATER CONSTRUCTION CREW, WAS BLASTING IN AREA CAUSING PIPE TO BREAK.NO DAMAGE OTHER THAN LOSS OF GAS. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1612 | 1994-01-19 | MD | other |  | COLUMBIA GAS OF MARYLAND INC | DAMAGE WAS INITIATED BY ACTIONS OF A SEWER CONTRACTOR APPROXIMATELY 10 YEARSAGO. COLUMBIA GAS OF MARYLAND, INC. IS THE OWNER AND OPERATOR OF A 2-INCH STEEL GAS MAIN (90 PSIG MAOP) ALONG STATE ROUTE 36 IN THE VILLAGE OF LONACONING, MARYLAND. THE NATURAL GA | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1613 | 1994-01-20 | OH | other |  | COLUMBIA GAS OF OHIO INC | GROUND FREEZING AND CONTRACTION OF PIPE PUT PULL-OUT STRESS ON COMPRESSION FITTING AT TOP OF METER RISER. PULL-OUT STRESS WAS INDUCED DUE TO EXTREME COLDTEMPERATURES (-22). THE ONE-INCH PLASTIC SERVICE LINE SEPARATED AT THE COMPRESSION NUT AND AT THE OPPO | 200000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1614 | 1994-02-14 | NJ | other |  | ELIZABETHTOWN GAS CO | LEAKING GAS FROM CRACKED MAIN, APPARENTLY CAUSED BY THE WEATHER. | 300000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1615 | 1994-02-03 | CO | other |  | GREELEY GAS CO | A LEAK CALL FROM 704 LINCOLN AVENUE WAS RECEIVED AT 12:10 P.M. A SERVICE MANWAS DISPATCHED AND GAS WAS DETECTED AT THE LEAK CALL SITE. WHILE THE BUILDING WAS BEING EVACUATED, THE FIRE WAS REPORTED AT 442 LINCOLN AVENUE UPON FURTHER INVESTIGATION NATURAL G | 1500000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1616 | 1994-01-28 | PA | other |  | PHILADELPHIA GAS WORKS | TED BY THE PHILADELPHIA FIRE DEPARTMENT AND ARE ATTRIBUTED TO A CIRCUMFERENTIAL BREAK ON A 6" CAST IRON GAS MAIN AT 148'6" EAST CURB LINE OF MANSFIELD STREET AND 7'6" SOUTH OF THE SOUTH CURB LINE OF SLOCUM STREET. THIS ALLOWED NATURAL GAS TO MIGRATE INTO | 4000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1617 | 1994-01-23 | PA | other |  | PHILADELPHIA GAS WORKS | THE FACTORS CONTRIBUTING TO THIS INCIDENT WERE UNDER INVESTIGATION BY THE PHILADELPHIA FIRE DEPARTMENT. THE INVESTIGATION CONCLUDED THAT THERE WAS A CIRCUMFERENTIAL BREAK ON A 6" CAST IRON GAS MAIN IN FRONT OF 4203 N. 9TH STREET (41'8" NNC HUNTING PARKS A | 240000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1618 | 1994-02-22 | MS | other |  | MISSISSIPPI VALLEY GAS | DAMAGE TO MAIN SUPPLYING GAS TO MOUND BAYOU CAUSED LOSS OF PRESSURE ON THE DISTRIBUTION SYSTEM. THE MAJOR PORTION OF THE DAMAGE COST WAS TURNING OFF CUSTOMER'S SERVICE AND RELIGHTING AFTER THE MAIN WAS REPAIRED. PART 3 - ELECTRIC UTILITY COMPANY, DRILLING | 20000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1619 | 1994-02-02 | CO | other | NORMAC | PUBLIC SERVICE CO OF COLORADO | PART 3- A COMPRESSION COUPLING CONNECTING PVI TO STEEL SLIPPED OFF THE PVC. | 25000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1620 | 1994-02-17 | OK | technical failure |  | OKLAHOMA NATURAL GAS CO | PLASTIC PIPE WAS NOT GROUNDED AND STATIC ELECTRICAL DISCHARGE COULD HAVE BEEN THE IGNITION SOURCE. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1621 | 1994-02-09 | MI | other | DRESSER | SOUTHEASTERN MICHIGAN GAS CO | CONTRACTOR HIT AND BROKE 2" RISER PIPE AT METER SET. | 30000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1622 | 1994-02-10 | MI | other | DRESSER | SOUTHEASTERN MICHIGAN GAS CO | NATURAL GAS EXPLOSION WAS CAUSED BY FROST HEAVING ON SERVICE LINE. | 20000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1623 | 1994-02-19 | NY | technical failure | DRISCO | NIAGARA MOHAWK POWER CORP | SUPPLEMENTAL REPORT 4/8/1994 INDICATES AT APPROX. 12:30PM. A GAS FIRE ERUPTEDDURING A SQUEEZE OFF OPERATION ON A 6INCH PLASTIC MAIN; THE MAIN WAS LEAKINGDUE TO BREAKAGE OF A PLASTIC FUSION JOINT. THE ENSUING FIRE CAUSEDSECOND-DEGREE BURNS TO TWO EMPLOYEES | 52000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1624 | 1994-03-14 | LA | other |  | NEW ORLEANS PUBLIC SERVICE INC |  | 75000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1625 | 1994-02-17 | IL | other |  | NORTHERN ILLINOIS GAS CO | MAIN DAMAGED BY OUTSIDE FORCE CAUSING PIPE STRESSES THAT LEAD TO PIPE FAILURE | 90000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1626 | 1994-02-02 | TX | other |  | SOUTHERN UNION GAS CO |  | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1627 | 1994-02-28 | CO | other | SPRAGUE MTR,ECONOMY REG,DRESSER,CAP. UN. | PUBLIC SERVICE CO OF COLORADO | FIRE ON STRUCTURE DAMAGED PUBLIC SERVICE COMPANY FACILITIES AT STRUCTURE. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1628 | 1994-03-04 | IN | other | UPONOR | INDIANA GAS CO INC | A 1" PLASTIC SERVICE TO 117 BLUE RIVER ROAD, IN EDINBURG, JOHNSON COUNTY, INDIANA, WAS MISLOCATED. LOCATOR LOCATED RETIRED 3/4" STEEL SERVICE THAT RAN PARALLEL AND 3" NORTH OF LIVE PLASTIC SERVICE. THE ESTIMATED DAMAGE OF $78,000 CONSISTED OF; DAMAGE TO T | 78000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1629 | 1994-03-22 | NE | technical failure | LTB STEEL TUBULAR PROD. CO | METROPOLITAN UTILITIES DISTRICT | EXIST. 12" 125# MAIN REQUIRED RELOCATION FOR SEWER CONST. NEW SEGMENT INSTALLED & PRESSURE TESTED-OK. NEW SEGMENT CONNECTED TO EXIST MAIN W/OFFSET OF 2-90 BENOS & COMPRESION CPLG'S. OFFSETS BLOCKED, MAIN PURGED OF AIR & BROUGHT UPTO 15 PSIG. WELDER STARTE | 3000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1630 | 1994-02-10 | NJ | other |  | NEW JERSEY NATURAL GAS CO |  | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1631 | 1994-03-03 | LA | other |  | BERWICK, TOWN OF |  | 32000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1632 | 1994-01-13 | AK | other | DRISCO PIPE | BARROW UTILITIES & ELECTRIC CORP | AT APPROXIMATELY 2:39 A.M. ON FEBRUARY 10, 1994, NEW JERSEY NATURAL GASCOMPANY (NJNG) RECEIVED A TELEPHONE REPORT OF AN EXPLOSION FROM THE SHIPBOTTOMPLOICE DEPARTMENT. AN NJNG SERVICEMAN ARRIVED ON THE SCENE AT 3:30 A.M.AND FOUND THE BUILDING DESTROYED AN | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1633 | 1994-01-15 | IL | other |  | NORTH SHORE GAS CO | A CIRCUMFERENTIAL CRACK IN 4-INCH CATHODICALLY PROTECTED STEEL PIPE LEAKED CAUSING GAS TO MIGRATE UNDERGROUND TO THE BUILDING. GAS IGNITED BY UNKNOWN CAUSE. CAUSE OF CRACK UNKNOWN AT THIS TIME. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1634 | 1994-01-15 | MA | other |  | BAY STATE GAS CO | THE FRACTURE WAS A 16" MIXING CHAMBER AS IT ENTERS OUR 12" DISTRIBUTION SYSTEM. IT OCCURRED SHORTLY AFTER STARTING UP THE PORTABLE LNG VAPORIZER. THERE IS SOME EVIDENCE OF COLD GAS CARRY OVER. WE DO NOT KNOW IF IT OCCURRED BEFOREOR AFTER THE FRACTURE. THE | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1635 | 1994-01-21 | IL | other |  | ILLINOIS POWER CO | AT 8:32 A.M. ON JANUARY 21, 1994, ILLINOIS POWER WAS NOTIFIED OF A FIRE AND WXPLOSION AT 127 COOPER AVENUE, EAST ALTON, ILLINOIS. UPON ARRIVAL AT THE SCENE, IT WAS NOTED THAT AN EXPLOSION HAD OCCURRED AND THE RISER WAS BROKEN "FUELING THE FIRE". AN INVEST | 150000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1636 | 1994-01-26 | PA | other | ROCKWELL | NATIONAL FUEL GAS DISTRIBUTION CORP | A PRESSURE REDUCING REGULATOR IN A GAS SUPPLY REGULATOR STATION FAILED IN THEOPEN POSITION ACTIVATING THE PRESSURE RELIEF VALVE AT THE STATION. THE SUBSEQUENT CLOSED FAILURE OF THIS PRESSURE RELIEF VALVE OVER-PRESSURED THE DOWNSTREAM GAS DISTRIBUTION SYST | 35000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1637 | 1994-01-23 | PA | maintenance |  | PHILADELPHIA ELECTRIC CO | CORRODED SERVICE AT 2289 WAS A PROBABLE CONTRIBUTOR TO THE FIRE. A CRACKED MAIN AND LEAKING GAS SERVICE CAUSED GAS TO MIGRATE UNDER THE PAVEMENT AND INTOTHE HOME AT 2289 MULBERRY. THE GAS BUILT UP BEHIND AN ELECTRIC DRYER LOCATEDIN THE BASEMENT. WHILE THE | 200000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1638 | 1994-01-17 | CA | other |  | SOUTHERN CALIFORNIA GAS CO | ON JANUARY 17, 1994, AT 0431 HOURS, AN EARTHQUAKE WITH A RICHTER SCALE MAGNITUDE OF 6.7 HIT THE SOUTHERN CALIFORNIA AREA. THE AREAS MOST SEVERELY IMPACTED IN SOUTHERN CALIFORNIA GAS COMPANY SERVICE TERRITORY WERE THE AREAS OF NORTHRIDGE, VALENCIA, SIMI VA | 30000000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1639 | 1994-01-12 | IN | other |  | CITIZENS GAS & COKE UTILITY | 16" CAST IRON MAIN BROKE ALLOWING GAS TO MIGRATE INTO THE BUILDING. THE GAS WAS IGNITED BY AN UNKNOWN SOURCE CAUSING THE BUILDING TO EXPLODE, BLOWING OUTSEVERAL WINDOWS AND CAUSING EXTENSIVE FIRE DAMAGE. ONE EMPLOYEE OF THE WAREHOUSE WAS SEVERELY BURNED. | 30000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1640 | 1994-03-26 | CA | other |  | PACIFIC GAS & ELECTRIC CO | U.S.A. INFORMATION DOES NOT APPLY DUE TO NATURE OF INCIDENT. SEE PART 3 DESCRIPTION. AUTOMOBILE STRUCK METER SET AND IGNITED. FIRE SPREAD TO RESIDENCE. | 30000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1641 | 1994-03-20 | LA | maintenance |  | NEW ORLEANS PUBLIC SERVICE INC |  | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1642 | 1994-03-22 | CA | technical failure |  | PALO ALTO, CITY OF |  | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1643 | 1994-04-05 | VA | ACCIDENTALLY CAUSED BY OPERATOR |  | VIRGINIA NATURAL GAS |  | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1644 | 1994-04-02 | PA | other |  | UNION GAS CO | UNDETERMINED AND UNDER INVESTIGATION. SUPPLEMENTAL REPORT 1/19/95 INDICATESTHE FOLLOWING: UNION GAS CO, PITTSTON DISTRICT ON APRIL 2, 1994, CONDUCTED AHOUSE TO HOUSE INVESTIGATION INSIDE THE BASEMENTS, FIRST FLOORS, AND SECONDFLOORS OF THE HOMES IN THE 30 | 200000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1645 | 1994-04-11 | MO | other | CONTINENTAL INDUSTRIAL | LACLEDE GAS CO | THE AREA SURROUNDING THE SERVICE TEE HAD BEEN EXCAVATED ON AUGUST 2,1993, BYSOUTHWSTERN BELL TELEPHONE COMPANY OR THEIR SUBCONTRACTOR TO EXPOSE HE TELEPHONE CABLES THAT HAD BEEN INSTALLED IN THE SAME TRENCH WITH THE GAS MAIN AND SERVICE LINE. THE GAS MAIN | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1646 | 1994-04-09 | IA | other |  | PEOPLES NATURAL GAS | FIRE IN GARAGE BELIEVED TO HAVEE BEEN CAUSED BY GASOLINE LEAK FROM AUTOMOBILE(PER FIRE MARSHALL). | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1647 | 1994-04-23 | IL | ACCIDENTALLY CAUSED BY OPERATOR | PLEXCO PE 2406 | MORTON MUNICIPAL GAS UTILITY, CITY OF | 2" PE GAS MAIN STRUCK BY UTILITY OWNED BACKHOE AND EMPLOYEES. AT APPROXIMATELY 08:15 AM ON PRIL 23, 1994, MORTON UTILITY GAS & WATER DISTRIBUTION CREWS, STRUCK A 2 IN. PE 2406 GAS MAIN WHILE ATTEMPTING TO REPAIR A WATER LEAK THAT WAS LOCATED BELOW THE GAS | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1648 | 1994-02-25 | IA | other |  | PEOPLES NATURAL GAS |  | 110000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1649 | 1994-05-18 | MD | technical failure |  | WASHINGTON GAS | GAS DISTRIBUTION CONTRACTOR TAPED A LOW PRESSURE CUSTOMER-OWNED UNDERGROUND HOUSELINE AND INTRODUCED HIGH PRESSURE. THE GAS WAS CONTROLLED IMMEDIATELY. THERE WERE NO INJURIES. DAMAGE WAS LIMITED TO 34 GAS RANGES AND MINOR PAINT DAMAGE IN A FEW APARTMENTS. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1650 | 1994-05-18 | AR | ACCIDENTALLY CAUSED BY OPERATOR |  | ARKANSAS LOUISIANA GAS CO (ARKLA GAS CO) | AGENT FOR OPERATOR ACCIDENTLY CUT & IGNITED 2" PLASTIC WHILE REMOVING ABANDONED LINE. 16" CI BROKE DUE TO EXPOSURE TO HEAT . | 75000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1651 | 1994-05-18 | OK | other |  | OKLAHOMA NATURAL GAS CO | DEPTH OF GAS LINE RELATIVE TO DEPTH OF STREET REPAIR WAS NOT DETERMINED BUT LINE WAS LOCATED IN A PLAN VIEW. STREET REPAIR MACHINE CUT DEEPER THAN EXPECTED AND STRUCK THE PIPE DURING PREPARATION FOR RESURFACING. OPERATOR KILLED THE ENGINE AND LEFT THE MAC | 150000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1652 | 1994-05-11 | NJ | other | DRISCOPIPE | PUBLIC SERVICE ELECTRIC & GAS CO | ON 04/11/1994 AT APPROXIMATELY 8:11 A.M. A 2" PLASTIC 15 PSI DESIGN GAS SERVICE TO #7301 RIVER ROAD, NORTH BERGEN WAS DAMAGED BY JAF EQUIPMENT INC. OF 88FOREST WAY, ESSEX FELLS, N.J. 07021, WHILE EXCAVATING WITH A VERMEER WHEEL TO INSTALL A SEWER LINE. ES | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1653 | 1994-04-12 | IL | technical failure |  | CENTRAL ILLINOIS PUBLIC SERVICE | A LEAKING WELD WAS FOUND APPROXIMATELY 70 FEET FROM THE BUILDING WHERE THE EXPLOSION OCCURED. AN ONGOING INVESTIGATION IS BEING CONDUCTED TO DETERMINE IFTHIS WAS A CONTRIBUTING FACTOR. PRELIMINARY FINDINGS INDIATE ABNORMALLY HIGHCONCENTRATION OF NATURALLY | 20000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1654 | 1994-02-06 | TX | other | DUPONT | ENTEX - DIVISION OF ARKLA INC | ELECTRICAL CONTRACTOR WAS TRENCHING AND HIT 2" PLASTIC MAIN LINE IN UTILITY EASEMENT, GAS IGNITED RESULTING IN LOSS OF ADJACENT HOME UNDER CONSTRUCTION. (APPROX. 60% COMPLETE) NO REQUEST WAS MADE FOR A LINE LOCATION. PART B - STAKED WITH FLAGS WHEN INSTAL | 81786 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1655 | 1994-04-13 | CA | other | SINGER/ROCKWELL | PACIFIC GAS & ELECTRIC CO | LOW PRESSURE REGULATOR AND SECURITY VALVE FAILED, THUS OVERPRESSURIZING THEALAMEDA LOW PRESSURE SYSTEM. LOW PRESSURE REGULATOR AND SECURITY VALVE FAILED AND OVERPRESSUED THE SYSTEM. | 3600000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1656 | 1994-04-08 | TX | other | UPONOR | ENTEX - DIVISION OF ARKLA INC | PIPE RUPTURED AND THE GAS IGNITED. THE TWO INCH PIPE RUPTURED AT THE SQUEEZER AND IGNITED, BURNING ONE EMPLOYEE ON HIS HANDS AND FACE. THIS EMPLOYEE WAS ABLE TO REPORT TO WORK THE NEXT WORK DAY. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1657 | 1994-04-14 | MI | technical failure |  | MICHIGAN CONSOLIDATED GAS CO (MICHCON) | OPERATOR FAILED TO PROPERLY LOCATE PIPELINE BEFORE FINAL SERVICE LINE TIE-ININSTALLATION AND MISTAKENLY TAPPED A HIGH PRESSURE DISTRIBUTION MAIN INSTEADOF THE LOW PRESSURE MAIN. OPERATOR FAILED TO FOLLOW COMPANY STANDARDS WHILE ABADONING THE SERVICE UNTIL | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1658 | 1994-05-18 | GA | other | MAVERICK STEEL | ATLANTA GAS LIGHT CO | REYNOLDS CONSTRUCTION, INC. CUT 6" MHP GAS MAIN WITH A TRACK HOE, WHILE INSTALLING FORCED SEWER MAIN FOR GWINNETT COUNTY. | 41976 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1659 | 1994-05-22 | PA | other |  | COLUMBIA GAS OF PENNSYLVANIA | VEHICLE STRUCK METER RISER. TRUCK DRIVER LOST CONTROL OF RENTAL TRUCK AND THE VEHICLE DRIFTED BACK INTO THE GAS AND ELECTRIC METERS. THE GAS METER WAS SHEARED OFF AT THE METER RISER AND ESCAPING GAS WAS APPARENTLY IGNITED FROM THEARCING DAMAGED ELECTRIC M | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1660 | 1994-05-27 | NE | other |  | PEOPLES NATURAL GAS | FAULTY TAR HEATER. FIRE IS NOT NATURAL GAS RELATED. PART 2 FAILURE OF TAR HEATER. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1661 | 1994-06-03 | CA | other | STAUFFER | SOUTHWEST GAS CORP | PIPE WAS DAMAGED BY TREE ROOT GROWTH WHICH BOWED THE PIPE UP FROM ON ROOT AND DOWN FROM ANOTHER. THIS CAUSED A CRACK IN THE PIPE. ESCAPING GAS MIGRATED TO 910 WEST COUNTRY CLUB WHERE THE EXPLOSION AND FIRE OCCURRED. BIG BEAR CITY FIRE DEPARTMENT EXTINGUIS | 90000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1662 | 1994-04-20 | OH | other |  | EAST OHIO GAS CO | DURING A ROUTINE LEAKAGE SURVEY ON THURSDAY, MARCH 31, 1994, A LEAK WAS FOUND AT THE NORTH SIDE OF LAKESHORE BLVD., AND THE EAST SIDE OVERLOOK PARK DRIVE, IN CLEVELAND, OHIO. THIS LEAK WAS DETERMINED TO BE A CLASS 11 LEAK, MEANINGTHAT REPAIR OR RECLASSIFI | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1663 | 1994-04-23 | IL | other |  | NORTHERN ILLINOIS GAS CO | A FIRE CAUSING DAMAGE TO A FOUR UNIT CONDOMINIUM STARTED ON THE OUTSIDE OF THE STRUCTURE NEAR OUR SERVICE RISER. INVESTIGATION OF THE SERVICE MATERIAL AFTER THE INCIDENT REVEALED THE PLASTIC AND ALUMINUM HAD MELTED. SOURCE OF FIREAND IGNITION IS UNKNOWN. | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1664 | 1994-06-20 | TX | other |  | ARKANSAS LOUISIANA GAS CO (ARKLA GAS CO) | COPPER TUBING LINE SERVING RANGE TOP WAS DISCONNECTED AND UNCAPPED. | 10000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1665 | 1994-06-17 | NY | ACCIDENTALLY CAUSED BY OPERATOR |  | LONG ISLAND LIGHTING COMPANY | THE DEPARTMENT OF TRANSPORTATION BASED UPON PRELIMINARY INFORMATION RECEIVEDFROM THE FIELD AT THE TIME OF THE INCIDENT. THIS INFORMATION INDICATED THAT TWO (2) LILCO EMPLOYEES (WHO WERE IN THE PROCESS OF REPAIRING A CUSTOMER OWNED UNIT HEATER) HAD RECEIVE | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1666 | 1993-06-16 | MI | other |  | MICHIGAN CONSOLIDATED GAS CO (MICHCON) |  | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1667 | 1994-05-02 | MI | ACCIDENTALLY CAUSED BY OPERATOR | FISHER | MICHIGAN CONSOLIDATED GAS CO (MICHCON) | FIELD EMPLOYEES WERE PERFORMING MAINTENANCE ON A REGULATOR IN A VAULT SUPPLYING GAS TO APPROXIMATELY 800 CUSTOMERS. TWO EMPLOYEES WERE IN THE VAULT WHEN A SUDDEN RELEASE OF GAS FILLED THE VAULT. THE TWO EMPLOYEES VACATED THE VAULTWITH THE ASSISTANCE FROM | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1668 | 1994-06-24 | UT | other |  | MOUNTAIN FUEL SUPPLY CO | ON JUNE 24, 1994, A PRIVATE CONTRACTOR INSTALLING A WATER LINE IN THE MIDDLEOF WEST TEMPLE STREET, SALT LAKE CITY, UTAH, HIT A 3/4" STEEL SERVICE LINE DURING EXCAVATION. THIS CAUSED THE SERVICE LINE TO BE PULLED OUT OF A COMPRESSION COUPLING WHERE THE SER | 80000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1669 | 1994-05-23 | ND | other |  | MONTANA - DAKOTA UTILITIES CO | AN AUTOMOBILE WENT OUT OF CONTROL, LEFT THE HIGHWAY STRIKING A REGULATOR STATION BARRIER. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1670 | 1994-06-15 | CA | other | DUPONT | PACIFIC GAS & ELECTRIC CO | AT 6:19 A.M. ON WEDNESDAY, JUNE 15, 1994, PG&E WAS NOTIFIED BY THE CALIFORNIA DIVISION OF FORESTRY (CDF) OF A HOUSE EXPLOSION AND FIRE AT "10635 SILVER WAY" (NOTE: THE ACTUAL ADDRESS TURNED OUT TO BE 11058 COLFAX HIGHWAY)., GRASS VALLEY, NEVADA COUNTY. A | 48000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1671 | 1994-06-23 | RI | maintenance |  | PROVIDENCE GAS CO | A CORROSION HOLE WAS DISCOVERED ON THE UNDERSIDE OF THE SERVICE LINE, INSIDETHE BASEMENT, APPROXIMATELY ONE-HALF INCH FROM THE WALL. POSSIBLE SOURCE OF IGNITION MAY HAVE BEEN THE OIL BURNER IN THE CELLAR. THERE WAS NO RECORD OF THIS SERVICE LINE OR ANY CU | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1672 | 1994-03-22 | PA | other |  | U G I CORP | TED IN THE 00 BLOCK OF S. 24TH ST. IN ALLENTOWN LEHIGH COUNTY, PA MIGRATED INTO THE CORNER PROPERTY AT 2349 READING ROAD. THE GAS WAS SUBSQUENTLY IGNITEDBY AN UNKNOWN SOURCE CAUSING A LOW LEVEL EXPLOSION AND BRIEF FLASH FIRE. THERE WERE NO FATALITIES OR I | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1673 | 1994-06-09 | PA | other |  | U G I CORP |  | 2000000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1674 | 1994-06-24 | DC | other | UPONOR | WASHINGTON GAS LIGHT CO | WHILE GRADING A PARKING LOT DRIVEWAY, D&J EXCAVATING, WHO WAS WORKING FOR GOLDIN STAFFORD, ACCIDENTALLY HIT AND TORE OFF A 3" X 4" PIECE OF THE TOP OF THE 4" PLASTIC MAIN AND PUNCTURED THE SIDE WITH A SLIT 2" X1". THIS RELEASED GAS TO THE ATMOSPHERE. AS A | 1560 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1675 | 1993-06-09 | NJ | other |  | NEW JERSEY NATURAL GAS CO |  | 160000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1676 | 1993-03-03 | WV | other |  | SOUTHERN PUBLIC SERVICE CO |  | 30000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1677 | 1994-07-06 | MD | technical failure |  | WASHINGTON GAS LIGHT CO |  | 64000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1678 | 1994-07-05 | VT | other |  | VERMONT GAS SYSTEMS INC |  | 90000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1679 | 1994-04-25 | TX | other | DUPONT | ENTEX - DIVISION OF ARKLA INC |  | 60000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1680 | 1994-08-02 | MA | ACCIDENTALLY CAUSED BY OPERATOR |  | BAY STATE GAS CO |  | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1681 | 1994-07-13 | CA | ACCIDENTALLY CAUSED BY OPERATOR | UPINOR | SOUTHERN CALIFORNIA GAS CO |  | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1682 | 1994-08-12 | CA | ACCIDENTALLY CAUSED BY OPERATOR | PLEXCO | SAN DIEGO GAS & ELECTRIC CO | ON FRIDAY, AUGUST 12, 1994 AT APPROXIMATELY 10:30 A.M. DURING PURGING OPERATIONS NATURAL GAS FROM A POLYETHYLENE (PE) PIPE IGNITIED ON A CONSTRUCTION SITE ON MIRAMAR ROAD. THE RELIEF FOREMAN, BILL DIMMOCK, WAS BURNED ON HIS ARMS, FACE AND NECK AND TAKEN T | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1683 | 1994-08-24 | NJ | technical failure |  | SOUTH JERSEY GAS CO | LNG TANK TRUCK OPERATOR FAILED TO PROPERLY SECURE CONNECTOR HOSE TO THE TANKER EXIT PORT WHILE OFFLOADING LNG. LNG SPILLED AND VAPORIZED FROM/AT THE LOOSECONNECTION. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1684 | 1994-08-01 | CO | other | AMERICAN | PUBLIC SERVICE CO OF COLORADO | STRUCTURAL FIRE IN THE GARAGE MELTED GAS METER IN GARAGE. ORIGINAL CAUSE OF FIRE UNKNOWN. INSIDE STRUCTURE FIRE MELTED THE GAS METER. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1685 | 1994-07-28 | NY | other |  | CENTRAL HUDSON GAS & ELECTRIC CORP | ON JULY 28, 1994, A GAS MECHANIC, ALONG WITH TWO PROFESSIONAL ENGINEERS, TWOCONTRACT WELDERS, A GAS FORMAN AND A SECOND GAS MECHANIC, WAS WORKING ON A3000 GALLON ABOVE GROUND BULK ODORANT TANK CONTAINING TERTIARY BUTYLMERCAPTAN. THIS WORK WAS PERFORMED AT | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1686 | 1994-07-13 | MO | other |  | MISSOURI PUBLIC SERVICE CO | ON JULY 13, 1994 AT APPROXIMATELY 6:45 PM, A BARGE OPERATED BY CANTON TOWINGSTRUCK A NATURAL GAS PIPELINE OWNED BY MISSOURI PUBLIC SERVICE COMPANY. THE BARGE WAS TRAVELING EAST BOUND ON THE MISSOURI RIVER TOWARDS THE HIGHWAY 13 BRIDGE AT LEXINGTON, MO. TH | 200000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1687 | 1994-07-19 | OH | other | UPONOR ALDYL A | COLUMBIA GAS OF OHIO INC | OUPS LOCATED REQUEST TO OTHER UTILITIES PLACED ON 07/12/1994 AT 1502 HOURS BY MAINTENANCE UNLIMITED. A COLUMBIA GAS OF OHIO CONTRACTOR, MAINTENANCE UNLIMITED, INC., WAS INSTALLING A NEW SERVICE TAP ON A 2-INCH DIAMETER PLASTIC MEDIUM PRESSURE (32 PSIG) MA | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1688 | 1994-08-10 | LA | other | ROCKWELL | TERREBONNE PARISH CONSOLIDATED GOVERNMENT | X-RAY OF REGULATOR SHOWS LINKAGE DISCONNECTED FROM DIAPHRAGM CONTROL ARM. X-RAY INDICATES REGULTOR ARM TO BE DISCONNECTED FROM DIAPHRAGM CONTROL LINKAGE.CAUSE IS UNKNOWN AT THIS TIME, AND WE ARE CURRENTLY INVESTIGATING THE CAUSE OF THE REGULATOR FAILURE. | 65000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1689 | 1993-03-25 | CT | other |  | SOUTHERN CONNECTICUT GAS CO | A CIRCUMFERENCIAL CRACK WAS FOUND ON THE EAST SIDE OF A 4" BY 1 1/4" TAPPINGSLEEVE INSTALLED ON NOVEMBER 21, 1931, WHEN THE 1 1/4" SERVICE TO 84 FIRST STREET, HAMDEN, CT, WAS INSTALLED. | 250000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1690 | 1993-06-10 | CT | other |  | SOUTHERN CONNECTICUT GAS CO | AS PART OF A DWELLING REHABILITATION, A THIRD PARTY REMOVED A SECTION OF A LIVE SERVICE AND LEFT IT UNCAPPED. ESCAPING GAS WAS APPARENTLY IGNITED BY A GAS HOT WATER HEATER AND AN EXPLOSION RESULTED. | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1691 | 1994-10-18 | PA | technical failure | PLEXCO | NORTH PENN GAS CO | SQUEEZE TOOL FAILURE CAUSING RELEASE OF NATURAL GAS, DURING TIE IN OPERATION,IGNITION OF PRODUCT CAUSING FLASH FIRE, INJURING EMPLOYEES AT WORK SITE.SUBSEQUENT INVESTIGATION RECLASSIFIED APPARENT CAUSE - PART 2 - AS "C"CONSTRUCTION/OPERATING ERROR. ALSO R | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1692 | 1994-09-28 | NY | other | UNAVAILABLE | NEW YORK STATE ELECTRIC & GAS CORP | APPARENT CONTRACTOR NEGILIGENCE. | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1693 | 1994-09-26 | CO | other | PLEXCO | PUBLIC SERVICE CO OF COLORADO | A. 75" PED SVC TEE CAP CRACKED COMPLETELY ALONG THE TOP EDGE OF CAP, ALLOWINGGAS TO ESCAPE AND ENTER THE WATER SERVICE DITCH. THIS WAS A 0.75" PEDSERVICE ON A 1.25" PED MAIN. | 125000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1694 | 1994-10-17 | TX | other |  | ONALASKA, CITY OF | TOTAL WASHOUT OF APPROXIMATELY 220' ABOVEGROUND STEEL PIPE ACROSS BRUSHY CREEK IN POLK COUNTY, TEXAS.AREA RECEIVED APPROX. 15 INCHES OF RAIN CAUSING CREEK FLOODING, WASHING OUT. | 21894 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1695 | 1994-10-12 | IA | other |  | IOWA - ILLINOIS GAS & ELECTRIC CO | AT APPROXIMATELY 12:45 AM, OCTOBER 12, 1994, THE RRESIDENT OF 1267 ELMHURST DRIVE NE HIT THE GAS METER INSTALLATION AT HIS HOME WHEN THE BRAKES ON HIS CAR FAILED. THE IMPACT BROKE THE SERVICE RISER ON THE UPSTREAM SIDE OF THE SERVICE TERMINATION VALVE REL | 60000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1696 | 1994-10-15 | PA | other | ROCKWELL | COLUMBIA GAS OF PENNSYLVANIA | ON OCTOBER 15, 1994 AT 6:20 P.M., MR. ERNEST MILLER, AGE 84 BACKED HIS VEHICLE INTO A RESIDENTIAL METER/REGULATOR SET WHICH RESULTED IN THE RELEASE AND IGNITION OF NATURAL GAS. THE VEHICLE CAUGHT FIRE. MR. MILLER WAS ABLE TO EXIT THE VEHICLE; HOWEVER, HE | 3000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1697 | 1994-10-14 | OH | other | APPALACHIAN GAS TUBING | COLUMBIA GAS OF OHIO INC | ON 10/14/1994 A FIRE OCCURRED IN THE ATTACHED GARAGE OF AN APARTMENT AT 2950MALLARD MEADOWS, COLUMBUS, OHIO. DAMAGES TO THE GARAGE THE APARTMENT AND THREE MOTOR CYCLES ARE ESTIMATED AT APPROXIMATELY $50,000. A VERY SMALL LEAK WASFOUND ON THE CUSTOMER OWNE | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1698 | 1994-10-25 | LA | other |  | ARKANSAS LOUISIANA GAS CO (ARKLA GAS CO) | THIRD PARTY CONTRACTOR WAS CLEANING R-O-W AND HIT LINE. CONTRACTOR LOCATION REQUEST WAS NOT FOR THIS LOCATION.THIRD PARTY DAMAGE. | 4800 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1699 | 1994-10-07 | NE | other | UNKNOWN | PEOPLES NATURAL GAS | BACKHOE INSTALLING STORM SEWER HIT 1 1/4INCH SERVICE LINE. NO LOCATE REQUESTED. SERVICE LINE WAS PULLED AWAY FROM METER. | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1700 | 1994-09-15 | MI | other |  | MICHIGAN GAS CO | INVESTIGATING OF FIRE AND EXPLOSION AT ABOVE ADDRESS IS STILL UNDER INVESTIGATION. COMPLETE REPORT WILL FOLLOW. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1701 | 1994-11-07 | TN | other | CLAN & SONS | KNOXVILLE UTILITIES BOARD | UPON THE COMPLETION OF THE REPAIR THE EFFECTED SECTION OF 6-INCH CIMJ PIPE WAS EXAMINED. NO EVIDENCE OF PITTING OR GRAPHITIZATION WAS FOUND.FULL CIRCLE BREAK APPARENTLY DUE TO EARTH MOVEMENT, MIGRATED TO STRUCTURE VIA SEWER DRAIN FIELD CAPPED BY ASPHALT D | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1702 | 1994-10-17 | IA | other |  | MIDWEST GAS - DIV OF IOWA PUBLIC SERVICE CO | BY N.T.S.B WE HAVE BEEN ASKED BY N.T.S.B NOT TO SPECULATE AS TO CAUSE. WE WILL FILE A SUPPLEMENTAL REPORT AS SOON AS N.T.S.B. ISSUES THEIR OPINION. MWG HAS DISCOVERED A BREAK IN A PLASTIC SERVICE LINE AT THE TEE TO A STEEL MAIN. THE SERVICE LINE SERVED TH | 250000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1703 | 1994-11-07 | WV | other |  | HOPE GAS INC | CONTRACTOR WAS IN THE PROCESS OF TIEING IN REPLACEMENT PIPE. GAS WHICH WAS LEAKING THROUGH A GATE VALVE WAS IGNITED BY AN UNKNOWN SOURCE. TWO MEN WORKINGIN THE DITCH WERE BURNED AND HOSPITALIZED. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1704 | 1994-10-20 | NY | other |  | LONG ISLAND LIGHTING COMPANY | THE LONG ISLAND LIGHTING COMPANY (LILCO) PLACED A TELEPHONIC NOTIFICATION TOTHE DOT BASED UPON PRELIMINARY INFORMATION RECEIVED FROM THE FIELD AT THE TIME OF INCIDENT. THIS INFORMATION INDICATED THAT ONE (1) FATALITY OCCURRED, AND TWO (2) INJURED PERSONS | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1705 | 1994-11-07 | VA | other |  | VIRGINIA NATURAL GAS | OUR DISPATCHER RECEIVED A CALL FROM THE VIRGINIA BEACH FIRE DEPARTMENT REPORTING THAT THERE HAD BEEN AN EXPLOSION AND FIRE AT THIS LOCATION AND A FIFTEENYEAR OLD BOY HAD BEEN KILLED. THE INVESTIGATION INDICATES THAT THE BOY WAS WORKING WITH GASOLINE IN T | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1706 | 1994-11-18 | OH | technical failure | UPONOR ALDYL | COLUMBIA GAS OF OHIO INC | A 2" BUTT FUSION JOINT FAILED, ALLOWING ESCAPING GAS TO ENTER A COLLEGE DORMITORY. GAS WAS IGNITED BY A STUDENT LIGHTING AN INCENSE CANDLE. THE STUDENT SUFFERED SECOND AND/OR THIRD DEGREE BURNS TO UPPER BODY AND UPPER EXTREMITIES. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1707 | 1994-11-19 | KS | other |  | WESTERN RESOURCES, INC | A PVC SERVICE LINE IN THE VICINITY OF THIS RESIDENCE EXPERIENCED A BREAK,POSSIBLY DUE TO SOIL SETTLEMENT, RESULTING IN A LEAK WHICH APPARENTLY MIGRATEDTO THIS STRUCTURE AND WAS IGNITED BY AN UNKNOWN SOURCE. THE IGNITION OF GASRESULTED IN AN EXPLOSION AND | 90000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1708 | 1994-12-12 | MS | other |  | MISSISSIPPI VALLEY GAS | A 2" CAST IRON MAIN, CROSSING UNDERNEATH A DRIVEWAY, DEVELOPED A HAIRLINE CRACK ALLOWING NATURAL GAS TO ESCAPE AND APPARENTLY MIGRATE UNDER THE ADJOINING FOUNDATION OF THE RESIDENCE. GAS THEN ENTERED THE BUILDING THROUGH CRACKS IN THE CONCRETE SLAP TYPE F | 98000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1709 | 1994-11-12 | CA | other | MUELLER | PACIFIC GAS & ELECTRIC CO | THIS INCIDENT OCCURRED AS EMPLOYEES OF A FUMIGATING COMPANY WERE ATTEMPTINGTO SHUT OFF THE GAS SERVICE PRIOR TO FUMIGATING THE RESIDENCE. THE FUMIGATINGCOMPANY EMPLOYEE ATTEMPTED TO CLOSE THE RISER VALVE BY TURNING THE NUT THATHOLDS THE CORE IN PLACE INST | 250000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1710 | 1994-10-28 | CA | other |  | PACIFIC GAS & ELECTRIC CO | A CONTRACTOR INSTALLING NEW GAS DRYERS IN THE LAUNDROMAT BROKE THE HOUSE GASLINE WHICH SUBSEQUENTLY IGNITED AND STARTED A STRUCTURE FIRE. THE GASBUILDING WAS TURNED OFF AT THE METER SET BY THE FIRE DEPARTMENT AND CHECKEDBY THE SERVICEMAN UPON HIS ARRIVAL | 1500000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1711 | 1994-12-10 | NV | other |  | SIERRA PACIFIC POWER CO | ON SATURDAY, DECEMBER 10, 1993, A BACKHOE OPERATOR DIGGING A TRENCH FOR AREPLACEMENT SEWER LINE MADE CONTACT WITH THE 3/4" STEEL SERVICE LINE OWNEDBY SIERRA PACIFIC POWER COMPANY. THE LINE SERVED A SINGLE FAMILY DWELLING.THE LINE WAS PULLED FROM ITS LOCA | 120000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1712 | 1994-11-07 | IL | other |  | IOWA - ILLINOIS GAS & ELECTRIC CO | APPLIANCE CONNECTOR WAS DISCONNECTED ALLOWING GAS TO FLOW INTO STRUCTURE.NATURAL GAS CONNECTION TO STOVE WAS DISCONNECTED ALLOWING GAS TO FILL STRUCTURE.SOURCE OF IGNITION IS UNKNOWN. | 55000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1713 | 1994-12-02 | MD | ACCIDENTALLY CAUSED BY OPERATOR |  | BALTIMORE GAS & ELECTRIC CO | WILLIAM'S CONSTRUCTION COMPANY HAD MADE A MISS UTILITY CALL ON 11/15/1994 THE LOCATION OF THE PIPELINE WAS AGREED UPON. ON A FOLLOW-UP VISIT THE LOCATIONWAS STILL IN AGREEMENT. AT THIS TIME THE GRADING COMPANY WAS INFORMED THE BLOW OFF STAND PIPE WAS ABA | 55000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1714 | 1994-12-10 | NY | other | U.S. STEEL | NIAGARA MOHAWK POWER CORP | FATALITY WAS THE RESULT OF PLANE CRASH. DAMAGED PIPE WAS THE RESULT OF PLANECRASH, WHICH WAS ACCIDENTAL. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1715 | 1994-08-31 | PA | technical failure | UPONOR | PENNSYLVANIA GAS & WATER CO | PURGING AIR OUT OF NEWLY INSTALLED GAS MAIN. GAS IGNITED AS A RESULT OFSTATIC DISCHARGE. COMPANY EMPLOYEE RECEIVED 1ST AND SECOND DEGREE BURNS WHICHREQUIRED IN-PATIENT HOSPITALIZATION. MISPLACED FILES CAUSED THE DELAY OFWRITTEN REPORT. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1716 | 1994-12-21 | KY | technical failure |  | COLUMBIA GAS OF KENTUCKY INC | CREW WAS REBUILDING A DISTRICT REGULATOR STATION. AN EMPLOYEE REMOVED A 2"THREADED RELIEF VALVE WITHOUT CLOSING THE 2"GATE VALVE AT ITS INLET. THERESULTING 5 PSIG OF GAS IGNITED CAUSING FIRST AND SECOND DEGREE BURNS TO THEEMPLOYEE'S FACE AND THIRD DEGREE | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1717 | 1994-12-22 | NJ | other |  | NEW JERSEY NATURAL GAS CO |  | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1718 | 1994-12-28 | FL | other |  | LAKE APOPKA NATURAL GAS DISTRICT | DAMAGED FUEL LINE. AT APPROXIMATELY 1:20 P.M. ON THURSDAY, DECEMBER 22,1994,NEW JERSEY NATURAL GAS COMPANY (NJNG) RECEIVED A REPORT FROM THE SPRINGLAKE HEIGHTS POLICE IN MONMOUTH COUNTY, NEW JERSEY THAT AN EXPLOSION AND FIREHAD OCCURRED IN A TOWNHOUSE AT | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1719 | 1995-01-11 | TX | other |  | LONE STAR GAS CO OF TEXAS, INC | PLUMBER HIT SERVICE LINE WITH DITCHING MACHINE WHILE INSTALLING POOL HEATER AND IGNITED GAS. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1720 | 1994-12-29 | PA | other |  | U G I CORP | A CONTRACTOR WAS EXCAVATING TO INSTALL STORM DRAINS ON HALSTEAD STREET IN SALISBURY TOWNSHIP, LEHIGH COUNTY. THE CONTRACTOR HIT AND PULLED AN UNMARKED SERVICE LATERAL TO 831 EAST FEDERAL STREET. WHILE THE HOUSE'S ADDRESS WAS 831 EAST FEDERAL, BEING A CORN | 122000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1721 | 1995-01-11 | CA | other |  | PACIFIC GAS & ELECTRIC CO | GAS METER AND HOUSE STRUCK BY THIRD-PARTY VEHICLE. METER AND HOUSE WERE LOCATED BEHIND CURB AND FRONT YARD. AUTOMOBILE ACCELERATOR PEDAL STUCK. CAR DROVEACROSS SIDEWALK, LAWN AND FLOWERBED BEFORE STRIKING THE GAS METER SET.THEREFORE, NO ADDITIONAL METER | 150000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1722 | 1995-01-09 | UT | ACCIDENTALLY CAUSED BY OPERATOR |  | MOUNTAIN FUEL SUPPLY CO | DURING ROUTINE INSPECTION OF VALVES CONTAINED IN A SMALL VALVE PIT, LOCATEDAT 800 EAST 300 SOUTH, SALT LAKE CITY, UTAH, ATMOSPHERIC CORROSION WASDETECTED ON A NEEDLE VALVE NIPPLE. AS A COURSE OF CORRECTIVE ACTION, TOELIMINATE THIS ATMOSPHERIC CORROSION, I | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1723 | 1995-01-20 | HI | other | PLEXCO | BHP GAS CO. | GAS WARNING TAPE INSTALLED. THE INCIDENT OCCURRED WHEN A CONTRACTOR PUNCTURED OUR 4-INCH MAIN WHILE EXCAVATING FOR AN ELECTRICAL CONDUIT. THE ESCAPING GAS IGNITED, AND TWO OF THE CONTRACTOR'S EMPLOYEES WERE BURNED WHILE THEY EXITED THE TRENCH. IGNITION SO | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1724 | 1994-12-27 | TX | other | LONE STAR | SOUTHERN UNION GAS CO | SMALL AIRCRAFT CRASHED INTO METER AND REGULATOR STATION. | 49150 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1725 | 1995-01-04 | VA | technical failure | UPENDOUT | WASHINGTON GAS LIGHT CO | TWO WASHINGTON GAS COMPANY EMPLOYEES, WHILE REPLACING STEEL 3/4" GAUGE LINESFAILED TO GUARD AGAINST STATIC DISCHARGE WHILE HANDLING PLASTIC PIPE IN A GASEOUS ATMOSPHERE CAUSING SUBSEQUENT IGNITION. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1726 | 1994-10-07 | TX | other |  | ENTEX - DIVISION OF ARKLA INC | DRIVER LOST CONTROL OF AUTOMOBILE. DRIVER LEFT SCENE. | 85000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1727 | 1995-02-06 | NC | other |  | PUBLIC SERVICE CO OF NORTH CAROLINA | 107 CHATSWORTH WAS MARKED. SERVICE LINE TO 105 SPLIT FROM 107 AND WAS NOTMARKED. 105 CHATSWORTH HAD BEEN MARKED ON PREVIOUS LOCATE CALL. MARKS HAD BEENBY RAIN. J & L SERVICES CALLED PUBLIC SERVICE DISPATCHER AND REPORTEDA DAMAGED SERVICE AT 114 CHANCELLOR | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1728 | 1995-02-02 | GA | other | DRISCOPIPE | LAWRENCEVILLE, CITY OF | GEORGIA STAT LAW REQUIRES CALL TO THE UPC PRIOR TO DIGGING. ON THURSDAY FEB 2, 1995 AT 3:00 P.M. LAWRENCEVILLE GAS WAS NOTIFIED OF A CUT GAS MAIN AND HOUSEFIRE AT A NEW CONSTRUCTION SITE NEXT DOOR TO 390 TWIN BROOKS WAY IN TWINBROOKS SUBDIVISION. THE 4" P | 65000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1729 | 1995-01-27 | OK | other | TEX TUBE | OKLAHOMA NATURAL GAS CO | STORM SEWER CONTRACTOR EXCAVATED TO A DEPTH BELOW THE ELEVATION OF THE GAS LINE AND THE LINE WAS HIT BY A TRACKHOE. THE GAS LINE HAD BEEN RELOCATED BELOWGRADE TO ACCOMMODATE THE STREET IMPROVEMENT PROJECT. THE LINE HAD BEEN MARKED PRIOR TO THE INCIDENT. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1730 | 1995-01-19 | MD | other | DRISCO 8000 | BALTIMORE GAS & ELECTRIC CO | A FOUR INCH PLASTIC HIGH PRESSURE MAIN RUNNING ALONG THE WEST SIDE OF WESTSUNSHINE WAY, BETWEEN THE CURB AND SIDEWALK, WAS STRUCK AND PENETRATED BY ABORING MACHINE OPERATED BY APOLLO TRENCHING COMPANY AT 10:26, ON 01/19/95.THE STRIKE OCCURRED BETWEEN #88 | 1500000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1731 | 1994-12-14 | MN | other | FISHER | MINNEGASCO INC | FISHER S252-4 SERVICE REGULATOR FAILED IN THE OPEN POSITION WHILE IT WAS BEING PREPARED FOR REPLACEMENT. | 150000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1732 | 1995-02-04 | AZ | other | DUPONT | SOUTHWEST GAS CORP |  | 200000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1733 | 1995-02-15 | PA | other |  | PHILADELPHIA GAS WORKS | NATURAL GAS FROM A DAMAGED MAIN MIGRATED INTO A RESIDENCE AND IGNITED.NATURAL GAS FROM A 3RD PARTY, DAMAGED MAIN, MIGRATED INTO A RESIDENCE. THEHOMEOWNER LIT A CIGARETTE WITH A LIGHTER AND IGNITED THE NATURAL GAS CAUSINGTWO SEPARATE EXPLOSIONS WITHIN THE | 120000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1734 | 1995-02-22 | CA | other |  | PACIFIC GAS & ELECTRIC CO | WHILE GAS USED TO FILL APARTMENT DID IGNITE, CREATING AN EXPLOSION, THE CAUSEOF DEATH IS UNDER INVESTIGATION. THE VICTIM MAY HAVE BEEN DEAD PRIOR TO THEEXPLOSION AND FIRE. IGNITION OF GAS USE TO FILL APARTMENT IN ATTEMPTED SUICIDE. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1735 | 1995-02-28 | IL | other |  | NORTHERN ILLINOIS GAS CO | FIRE AT 1822 PLAINFIELD ROAD (MICHAEL'S RIBS) IN CREST HILL. ARSON INVESTIGATION CURRENTLY UNDERWAY BY STATE FIRE MARSHALL. SERVICE LINE TESTED AT OPERATING PRESSURE WITH NO LEAKS FOUND. MAIN AND SERVICES F.I. ADJACENT TO ADDESS WITH NO GAS FOUND. | 250000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1736 | 1995-02-21 | PA | other | UNKNOWN | U G I CORP | IT APPEARS THAT NATURAL GAS ESCAPING FROM A CRACK IN A 4" CAST IRON MAIN LOCATED IN THE 700 BLOCK OF NORTH 2ND STREET IN ALLENTOWN, LEHIGH COUNTY, MIGRATED INTO THE CORNER PROPERTY AT 191 TILGHMAN ST. THE GAS WAS SUBSEQUENTLY IGNITED BY AN UNKNOWN SOURCE | 170000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1737 | 1995-03-13 | MS | other | MCWANE | MISSISSIPPI VALLEY GAS | THE INDIVIDUAL WAS EXPOSED TO NATURAL GAS FOR APPROXIMATELY TWO MINUTES WHILE ATTEMPTING TO INSTALL A CLAMP ON A 4" CAST IRON MAIN. THE INDIVIDUAL WAS TREATED FOR ASPHYXIATION AND REMAINED IN THE HOSPITAL ONE NIGHT FOR OBSERVATION. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1738 | 1995-02-02 | TX | technical failure | DUPONT | ENTEX - DIVISION OF ARKLA INC | BUTT FUSION JOINT FAILED DURING BACK FILLING OPERATION. GAS COMPANY CONTRACTOR MADE A BAD BUTT FUSION (6"PLASTIC MAIN) WHILE BACK FILLING THE HOLE THE LEAKING GAS WAS IGNITED BY A BACKHOE - THE BACKHOE WAS DESTROYED. | 27127 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1739 | 1994-10-30 | TX | other |  | DUMAS, CITY OF | UNDECIDED CAUSE. DAMAGED BY OUTSIDE FORCES - OTHER - UNKNOWN. | 400000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1740 | 1995-03-14 | UT | other | PHILLIPS | MOUNTAIN FUEL SUPPLY CO | ON MARCH 14, 1995, ICE AND SNOW SLUFFED OFF OF THE ROOF OF THE DEER VALLEYCLUB LOCATED AT 7720 ROYAL STREET PARK CITY, SUMMIT COUNTY,UTAH. THIS ICE ANDSNOW LANDED ON A VERY STEEP SLOPE AND SLID IN A DOWNWARD DIRECTION INTO THESERVICE LINE RISER AND METER | 250000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1741 | 1994-05-05 | OH | other |  | COLUMBIA GAS OF OHIO INC | FOR A LOCATION 25' FROM WHERE THEY EXCAVATED COLUMBIA REPRESENTATIVE SHOWEDUP TO MAKE THE LOCATE BUT WAS INFORMED BY THE REQUESTING PARTY THAT NO EXCAVATION WOULD BE MADE IN THE VICINITY OF OUR FACILITIES. COLUMBUS SOUTHERN POWER(CSP) WAS REPAIRING BURIED | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1742 | 1995-04-05 | NM | other | NATIONAL METER | GAS CO OF NEW MEXICO | METER ASSEMBLY WAS HIT BY A VEHICLE. APRIL 5, 1995, 10:00AM, PNM CUSTOMERSERVICE REPRESENTATIVE JANET MOSIER RECEIVED A TELEPHONE CALL FROM AURORAPADILLA. MS. PADILLA INFORMED MS. MOSIER THAT THER WAS GAS IN THE HOUSELOCATED AT 11 PEACH. MS. MOSIER ASKED | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1743 | 1995-02-21 | WY | other |  | CHEYENNE LIGHT FUEL & POWER | ALTHOUGH THERE WAS A CRACKED WELD, IT HAS NOT BEEN DETERMINED WHETHER IT WASA RESULT OF THE WELD FAILING OR CAUSED BY OUTSIDE FORCES, OTHER SUBSIDENCE OROVERBEARING SOIL CONDITIONS.AT APPROXIMATELY 5:05 A.M., 02/21/1995, A CALLWAS RECEIVED FROM FRONTIER R | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1744 | 1995-04-17 | IN | other | DUPONT | CITIZENS GAS & COKE UTILITY | DESCRIPTION OF INCIDENT: WE RECEIVED A CALL FROM PIKE TOWNSHIP FIRE DEPARTMENT REPORTING THAT WE HAD A GAS LINE ON FIRE AT 8733 LOG RUN NORTH DRIVE. A CONTRACTOR, HAMMER AND NAILS CONSTRUCTION, HAD BEEN USING A GASOLINE POWERED POST HOLE DIGGER WHEN THEY | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1745 | 1995-03-13 | CO | other | PHILLIPS DRISCO | PUBLIC SERVICE CO OF COLORADO | TV CABLE CONTRACTOR WAS MAKING APPROXIMATELY 400' DIRECTIONAL BORE. AFTER COMPLETING PILOT BORE AND CROSSING PUBLIC SERVICE COMPANY'S 1 1/4" GAS MAIN, THIS CONTRACTOR BEGAN TO BACK BORE WITH A CUTTING AUGER AND PULL 2" PLASTIC CONDUIT FOR CABLE. WHEN THE | 1500000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1746 | 1995-03-24 | OH | other |  | OXFORD NATURAL GAS CO |  | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1747 | 1995-04-30 | MS | other |  | WAVELAND WATER & GAS DEPT, CITY OF | THE DRIVER OF A 1975 CAMARO RAN-OFF THE ROAD AND HIT OUR REGULATOR LOCATED AT HWY 603 AND LAGAN STREET. | 8002 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1748 | 1995-05-05 | IL | ACCIDENTALLY CAUSED BY OPERATOR |  | NORTHERN ILLINOIS GAS CO | 2" MAIN DAMAGED BY THIRD PARTY. DURING EXCAVATION TO REPAIR, GAS WAS IGNITED. OPERATOR'S EMPLOYEE SUFFERED FIRST AND SECOND DEGREE BURNS TO FACE AND HANDS | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1749 | 1995-04-23 | MI | other |  | MICHIGAN CONSOLIDATED GAS CO (MICHCON) | CONTRACTOR USING EXCAVATOR PULLED UP SERVICE LINE CAUSING IT TO BREAK AT 90 DEGREE ELL FITTING. | 1000000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1750 | 1995-04-26 | LA | other |  | NEW ORLEANS PUBLIC SERVICE INC | GAS ESCAPED THROUGH A .5" FUEL LINE VALVE IN THE LAUNDRY ROOM. NO APPLIANCE W AS ATTACHED. | 60000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1751 | 1995-05-13 | NJ | other |  | ELIZABETHTOWN GAS CO | MAIN CRACK IN SERVICE CONNECTION/ TAP. ESCAPE OF GAS RESULTING FROM CRACKIN 4" CAST IRON MAIN. | 160000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1752 | 1995-04-23 | MS | maintenance |  | CANTON MUNICIPAL UTILITY | UPON ARRIVAL AT 1:45 AM DEPUTY SPENCER OBSERVED THREE UNITS OF THE CANTON FIREDEPARTMENT ON THE SCENE WITH FIREMEN FIGHTING THE FIRE FROM THE WEST, SOUTH,AND EAST SIDES OF THE BUILDING. DEPUTY SPENCER DISCONNECTED THE ELECTRICALMETER AND OBSERVED THAT THE | 25000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1753 | 1995-05-07 | KS | other | FISHER | WESTERN RESOURCES, INC | A METER SETTING AT 600 CLARK IN EMPORIA, KANSAS, WAS STUCK BY AN AUTOMOBILERESULTING IN DAMAGE TO A PRESSURE REGULATOR WHICH LED TO HIGHER THAN NORMALDELIVERY PRESSURE TO A CUSTOMER-OWNED DISTRIBUTION SYSTEM. | 150000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1754 | 1995-05-16 | TN | other | ROCKWELL | NASHVILLE GAS CO | SECONDARY CAUSATION FROM DAMAGE TO GAS METER AND SUBSEQUENT IGNITION RESULTING FORM LIGHTNING STRIKE TO HOUSE DURING ELECTRICAL STORM. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1755 | 1995-05-20 | OK | other | UNIVERSAL | OKLAHOMA NATURAL GAS CO | THE INCIDENT WAS ON VISIBLE ABOVE GROUND METER SETTING.HOMEOWNER HIT METER AND REGULATOR SETTING WITH CAR RESULTING IN DAMAGE TO REGULATOR CAUSING OVERPRESSURE ON HOUSE PIPING RESULTING IN A FIRE. HOMEOWNER ENTERED HER RESIDENCE THREE TIMES BUT DID NOT CO | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1756 | 1995-05-22 | VA | technical failure | DRISOPIPE 8000 | DANVILLE GAS DEPT | A SIX INCH SERVICE CONNECTION INTO A TWELVE INCH MAIN HAD BEEN MADE. THE LINE WAS BEING PURGED. A SPARK APPARENTLY IGNITED THE PURGING GAS. A FLASH BURNED AN EMPLOYEE WHO WAS LOCATED APPROXIMATELY 25-30 FEET FROM THE PURGING LOCATION. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1757 | 1995-06-03 | CA | other |  | SAN DIEGO GAS & ELECTRIC CO | A 3/4-INCH GAS RISER WAS BROKEN OFF BELOW THE STOP COCK BY VEHICLE CONTACT. THE ESCAPING GAS WAS IGNITED BY AN UNKNOWN IGNITION SOURCE. THE RESULTING FIRE DESTROYED THREE VEHICLES AND A PALM TREE. A FOURTH VEHICLE AND A RETAINING WALL SUFFERED SMOKE DAMAG | 75000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1758 | 1995-05-22 | MI | other | PHILLIPS | CONSUMERS POWER CO | MAINTENANCE WORKER DROVE METAL STAKE INTO GROUND IN FLOWER BED AND PUNCTURED5/8" PLASTIC GAS SERVICE. GAS ENTERED BUILDING THROUGH AN OPEN WINDOW IN THEUTILITY ROOM. POSSIBLE SOURCE OF IGNITION WAS A WATER PUMP. | 80000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1759 | 1995-05-22 | KY | other | INTERLAKE STEEL | LOUISVILLE GAS & ELECTRIC CO | ON 05/22/95 AT APPROXIMATELY 3:00 PM, OUR TROUBLE COMPLAINT DESK BEGAN RECEIVING COMPLAINTS OF GAS OUTAGES IN THE CANE RUN ROAD AND CRUMS LANE AREA. APPROXIMATE TIMES: 3:15 PM - A CREW AND THE AREAL SUPERVISOR WERE DISPATCHED TO THE SCENE. IT SOON BECAME | 60000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1760 | 1995-06-09 | NV | other | UNKNOWN | SIERRA PACIFIC POWER CO | ON JUNE 9, 1995 AT 8:20 A.M. (PST) TW CONSTRUCTION COMPANY, A LOCAL CONTRACTOR, STRUCK AND RUPTURED A 4" STEEL MAIN WHILE EXCAVATING FOR THE INSTALLATIONOF A SEWER LINE AT THE INTERSECTION OF NORTH VIRGINIA STREET AND WEST 5TH STREET IN RENO, NEVADA. AS A | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1761 | 1995-06-21 | LA | other |  | TERREBONNE PARISH CONSOLIDATED GOVERNMENT | GRASS WAS BEING CUT WITH A RIDING LAWNMOWER ON VACANT LOT. LAWNMOWER HIT STEEL RISER AND BROKE OFF AT GROUND LEVEL. LAWNMOWER CAUGHT FIRE AND OPERATOR WAS BURNED. HE WAS TRANSFERRED TO THE HOSPITAL FOR TREATMENT. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1762 | 1995-06-23 | WA | other | RW LYALL | WASHINGTON NATURAL GAS CO | MR. M. PETERMAN, NEIGHBOR, WAS USING A BACKHOE TO CLEAR AND GRADE THE BACK YARD AT 18404 SE 264 PL WHEN HE CAUSED THE MOVEMENT OF 2" X 4" TIMBERS WHICH STRUCK AND DAMAGED OUR METER SET ASSEMBLY. THE SERVICE RISER WAS DAMAGED BELOWTHE SHUT OFF VALVE AND MR | 60000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1763 | 1995-06-24 | NY | other |  | BROOKLYN UNION GAS CO | A SEWER MANHOLE IGNITIED AS CHILDREN WERE PLAYING WITH FIREWORKS AROUND THE MANHOLE. ONE CHILD WAS HOSPITALIZED WITH BURNS. NATURAL GAS, AS WELL AS HEAVYHYDROCARBONS, WERE CONFIRMED TO EXIST WITHIN SAID MANHOLE. A CRACKED 4 INCH CAST IRON MAIN WAS DISCOVE | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1764 | 1995-07-20 | DE | other |  | DELMARVA POWER & LIGHT CO | RECEIVED INFORMATION 8-1-95 THAT ESTIMATED PROPERTY LOSS COULD EXCEED $50,000. BASED ON THAT NEW INFORMATION, TELEPHONIC NOTICE WAS MADE IMMEDIATELY. CONTRACTOR REPRESENTATIVE ADVISED OF LINE LOCATION ON SITE. THE BURIED 12"DIAMETER STEEL NATURAL GAS DI | 60000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1765 | 1995-07-12 | MI | other | PHILLIPS DRISCOPIPE M8000 HDPE | MICHIGAN CONSOLIDATED GAS CO (MICHCON) | INVESTIGATION AND EXTENSIVE LABRATORY TESTING CONFIRMED THE EXISTENCE OFFERMENTATION GAS CONTRIBUTING TO THE INCIDENT. NUMEROUS GROUND/AIR ATMOSPHERICSAMPLES CONFIRMED THE EXISTENCE OF FERMENTATION GAS. THE LABRATORY TESTRESULTS WERE CONVEYED VERBALLY 7/1 | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1766 | 1995-07-19 | CA | other |  | PALO ALTO, CITY OF | ON JULY 19, 1995 AT 3:15 PM, THE CITY OF PALO ALTO GAS CREW SUPERVISOR (MIKEROGERS) RECEIVED A RADIO CALL FROM A PUBLIC WORKS DEPARTMENT INSPECTOR (DONPETERS) THAT A PLASTIC GAS SERVICE, AT 1001 FOREST AVE., HAD BEEN SEVERED ANDHAD IGNITED. THE PALO ALTO | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1767 | 1995-07-16 | TX | other | US STEEL CORP | ARKANSAS LOUISIANA GAS CO (ARKLA GAS CO) | MR. HORACE SONNY LACY WAS MOWING ADJACENT PROPERTY AND HIGHWAY RIGHT-OF-WAY IN THE PROCESS OF MOWING, MR. LACY STRUCK AN ABOVE-GROUND METER SET ASSEMBLY.AT A TIME APPROXIMATING THE TIME OF THE INCIDENT, MR. LACY SUCCUMBED TO A HEART ATTACK. IT IS OUR UNDE | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1768 | 1995-08-01 | NV | other | DRISCO | SOUTHWEST GAS CORP | THIS INCIDENT OCCURRED WHEN A PLUMBER ACCIDENTLY BURNED A SOUTHWEST GAS PLASTIC SERVICE LINE WITH HIS TORCH, WHICH RESULTED IN AN UNCONTROLLED ESCAPE OF NATURAL GAS. FURTHER, THE TORCH CAUSED IGNITION OF THE NATURAL GAS, RESULTINGIN MINOR BURNS TO THE ARM | 400 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1769 | 1995-07-24 | LA | other | UPONOR | NEW ORLEANS PUBLIC SERVICE INC | AFTER COMPLETING THE WRAPPING OF A SERVICE TEE AND TRANSITION FITTING ON ANEWLY INSTALLED POLYETHYLENE SERVICE, OUR CONTRACT EMPLOYEE HEARD GAS ESCAPING BEHIND HIM WHILE HE WAS CLIMBING OUT OF THE EXCAVATION. BEFORE THE CONTRACT EMPLOYEE COULD COMPLETELY | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1770 | 1995-07-24 | IN | maintenance |  | INDIANA GAS CO INC | INDIANA GAS CO. WAS REPAIRING A LEAK ("LEAK #1") ON AN 8" BARE STEEL MAIN AT2202 S. NEBRASKA ST. IN MARION, IN. THE REPAIR WAS BEING MADE BY WELDING A REINFORCING SLEEVE (PUMPKIN) AROUND THE AREA OF LEAKAGE.AS THE WELDER WAS COMPLETING THE FINAL PASS ON | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1771 | 1995-08-09 | GA | other |  | SUMMERVILLE GAS SYSTEM, CITY OF |  | 61294 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1772 | 1995-07-31 | PA | other | PLEXCO | PHILADELPHIA ELECTRIC CO | THIS REPORT IS FOLLOW UP TO THE CALL TO MR. BLANCHARD & CLAIM #302096 (SEE ATTACHED)CORROSION SECTION NOT APPLICABLE DUE TO PLASTIC PIPING.STRUCTURE FIRE AT LOCATION CAUSED DAMAGE TO GAS FACILITIES AS DESCRIBED IN ATTACHMENT.NO CONSTRUCTION DEFECTS - SERV | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1773 | 1995-08-16 | CA | other | NORDSTROM | PACIFIC GAS & ELECTRIC CO | A DISGRUNTLED CUSTOMER WHO WAS TURNED OFF FOR NON-PAYMENT ATTEMPTED TO OPEN THE VALVE ON THE RISER TO RE-ESTABLISH SERVICE. THE THIRD PARTY LOOSENED THE NUT ON THE BACK OF THE VALVE CORE, RESULTING IN THE ESCAPE OF GAS. ANOTHER PERSON, DEBBIE RICH, APPROA | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1774 | 1995-07-28 | OH | ACCIDENTALLY CAUSED BY OPERATOR | DRISCOPIPE | WEST OHIO GAS CO | CONTRACTOR EMPLOYEES, WORKING ON BEHALF OF WEST OHIO GAS (WOG), WERE REPLACING A SECTION OF 6" STEEL MAINLINE WITH 6" PLASTIC. INSTALLATION OF THE NEW SECTION OF MAINLINE HAD BEEN COMPLETED. CONTRACTOR AND WOG EMPLOYEES WERE PURGING AIR FROM THE LINE IN O | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1775 | 1995-08-29 | NY | ACCIDENTALLY CAUSED BY OPERATOR |  | NEW YORK STATE ELECTRIC & GAS CORP | 2 CUSTOMERS REMODELING HOME NOTICED GAS ODOR IN DWELLING. TRACED ODOR TO KITCHEN AREA WHERE A PIPE FOR A GAS APPLIANCE WAS NOTICED WITHOUT A PLUG AND THE VALVE PARTIALLY OPENED. GAS/AIR MIXTURE IGNITED RESULTING IN AN EXPLOSION,INJURING BOTH PERSONS. NEAR | 80000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1776 | 1995-09-05 | NM | other |  | PUBLIC SERVICE CO OF NEW MEXICO GAS SERVICES | ON TUESDAY SEPTEMBER 5, 1995, CONDOR CONSTRUCTION OF ALBUQUERQUE, NEW MEXICOWAS INSTALLING NEW WATER LINES ON JEWEL PLACE WHEN A TRACKHOE OPERATOR DUG INTO THE GAS SERVICE LINE FOR 1027 JEWEL PLACE NE. THE SERVICE LINE WAS BENT AND THE TEE AT THE MAIN TIE | 225000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1777 | 1995-09-02 | WV | other | PHILLIPS DRISCOPIPE | MOUNTAINEER GAS CO | AT APPROXIMATELY 9:15 AM ON SEPTEMBER 2, 1995, A BACKHOE OPERATOR EMPLOYED BY HOSKINS CONSTRUCTION COMPANY A 2" PLASTIC GAS MAIN BELONGING TO MGC. A MGC CREW CONSISTING OF GARY WOOFTER AND RON TROWBRIDGE AND SUPERVISED BY JORDAN WEBER ARRIVED AT APPROXIMA | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1778 | 1995-08-19 | LA | other | UPONOR ALDYL | ARKANSAS LOUISIANA GAS CO (ARKLA GAS CO) | GENE KENT OF G & L IRRIGATION WAS TRENCHING & STRUCK 3/4 PLASTIC SERVICE LINE.GENE KENT OF G & L IRRIGATION WAS TRENCHING IN FRONT YARD OF 441 CREEK HOLLOW ST. TRENCHER STUCK A 3/4 PLASTIC SERVICE LINE TO THIS ADDRESS. GAS ESCAPEDTO THE ATMOSPHERE AND IGN | 1350 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1779 | 1995-08-17 | NY | technical failure | PHILLIPS PETROLEUM CO | ROCHESTER GAS & ELECTRIC CORP | ON AUGUST 17, 1995, AT APPROXIMATELY 1400 HOURS A NATURAL GAS EXPLOSION AND SUBSEQUENT FIRE CAUSED EXTENSIVE DAMAGE TO THE TOWNHOUSE COMPLEX AT THE SUBJECT ADDRESS. THE GAS AND ELECTRIC SERVICES TO THE TOWNHOUSE COMPLEX HAD BEEN INSTALLED IN A COMMON TREN | 1000000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1780 | 1995-08-15 | KY | other |  | COLUMBIA GAS OF KENTUCKY INC | A WATER LINE CONTRACTOR STRUCK A 4" STEEL GAS MAIN WITH A ROCK TRENCHER. THEESCAPING GAS IGNITED AND CAUSED APPROXIMATELY $70,000 DAMAGE TO THE TRENCHER. A LINE LOCATE REQUEST HAD BEEN MADE, BUT THE LOCATING CONTRACTOR EMPLOYED BY COLUMBIA GAS OF KENTUCKY | 70000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1781 | 1995-09-29 | KS | other |  | MIDWEST ENERGY INC | INSIDE PIPING IN HOUSE - NON JURISDICTIONAL | 85000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1782 | 1995-09-05 | PA | other | DU PONT | EQUITABLE GAS CO | A NOTICE WAS PLACED ON THE PA ONE-CALL SYSTEM BY THE OUTSIDE PARTY AT 2:20 PM, FRIDAY, SEPTEMBER 1, 1995 (9/4/95 LABOR DAY). HOWEVER, THE INCIDENT OCCURRED BEFORE THE UTILITY HAD SUFFICIENT TIME TO MARK OUT ITS FACILITIES. | 120000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1783 | 1995-09-25 | OK | other |  | OKLAHOMA NATURAL GAS CO | DAMAGE RESULTED WHEN A VEHICLE LEFT THE ROADWAY, JUMPED A CURB, CROSSED A SIDEWALK, TRAVELED APPROXIMATELY 15 FEET AND STRUCK THE GAS METER PUSHING IT INTO THE WALL OF THE BUILDING. A FIRE RESULTED WHICH VIRTUALLY DESTROYED THE BUILDING. | 180000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1784 | 1995-10-18 | WV | other | PLEXCO | HOPE GAS INC | CONTRACTOR (J & L DITCHWITCH) WAS IN THE PROCESS OF EXCAVATING A DITCH FOR AWATER LINE USING A DITCH-WITCH TYPE TRENCHER. THE TRENCHER CUT INTO THE GAS PIPELINE CAUSING A RELEASE OF GAS AND IGNITION. THE TRENCHER OPERATOR WAS BURNED AND HOSPITALIZED. WARN | 3000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1785 | 1995-09-20 | PA | other | U.S. STEEL GROUP | PHILADELPHIA ELECTRIC CO | CONTRACTOR WORKING TO INSTALL OVERHEAD TRAFFIC SIGNALS AUGERED INTO HIGHPRESSURE GAS LINE THAT SUPPLIES MERCK, SHARP & DOHME. THE LINE WAS MARKEDINCORRECTLY AND REPAIRS TO THE FACILITIES HAVE BEEN MADE IN THE FORM OFREPLACEMENT OF THE DAMAGED SECTION OF P | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1786 | 1995-10-16 | NE | other |  | METROPOLITAN UTILITIES DISTRICT | PROPERTY OWNER HIRED CONTRACTOR TO DO MASON WORK ON PROPERTY INCLUDING REMOVAL OF CONCRETE PARKING AREA ADJACENT TO INVOLVED STRUCTURE. AS CONTRACTOR REMOVED CONCRETE PARKING AREA WITH FRONT LOADER, CONCRETE DEBRIS WAS PUSHED UP AGAINST SOUTH SIDE OF INVO | 35000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1787 | 1995-10-12 | VA | other |  | RICHMOND DEPT OF PUBLIC UTILITIES, CITY OF | AT APPROXIMATELY 05:15, THURSDAY, OCTOBER 10, 1995 THE CHESTERFIELD COUNTY FIRE DEPARTMENT NOTIFIED THE CITY OF RICHMOND DEPARTMENT OF UTILITIES NIGHT DISPATCHER OF A GAS FED FIRE AT CLOVERLEAF MALL SHOPPING CENTER AT 2201 MIDLOTHIAN TURNPIKE. OUR DISPATC | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1788 | 1995-10-16 | TX | ACCIDENTALLY CAUSED BY OPERATOR | PLEXCO | SOUTHERN UNION GAS CO | A THREE-MAN CREW WAS WORKING ON OFFSETTING A 4" PE GAS MAIN IN THE 9600 BLOCKOF KENWORTHY, BEHIND COHEN STADIUM. THE GAS MAIN WAS ACCIDENTALLY PUNCTUREDWITH THE BACKHOE. WITHIN 30 SECONDS THE GAS IGNITED CAUSING FIRST, SECOND ANDTHIRD DEGREE BURNS TO THE | 10000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1789 | 1995-10-30 | CA | other |  | AMERIGAS PROPANE, L.P. | MOTOR VEHICLE ACCIDENT- VEHICLE FAILED TO NEGOTIATE TURN - VEHICLE STRUCK BUILDING "DAYS INN" HIT AND RUN - IMPACT AT POINT OF SECOND STAGE REGULATOR - BROKEN PIPELINE AND UPSTREAM OF SECOND STAGE REGULATOR - WITNESS SMELLED GAS CONTACTED FIRE DEPARTMENT. | 60000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1790 | 1995-10-11 | CA | other | UPONOR | PACIFIC GAS & ELECTRIC CO | ELECTRIC LIGHTING CONTRACTOR DUG INTO MAIN, WHICH WAS AT A DEPTH OF 48 INCHES. EMPLOYEE LAID ON GROUND AND REACHED DOWN INTO HOLE TO PREPARE PIPE TO INSTALL PLASTIC SQUEEZERS. FELLOW EMPLOYEE NOTICED THE OTHER SLUMPED IN THE HOLE AND PULLED HIM OUT. EMPLO | 1000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1791 | 1995-10-18 | TN | other | PHILLIPS-DRISCO PIPE | KNOXVILLE UTILITIES BOARD | GAS FACILITIES HAD BEEN PREVIOUSLY MARKED IN AREA AT THE REQUEST OF ANOTHER EXCAVATOR - NO REQUEST AT THIS SITE BY THIRD PARTY CAUSING DAMAGE. A 4-INCH POLYETHYLENE GAS MAIN WAS DAMAGED BY ACTION OF THIRD PARTY WHILE INSTALLING AN18-INCH STORM DRAIN. WHIL | 150000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1792 | 1995-11-05 | NV | other | KRALOY | SOUTHWEST GAS CORP | AN EXPLOSION AND FIRE OCCURRED IN AN EIGHT-UNIT, TWO-STORY APARTMENT STRUCTURE AT THE GRAND PLAZA APARTMENTS LOCATED AT 286 E. HARMON AVENUE. ACTUAL CAUSE OF THE INCIDENT IS UNKNOWN. PROBABLE CAUSE WAS AN ACCUMULATION OF GAS, EITHER METHANE SEWER GAS, NAT | 500000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1793 | 1995-11-01 | MT | other |  | MONTANA - DAKOTA UTILITIES CO | INVESTIGATION SHOWED THAT INITIAL EXPLOSION WAS NOT CAUSED BY LEAKAGE FROM JURISDICTIONAL PIPING. EXPLOSION OF UNKNOWN ORIGIN INSIDE BUILDING COLLAPSED WALL ON METER SET CAUSING LEAKAGE. | 212000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1794 | 1995-11-28 | LA | other | PLEXCO | GULF STATES UTILITIES CO | ON NOVEMBER 28, 1995, A BARBER BROTHERS CONSTRUCTION ROAD REPAIR CREW, RUPTURED AN UNDERGROUND NATURAL GAS SERVICE LINE OWNED AND OPERATED BY GULF STATESUTILITIES. THIS WAS A 1-INCH PLASTIC LINE SERVING A SINGLE RESIDENCE AT 13310 PALOMINO STREET IN BATON | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1795 | 1995-11-08 | CA | other |  | SOUTHERN CALIFORNIA GAS CO | AT 1:57 PM, ON WEDNESDAY, NOVEMBER 11, 1995, ORTIZ ENTERPRISES INC. WAS EXCAVATING IN INSTALL A NOISE ABATEMENT WALL ADJACENT TO THE NORTHBOUND LANES OF THE SANTA ANA FREEWAY (1-5), WHEN THEY STRUCK AND DAMAGED A SIX INCH GAS MAIN. THEY WERE WORKING FOR C | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1796 | 1995-11-05 | TN | other |  | CITIZENS GAS UTIL DIST | ON SUNDAY, NOVEMBER 5, 1995, AT APPROXIMATELY 8:00 A.M., DARRYL CROSS AND DENNIS GOAD WENT TO THE METER STATION NEAR ELGIN TOINVESTIGATE AND CORRECT A LOW PRESSURE PROBLEM ON THE DISTRIBUTION SYSTEM IN THE ELGIN/HIGHWAY 52 AREA. THE METERING STATION NEAR | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1797 | 1995-11-22 | MS | maintenance |  | MISSISSIPPI VALLEY GAS | THE OCCUPANT WAS ATTEMPTING TO LIGHT A BATHROOM HEATER WHEN THE FLASH FIRE OCCURRED AND WAS BURNED ON THE FACE AND ARMS. FIRE DAMAGE TO THE BUILDING WAS ESTIMATED TO BE $6,000.00. LEAKAGE ON THE SERVICE LINE WAS LOCATED AT THE EDGE OF A FOUNDATION FOOTING | 6000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1798 | 1995-11-11 | PA | other |  | COLUMBIA GAS OF PENNSYLVANIA | AN 1.25" STEEL METER RISER SEPARATED FROM AN 1.25" COMPRESSION ELBOW ALLOWING ESCAPING GAS TO ENTER THROUGH THE FOUNDATION WALL OF THE RESIDENCE. GAS WASIGNITIED FROM AN UNDETERMINED SOURCE RESULTING IN AN EXPLOSION AND FIRE. THECAUSE OF THE SERVICE LINE | 75000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1799 | 1995-11-14 | CT | other |  | YANKEE GAS SERVICES CO | SEVERE WINDS CAUSED A HIGH VOLTAGE ELECTRIC DISTRIBUTION CONDUCTOR (APPROXIMATELY 13,200 VOLTS AC, PHASE TO GROUND) TO PART AND FALL FROM ITS OVERHEAD POSITION. THE CONDUCTOR LANDED ON THE BRIDGE DECKING IN DIRECT CONTACT WITH A STEEL EXPANSION JOINT IN T | 20000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1800 | 1995-12-04 | CA | technical failure | DUPONT | SOUTHERN CALIFORNIA GAS CO | AN EMPLOYEE OF NURSERYLAND CARE CENTER WAS ATTEMPTING TO TURN THE WATER OFF AT THE WATER METER WHILE USING A CIGARETTE LIGHTER TO SEE IN THE DARK. AS HE LIT THE LIGHTER, GAS THAT HAD ACCUMULATED IN THE WATER METER VAULT IGNITED, FLASHED, AND BURNED HIM. T | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1801 | 1995-11-30 | CA | other |  | PACIFIC GAS & ELECTRIC CO | STRUCTURE FIRE CAUSED BY DEBRIS AROUND WATER HEATER. | 40000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1802 | 1995-12-15 | AK | other | PHILLIP DRISCOPIPE | ENSTAR NATURAL GAS CO | THE BUILDING OWNER WAS RELOADING AMMUNITION AND SMOKING AT THE TIME. A CIGARETTE IGNITED GUNPOWDER AND THE BUILDING CAUGHT FIRE. THE FIRE CAUSED THE GAS METER AND PLASITC SERVCIE LINE TO MELT INSIDE THE STEEL RISER, RESULTING IN ARELEASE OF NATURAL GAS. T | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1803 | 1995-08-11 | TN | other |  | COOKEVILLE GAS DEPT, CITY OF | WAS IN THE PROCESS OF LOWERING A 6' SECTION OF 1" STEEL SERVICE LINE BY INSTALLING A PIECE OF 1" PLASTIC. HAD THE UPSTREAM CONNECTION MADE USING DRESSER COUPLING AND WAS GETTING READY TO CONNECT OTHER END OF PIPE TO EXISTING LINE WHEN FIRE ERUPTED. THREE | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1804 | 1995-12-13 | TN | other |  | UNITED CITIES GAS CO | SECTION OF PIPE DAMAGED WAS NOT MARKED. SECTION THAT WAS DAMAGE WAS STUB OUTLEFT FROM LAST RELOCATION TO SERVE FARM TAP. WAS NOT MARKED BY LOCATER. HE WAS NOT AWARE OF THIS SECTION. TRACK HOE HIT 4 STEEL LINE CAUSING LINE CUT. | 25000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1805 | 1995-11-25 | GA | other | PLEXCO | ATLANTA GAS LIGHT CO | CONTRACTOR REQUESTED THAT LOCATOR NOT LOCATE SERVICE LINE COMPLETELY AT THE JOB SITE. THE UNLOCATED PORTION OF THE SERVICE LINE IS WHERE DAMAGE OCCURRED. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1806 | 1995-12-17 | NJ | other |  | ELIZABETHTOWN GAS CO | POSSIBLE ESCAPE OF GAS RESULTING FROM CRACK IN 4" CAST IRON MAIN.7 | 200000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1807 | 1995-12-22 | MA | other |  | BOSTON GAS CO | COMPANY PERSONNEL WERE REQUESTED TO RESPOND TO A FIRE THAT OCCURRED AT 69 OLIVE AVENUE, MALDEN, MASSACHUSETTS. A LEAK INVESTIGATION WAS CONDUCTED AND A SIX INCH (6") LOW PRESSURE CAST IRON CIRCUMFERENTIAL BREAK (270) WAS FOUND ON THE MAIN LOCATED IN THE S | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1808 | 1995-12-04 | GA | other |  | ATLANTA GAS LIGHT CO | OPERATOR'S CONTRACTOR HIT AN OLD SERVICE STUB WHILE BORING TO INSTALL NEW MAIN. GAS MIGRATED BACK UP BORING DITCH TO SANITARY SEWER LATERAL WHICH HAD BEEN BORED THROUGH. GAS THEN MIGRATED INTO SANITARY SEWER MAIN LINE AND FROM THERE UP SEWER LATERAL INTO | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1809 | 1995-12-08 | IL | ACCIDENTALLY CAUSED BY OPERATOR | US PIPE | PEOPLES GAS LIGHT & COKE CO | A FOUR PERSON CREW WAS REPLACING A LEAKING 6" STAINLESS STEEL BAND CLAMP WHICH WAS COVERING A CRACK ON A 6" LOW PRESSURE CAST IRON MAIN. THE CREW DID NOTFOLLOW COMPANY PROCEDURES. DURING THE JOB, THREE OF THE CREW MEMBERS WERE OVERCOME BY GAS. ONE SUBSEQU | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1810 | 1995-12-14 | MO | other |  | UNITED CITIES GAS CO | THE 2 1/4" C.I. MAIN BROKE AND LET GAS TRAVEL BY PIPE TO WATER LINE DITCH AND THIS LET GAS INTO HOUSE WHERE WATER PIPE ENTERED. THE 2 1/4" PIPE WAS FOUNDTO BE ON A ROCK AND SETTLEMENT CAUSED THE PIPE TO BREAK. THIS CAST IRON PIPEWAS INSTALLED IN 1965 IN C | 80000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1811 | 1995-12-11 | LA | other |  | ARKANSAS LOUISIANA GAS CO (ARKLA GAS CO) | INCIDENT WAS TELEPHONICALLY REPORTED 12 12 95 AT 12:28 AM AND WAS REPORTED AS POSSIBLE GAS RELATED. AFTER INVESTIGATION BY FIRE DEPARTMENT, CAUSE OF FIREDETERMINED TO BE NOT GAS RELATED. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1812 | 1995-12-19 | PA | other |  | PHILADELPHIA ELECTRIC CO | CAST IRON MAIN BREAK IN STREET IN FRONT OF #840 TREMONT AVE., NORRISTOWN, PARESULTED IN THE MIGRATION OF NATURAL GAS THROUGH THE SOIL AND INTO THE AMBIENT ATMOSPHERE INSIDE OF THE STRUCTURE LOCATED AT #831 TREMONT AVE, NORRISTOWN.DURING THE MIGRATION OF T | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1813 | 1995-12-29 | PA | other |  | PHILADELPHIA GAS WORKS | THE PHILADELPHIA FIRE DEPARTMENT, FIRE MARSHALL'S OFFICE, PHILADELPHIA POLICE DEPARTMENT AND THE BUREAU OF ALCOHOL, TOBACCO AND FIREARMS ARE CURRENTLY CONDUCTING A CRIMINAL INVESTIGATION INTO THE SUBJECT INCIDENT. THEY HAVE DETERMINED THAT THE INCIDENT WA | 250000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1814 | 1995-12-01 | MN | other |  | NORTHERN STATES POWER CO | SNOW MELT OFF ROOF CAUSED ICE BUILD-UP ON SERVICE REGULATOR, CAUSING OVER PRESSURIZED CUSTOMER HOUSE PIPING. | 40000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1815 | 1995-12-26 | OH | other |  | COLUMBIA GAS OF OHIO INC | INVESTIGATION HAS REVEALED THAT THE MOST LIKELY CAUSE OF ESCAPING GAS WAS THAT AN 1 1/4" STEEL RISER TO A METER SET PULLED OUT OF THE TOP OF AN 1 1/4" COMPRESSION ELL IN THE CUSTOMER SERVICE LINE. THE ESCAPING GAS MIGRATED TO THE HOUSE AND WAS IGNITIED FR | 150000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1816 | 1996-01-02 | NV | other | KRALOY | SOUTHWEST GAS CORP | AN INVESTIGATION AFTER THE INCIDENT REVEALED THAT A LARGE TREE ROOT HAD GROWN ALONG SIDE OF, AND A SMALLER ROOT HAD GROWN FROM THE LARGER ROOT AND WRAPPED AROUND THE 2" PVC MAIN SERVING THE RESIDENCE INVOLVED IN THE INCIDENT. THE 2" PVC MAIN WAS FOUND TO | 250000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1817 | 1995-12-28 | MA | other |  | BOSTON GAS CO | ON DECEMBER 28, 1995 AN EXPLOSION OCCURRED IN THE BASEMENT OF A FIVE-STORY BUILDING LOCATED AT 396 MARLBOROUGH STREET, BOSTON. A LEAK INVESTIGATION WAS CONDUCTED AND A SIX (6) INCH CAST IRON CIRCUMFERENTIAL BREAK WAS FOUND ON MAINLOCATED IN THE STREET UND | 500000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1818 | 1995-12-25 | PA | other |  | PEOPLES NATURAL GAS CO | MR. RICHARD CASKEY SLID OFF THE HIGHWAY, STRUCK A RAILROAD TIE RETAINING WALL, A GAS METER, AND A TELEPHONE POLE. ESCAPING NATURAL GAS IGNITED AND DESTROYED THE VEHICLE. THERE WAS ALSO CONSIDERABLE DAMAGE TO TELEPHONE, ELECTRIC, AND CABLE T.V. LINES.0 | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1819 | 1995-12-23 | MI | other | CENTURY | MICHIGAN GAS CO | MINOR FLASH FIRE AND SMALL EXPLOSION CAUSED BY A CRACK IN A 1" CENTURY PIPE SERVICE LINE. THIS A FOLLOW UP REPORT OF THE INCIDENT THAT HAPPENED IN NILES TOWNSHIP ON DECEMBER 23, 1995 AT 2702 N. FIFTH STREET. AS WE HAVE DISCUSSED, THIS WAS A MINOR FLASH FI | 500 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1820 | 1995-12-24 | TX | other |  | SOUTHERN UNION GAS CO | THE CAUSE OF THIS GAS LEAK IS BEING INVESTIGATED. THE AFFECTED SECTION OF THE MAIN HAS REMAINED OUT OF SERVICE. DUE TO THE HIGH TRAFFIC VOLUME ON SOUTH CONGRESS AVE, THE INVESTIGATION HAS BEEN DELAYED UNTIL PERMANENT REPAIRS ARE MADE. THE OLD MAIN WILL BE | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1821 | 1996-01-13 | PA | other |  | PENNSYLVANIA GAS & WATER CO | EXCAVATION ON JEFFERSON ST. REVEALED A FOUR INCH (4) CAST IRON GAS MAIN BREAK WHICH LEAKED THROUGH NATURAL OPENINGS IN THE SOIL, ENTERING BOTH BUILDINGS.INSPECTION SUBSEQUENT TO EXCAVATION REVEALED A DEEP FROST LINE CREATING PRESSURE ON THE GAS MAIN, CAUS | 275000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1822 | 1996-01-08 | KS | other |  | WESTERN RESOURCES, INC | JOHNSON COUNTY WATER DISTRICT #1 EMERGENCY LOCATE REQUESTED AT 7001 RUSSELL ON 07/24/95. LOCATED ON 07/24/95. A TWO-INCH STEEL MAIN, WHICH APPARENTLY HADBEEN DAMAGED SOMETIME PRIOR TO THIS INCIDENT FAILED AT THE POINT OF THE PREVIOUS THIRD-PARTY DAMAGE, A | 90000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1823 | 1996-01-17 | IN | other |  | INDIANA GAS CO INC |  | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1824 | 1996-01-24 | MO | other |  | LACLEDE GAS CO | THE INVESTIGATION IS CONTINUING AS TO THE CAUSE OF THE FAILURE AT THE LAST THREAD OF THE COUPLING OF THE 2-INCH SCREWED, STEEL MAIN. THE FAILURE WAS A FULL CIRCUMFERENCE BREAK WITH A SEPARATION OF APPROXIMATELY 1/2 INCH. THERE WERE TWO SEPARATE EXPLOSIONS | 315000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1825 | 1996-01-29 | ND | other |  | MONTANA - DAKOTA UTILITIES CO | AT 2:25 PM CST, GAS MIGRATING FROM A LEAK ON A 2" ST MAIN COLLECTED IN A HOUSE AND WAS IGNITED. THE RESULTING FIRE DESTROYED THE HOME. ONE RESIDENT RECEIVED MINOR BURNS AND WAS TRANSPORTED TO THE HOSPITAL. OTHER CIRCUMSTANCES: A MONTANA-DAKOTA SERVICEMAN | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1826 | 1996-01-19 | MD | other |  | BALTIMORE GAS & ELECTRIC CO | ON 01/19/96, THERE WAS AN APPARENT EXPLOSION AND FIRE AT 822 BONAPARTE AVE.OBSERVATIONS OF THE TWO STORY BRICK BUILDING SHOWED THE STRUCTURE COLLAPSED INTO THE BASEMENT. NO INJURIED WERE REPORTED WITH A PROPERTY DAMAGE OF APPROXIMATELY $75,000.00. TELEPHO | 75000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1827 | 1996-01-22 | OH | other | SPRAGUE | EAST OHIO GAS CO | A FIRE OF UNDETERMINED ORIGIN CAUSED EXTENSIVE DAMAGE TO A SINGLE FAMILY HOME. WHILE IT HAS NEVER BEEN DETERMINED WHAT THE EXACT CAUSE OF THE FIRE WAS, IT IS SUSPECTED THAT AN OVER-PRESSURIZATION OF THE NATURAL GAS HOUSELINE MAY HAVE CAUSED THE FLAME ON E | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1828 | 1996-02-02 | WY | other |  | MONTANA - DAKOTA UTILITIES CO | FROST CAUSED THE LINE TO BURST AT A LOCATION THAT HAD PREVIOUSLY BEEN DAMAGED BY A CONTRACTOR OR UNKNOWN PARTY. AT ABOUT 11:25 AM MST, 02/02/96, GAS MIGRATING FROM A LEAK ON A 2" STEEL MAIN COLLECTED IN AN ADJACENT HOUSE IGNITED. THE EXPLOSION SEVERLY DAM | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1829 | 1995-11-04 | OK | other |  | ARKANSAS LOUISIANA GAS CO (ARKLA GAS CO) | DOOR TO BLOWER SECTION OF FURNACE (CENTRAL HEATER) HAD BEEN REMOVED. FLUEVENT WAS NOT PROPERLY FITTED TO CENTRAL HEATER, APPROXIMATELY 1" ABOVE HEATEXCHANGER. FLUE VENT ON WATER HEATER WAS NOT PROPERLY INSTALLED ON APPLIANCE.CARBON MONOXIDE EMISSION DOOR | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1830 | 1996-02-04 | GA | other | AMERICAN METER | ATLANTA GAS LIGHT CO | WATER RAN OFF THE ROOF TOP ONTO THE NATURAL GAS METER SET ASSEMBLY DURING SUB-FREEZING TEMPERATURE. THE WATER HAD TRAVELED AROUND THE 1313 REGULATOR FORMING ICE OVER THE RELIEF VENT WHICH WAS IN THE DOWNWARD POSITION. WHEN THE REGULATOR FAILED IN THE OPEN | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1831 | 1996-02-07 | MO | other |  | GRANBY GAS, CITY OF | ON ADVICE OF COUNSEL, NO STATEMENT IS BEING MADE AT THIS TIME SINCE THE CITYIS ON NOTICE OF POSSIBLE LITIGATION CONCERNING THIS INCIDENT. | 35000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1832 | 1996-02-03 | MI | other | US STEEL | CONSUMERS POWER CO | PIPE FAILED AT THIRD-PARTY DAMAGE. GAS MIGRATED INTO HOUSE CAUSING AN EXPLOSION AND FIRE. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1833 | 1996-02-23 | WV | other | PLEXCO | ASHFORD GAS CO | THE 1.250 INCH SERVICE LINE WAS ON TOP OF THE GROUND WHEN ALLEGEDLY TWO CHILDREN STARTED A FIRE ON TOP OF THE GAS LINE. MR. SEAN BOWLES NOTICED THE FIRE AND TRIED TO PUT THE FIRE OUT WITH HIS FEET WHEN THE GAS IGNITED. | 267 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1834 | 1996-01-23 | WI | other | PLEXCO | WISCONSIN NATURAL GAS CO | AREA OF INCIDENT WAS RELOCATED THE SAME DAY OF INCIDENT.THE EXPLOSION OCCURRED AFTER HOLTGER BROTHER ACCIDENTALLY STRUCK AND DAMAGED OUR 2" PE (PLASTIC) GAS MAIN WHILE DIRECTIONALLY BORING TELEPHONE CABLE. THE GAS MAIN HAD BEEN MARKED CORRECTLY. GAS FROM | 150000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1835 | 1996-02-07 | MI | other |  | MICHIGAN GAS UTILITIES CO | DAMAGE TO PIPE APPEARS TO BE MONTHS OR YEARS OLD. N. RECENT CONSTRUCTION IN AREA. PIPE BROKE AT LOCATION OF PREVIOUS DAMAGE. 2" PIPE HAD BEEN STRUCK. | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1836 | 1996-02-03 | AL | other |  | ALABAMA GAS CORP | DURING A WINTER STROM THE DISPATCHER RECEIVED A REPORT OF A HOUSE FIRE FROM THE FIRE DEPARTMENT AT THE ABOVE MENTIONED ADDRESS. THE FIRE DEPARTMENT REQUESTED ASSISTANCE IN TURNING OFF THE GAS. THE GAS WAS TURNED OFF BY A CREWMAN APPROXIMATELY FIFTEEN (15) | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1837 | 1996-02-18 | OR | other |  | WP NATURAL GAS CO | ON SUNDAY, FEBRUARY 18, 1996, A LITTLE BEFORE 10:00 AM.,AN EXPLOSION OCCURRED THAT DESTROYED A HOUSE AT 2404 RIDDLE ROAD IN LA GRANDE, OREGON.OUR SEVICE MAN RECEIVED A CALL FROM 911 AT 10:04 AM. HE CONTACTED THE AREA MANAGER WHO MEET HIM AT THE SITE OF TH | 170000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1838 | 1996-03-08 | AK | other | PHILLIPS DRISCOPIPE | ENSTAR NATURAL GAS CO | ON FRIDAY, MARCH 8, 1996, AT APPROXIMATELY 4:48 PM AST, ENSTAR NATURAL GAS COMPANY PERSONNEL RESPONDED TO A HOUSE FIRE AT 1718 CARA LOOP, ANCHORAGE, ALASKA (LOT 22, BLOCK 1 COLONIAL MANOR SUBDIVISION). ACCORDING TO ANCHORAGE FIRE DEPARTMENT OFFICIALS, THE | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1839 | 1996-02-23 | PA | other |  | PHILADELPHIA GAS WORKS | THE PHILADELPHIA FIRE DEPARTMENT AND PHILADELPHIA GAS WORKS HAVE CONCLUDED THAT THIS FIRE WAS CAUSED BY AN UNKNOWN PERSON TAMPERING WITH THE GAS METER. THE GAS METER SWIVELS WERE FOUND LOSSENED AND LEAKING WITH ADDITIONAL INDICATIONS THAT THE FIRE HAD STA | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1840 | 1996-03-16 | TX | other |  | ENTEX - DIVISION OF ARKLA INC | AT FIRST REPORT A GAS LEAK EXPLOSION WAS SUSPECTED; HOWEVER, INVESTIGATION HAS REVEALED THAT NO GAS LEAKS OR MALFUNCTIONS OF EQUIPMENT & SIGNS OF HOMICIDE. INVESTIGATION REVEALED THAT GAS METER, REGULATOR & CUSTOMER HOUSELINE WERENOT DEFECTIVE. A BAR TEST | 45000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1841 | 1996-03-17 | IA | other |  | PEOPLES NATURAL GAS | ELECTRICAL ARC ON STEEL SERVICE CAUSED RELEASE OF GAS. FIRE DESTROYED 2 BUILDINGS, SMOKE AND WATER DAMAGE TO OTHERS. | 500000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1842 | 1996-03-11 | GA | other | DUPONT | ATLANTA GAS LIGHT CO | AN 1 1/4" PLASTIC NATURAL GAS SERVICE WAS RUPTURED BY A PLUMBING CONTRACTOR WHILE REPAIRING A COPPER WATER LINE. WHILE REPAIRING THE DAMAGED PIPE, THE CONTRACTOR ACCIDENTALLY BURNED A HOLE IN THE PLASTIC GAS SERVICE USING A SOLDERING TORCH. THE ESCAPING G | 90000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1843 | 1996-03-05 | WA | other | PLEXCO | WASHINGTON NATURAL GAS CO | A CABLE TV CONTRACTOR RUPTURED AN 1 1/4" PE GAS DISTRIBUTION MAIN WHILE USING A BORING TOOL TO REPLACE A CABLE TV WIRE LOCATED UNDER THE CONCRETE DRIVEWAY OF THE ABOVE ADDRESS. THE CONTRACTOR NOTIFIED WASHINGTON NATURAL GAS COMPANY(WNG) OF THE DAMAGED LIN | 350000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1844 | 1996-03-05 | IA | other | WALWORTH | INTERSTATE POWER CO | FROST HEAVE CRACKED THE CAST IRON BODY OF THE UNDERGROUND 3/4" WALWORTH SERVICE VALVE. THE GAS MIGRATD INTO THE UNOCCUPIED BUILDING AND WAS PROBABLY IGNITED BY A CEILING MOUNTED GAS HEATER. | 161490 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1845 | 1996-02-26 | IL | other |  | NORTH SHORE GAS CO | THE SERVICE PIPE WAS HIT AND DAMAGED BY SOME UNKNOWN THIRD PARTY. OVER TIME THE DAMAGED SECTION OF PIPE LEAKED, GAS MIGRATED INTO THE SINGLE FAMILY RESIDENCE AND IGNITED.THIRD PARTY HIT & DAMAGED SERVICE PIPE (DATE & THIRD PARTY UNKNOWN). A GAS LEAK RESUL | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1846 | 1996-02-28 | CT | other |  | YANKEE GAS SERVICES CO | STRUCTURE FIRE INVOLVED 3 GAS METERS ON OUTSIDE REAR OF BUILDING. NO LEAK ONSERVICE PIPING. A STRUCTURE FIRE AT #263 GREENWOOD AVENUE ORIGINATED IN THE AREA OF THREE (3) ABOVE GROUND METERS LOCATED AT THE OUTSIDE REAR OF THE BUILDING. THE METERS AND REGUL | 200000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1847 | 1996-03-03 | PA | other |  | NATIONAL FUEL GAS DISTRIBUTION CORP | 1" SERVICE REGULATOR WAS STRUCK BY SNOW PLOW. PRIVATE CONTRACTOR SNOW PLOW OPERATOR STRUCK 1" SERVICE REGULATOR AND PIPING. IMPACT CAUSED 1" PIPING TO BREAK AT THREAD AT REGULATOR INLET. IN ADDITION, THE METER (LOCATED INSIDE THE BUILDING) INLET BROKE OFF | 180000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1848 | 1996-03-11 | TN | ACCIDENTALLY CAUSED BY OPERATOR |  | WEST TENNESSEE PUBLIC UTIL DIST | THE INCIDENT OCCURRED WHEN A EMPLOYEE OF HUGHEY CONSTRUCTION COMPANY OF WAVERLY, TENNESSEE, UNDER CONTRACT WITH WEST TENNESSEE PUBLIC UTILITY DISTRICT TORELOCATE NATURAL GAS LINES DUE TO THE ROAD CONSTRUCTION ON HIGHWAY 22 IN CARROLL COUNTY, TENNESSEE. TH | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1849 | 1996-03-14 | CA | other |  | PACIFIC GAS & ELECTRIC CO | LINE WAS MARKED INACCURATELY. CITY OF SANTA CLARA WATER DEPARTMENT STRUCK 4-INCH PLASTIC MAIN WHILE EXCAVATING FOR A FIRE HYDRANT. | 60000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1850 | 1996-04-01 | WI | other |  | WISCONSIN GAS CO | ON APRIL 1, 1996, AN EXPLOSION OCCURRED IN A HOME AT 2610 THIRD STREET SOUTHIN WISCONSIN RAPIDS. TWO OCCUPANTS WERE ON THE PREMISES AT THE TIME OF THE EXPLOSION BUT ESCAPED WITHOUT INJURY. APPROXIMATELY $70,000 OF DAMAGE OCCURRED TO THE HOME. NATURAL GAS | 70000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1851 | 1996-03-13 | CO | other |  | COLORADO SPRINGS, CITY OF | IN THE PROCESS OF ADDING A BASEMENT WINDOW TO THE RESIDENCE, A CONTRACTOR HAND EXCAVATED TO INSTALL A WINDOW WELL AND EXPOSED THE GAS SERVICE LINE WHICH WAS LOCATED APPROXIMATELY 4 INCHES LATERALLY FROM THE EXTERIOR BASEMENT WALL.CONTRACTOR PROCEEDED TO S | 200000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1852 | 1996-03-06 | PA | other | ROCKWELL | PEOPLES NATURAL GAS CO | THE SERVICE REGULATORY ON THE METER SET SUPPLYING GAS TO THE RESIDENCE FAILED TO OPERATE PROPERLY AND ALLOWED 6 PSIG GAS PRESSURE TO ENTER THE HOUSE AND ITS GAS APPLIANCES. FLAMES FROM A GAS WAER HEATER MAY HAVE INITIATED THE FIRETO THE RESIDENCE WHICH SU | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1853 | 1996-03-23 | MD | other | UPONOR | WASHINGTON GAS LIGHT CO | THIS INCIDENT IS A RESULT OF A CABLE SUBCONTRACTOR BORING UNDER THE ROAD. THE SUBCONTRACTOR BORED THROUGH A BURIED 2" PLASTIC MAIN, CAUSING NATURAL GAS TO ESCAPE. THE ESCAPING GAS WAS VENTING OUT OF THE GROUND AND TRAVELLING AIRBORNE THROUGH THE SUBDIVISI | 13871 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1854 | 1996-04-24 | AK | other | PHILLIPS DRISCOPIPE | ENSTAR NATURAL GAS CO | AT APPROXIMATELY 2:30 AM AST, WEDNESDAY MORNING, APRIL 24, 1996, A FIRE OF UNKNOWN ORIGIN DEVELOPED INSIDE THE STRUCTURE AT 137 W. 13TH AVE., ANCHORAGE, ALASKA. THE FIRE CAUSED ONE FATALITY AND DESTROYED THE STRUCTURE. THE FIRE BURNED THE GAS METER AND RE | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1855 | 1996-03-31 | AZ | other | TEXTUBE | SOUTHWEST GAS CORP | A VEHICLE WAS WESTBOUND ON BASELINE ROAD. WHEN IT VEERED ACROSS THE EASTBOUND LANES AND COLLIDED WITH AN ABOVE-GROUND REGULATOR STATION. THE DRIVER WAS TRANSPORTED TO THE HOSPITAL AND LATER DIED FROM INJURIES SUSTAINED IN THE COLLISION. | 7475 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1856 | 1995-12-17 | TX | other | DUPONT | ENTEX - DIVISION OF ARKLA INC | 3/4" PLASTIC SERVICE INE FAILED DUE TO EXTERNAL STRESS FROM IMPROPER BACKFILLING OPERATION BY UNKNOWN PARTY. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1857 | 1996-04-15 | NY | other |  | NIAGARA MOHAWK POWER CORP | DAMAGE DIRECTLY ATTRIBUTED TO PROPERTY OWNER WORKING ON GAS FUEL LINES INSIDE BUILDING. INCIDENT LABELED ACCIDENTAL BY CITY OF SYRACUSE FIRE INVESTIGATION TEAM. | 60000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1858 | 1996-05-01 | LA | other |  | ARKANSAS LOUISIANA GAS CO (ARKLA GAS CO) | RESIDENCE AT 6218 SONHAVEN, SHREVEPORT, LA, CAUGHT FIRE CAUSING (3) INJURIES AND (2) PERSONS REQUIRING HOSPITALIZATION. CAPTAIN ROBERT MCWHERTER OF SHREVEPORT FIRE DEPARTMENT REPORTED CAUSE OF FIRE WAS NON-GAS RELATED AFTER INVESTIGATION. HOUSE FIRE AT AB | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1859 | 1996-05-09 | LA | other |  | ARKANSAS LOUISIANA GAS CO (ARKLA GAS CO) | ELECTRICAL FIRE DOMESTIC RESIDENCE. FRAYED CORD ON ELECTRIC DRYER SHORTED OUT CAUSING FIRE. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1860 | 1996-04-20 | TN | other | GRINNELL | MIDDLE TENNESSEE NATURAL GAS UTIL DIST | WIND AND RAIN STORM BLEW DOWN APPROXIMATELY AN 18" DIAMETER TREE IN THE YARDAT 325 MCKINNON. WHEN THE TREE FELL, IT HIT THE METER SET BREAKING THE STEEL PIPE AT THE THREADS JUST DOWNSTREAM OF THE METER STOP, BEFORE THE SERVICE REGULATOR. THE ESCAPING GAS | 150000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1861 | 1996-05-04 | MO | other |  | LACLEDE GAS CO | LIGHTNING STRUCK A NEARBY TREE AND TRAVELED TO METER, DAMAGING SAME. OUTSIDEGAS METER WAS SITUATED ON THE SOUTH SIDE OF THE BUILDING AND CAUGHT FIRE. | 60000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1862 | 1996-04-29 | MT | other |  | MONTANA - DAKOTA UTILITIES CO | POST-INCIDENT INVESTIGATION SHOWED THAT THE INITIAL EXPLOSION WAS NOT CAUSEDBY LEAKAGE FROM JURISDICTIONAL PIPING. EXPLOSION OF UNKNOWN ORIGIN INSIDE BUILDING COLLAPSED ROOF ON METER SET CAUSING LEAKAGE. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1863 | 1996-04-27 | CA | other | SINGER | PACIFIC GAS & ELECTRIC CO | GRASS FIRE IGNITED WOOD STRUCTURE FAILING REGULATOR CAUSING OVERPRESSURE. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1864 | 1996-05-10 | OH | other |  | COLUMBIA GAS OF OHIO INC | INCIDENT IS STILL UNDER INVESTIGATION. AN OUTSIDE AGENCY HAS BEEN ENGAGED. CURRENTLY NATURAL GAS CAN NOT BE CONFIRMED NOR DENIED AS THE CAUSE. A FINAL REVISED REPORT WILL BE FILED AT THE CONCLUSION OF THIS INVESTIGATION. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1865 | 1996-05-10 | MI | technical failure | GROVE - VALVE | MICHIGAN CONSOLIDATED GAS CO (MICHCON) | DUE TO DESIGN, NO REPRESSURE EQUALIZER LINE. | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1866 | 1996-05-21 | PA | other |  | PHILADELPHIA ELECTRIC CO | ON 5/21/96 A NATURAL GAS EXPLOSION OCCURED AT 16 STEEPLECHASE DR. INDYLESTOWN, PA. PRIOR TO THE EXPLOSION, AN UNDERGROUND ELECTRIC CABLE FAULTWAS EXPERIENCED IN THE AREA OF 16 STEEPLECHASE DR. THE SOURCE OF THE NATURALGAS WAS A GAS MAIN WHICH HAD BEEN DAM | 350000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1867 | 1996-05-08 | OH | other |  | COLUMBIA GAS OF OHIO INC | A CONTRACTOR INSTALLING A WATER LINE STRUCK AND DAMAGED A 20" HIGH PRESSURE STEEL GAS MAIN. THE MAIN HAD BEEN LOCATED, STAKED AND MARKED WITH MARKING PAINT. THE LINE WAS OPERATING AT 138 PSIG. ATTEMPTS TO REPAIR THE LINE BY REDUCINGTHE PRESSURE TO 50 PSIG | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1868 | 1996-05-24 | IL | other |  | NORTH SHORE GAS CO | A CAR LOST CONTROL WHILE IT WAS IN THE LEFT INSIDE LANE AND VEERED TO THE RIGHT CROSSING THE RIGHT LAND AND JUMPED THE CONCRETE CURB. CAR CONTINUED OVER THE GRASS EASEMENT, CRASHED THROUGH A 6-FOOT TALL STOCKADE FENCE AND SMALL TREES AND BRUSH AND THEN ST | 200000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1869 | 1996-06-04 | DE | other | DUPONT | DELMARVA POWER & LIGHT CO | OUTSIDE PARTY NOT HAND DIGGING TO LOCATE AS REQUIRED BY STATE STATUTE. HIGHWAY CONTRACTOR DAMAGED GAS MAIN WHILE EXCAVATING WITH TRACK-HOE. CONTRACTOR WAS EXCAVATING TO INSTALL STORM SEWER. OPERATOR HAD MARKED LINE FOR CONTRACTOR.CONTRACTOR HAD CONFIRMED | 200000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1870 | 1996-05-27 | TX | other |  | ENTEX - DIVISION OF ARKLA INC | HOUSE FIRE. FIRE STARTED ON WEST SIDE OF HOUSE NEAR UTILITY ROOM. FIRE SPREADFROM WEST TO EAST DAMAGING METER & REGULATORE ASSEMBLY, INGITING GAS _ NATURALGAS NOT INVOLVED IN INITIAL FIRE. SUPPLEMENTAL REC'D 7/22/1996 INDICATESCHANGE OF CAUSE FROM OTHER | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1871 | 1996-05-31 | CA | other |  | PACIFIC GAS & ELECTRIC CO | VEHICLE STRUCK METER LOCATION, CAUSING GAS TO ESCAPE UNDER BUILDING. THE GASUNDER THE BUILDING THEN IGNITED. THE RESULTING EXPLOSION AND FIRE CAUSED EXTENSIVE DAMAGE TO THE HOUSE. | 25000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1872 | 1996-05-30 | OH | technical failure | LATTIMER STEVENS | COLUMBIA GAS OF OHIO INC | TWO EMPLOYEES ATTEMPTING TO REPLACE A SERVICE LINE CURB VALVE DIED FROM APPARENT ACCIDENTAL ASPHYXIATION EXACT DETAILS ARE UNKNOWN AS THERE WERE NO WITNESSES. EMPLOYEES WERE FOUND IN EXCAVATION WITH BLOWING NATURAL GAS. OLD CURB VALVE HAD BEEN REMOVED FRO | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1873 | 1996-05-31 | KS | other |  | TWIN COUNTY GAS CO INC |  | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1874 | 1996-06-10 | ID | technical failure | UNKNOWN | INTERMOUNTAIN GAS CO | 3/4" SERVICE PIPE FAILED AT CONTROL POINT WHERE SQUEEZE TOOL WAS IN USE, RESULTING IN ACCIDENTAL IGNITION. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1875 | 1996-06-22 | TX | other |  | ENERGAS CO | DITCH APPEARED TO HAVE SETTLED AND BROKE PIPE. LEAKING GAS MIGRATED INTO STRUCTURE AND WAS IGNITED, POSSIBLY BY ELECTRICAL EQUIPMENT. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1876 | 1996-06-15 | AR | other | TEX TUBE | ARKANSAS LOUISIANA GAS CO (ARKLA GAS CO) | CAR RAN OFF ROAD AND TRAVELED 237FT. HIT METER SETTING & HOUSE CAUSING AN IGNITION AND FIRE. DRIVER SITED FOR D.W.I. | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1877 | 1996-07-10 | MI | technical failure |  | MICHIGAN CONSOLIDATED GAS CO (MICHCON) | ON 07/10/96, THIS INCIDENT WAS REPORTED TO D.O.T. ON THE BELIEF THAT THE EMPLOYEE'S INJURY REQUIRED INPATIENT HOSPITALIZATION. HOWEVER ON 07/10/96 AT 4:40PM WHEN WE CONFIRMED THE EMPLOYEE HAD BEEN TREATED AND RELEASED ON 07/10/96WE CALLED D.O.T. LT. PETTI | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1878 | 1996-06-11 | NJ | ACCIDENTALLY CAUSED BY OPERATOR |  | PUBLIC SERVICE ELECTRIC & GAS CO | ON TUESDAY, JUNE 11, 1996 AT APPROXIMATELY 2:10 P.M., A 1" PLUG ON THE END OFAN 8" DRESSER END CAP WAS INADVERTENTLY REMOVED BY A UTILITY MECHANIC IN ANOPEN EXCAVATION. ONCE THE 1" PLUG WAS REMOVED, A RELEASE OF NATURAL GAS OCCURRED. THIS RELEASE WAS DIRE | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1879 | 1996-06-28 | AZ | other | PHILLIPS DRISCO | CITIZENS UTILITY CO | CALLED IN AS EMERGENCY BLUESTAKE #96261159. DURING LINE (P.E.) SQUEEZE OFF OF 1" LINE, GAS FOREMAN OVERCAME BY GAS FUMES. | 700 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1880 | 1996-07-08 | UT | other | PLEXCO | MOUNTAIN FUEL SUPPLY CO | ON JULY 8, 1996, MR. RICK ASHCROFT, OWNER/OPERATOR OF CEDAR FENCE COMPANY WAS DIGGING 5-FOOT DEEP FENCE POST HOLES USING A CASE AUGER MACHINE. DURING THEPROCESS HE HIT A 2-INCH PLASTIC DISTRIBUTION MAIN. THIS RESULTED IN A FIRE BURNING MR. ASHCROFT, THE C | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1881 | 1996-08-01 | LA | other |  | NEW ORLEANS PUBLIC SERVICE INC | PARTY AT ABOVE MENTIONED ADDRESS WAS ATTEMPTING TO LITE KITCHEN STOVE WHEN EXPLOSION OCCURED, BLOWING THE RIGHT SIDE WALL OUT INTO THE SIDE YARD. PARTY WAS TAKEN TO THE HOSPITAL WITH BURNS. | 80000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1882 | 1996-07-06 | NY | other |  | BROOKLYN UNION GAS CO | THIRD PARTY DAMAGE OF 10 INCH CAST IRON LOW PRESSURE GAS MAIN, SUBSEQUENT IGNITION, SOURCE OF WHICH STILL UNDER INVESTIGATION. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1883 | 1996-07-25 | OH | other |  | HAMILTON GAS DEPT, CITY OF | AT APPROXIMATELY 8:45P.M. ON THURSDAY, JULY 25, 1996; I RECEIVED A PHONE CALL FROM THE CLERK-GUARD ON DUTY ADVISING ME THAT WE HAD A GAS EXPLOSION AT 528SYCAMORE STREET. I ARRIVED AT THE SCENE AT APPROXIMATELY 9:15P.M. AND IMMEDIATELY INQUIRED OF THE UTIL | 20000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1884 | 1996-07-22 | NY | other |  | NIAGARA MOHAWK POWER CORP | WHILE THIRD PARTY WAS EXCAVATING, PULLED APART CUSTOMER-OWNED FUEL LINE AND FILLED HOUSE WITH GAS; UNKNOWN IGNITION CAUSED EXPLOSION. REPORT TO DOT PETTIOFFICER - FINK BEINER. RESIDENTIAL CUSTOMER FUEL LINE. CONTRACTOR PULLEDMETER CONNECTION BREAKING LINE | 75000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1885 | 1996-07-07 | IL | other |  | SALEM, CITY OF | IT IS ASSUMED THAT THE PROBABLE CAUSE OF THE EXPLOSION WAS A DISCONNECTEDCOPPER FUEL LINE TO THE H OT WATER HEATER. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1886 | 1996-07-15 | PR | ACCIDENTALLY CAUSED BY OPERATOR |  | SAN JUAN GAS CO | AT APPROXIMATELY 11:15AM ON JULY 15, 1996, GAS UNDER 25 PSIG IGNITED FROM ANUNDETERMINED SOURCE WHILE TWO SAN JUAN GAS CO. EMPLOYEES WERE WORKING IN A HELLHOLE ON ARECIBO STREET IN SAN JUAN, PUERTO RICO. THE TWO MEN WERE ATTEMPTING TO INSTALL A DRESSER CO | 30000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1887 | 1996-07-09 | MN | technical failure | UPONOR | MINNEGASCO INC | A HIGH-VOLUME TAPPING TEE WAS BEING INSTALLED, THE HEATING IRON DID NOT HAVEA RECESSED FACE AND WENT ABOVE MAXIMUM ALLOWED TEMP. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1888 | 1996-07-17 | VA | ACCIDENTALLY CAUSED BY OPERATOR |  | WASHINGTON GAS LIGHT CO | ON JULY 17, 1996, THE GAS UTILITY COMPANY WAS IN THE PROCESS OF CONVERTING ALOW PRESSURE (7.5" WATER COLUMN) GAS DISTRIBUTION SYSTEM TO A HIGH PRESSURE (20 PSIG) GAS SYSTEM. AT 4:21 P.M.(EST.) AFTER ACHIEVING 20 PSIG GAS DISTRIBUTION PRESSURE, AN EXPLOSIO | 650000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1889 | 1996-07-16 | MT | other |  | MONTANA - DAKOTA UTILITIES CO | AN INVESTIGATION DETERMINED THAT THE GAS LEAKAGE FROM THE METER SET WAS SECONDARY AND RESULTED WHEN THE BUILDING FIRE DAMAGED THE METER AND REGULATOR. A BUILDING FIRE CAUSED A WALL TO COLLAPSE ON A METER SET CAUSING THE METER SET TO LEAK. | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1890 | 1996-07-24 | WI | other |  | WISCONSIN FUEL & LIGHT CO | MERRILL GRAVEL & CONSTRUCTION COMPANY, 2505 EAST STURDEVANT STREET, MERRILL,WI 54452, WAS A WAUSAU, WI. THE PROJECT SPANNED SEVEN BLOCKS, FROM FOREST STREET ON THE SOUTH TO FRANKLIN STREET ON THE NORTH. WORK HAD BEEN UNDERWAY FORSEVERAL WEEKS AT THE TIME | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1891 | 1996-08-01 | OH | other |  | HAMILTON GAS DEPT, CITY OF | ON MONDAY (JULY 29, 1996) I NOTIFIED AL ROSE (GAS SUPV) THAT THE EXISTING 12" GAS MAIN NEEDED TO BE SHUT DOWN FROM CLEVELAND AVE EAST ON N.W. WASHINGTON BLVD. TO WEST ELKTON RD. AND AFTER SHUTING DOWN AND BLEEDING OFF ALL GAS, THECONTRACTOR COULD REMOVE T | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1892 | 1996-08-30 | LA | other | PLEXCO | ARKANSAS LOUISIANA GAS CO (ARKLA GAS CO) | A THIRD PARTY BORING CREW DAMAGED ARKLA'S 4" PLASTIC DISTRIBUTION GAS MAIN. TWO OF ARKLA'S CONSTRUCTION WORKERS, JAMES ROBERSON, AGE 56 AND WILLIAM COOKS,JR., AGE 46, WERE ATTEMPTING TO INSTALL A FULL CIRCLE BAND CLAMP OVER THE DAMAGED PIPE WHEN THE GAS I | 28039 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1893 | 1996-08-20 | TX | other | PHILLIPS | GREY FOREST UTILITIES | GAS LINE WAS MARKED ON 8/7/96 BY OPERATOR. CONTRACTOR HIT THE GAS MAIN WITH A VERMEER T-800 TRENCHER. THE GAS IGNITED AND BURNED THE TRENCHER AND THE TRENCHER OPERATOR. | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1894 | 1996-08-28 | NJ | other | PHILLIPS | PUBLIC SERVICE ELECTRIC & GAS CO | WHILE USING AN OXYACETYLENE TORCH TO CUT METAL GRATING, A LONG HILL TOWNSHIPBOARD OF EDUCATION EMPLOYEE BURNED A HOLE IN A 1 1/4" PLASTIC 60 PSI DESIGN GAS SERVICE WHICH CAUSED AN IGNITION. THE INDIVIDUAL SUSTAINED SERIOUS BURNS AND WAS TRANSPORTED TO ST. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1895 | 1996-08-07 | PA | other | REPUBLIC STEEL | VALLEY CITIES GAS SERVICE | ATHENS TOWNSHIP IS HAVING SANITARY SEWERS INSTALLED IN AN AREA PREVIOUSLY WITHOUT SEWER SERVICE. THE GENERAL CONTRACTOR IS HAROLD R. TRIPP, INC., FROM KULPSVILLE, PA. TO INSTALL THE SEWER UNDER RAILROAD TRACKS BY BORING. THE GENERAL CONTRACTOR HAD PLACED | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1896 | 1996-08-30 | AL | other |  | MARSHALL COUNTY GAS DISTRICT | INVESTIGATION INCOMPLETE AT THIS TIME. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1897 | 1996-08-30 | DC | other |  | WASHINGTON GAS LIGHT CO | AN AIRPORT SHUTTLE BUS, MOVING SOUTH TO NORTH IN A TUNNEL THAT RUNS BENEATH THE MAIN TERMINAL AT NATIONAL AIRPORT, MOVED TO THE OPERATOR'S RIGHT TO ALLOWCLEARANCE FOR AN APPROACHING LARGER AIRLINE EMPLOYEE SHUTTLE BUS. IN DOING SO, ITS RIGHT SIDE MIRROR M | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1898 | 1996-08-25 | MO | other |  | LACLEDE GAS CO | FRACTURED SERVICE LINE-LAB ANALYSIS IS IN PROCESS TO DETERMINE CAUSE OF FAILURE PER 49 CFR 192.61. LAB ANALYSIS IS IN PROCESS TO DETERMINE CAUSE OF FAILURE PER 49 CFR 192.61. UPON EXCAVATION OF THE SERVICE FOLLOWING THE INCIDENT, A FULL CIRCUMFERENCE BREA | 95000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1899 | 1996-09-02 | CA | other |  | PACIFIC GAS & ELECTRIC CO | A HOUSE FIRE WHERE THE FIRE SPREAD TO THE GAS METER SET, MELTING THE REGULATOR AND IGNITING GAS. | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1900 | 1996-09-16 | WA | other | PLEXCO | WASHINGTON NATURAL GAS CO | THIS WAS AN ON-GOING JOB THAT HAD BEEN ONE-CALLED SEVERAL TIMES. THE GAS MAIN WAS MARKED CORRECTLY JUST 6 DAYS PRIOR TO THE OCCURENCE OF THE DAMAGE. A CONTRACTOR USING A BULLDOZER ON A STREET IMPROVEMENT JOB WAS REMOVING UNSUITABLE MATERIAL FROM A PORTION | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1901 | 1996-09-16 | PA | other |  | PHILADELPHIA GAS WORKS | THE CONTRACTOR USING THE EQUIPMENT NOTIFIED PHILADELPHIA GAS WORKS THAT THEYWOULD NOT ONLY BE CUTTING THE PAVING AREA AND WOULD NOT BE DEEP ENOUGH TO AFFECT OUR FACILITY. A THIRD PARTY CONTRACTOR WAS USING A VERMEER WHEEL TRENCHING MACHINE TO INSTALL ELEC | 75000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1902 | 1996-10-01 | TX | ACCIDENTALLY CAUSED BY OPERATOR |  | ENERGAS CO | TWO CONTRACT EMPLOYEES SUFFERED BURNS WHEN GAS IGNITED WHILE THEY WRE DISCONTINUING A SERVICE TAP. ONE VICTIM HOSPITALIZED. SOURCE OF GAS AND IGNITION SOURCE ARE BEING INVESTIGATED. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1903 | 1996-06-05 | TX | maintenance | FISHER | LONE STAR GAS CO | CORROSION DUE TO WATER INFILTRATION OF ENCLOSED BODY. STRUCTURE FIRE DAMAGE POSSIBLY CAUSED BY OVER PRESSURE OF WATER HEATER PILOT. | 70000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1904 | 1996-09-09 | IN | other | SPRAGUE | NORTHERN INDIANA PUBLIC SERVICE CO | ON MONDAY, SEPT. 9, 1996, AT APPROX. 11:30A.M., A PAVING CONTRACTOR, PALMER & SONS PAVING, OF LAKE STATION, INDIANA WAS PLACING BLACKTOP THROUGHOUT THE PARKING LOT OF THE CHESTERTON TERRACE APTS. LOCATED AT 1101 PORTER AVENUE, CHESTERTON, IN. WHILE USING | 913000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1905 | 1996-09-23 | TN | other | PHILLIPS DRISCOPIPE | MEMPHIS LIGHT GAS & WATER DIVISION | AN OUT OF CONTROL AUTOMOBILE STRUCK GAS METER ASSEMBLY BREAKING SERVICE RISER. THE ESCAPING GAS IGNITED, RESULTING IN EXTENSIVE FIRE DAMAGE TO SAID AUTOMOBILE, A ONE-STORY SINGLE-FAMILY RESIDENTIAL DWELLING, AND ANOTHER AUTOMOBILEPARKED IN DRIVEWAY OF ADJ | 108000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1906 | 1996-10-03 | KS | other | DRISCO | UNITED CITIES GAS CO |  | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1907 | 1996-10-01 | MO | other |  | LACLEDE GAS CO | THIRD PARTY REMOVED THE RETAINING BRASS NUT AND WASHER ASSEMBLY FROM LOCK COCK CORE. THIRD-PARTY OCCUPANT STATES THAT HE WAS ATTEMPTING TO TURN ON WATER IN BASEMENT WHEN HE MISTAKENLY REMOVED THE RETAINING BRASS NUT AND WASHER ASSEMBLY FROM THE LOCK COCK | 750000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1908 | 1996-09-24 | IA | other |  | INTERSTATE POWER CO | IPC WAS NOTIFIED OF AN EXPLOSION AT 10:43A.M. SEPT 24, 1996. THE CLEAR LAKE FIRE DEPARTMENT RECEIVED A 911 CALL AT 10:41A.M. THE INCIDENT OCCURRED WITHINTHE HOME OF 805 SOUTH 8TH ST, CLEAR LAKE, IA. IPC'S CLEAR LAKE, IA OFFICE WAS NOTIFIED OF AN EXPLOSION | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1909 | 1996-10-04 | IN | other | DUPONT | NORTHERN INDIANA PUBLIC SERVICE CO | ON OCTOBER 1, 1996, NORTHERN INDIANA PUBLIC SERVICE COMPANY MARKED ITS 2 INCH PE PLASTIC GAS MAIN OPERATING AT 50 PSI ON SOUTH MAPLE LANE, WAKARUSA, INDIANA AT THE REQUEST OF NETWORK FIELD SERVICES. ON FRIDAY, OCTOBER 4, 1996, A SUBCONTRACTOR ON NETWORK F | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1910 | 1996-10-02 | CA | other |  | SOUTHERN CALIFORNIA GAS CO | FIRE AND EXPLOSION AT ABOVE LOCATION RESULTED FROM AT LEAST TWO CAUSES. (1) OUTSIDE CONTRACTOR WORKING FOR CITY OF SAN JACINTO INSTALLED 12" PVC WATER MAIN IN ORDER TO MAINTAIN PROPER DEPTH BENT 3/4" STEEL GAS SERVICE UP AND OVER PVC WATER MAIN. THIS ACTI | 750000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1911 | 1996-09-27 | CA | technical failure | US STEEL | SOUTHERN CALIFORNIA GAS CO | PIPELINE WALL RUPTURED IN SEVERAL LOCATIONS ALONG A 226 FOOT AREA DURING A NITROGEN PRESSURE TEST. THE ABRUPT RELEASE OF THE TEST MEDIUM HURLED SOIL, PAVEMENT & DEBRIS INTO THE ADJACENT AREA, DAMAGING SOME STRUCTURES. TESTED PIPELINE NOT COMPLETELY PURGED | 300000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1912 | 1996-10-08 | OH | other | DRISCO | EAST OHIO GAS CO | WATER DEPARTMENT EXCAVATED TO PERFORM EMERGENCY REPAIR TO WATER LINE. A BACKHOE SNAGGED AND CUT THE TOP OF A 4-INCH PLASTIC GAS MAIN. WATER ENTERED THE LOW PRESSURE GAS PIPING SYSTEM, CAUSING LOSS OF SERVICE TO 246 CUSTOMERS. THE PIPE WAS REPLACED AND SER | 80000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1913 | 1996-11-21 | WA | other | UPONOR | WASHINGTON WATER POWER CO | ELECTRIC FEEDER TURNED OFF REMOTELY AFTER EMERGENCY CALL PLACED TO CENTRAL DISPATCH. ON 11/21/96 AT APPROX 8:20 P.M. JIMMIE DEAN, A GAS CREW FOREMAN, WASKILLED WHEN HE ACCIDENTALLY CAME INTO CONTACT WITH A DOWNED PRIMARY CONDUCTOR. THE GAS CREW, OF WHICH | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1914 | 1996-11-07 | CA | other | MOONEY | PACIFIC GAS & ELECTRIC CO | FOREIGN PARTICLES PASSED THROUGH THE FILTER OF A REGULATOR STATION AND DAMAGED THE WORKING AND BACK-UPS REGULATORS, CAUSING THE TRANSMISSION PRESSURE GASTO ENTER INTO THE DISTRIBUTION MAIN SYSTEM. APPARENT CAUSE - REGULATORS FAILED. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1915 | 1996-12-01 | AK | other | DRISCOPIPE | ENSTAR NATURAL GAS CO | ON SUNDAY MORNING, DECEMBER 1, 1996, AT 5:14 AM AST, ENSTAR PERSONNEL WERE CALLED TO RESPOND TO A HOUSE FIRE AT LOT 7 BIRCH BLUFF SUBDIVISION IN SOLDOTNA, ALASKA. THE ORIGIN OF THE FIRE WAS DETERMINED TO BE THE SPONTANEOUS COMBUTION OF SOME OILY RAGS. NAT | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1916 | 1996-10-27 | OH | other |  | COLUMBIA GAS OF OHIO INC | ON SUNDAY, OCTOBER 27, 1996, AT 12:13P.M. OPERATOR RECEIVED A CALL FROM THE BATTLE RUN FIRE DEPT. REQUESTING A PRESSURE CHECK AFTER A FIRE AT THE AMERICAN LEGION POST IN PROSPECT, OH. AFTER ARRIVING AT THE SCENE AND PERFORMING AN INVESTIGATION, IT WAS DET | 125000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1917 | 1996-11-18 | NE | other |  | METROPOLITAN UTILITIES DISTRICT | WELD FAILURE | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1918 | 1996-11-30 | IL | other |  | NORTHERN ILLINOIS GAS CO | CURRENTLY UNDER INVESTIGATION - CAUSE OF CUSTOMER'S FUEL SYSTEM INSIDE RESIDENCE. CURRENTLY UNDER INVESTIGATION - INSIDE PIPING - CUSTOMER OWNED. | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1919 | 1996-12-02 | MO | other | PHILLIPS/DRISCO PIPE | LACLEDE GAS CO | WHILE ATTEMPTING TO CLEAR A BLOCKED SEWER, A PRIVATE CONTRACTOR'S SEWER AUGERCONTACTED A 1" DIAMETER PLASTIC GAS SERVICE LINE. THE SERVICE LINE HAD BEENINSTALLED WITH A PNEUMATIC BORING TOOL WHICH TRAVELED THROUGH AN 8" OD SEWERLATERAL APPROX 51" DEEP. GA | 115000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1920 | 1996-11-18 | RI | other |  | PROVIDENCE GAS CO | THE LOCATION WAS POINTED OUT AND VERBALLY INDICATED BY THE OPERATOR. D'AMBRACONSTRUCTION WAS INSTALLING SANITARY SEWER MAINS ON SAMUEL GORDON AVENUE IN WARWICK, RI. THE SEWERS WERE BEING INSTALLED AT A DEPTH OF APPROX. 12 FEET. APROVIDENCE GAS COMPANY REP | 250000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1921 | 1996-12-23 | TX | other | DUPONT | ENTEX - DIVISION OF ARKLA INC | GAS MAIN WAS DAMAGED BY A BACKHOE WORKING AT THIS LOCATION. COMPANY EMPLOYEES WERE INSTALLING BY-PASS FITTINGS, PRIOR TO SQUEEZING OFF THE 2" MAIN, WHEN GAS WAS IGNITED FROM AN UNDETERMINED SOURCE. PARTY CAUSING DAMAGE WAS LAREDO CITY SEWER DEPARTMENT. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1922 | 1996-11-21 | PR | other |  | SAN JUAN GAS CO | ATTACHMENT: ADDENDUM - PART I GENERAL REPORT INFORMATION ATTACHMENT -- NOTE: NTSB FOUND THAT NATURAL GAS WAS INVOLVED IN THE ACCIDENT. FOR FURTHER INFORMATION SEE NTIS REPORT NUMBER PB97-916501: TITLE: SAN JUAN GAS COMPANY, INC./ENRON CORP. PROPANE GAS | 5000000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1923 | 1997-01-02 | MS | other |  | MISSISSIPPI VALLEY GAS | INADEQUATE SUPPORT UNDER PLASTIC PIPE ALLOWED BACKFILL TO BEND PIPE WHICH CAUSED STRESS AT A POINT WHERE THE PIPE MADE CONTACT WITH METAL STIFFENER IN COMPRESSION FITTING AND RESULTED IN A BREAK IN THE PLASTIC PIPE. LEAKING GAS FROMBROKEN SERVICE LINE MIG | 30000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1924 | 1996-12-09 | CT | other |  | YANKEE GAS SERVICES CO | AT THE DATE, TIME AND LOCATION INDICATED IN PART 1 -GENERAL REPORT INFO, A FIRE AND EXPLOSION OCCURRED RESULTING IN ONE INJURY REQUIRING MEDICAL ATTENTION AND PROPERTY DAMAGE OF APPROX $200,000. SUBSEQUENTLY, A NATURAL GAS LEAK WASDISCOVERED ON THE GAS DI | 200000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1925 | 1996-11-29 | TX | other | FARRIS | SOUTHERN UNION GAS CO | ON 11/29/96, SUG WAS NOTIFIED BY THE PORT ARTHUR FIRE DEPT THAT A RELIEF VALVE ON THE DISTRIBUTION SYSTEM WAS RELIEVING GAS AND HAD IGNITED. SUG RESPONDED AND ISOLATED THE VALVE. THE VALVE WAS THEN REMOVED AND TRANSPORTED TO THE SUG SHOP LOCATION FOR EVAL | 5000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1926 | 1996-12-03 | TX | other | NIPAK | LONE STAR GAS CO | A HOUSE LOCATED AT 502 CHICAPOO TRACE IN GRAND PRAIRIE, TX WAS DESTROYED BY AN EXPLOSION. IMPACT FROM THE EXPLOSION DAMAGED SEVERAL HOUSES IN THE VICINITY. INVESTIGATION BY LONE STAR GAS COMPANY PERSONNEL REVEALED GAS IN THE SEWERVENTS OF THE HOUSES ON EI | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1927 | 1996-10-24 | PA | maintenance |  | COLUMBIA GAS OF PENNSYLVANIA | A CORROSION LEAK ON A 1 1/2" CUSTOMER OWNED SERVICE LINE 17" FROM THE STRUCTURE ALLOWED GAS TO ENTER A HOME. AN EXPLOSION FOLLOWED BY A FIRE WHICH DESTROYED THE SINGLE STORY RESIDENCE. TWO OCCUPANTS WERE HOSPITALIZED FOR TREATMENTOF BURNS. REPORT IS BEING | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1928 | 1996-12-11 | PA | ACCIDENTALLY CAUSED BY OPERATOR |  | NORTH PENN GAS CO | ON 11/27/96, IN ANTICIPATION OF THE INSTALLATION OF A NEW MAIN ON SOUTH MAINST., A DISTRIBUTION CONSTRUCTION CREW FROM NORTH PENN GAS COMPANY INSTALLED A PORTION OF A NEW SERVICE TO THE RESIDENCE OF 608 SOUTH MAIN ST., COUDERSPORT. THIS SECTION OF SERVICE | 250000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1929 | 1997-01-08 | IL | other |  | NORTHERN ILLINOIS GAS CO | FACILITIES WERE DAMAGED SOME TIME IN THE PAST. CURRENTLY UNDER INVESTIGATION. | 75000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1930 | 1996-12-21 | PA | other |  | CENTRAL PENN GAS CO - DAUPHIN DISTRICT | ON 12/21/96, AN INDIVIDUAL BELIEVED TO BE AN EMPLOYEE OF TROXELL'S TRUCKING,INC., EXCAVATING WITH A BULLDOZER, RUPTURED A FOUR INCH HIGH PRESSURE DISTRIBUTION LINE. THE LINE WHICH WAS OPERATING AT 200 PSIG, SERVES AS THE ONLY FEED TO PFG GAS' DISTRIBUTION | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1931 | 1996-12-10 | TX | other |  | LONE STAR GAS CO (DISTRIBUTION DIVISION) | A 1-1/4" COMPRESSION COUPLING ON SERVICE TAP WAS LEAKING AND IGNITED WHICH CAUSED DAMAGE TO A HOUSE. | 40000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1932 | 1997-01-16 | IA | other | X-TRUBE | PEOPLES NATURAL GAS | GROUND FROST APPARENTLY CAUSED A X-TRUBE SERVICE LINE BEHIND THE SPORTSMAN BAR TO PULL OUT OF A TEE. GAS MIGRATED INTO THE MEN'S RESTROOM IN THE BACK OF THE BAR. AN EXPLOSION OCCURRED AT THE TIME WHEN THE INDIVIDUAL INJURED LIT A CIGARETTE IN THE RESTROOM | 200 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1933 | 1997-01-18 | IL | other |  | NORTHERN ILLINOIS GAS CO | INCIDENT RESULTED FROM AN APPLIANCE INSIDE THE BUILDING. ORIGIN OF THE CAUSEWAS FROM AN APPLIANCE INSIDE THE BUILDING. | 40000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1934 | 1997-01-20 | OH | other | EAST OHIO GAS | EAST OHIO GAS CO | THE DRIP RISER IS LOCATED IN A GRAVELLED DRIVEWAY OR PARKING AREA NEAR A SMALL COMMERCIAL BUILDING. IT APPEARS THAT RECENTLY THIS AREA WAS REGARDED AND FRESH GRAVEL WAS APPLIED. APPARENTLY THE RISER WAS BUMPED OR PUSHED TO ONE SIDE, CAUSING A CRACK AT ITS | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1935 | 1997-01-21 | PA | other |  | PHILADELPHIA ELECTRIC CO | 8" CAST IRON MAIN BREAK UNDER SIDEWALK IN FRONT OF 504 E. GLENOLDEN AVENUE, IN GLENOLDEN, PA RESULTED IN AN EXPLOSION AND FIRE AT 504 AND 502 E. GLENOLDEN AVE. NO DEATHS OR INJURIES KNOWN. THE PROPERTIES AT 504 AND 502 E. GLENOLDEN WERE DESTROYED BY THE E | 400000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1936 | 1997-01-25 | PA | other |  | PHILADELPHIA ELECTRIC CO | MAIN LOCATED UNDER GRASS AREA BETWEEN CURB AND SIDEWALK. 4" CAST IRON MAIN BREAK GRASSY AREA BETWEEN CURB AND SIDEWALK IN FRONT OF 4938 JACKSON DRIVE, BROOKHAVEN, PA RESULTED IN AN EXPLOSION AND PROPERTY DAMAGE AT THAT LOCATION. NO DEATHS OR INJURIES KNOW | 200000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1937 | 1996-10-17 | AL | other |  | ALABAMA GAS CORP | ACCORDING TO RODDY SAMPLE WITH M.U.I., A HOME REMODELING COMPANY DAMAGED THESERVICE LINE TO 711 EASTWOOD PLACE AROUND 10:00AM ON OCT.16. TWO EMPLOYEES, MYSON BLOCKER AND ANDRE BLOCKER, ATTEMPTED TO MAKE THE SERVICE LINE SAFE. MYSON LOST CONSCIOUSNESS AND | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1938 | 1997-01-15 | PA | other |  | U G I CORP | ESCAPING GAS FROM A TWO-INCH FRACTURED MAIN MIGRATED UNDERGROUND INTO THE HOUSE AT 2211 CULLUM DRIVE WHERE IT ACCUMULATED AND SUBSEQUENTLY WAS IGNITED BYAN UNKNOWN SOURCE. THE HOUSE WAS DESTROYED BY THE RESULTING EXPLOSION AND ENSUING FIRE. THERE WERE NO | 250000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1939 | 1997-01-24 | PA | other |  | PHILADELPHIA GAS WORKS | THE FACTORS BELIEVED TO HAVE CONTRIBUTED TO THIS INCIDENT HAVE BEEN INVESTIGATED BY THE PHILADELPHIA FIRE DEPT. AND THE PHILADELPHIA GAS WORKS (PGW). PWGFOUND A CIRCUMFERENTIAL BREAK ON A 6" CAST IRON GAS MAIN AT 139'6" SOUTH OF THE SOUTH CURB LINE OF ERI | 75000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1940 | 1997-02-14 | MN | other | DUPONT ALDYL A | PEOPLES NATURAL GAS | METER SET SERVICE REGULATOR APPARETLY OVERPRESSURED THE CUSTOMER'S FUEL LINEPIPING RESULTING IN A FIRE AND EXPLOSION. REGULATOR VENT APPARENTLY FROZEOVER CAUSING OR CONTRIBUTING TO THE INCIDENT. SERVICE REGULATOR ICED OVER. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1941 | 1997-01-29 | DE | other | CENTRAL PLASTIC | CHESAPEAKE UTILITY CORP | METER ASSEMBLY WAS STRUCK BY A PASSENGER VEHICLE. THE SERVICE RISER WAS DAMAGED BELOW THE INLET VALVE. THE CAUSE OF THE INCIDENT WAS A VEHICULAR ACCIDENT. A PASSENGER VEHICLE STRUCK AND DAMAGED AN APARTMENT BUILDING AND ADJACENT NATURAL GAS METER SET. A R | 1500000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1942 | 1997-01-30 | OH | other |  | CINCINNATI GAS & ELECTRIC CO | THE RESPONDING POLICE DEPT REPORTED THAT THERE WAS A HOUSE ON FIRE AND AN INDICATION OF GAS IN THE SEWERS. FOUND WAS A FOUR INCH CAST IRON MAIN BROKEN WHERE THE WATER SERVICE CROSSED THE MAIN. THIS WAS LOCATED APPROX 42' FROM THE FACE OF THE BUILDING & DI | 118000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1943 | 1997-02-24 | MS | other |  | MISSISSIPPI VALLEY GAS | FEBRUARY 24, 1997, THE CITY OF JACKSON FIRE DEPT. CALLED OUR COMPANY AT 9:42P.M. REQUESTING ASSISTANCE WITH A HOUSE FIRE AT 2529 UTAH STREET. OUR SERVICE REP. ARRIVED ON THE SCENE AT 9:53 P.M. AND FOUND GAS SERVICE WAS ALREADY CUT OFF AT THE METER. DUE TO | 75000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1944 | 1997-02-27 | AK | other |  | ENSTAR NATURAL GAS CO | ON THURSDAY, 02/27/97 AT APPROX. 6:15 AM AST, ENSTAR NATURAL GAS COMP RESPONDED TO A HOUSE FIRE AT 821 BOUNTY DRIVE, ANCHORAGE, AK (LOT 22, BLOCK 13 OCEAN VIEW SUBDIVISION). ANCHORAGE FIRE DEPT OFFICIALS REPORTED THE FIRE ORIGINATED WHEN THE OCCUPANT THRE | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1945 | 1997-02-18 | GA | technical failure |  | GEORGIA NATURAL GAS CO | WHILE REMOVING A SECTION OF PIPE FROM SERVICE, NATURAL GAS BEGAN ESCAPING AND IGNITED. THREE CREW MEMBERS WERE BURNED REQUIRING HOSPITALIZATION. ONE OF THE CREW MEMBERS DIED FROM THESES INJURIES ON 3/4/97. | 50 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1946 | 1997-03-12 | AL | other |  | TRUSSVILLE, UTILITIES BOARD, CITY OF | LIQUID BUTYL AND PROPYL MERCAPTAN, TRADE NAME, B.P. CAPTAN, SPILLED FROM A ODORANT STORAGE TANK AS THE RESULT OF AN AUTOMOBILE ACCIDENT. 3RD PARTY DAMAGECAUSED BY AUTOMOBILE ACCIDENT. ON MARCH 12, 1997 A NATURAL GAS ODORIZING LIQUID LINE RUPTURED, SPILLIN | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1947 | 1997-02-16 | MI | other | U.S. STEEL | CONSUMERS POWER CO | CUSTOMER HIT METER ASSEMBLY WITH SNOW PLOW BLADE BREAKING ABOVE GROUND PIPING. GAS ENTERED THROUGH BASEMENT WALL. | 60000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1948 | 1997-02-14 | MI | other |  | SOUTHEASTERN MICHIGAN GAS CO | THIS INCIDENT OCCURRED ON 2/14/97 AT APPROX 8:00PM WHEN A 1/2" PLASTIC SERVICE LINE SERVICING A MOBILE HOME AT 10423 MIDDLE LANE, CASCO TOWNSHIP SEPARATED FROM A 3/4" METAL HEAD ADAPTOR ABOVE GROUND CAUSING GAS LEAKAGE WHICH MIGRATED UNDERNEATH THIS MOBIL | 80000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1949 | 1997-02-22 | IL | other |  | NORTHERN ILLINOIS GAS CO | INSIDE APPLIANCE OR PIPING MAY HAVE MALFUNCTIONED RESULTING IN AN EXPLOSION IN THE ATTIC/CHIMNEY AREA. CURRENTLY UNDER INVESTIGATION - CUSTOMER'S INSIDE APPLIANCE OR PIPING. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1950 | 1997-02-24 | MO | other |  | LACLEDE GAS CO | NATURAL GAS, FROM AN UNDETERMINED SOURCE, WAS APPARENTLY IGNITED WHEN A FLUORESCENT LIGHT WAS BEING CHANGED IN THE BASEMENT OF THE BUILDING. A LEAK WAS FOUND ON A LOCK VALVE ON THE OUTLET SIDE OF THE METER AND NUMEROUS LEAKS WERE FOUND ON THE CUSTOMER'S F | 25000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1951 | 1997-02-21 | MN | other | FISHER | MINNEGASCO INC | REGULATOR MALFUNCTION POSSIBLY CAUSED BY ICE BUILDUP ON RELIEF VENT. POSSIBLEICE BUILDUP ON REGULATOR RELIEF VENT OF METER SET ASSEMBLY. | 350000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1952 | 1997-02-19 | CA | other |  | ULTRAMAR REFINING CO | ROADWAY CONSTRUCTION CO A SUBCONTRACTOR FOR HEATEHOG CONSTRUCTION WHO WAS THEPRIMARY CONTRACTOR FOR THE PORT OF L.A. ON THE "ALAMEDA CORRIDOR PROJECT"PUNCTURED ONE 8" CG-101 FUEL GAS PIPELINE. THIS PIPELINE WAS OUT OF SERVICE ATTHE TIME. PRIOR TO THE LINE | 20000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1953 | 1997-03-24 | TN | other | AMER STEEL | HENDERSON GAS DEPT, CITY OF | THIS PIPELINE WAS INSTALLED BY A PRIVATE CONTRACTOR HIRED BY THE CITY OFHENDERSON IN CONJUNCTIN WITH THE WIDENING OF STATE RT 45 WHICH WAS BEING DONEFOR THE STATE BY AA SEPERATE CONTRACTOR. NATURAL GAS WAS INTRODUCED INTO THEPIPE 10-09-96. AT THAT TIME TH | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1954 | 1997-03-04 | KY | other |  | WESTERN KENTUCKY GAS CO | AT APPROX. 1925, 3/4/97 CDT WKG RECIEVED NOTIFICATION FROM A 911 DISPATCHERREGARDING A HOUSE FIRE AT THE STATED ADDRESS IN DANVILLE KENTUCKY. THE CAUSEOF THE FIRE WAS UNKNOWN AT THE TIME AND WKG WAS DISPATCHED TH THE SCENE. THECAUSE OF THJIS INCIDENT IS S | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1955 | 1997-03-16 | MN | other |  | MINNEGASCO INC | THIS DAMAGE OCCURED IN 1973, WHEN A PLUMBING CONTRACTOR INSTALLED A WATERSERVICE. CORRESPONDENCE RECEIVED 5/27/1997 THAT REVISED THAT DAMAGE OCCURREDIN 1975, NOT 1973. | 60000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1956 | 1997-04-18 | AK | other | DRISCOPIPE | ENSTAR NATURAL GAS CO | ON FRIDAY APRIL 18, 1997 AT APPROX. 2:45 AM AST ENSTAR NATURAL GAS CO.PERSONNEL RESPONDED TO A HOUSE FIRE AT LOT 10 BLOCK 5 SHERWOOD ESTATES NO. 1IN THE MATANUSKA-SUSITNA BOROUGH. THIS LOCATION IS APPROX. 5 MILES NORTHWESTOF THE CITY OF WASILLA, ALASKA. A | 95000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1957 | 1997-03-18 | IL | other |  | WHITE HALL GAS DEPT, CITY OF | THE FAILURE OF A COPPER FLARE FITTING ON THE TUBING SERVING THE FURNACE CAUSEDBUILD-UP OF GAS IN THE BASEMENT AREA AND ULTIMATE IGNITION. | 200000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1958 | 1997-04-07 | LA | other |  | GULF STATES PIPELINE CORP | A 1000 GAL TANK OVERFLOWED THE CONTAINMENT WALL ALLOWING THE Y-GRADE CONDESATETOP FLOW ONTO THE GROUND , THEN OUTSIDE THE CONTAINMENT FENCE OF THE FACILITY. | 15000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1959 | 1997-04-26 | FL | other | EX-TRUBE | FLORIDA WATER SERVICES | LIGHTNING HIT 1/2" GAS SERVICE IGNITED GAS, BLOWING HOLE IN EX-TRUBING BELOWSERVICE VALVE. | 10000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1960 | 1997-04-13 | WY | other | UNK | K N ENERGY INC(KANSAS NEBRASKA GAS CO) | THE INCIDENT OCCURED WHEN AN ANODELESS RISER BROKE UPSTREAM OF A METER LOOPSERVING A TRAILER HOUSE. GAS ESCAPED AND WAS IGNITED BY THE TRAILER'S FURNACEOR WATER HEATER AND THE TRAILER WAS DESTROYED. THE APPARENT CAUSE OF THE BREAKWAS A SIGNIFICANT AMOUNT | 54000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1961 | 1997-04-30 | MI | other |  | MICHIGAN CONSOLIDATED GAS CO (MICHCON) | ON MAY 1 1997, UPON KNOWLEDGE THAT THE REAPIR COMPLTETED ON APRIL 30 1997 AT10:30 BY MEANS OF A 24" PIPE, TELEPHONIC WAS GIVEN TO THE DOT THAT DAMAGE/LOSSCOULD EXCEED 50,000.00. THE EVALUATION LATER CONCLUDED THE 24" REPAIR CLAMP TOBE PERMANENT REPAIR; RE | 41752 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1962 | 1997-01-30 | TX | other |  | BRADY MUNICIPAL GAS CORP, CITY OF |  | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1963 | 1996-09-26 | LA | other |  | SOUTH COAST GAS CO INC | A VEHICLE TRAVELING ON CANAL STREET LOST CONTROL AND STRUCK THE METER SETASSEMBLY AND HOUSE AT 309 CANAL ST. THE METER SET WAS BROKEN FROM THE SERVICELINE AND AN INGNITION OF THE NATURAL GAS OCCURED. THE VEHICLE AND THE HOUSESUFFERED FIRE DAMAGE. | 60000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1964 | 1997-05-20 | TX | other | NAPCO | UNIVERSAL NATURAL GAS, INC. | SPRINKLER SYSTEM INSTALLER TRENCHED INTO 3/4" POLY SERVICE LINE. TRENCHERCAUGHT FIRE. FIRE DEPT. PUT OUT FIRE. NO OTHER DAMAGE OR INJURY. | 600 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1965 | 1997-04-30 | MO | other | RW LYALL CO. | MISSOURI GAS ENERGY | MISSOURI GAS ENERGY'S SERVICEMAN WAS WORKING IN REPUBLIC MISSOURI THE MORNINGOF APRIL 30, 1997 WHEN HE NOTICED SMOKE IN THE SOUTHEAST SIDE OF THECOMMUNITY. HE PROCEEDED TO THE AREA TO INVESTIGATE AND FOUND A NEW HOME, UNDERCONSTRUCTION, ON FIRE AT 1155 HO | 120000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1966 | 1997-04-27 | OH | other |  | CINCINNATI GAS & ELECTRIC CO | VEHICLE BURNED ALONG WITH ITS OCCUPANT. THIS WAS RULED A SUICIDE BY THEHAMILTON COUNTY CORONER. THE METER ASSSEMBLY WAS ADAQUATELY PROTECTED WITH 2"AND CHAIN LINK FENCING. THE INDIVIDUAL WAS OPERATING A MOTOR VEHICLE WITHEXCESSIVE SPEED IN A PARKING AREA. | 17000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1967 | 1997-06-05 | OK | other | PLEXCO | OKLAHOMA NATURAL GAS CO | LINE WAS CUT BY TRENCHING MACHINE OPERATOR EXCAVATING BEYOND THE BOUNDRIESOF HIS LINE LOCATE REQUEST. | 62000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1968 | 1997-06-03 | CO | other |  | PUBLIC SERVICE CO OF COLORADO | A SINGLE WOOD FRAME RESIDENCE WAS DESTROYED. THE LONE ELDERLY FEMALEEXPLOSION OCCURRED INSIDE OF STRUCTURE. NO APPARENT OUTSIDE OF STRUCTURESOURCE OF NATURAL GAS. A SINGLE WOOD FRAME RESIDENCE WAS DESTROYED. THELONE ELDERLY FEMALE OCCUPANT WAS TRANSPORT | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1969 | 1997-05-26 | PA | other |  | PHILADELPHIA GAS WORKS |  | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1970 | 1997-05-15 | CA | other | UNKNOWN | PACIFIC GAS & ELECTRIC CO |  | 173000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1971 | 1997-07-02 | MI | other |  | CONSUMERS POWER CO | WINDS FROM TORNADO MOVED ODERIZER BUILDING FROM FOUNDATION CAUSING DAMAGE TOBUILDING AND INTERNAL PIPING. ODERIZER WAS NOT IN OPERATION AT TIME OFINCIDENT. HIGH WINDS FROM TORNADO DAMAGED ODORIZER BUILDING AND PIPING. | 80000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1972 | 1997-06-10 | KS | ACCIDENTALLY CAUSED BY OPERATOR | UNKNOWN | K N ENERGY INC(KANSAS NEBRASKA GAS CO) | EMPLOYEES MOVING METER FROM PROPERTY LINE TO HOUSE, INCLUDING INSTALLATION OFNEW YARD LINE. THE DESIGN OF THE EXISTING FACILITIES REQUIRED THE USE OF ANEXPANDABLE PLUG IN THE SERVICE STUB TO STOP THE FLOW OF GAS. AFTER WELDING AMUELLER "NO BLOW" FITTING T | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1973 | 1997-06-04 | TX | maintenance |  | LONE STAR GAS CO OF TEXAS, INC | CORROSION CAUSED A LEAK IN THE PIPELINE AND THE GAS LEAKED INTO THE BUILDING. | 150000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1974 | 1997-06-20 | IN | other |  | CITIZENS GAS & COKE UTILITY |  | 500 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1975 | 1997-06-21 | AZ | other | KERONA | SOUTHWEST GAS CORP | TREE ROOTS ENCAPSULATED AN 1 1/4 ABS SERVICE, CAUSING A LEAK TO DEVELOP.IGNITION OCCURED FROM AN UNDETERMINED SOURCE, CAUSING DAMAGE TO APARTMENT #17AT 534 E. HUNTINGTON. SUSEQUENT LABORATORY ANALYSIS CONFIRMED PIPE FAILURE DUETO EXTERNAL STRESS CAUSED B | 71000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1976 | 1997-06-10 | IA | other |  | MIDAMERICAN ENERGY CO | CONTRACTOR WAS DIGGING IN STREET WITH BACKHOE. BACKHOE BUCKET HOOKED ANDPULLED 3/4" SERVICE RESULTING IN DAMAGE TO METER SET IN BASEMENT OF RESIDENCE.THE DAMAGE CAUSED A LEAK IN THE BASEMENT WHICH RESULTED IN THE EXPLOSION. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1977 | 1997-06-14 | MI | other |  | MICHIGAN CONSOLIDATED GAS CO (MICHCON) | ON JUNE 14, 1997 A CAR RAN INTO A NATURAL GAS DISPENSER AT A MOBILE GASSTATION. REPAIRS INCLUDED REPLACEMENT IF STAINLESS STELL TUBE FROM COMPRESSORTO DISPENSER REPAIR OF AIR PURGE LINE AND ELECTRICALCONDUIT. THERE WAS NORELEASE OF GAS, AUTOMATIC SHUT OFF | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1978 | 1997-07-15 | AK | other | PHILLIPS DRISCOPE | ENSTAR NATURAL GAS CO | ON TUESDAY JULY 15 , 1997 AT APPROX. 1:15 PM , ENSTAR GAS CONTROL WAS NOTIFIEDBY MATANUSKA TELEPHONE ASSOC. THAT ONE OF THEIR CREWS HASD DAMAGED A GAS MAINAND IT WAS ON FIRE AT THE INTERSECTION OF REGENCY DRIVE AND BUISNESS BLVD. INEAGLE RIVER ALASKA. UPO | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1979 | 1997-07-12 | LA | other | TEXTUBE | ARKLA, A NORAM ENERGY COMPANY | THE CONTRACTOR FOR THE MOBILE HOME PARK WAS CLEARING A DITCH WITH A BACKHOEAND CUT A 2" PLASTIC MAIN. THE GAS IGNITED AND THE OPERATOR WAS BURNED.CONTRACTOR CLEANING DITCH WITH BACKHOE AND CUT A 2" PLASTIC LINE. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1980 | 1997-07-08 | TX | other | ROCKWELL | ARKLA, A NORAM ENERGY COMPANY | FIRE INVESTIGATORS SAID GAS WAS NOT INVOLVED.HOUSE FIRE HEATED METER ANDREGULATOR TO THE POINT OF MELTING. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1981 | 1997-08-07 | PA | other |  | PENNSYLVANIA GAS & WATER CO | A CAR ROLLED DOWN A HILL CRASHED THROUGH A WOODEN FENCE AND KNOCKED OFF A GASREGULATOR AT SAID ADRESS. THE STRUCTURE WAS HEAVILY DAMAGED. IT IS UNKNOWN ATHTIS TIME HOW THE CAR ROLLED DOWN THE HILL. | 80000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1982 | 1997-07-26 | CO | other | AMERICAN | COLORADO SPRINGS, CITY OF | TOWNHOUSE OWNER WAS OPERATING A CHARCOAL SMOKER IN PATIO/CARPORT AREA ANDPUSHED SMOKER AGAINST A CEDAR PRIVACY FENCE, WHICH IGNITED. FLAMES FROM THEBURNING FENCE IMPINGED ON THE GAS SERVICE REGULATOR WHICH FAILED AND ESCAPINGGAS ACCELERATED THE FIRE, WHIC | 180000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1983 | 1997-08-03 | VA | other |  | COMMONWEALTH GAS PIPELINE CORP | ON AUGUST 3, 1997, AT APPROX. 9:17 PM A TEENAGE BOY LOST CONTROL OF A STOLENCAR. THE CAR JUMPED THE CURB TRAVELED THROUGH A FIVE FOOT WOODEN FENCE ANDCRASHED INTO OUR METER SETTING WHICH RESULTED IN THE RELEASE AND IGNITION OFNATURAL GAS. THE FIRE DESTRO | 200000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1984 | 1997-08-15 | MA | other |  | BAY STATE GAS CO | A BAY STATE GAS COMPANY EMPLOYEE WAS BURNED WHEN GAS IGNITED DURING A MAINABNDONMENT PROCEDURE. SOURCE OF IGNITION IS UNKNOWN. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1985 | 1997-07-25 | MO | other |  | MISSOURI GAS ENERGY | ON JULY 25 1997 AN IGNITION OCCURED IN A SIUTHWESTERN BELL(SWB) MANHOLE ON THEWEST SIDE OF LEE SUMMIT RD. SOUTH OF INTERSTATE 70 IN IDEPENDENCE MISSOURI.THE INCIDENT WAS REPORTED BY THE INDEPENDENCE FIRE DEPT. DISPATCHER TO THEMISSOURI GAS ENERGY DISPATCH | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1986 | 1997-07-18 | MO | other |  | LACLEDE GAS CO | REIDENTIAL STRUCTURE EXPLOSION AS A RESULT OF APPARENT NATURAL GAS IGNITION.INVESTIGATION FOUND AN OPEN 3/8 INCH FUEL RUN IN THE BASEMENT OF THERESIDENCE. OPERATOR'S EMPLOYEE HAD RE-ESTABLISHED GAS SERVICE APPROX. 13 HRS.PRIOR TO IGNITION. | 75000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1987 | 1997-08-05 | NJ | ACCIDENTALLY CAUSED BY OPERATOR |  | SOUTH JERSEY GAS CO | THE OPERATOR IN PREPARING TO REPLACE A LEAKING 1-1/4" BARE STEEL SERVICE WASREMOVING AN EXISTING STEEL SERVICE TEEWHEN LEAKING GAS AROUND THE THREAD AREAOF THE SERVICE TEE IGNITED. CAUSE OF IGNITION IS UNDER INVESTIGATION. AS OFTHIS DATE IT APPEARS THAT A | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1988 | 1997-07-30 | TX | other |  | LONE STAR GAS CO (DISTRIBUTION DIVISION) | CITY CONTRACTOR HIT GAS LINE WITH MECHANIZED EQUIPMENT. | 15000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1989 | 1997-06-20 | OK | other |  | CHELSEA GAS AUTH | B.J.P. ENTERPRISES INC. LAYING 4" PVC WATER LINE. TRACKHOE KNOCKED HOLE IN TOPOF 6" COATED PIPELINE. CLAMP OFF LEAK TEMPORARALY, WILL MAKE PERMANENT REPAIR6/23/1997. | 6000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1990 | 1997-07-30 | OH | other | FISHER | EAST OHIO GAS CO | THE CAUSE OF THE INCIDENT WAS A LARGE COMMERCIAL LAWN MOWER THAT HIT A CLEARLYVISIBLE ABOVE GROUND 2-INCH NATURAL GAS SERVICE REGULATOR. THE IMPACT OF THELAWN MOWER BROKE THE REGULATOR , JAMMING IT IN AN OPEN POSITION AND ALLOWINGAN ELEVATED LEVEL OF GAS | 2500000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1991 | 1997-06-06 | PA | other | YZ INJET | PECO ENERGY CO | ON JUNE 6 , 1997 WE INJECTED TOO MUCH ODORANT INTO OUR NATURAL GASDISTRIBUTION SYSTEM. THE PRIMARY ODERIZER AT THE WEST CONHOHOCKEN GATE STATIONFAILED. DURING THE MANUAL TRANSFER OVER TO THE BACK UP SYSTEM , AN APPARENTOPERATOR ERROR RESULTED IN EXCESS AM | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1992 | 1997-08-04 | FL | other | PLECO | PEOPLES GAS SYSTEM INC | CONTRACTOR WAS TRENCHING PARALLEL TO OUR 2" PE MAIN AT APPROX. 12" AWAY.OPERATOR STOPPED TRENCHER TURNED IT AROUND DROPPED CHAIN TO ATRT TRENCHINGAGAIN AND HIT OUR MAIN. HITING MAIN RESULTED IN IGNITION AND CONTRACTOR'SEMPLOYEE SUFFERED BURNS. MAIN WAS MA | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1993 | 1997-07-30 | AR | technical failure |  | CITIZENS UTILITY CO | ON 7/30/1997 AT 8:00 AM TOM BROWN AND CHRIS RICE WENT TO 6500 MACCURDY DR. TORAISE A 1-1/4" STEEL METER STOP OUT OF THE DIRT FOR THE SERVICE DEPT. UPONARRIVAL CONES WERE SET UP TO MARK THE PERIMETER OF THE CONSTRUCTION ZONE ANDONE OF THE TWO FIRE EXTINGUI | 30000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1994 | 1997-08-13 | MI | other |  | MICHIGAN CONSOLIDATED GAS CO (MICHCON) | GAS LEAKING FROM A REPAIR COUPLING ON A 1-1/2 PLASTIC SERVICE MIGRATED INTO ANUNDERGROUND VAULT WHERE IT IGNITED. ORIGINALLY TWO EMPLOYEES WERE HOSPITALIZEDWITH BURN INJURIES. WE HAVE SUBSEQUENTLY LEARNED THAT ONE HAS DIED; WEBELIEVED DUE TO AN INFECTION | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1995 | 1997-08-01 | NC | other |  | PUBLIC SERVICE CO OF NORTH CAROLINA | EMPOLOYEE OF GENERAL CONTRACTED THAT BURT BUILDING WAS ATTEMPTING TO LIGHTCOMMERCIAL DRYER. EMPLOYEE REMOVER A PLUG FROM AN VALVE AND OPENED VALVE TOPURGE AIR FROM NEW GAS LINE IN BUILDING. VALVE WAS LEFT OPEN RESULTING IN ABUILD UP OF NATURAL GAS IN BUIL | 20000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1996 | 1997-07-15 | TN | other |  | MEMPHIS LIGHT GAS & WATER DIVISION | LIGHTNING STRUCK THE GAS METER AT THIS RESIDENCE, RUPTURING THE SERVICE RISERAPPROX. SIX INCHES ABOVE GROUND, AND IGNITING THE ESCAPING GAS. THE RESULTINGFIRE DID AN ESTIMATED 70,000 DAMGE TO THE STRUCTURE AND CONTENTS. THERE WERENO PERSONAL INJURIES. | 70000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1997 | 1997-08-08 | TX | other | UNK. | ENTEX, A NORAM ENERGY COMPANY (FORM. DIV OF ARKLA | SERVICE LINE WAS PULLED FROM COMPRESSION COUPLING AND ESCAPING GAS IGNITED.UNKNOWN FORCE PULLED SERVICE LINE FROM COMPRESSION COUPLING, ESCAPING GAS WASIGNITED. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1998 | 1997-08-15 | TX | other |  | LONE STAR PIPELINE CO (TRANSMISSION DIVISION) | CONTRACTOR DRILLED INTO A 6" POLY MAIN. | 68000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1999 | 1997-08-24 | CO | other | SPAGUE | COLORADO SPRINGS, CITY OF | APART. RESIDENT WAS OPERATING AN ELECTRIC RANGE INSIDE UNIT #4249 WHICHRESULTED IN A GREASE FIRE. THE FIRE SPREAD THROUGHOUT THE UNIT AND ALONG APATIO FENCE. FLAMES FROM THE BURNING FENCE INPINGED ON THE GAS SERVICEREGULATIONS OF UNITS 4249 AND 4247, WHIC | 250000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2000 | 1997-08-27 | MD | other | DRISCO 8000 | BALTIMORE GAS & ELECTRIC CO | ON AUGUST 27, 1997 AT 1051 ANNE ARUNDEL COUNTY FIRE DEPT. REPORTED A NATURALGAS PIPE ON FIRE WITH PERSONAL INJURIES INVOLVED. BALTIMORE GAS AND ELECRICRECIVED THE CALL AT 1051 DISPATHCHING A GAS MECHANIC TO THE SCENE. ARRIVING ONSCENE AT 11:10 BALTIMORE G | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2001 | 1997-08-17 | TX | other | UNK. | ENTEX, A NORAM ENERGY COMPANY (FORM. DIV OF ARKLA | A ONE INCH I.P. STEEL SERVICE LINE CRACKED AT THREADED ELL, RELEASING GASUNDERGROUND NEAR BUILDING. | 5000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2002 | 1997-09-03 | TX | other |  | ENTEX, A NORAM ENERGY COMPANY (FORM. DIV OF ARKLA | BUSHHOG OPERATOR EMPLOYED BY KOCH RAN OVER BARRICADED METER BREAKING NIPPLEOFF ABOVE SHUT OFF VALVE. ESCAPING GAS IGNITED AND DAMAGED TRACTOR. ALSO,FLASH BURNED TRACTOR OPERATOR ON HANDS AND ARMS. DOCTOR SAID ABOUT LIKE A BADSUNBURN. | 8000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2003 | 1997-09-11 | AZ | technical failure | KERONA | SOUTHWEST GAS CORP | AN ELECTRIC CABLE WAS INSTALLED IMMEDIATLEY ABOVE AND IN CONTACT WITH THE2"PVC GAS MAIN . THE CABLE HAD A SHORT, OR GROUND FAULT, MELTING THE PLASTICGAS MAIN. THE ESCAPING GAS WAS IGNITED BY AN UNKNOWN SOURCE WHICH DAMAGED ONEAPRTMENT BUILDING THAT CONTAI | 276500 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2004 | 1997-09-24 | IL | other | PLEXCO | ILLINOIS POWER CO | DIRECTIONAL BORING UNIT CUT 5/8" PLASTIC SERVICE GAS MIGRATED THROUGH BURIEDTILE INTO HOME AND WAS IGNITED BY AN UNIDENTIFIED SOURCE. | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2005 | 1997-08-28 | LA | other |  | LOUISIANA GAS SERVICE CO | MOST PROBABLE SCENARIO FOR FIRE EVENT - THIS AREA HAS A HISTORY OF SOILSUBSIDENCE. ALSO, THERE HAS BEEN NEW DRAINAGE CONSTRUCTION DONE ON ARTHURSTREET AND CROSS STREET EISENHOWER WITHIN THE PAST YEAR. IT IS PROBABLE THATSUBSIDENCE AND/OR RECENT CONSTRUCTI | 121500 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2006 | 1997-09-20 | MI | other |  | MICHIGAN CONSOLIDATED GAS CO (MICHCON) | ON SEPT 20, 1997 THE INCIDENT WAS REPORTED TO DOT DUE TO OPERATORJUDGEMENT/EMRGENCY ACTION DUE TO 50 PSIG OF NATURAL GAS BLOWING INTO THEATMOSPHERE. WOODWARD AVENUE BEING TOTALLY BLOCKEDTO TRAFFIC BOTH NORTH ANDSOUTHBOUND, POLICE AND FIRE PERSONNEL ON SIT | 8061 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2007 | 1997-09-16 | OH | maintenance |  | EAST OHIO GAS CO | A 2 INCH LOW PRESSURE BARE STEEL GAS MAIN EXTENMDED THROUGH AN ELECTRICUTILITY VAULT. DURING A BAND CLAMP REPAIR OPERATION, THE PIPE FAILED AS ARESULT OF SEVERE ATMOSPHERIC CORROSION. TWO EMPLOYEES WERE OVERCOME BYESCAPING NATURAL GAS. A SUPERVISOR CALLED | 5000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2008 | 1997-10-04 | PA | other |  | PENNSYLVANIA GAS & WATER CO | ON OCTOBER 1, 1997 THE SUNBURY MUNICIPAL WATER DEPT. WAS WORKING ON KELLERSTREET AND HIT AN ACTIVE GAS SERVICE. AT THIS TIME, THE DAMAGED SECTION OFPIPE WAS CUT OUT AND CAPPED BY PG ENERGY'S PERSONNEL ALLOWING TH EWATERCOMPANY TO CONTINUE IT'S WORK. THE R | 90000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2009 | 1997-11-05 | MO | other |  | LACLEDE GAS CO | EXTERNAL STRESSES ON A SIX-INCH CAST IRON LOW PRESSURE MAIN CAUSED A FRACTUREOF APPROXIMATELY 85% AROUND THE CIRCUMFERENCE. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2010 | 1997-11-11 | AL | other |  | MOBILE GAS SERVICE CORP | THE DISTRIBUTION SYSTEM RECEIVED CONSTRUCTION DAMAGE FROM A CONTRACTOR WHICHRESULTED IN A RELEASE OF GAS. BASED ON INVESTIGATION TO DATE, THE EVIDENCE ISRESULTED IN A RELEASE OF GAS. BASED ON INVESTIGATIONS TO DATE, THE EVIDENCENOT SUGGESTIVE OF A NATUR | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2011 | 1997-09-18 | KY | maintenance |  | LOUISVILLE GAS & ELECTRIC CO | SECTION OF MAIN HAS BEEN REPLACED. IGNITION OF GAS OCCURRED DURING LEAKPART A - SECTION OF MAIN HAS BEEN REPLACED. IGNITION OF GAS OCCURRED DURINGLEAK REPAIR. SOURCE OF IGNITION NOT DETERMINED.REPAIR. SOURCE OF IGNITION NOT DETERMINED. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2012 | 1997-08-13 | IA | ACCIDENTALLY CAUSED BY OPERATOR | PLEXCO-YELLOWSTRIPE | MIDAMERICAN ENERGY CO | PIPELINE CONTRACTOR WAS RELEASING RESIDUAL PRESSURE TO RETIRE A GAS MAIN WHENAN ACCIDENTAL IGNITION OCCURRED IN A TRENCH. ONE CONTRACTOR EMPLOYEESUSTAINED BURNS ON HIS FOREARMS AND REQUIRED IN-PATIENT HOSPITALIZATION.STATIC ELECTRICITY IS SUSPECTED AS TH | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2013 | 1997-10-05 | IL | other |  | MIDAMERICAN ENERGY CO | THE INCIDENT IS STILL UNDER INVESTIGATION. THE INVESTIGATION HAS NOTINDICATED NATURAL GAS FROM MIDAMERICAN PIPELINE AS THE CAUSE TO DATE. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2014 | 1997-10-13 | CA | other | DUPONT | SOUTHERN CALIFORNIA GAS CO | AXIAL CRACKS DEVELOPED ALONG 2" PE MAIN DUE TO TREE ROOTS. TREE ROOTPART 3 - AXIAL CRACKS DEVELOPED ALONG 2" PE MAIN DUE TO TREE ROOTS. PART D -TREE ROOT ENTANGLEMENT RESULTED IN AXIAL CRACKS DEVELOPING ON 2" PE MAINENTANGLEMENT RESULTED IN "AXIAL" CRAC | 250000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2015 | 1997-10-07 | NY | other |  | LONG ISLAND LIGHTING CO | THIS INCIDENT WAS INVESTIGATED BY THE NASSAU COUNTY OFFICE OF THE FIREMARSHAL. A LANDSCAPE CONTRACTOR DISCONNECTED A SECTON OF CONSUMER OWNED GASMARSHAL. A LANDSCAPE CONTRACTOR DISCONNECTED A SECTION OF CONSUMER OWNED GASPIPE FROM THE OUTSIDE WALL OF 2 | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2016 | 1997-10-18 | MI | other | HOERBIGER | MICHIGAN CONSOLIDATED GAS CO (MICHCON) | THE CRANK-END UPLOADER VALVE FAILED. A FAILURE OCCURRED WHEN THE CRANK-ENDA FAILURE OCCURRED WHEN THE CRANK-END UNLOADER VALVE BLEW OFF THE COMPRESSORALLOWING NATURAL GAS TO FLOW AT HIGH PRESSURE INSIDE THE BUILDING. THEUNLOADER VALVE BLEW OFF THE COMPR | 1400000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2017 | 1997-10-23 | AK | other | DRISCOPIPE | ENSTAR NATURAL GAS CO | A WOOD STOVE CAUSED A STRUCTURAL FIRE WHICH MELTED A 5/8" S/L INSIDE A STEELRISER. | 150000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2018 | 1997-11-16 | MI | technical failure | BRAUTCO | MICHIGAN CONSOLIDATED GAS CO (MICHCON) | A PIECE OF 1/2" STAINLESS STEEL TUBING PULLED OUT OF A COMPRESSION FITTINGALLOWING NATURAL GAS TO FLOW AT HIGH PRESSURE INSIDE THE COMPRESSOR BUILDING.THE THEN LEAKING NATURAL GAS IGNITED FROM AN UNKNOWN SOURCE DAMAGING THECOMPRESSOR BUILDING AND INJURING | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2019 | 1997-12-23 | TX | ACCIDENTALLY CAUSED BY OPERATOR |  | ENTEX, A NORAM ENERGY COMPANY (FORM. DIV OF ARKLA |  | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2020 | 1997-11-10 | TX | other |  | LONE STAR GAS CO (DISTRIBUTION DIVISION) | AN INDIVIDUAL WAS ATTEMPTING TO INSTALL AN ILLEGAL BYPASS AND WAS USING A TARPTO CONCEAL HIS ACTIVITY WHEN HE DIED. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2021 | 1997-12-02 | TX | other |  | ENTEX, A NORAM ENERGY COMPANY (FORM. DIV OF ARKLA | FIRE SPREAD FROM GARAGE APARTMENT TO HOUSE - HEAT MELTED 1/2" - PLASTIC PIPECAUSING GAS TO ESCAPE AND IGNITE. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2022 | 1997-12-01 | TX | other |  | ARKLA, A NORAM ENERGY COMPANY | CUSTOMER WAS COOKING ON AN ELECTRIC RANGE WHEN THE GREASE CAUGHT FIRE,RESULTING IN DAMAGE TO THE HOUSE AND TWO VEHICLES. | 120000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2023 | 1997-12-15 | TX | other |  | SOUTHERN UNION GAS CO | CONTRACTOR WAS USING ASPHALT SCRAPER TO PREPARE ROAD SURFACE FOR RE-PAVINGWHEN EQUIPMENT STRUCK AND DAMAGED A 2" WRAPPED STEEL CAUSING LEAKAGE. GASIGNITED, RESULTING IN MAJOR FIRE DAMAGE TO EQUIPMENT. FIRE DEPARTMENTRESPONDED AND WAS ON SCENE IN CONTROL | 357000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2024 | 1997-12-09 | OH | other |  | EAST OHIO GAS CO | A SEWER CONTRACTOR PERFORMED WORK AT THE SITE OF THE INCIDENT WITHOUTCONTACTING "OUPS" TO HAVE THE LOCATION OF THE SERVICE LINE MARKED. DURING THEWORK PERFORMED BY THE SEWER CONTRQACTOR, THE STEEL GAS SERVICE LINE WASUNDERMINED. THE GAS SERVICE LINE WAS | 380000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2025 | 1997-11-13 | MI | other | DU PONT | SEMCO ENERGY GAS COMPANY | HOMEOWNER (TIMOTHY D. DAVIS) WAS ASPHYXIATED WHILE ATTEMPTING AN UNAUTHORIZEDBY-PASS OF A 3/4" PE SERVICE LINE. MR. DAVIS WAS OUTSIDE LAYING ON THE GROUNDWITH HIS HEAD AND ARMS IN A SMALL HOLE HE HAD EXCAVATED. HE HAD CUT INTO THELIVE SERVICE WITHOUT AT | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2026 | 1998-01-22 | AK | other | DRISCOPIPE | ENSTAR NATURAL GAS CO |  | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2027 | 1998-01-13 | AK | other | PHILLIPS | ENSTAR NATURAL GAS CO |  | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2028 | 1998-01-02 | NY | other | UNKNOWN ( COUNTY) | CONSOLIDATED EDISON CO OF NEW YORK | A 48" WATER MAIN BREAK UNDERMINED THE STREET. THE ROADBED COLLAPSED ANDSEVERED A 24" LOW PRESSURE CAST IRON MAIN. THE MAIN SUBSEQUENTLY IGNITED. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2029 | 1997-12-08 | LA | other |  | ENTERGY GULF STATES |  | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2030 | 1997-12-23 | LA | other | MC WAYNE | ARKLA, A NORAM ENERGY COMPANY | ARKLA PERSONNEL WERE NOTIFIED AT 4:50 PM AND ARRIVED ON SITE AT APPROXIMATELY5:08 PM. FURTHER INVESTIGATION REVEALED A COLD BREAK ON A 2" CAST IRON GASMAIN BETWEEN 2720 AND 2724 MORNINGSIDE DR. THE FLOW OF NATURAL GAS WASTERMINATED AT APPROXIMATELY 7:35 | 125000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2031 | 1997-12-27 | TN | other |  | MEMPHIS LIGHT GAS & WATER DIVISION | MR. LUTHER WATKINS WAS ATTEMPTING TO SHUT OFF THE WATER METER AT 805 AYERSSTREET, AND LIT A MATCH TO LOOK INSIDE THE WATER METER BOX. A FLASH FIREOCCURRED, WHICH INJURED MR. WATKINS. HE WAS TAKEN BY HIS WIFE TO ST. JOSEPHHOSPITAL BUT WAS NOT ADMITTED. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2032 | 1997-11-26 | AZ | other |  | CITIZENS UTILITY CO | SEE NARRATIVE ATTACHED TO REPORT. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2033 | 1997-12-09 | FL | other |  | PENSACOL, CITY OF | BASED ON INFORMATION PROVIDED BY THE PENSACOLA FIRE DEPARTMENT AND THE STATEFIRE MARSHALL, THE PROBABLE CAUSE OF THIS INCIDENT WAS A BROKEN RANGECONNECTOR THAT LEAKED GAS THAT IS PRESUMED TO HAVE IGNITED FROM THE RANGEPILOTS. | 45000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2034 | 1997-12-23 | IA | other | WESTINGHOUSE | MIDAMERICAN ENERGY CO | THE TELEPHONIC REPORT IS RETRACTED. THE CAUSE OF THE INCIDENT WAS NOT NATURALGAS FROM MID AMERICAN ENERGY COMPANY PIPING. IT WAS PROCLAIMED BY THE IOWASTATE FIRE MARSHALL TO BE CAUSED BY ARSON. | 150000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2035 | 1998-01-01 | VA | maintenance |  | DANVILLE GAS DEPT | AT APPROXIMATELY 7:00 PM ON JANUARY 1, 1998, WATER AND GAS DISPATCH RECEIVED APHONE CALL FROM 148 WENDELL SCOTT DRIVE A STRONG GAS ODOR OUTSIDE OF THERESIDENCE. AT 7:10 PM, DARYL SMITH TECHNICIAN, ARRIVED AT THE SITE. UPONARRIVAL AT THE SITE, DARYLE WA | 48000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2036 | 1998-01-12 | PA | other | UNKNOWN | PENNSYLVANIA GAS & WATER CO | PENNSYLVANIA POWER & LIGHT'S ELECTRIC HIGH VOLTAGE POWER LINE FELL TO THEGROUND AT THE INTERSECTION OF MAIN AND CHURCH STREETS. AT SAID INTERSECTION,PG ENERGY HAS A 6" INTERMEDIATE PRESSURE STEEL GAS MAIN. THIS GAS MAIN WASAPPROXIMATELY 4' DEEP. WHEN T | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2037 | 1998-01-11 | TX | other | DUPONT | ENTEX, A NORAM ENERGY COMPANY (FORM. DIV OF ARKLA | THE CITY OF LUFKIN HAD BROKEN A 2 INCH PLASTIC MAIN WHILE ATTEMPTING TOREPAIR A WATER LINE ATTHE LOCATION. THE ENTEX SERVICEMAN RESPONDED ANDREALIZED IT WAS A MAIN. HE CALLED A CREW LEADER AT APPROXIMATELY 10:55 AM TOASK THAT A CREW COME OUT AND REPAIR | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2038 | 1998-01-05 | IA | other |  | MIDAMERICAN ENERGY CO | THE CAUSE OF THE INCIDENT IS UNKNOWN AND THE INCIDENT IS STILL UNDER | 200000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2039 | 1998-01-11 | WA | other |  | PUGET SOUND ENERGY | APARTMENT FIRE REPORTED TO OPERATOR BY LOCAL FIRE DEPARTMENT. THEY INDICATEDTHAT NATURAL GAS MAY BE INVOLVED. ACESS TO SITE DENIED. INVESTIGATION ISUNDERWAY, WITH NO CONCLUSION AT THIS TIME. ENCLOSED IS THE RSPA F 7100.0"INCIDENT REPORT - GAS DISTRIBU | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2040 | 1998-01-15 | LA | other |  | SOUTH COAST GAS CO INC | A GAS VALVE ON THE CUSTOMER PIPING WAS OPEN IN THE KITCHEN, WHICH ALLOWEDNATURAL GAS TO ACCUMALATE IN THE DWELLING. THE IGNITION OF THE NATURAL GASWAS CAUSED BY THE OPERATION OF THE CENTRAL HEATING UNIT. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2041 | 1998-01-15 | AZ | other | PHILLIPS | SOUTHWEST GAS CORP |  | 714611 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2042 | 1997-12-29 | CA | other |  | PACIFIC GAS & ELECTRIC CO | DUE TO MAPPING IRREGULARITY, FACILITY WAS MARKED 57 INCHES AWAY FROM ITSLOCATION. MAP SHOWED LOCATION OF TEST LEADS INCORRECTLY & LOCATOR MARKED THEWRONG LINE. TWO LINES WERE IN THE AREA. INDICATOR MARKED ONE LINE TWICE. | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2043 | 1998-01-26 | AZ | other | PHILLIPS | SOUTHWEST GAS CORP | GAS MAINS AND SERVICES WERE INSTALLED EARLY IN 1997 TO SERVE THE ARIZONAMILLES MALL. DURING SUBSEQUENT CONSTRUCTION ACTIVITY FOR THE MALL FACILITIES,ALONG 2" MAIN STUB SUFFERED SURFACE DAMAGE AND A FITTING WAS FORCEDLONGITUDINALLY ALONG THE MAIN, WHICH C | 163000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2044 | 1998-02-13 | AK | other | PHILLIPS DRISCOPIPE | ENSTAR NATURAL GAS CO | ON FRIDAY AFTERNOON, FEBUARY 13, 1998 AT 4:30 PM AST, ENSTAR PERSONNEL WERECALLED TO RESPOND TO A HOUSE FIRE AT LOT 5, BLOCK 8, EAGLE RIVER HEIGHTS EAGLERIVER ALASKA. THE ORIGIN OF THE FIRE IS UNKNOWN. THE FIRE CONSUMED THE SINGLEFAMILY HOME AND IN THE P | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2045 | 1998-01-27 | TX | other |  | ENTEX, A NORAM ENERGY COMPANY (FORM. DIV OF ARKLA | REPORTED TO DEPARTMENT OF TRANSPORTATION2/3/98 14:48 MR. MASON | 117492 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2046 | 1998-02-04 | NV | other |  | SOUTHWEST GAS CORP | THERE WAS CONSTRUCTION ACTIVICTIES FOR THE INSTALLATION OF A SEWER LINE DURINGJULY 1997. SEWER CROSSED UNDER AN EXISTING 2' PVC GAS MAIN. IMPROPERCOMPACTION AROUND A 2" SHORT STOP FITTING CAUSED A FAILURE ON THE 2" PVCMAIN. GAS MIGRATED INTO THE AREA O | 247850 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2047 | 1997-10-03 | KS | other | PHILLIP DISCO | WESTERN RESOURCES INC (AKA KPL CO. OR GAS SERVICE) | A 7/8 INCH PLASTIC SERVICE LINE WAS INADVERTENTLY INSTALLED BY A CONTRACTORTHROUGH A SANITARY SEWER LINE. WHILE PERFORMING MAINTENANCE CLEANING OF THESEWER, A THIRD PARTY CUT THE PLASTIC SERVICE LINE WHICH APPARENTLY ALLOWEDNATURAL GAS TO MIGRATE THROUGH | 110000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2048 | 1998-03-04 | IL | other |  | NICOR EXPLORATION CO | A DRYER FLEX CONNECTOR FAILED RESULTING IN A FIRE AND EXPLOSION INSIDE THEUTILITY ROOM AND KITCHEN AREA AT 318 N DRYDEN AVE. | 150000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2049 | 1998-02-24 | UT | other |  | QUESTAR GAS COMPANY | FOR YOUR INFORMATION, JUST PRIOR TO FEBRUARY 24, 1998. PARK CITY HAD RECEIVEDRECORD - BREAKING ACCUMALATIONS OF SNOW. ON FEBRUARY 24, 1998, ICE AND SNOWSLUFFED OF THE ROOF OF A CONDOMINIUM LOCATED AT 7155 LITTLE BELLE COURT, PARKCITY, UTAH, AND FELL APPR | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2050 | 1998-03-04 | MA | other |  | BAY STATE GAS CO | PIPELINE MARK ON STREET WAS NOT CORRECT. | 300000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2051 | 1998-02-26 | MI | other | PHILLIPS | CONSUMERS POWER CO | CONTRACTOR EXCAVTING FOR WATER LINE AND DAMAGED A 3/4" STEEL LINE. THESERVICE BROKE BELOW GROUND ON THE 5/8" PLASTIC SERVICE RISER TO THE METER. | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2052 | 1998-02-17 | CA | other |  | PACIFIC GAS & ELECTRIC CO | THE WATER COMPANY'S ( EAST BAY MUNICIPAL UTILITY DESRICT) CONSTRUCTIONPERSONNEL WHILE EXCAVATING A TRENCH WITH A BACKHOE PULLED A 1/2 INCH COPPERSERVICE OUT OF THE SERCICE TEE LOCATED ON A SIX INCH MAIN. THE ESCAPINGNATURE GAS MIGRATED UNDERNEATH THE AD | 500000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2053 | 1998-03-13 | MO | maintenance |  | LACLEDE GAS CO | THE TEE CONNECTION TO THE MAIN. THE SERVICE LINE SECTION WAS REMOVED AND SENTFOR METALLURGICAL ANALYSIS TO DETERMINE THE CAUSE OF FAILURE IN ACCORDANCEWITH 192.617. | 190000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2054 | 1998-03-11 | TX | other | ROCKWELL NORDSTOM | ENTEX, A NORAM ENERGY COMPANY (FORM. DIV OF ARKLA | AN ENTEX LOCK WAS CUT OFF A 4" SERVICE VALVE AND THE VALVE WAS DISASSEMBLEDRESULTING IN A RELEASE OF NATURAL GAS. THE NATURAL GAS WAS IGNITED AS ANATTEMPT TO MOVE A NEARBY VEHICLE. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2055 | 1998-03-24 | TN | other |  | CHATTANOOGA GAS CO | A CONTRACTOR RUPTURED A 4" STEEL NATURAL GAS MAIN WITH A ROCK SAW WHILEINSTALLING A SEWER LINE. THE ESCAPING GAS IGNITED DAMAGING THE ROCK SAW. | 250000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2056 | 1998-03-31 | MD | other |  | BALTIMORE GAS & ELECTRIC CO | ON 3/31/1998 WE RECEIVED A CALL FROM HOWARD COUNTY FD. OF A BUILDING FIRE.OUR SERVICE PERSON ARRIVED AT 17:59 AND REPORTED THAT THE BUILDING WAS FULLYINVOLVED AND THE GAS METER ISTALLATION WAS ON FIRE. IT COULD NOT BE TURNEDOFF AND SHE NEEDED SURVEY AND | 400000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2057 | 1998-03-29 | MN | other |  | MINNEGASCO INC | TORNADO UPROOTED TREES AND DEMOLISHED BUILDINGS. TREES AND BUILDING FELL ONMETER SETS AND REGULATOR STATIONS. TREE ROOTES DAMAGED MAINS AND SERVICE WHENTREES WENT DOWN. | 75000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2058 | 1998-03-17 | MO | maintenance |  | LACLEDE GAS CO | VISUAL INSPECTION FOUND A CORROSION HOLE ON THE COPPER SERVICE LINE BODY ATTHE TEE CONNECTION TO THE MAIN SERVING 358 PRALLE LANE. THIS LOCATION WAS INTHE RIGHT OF WAY ADJACENT TO THE PROPERTY OF 401 PRALLE LANE. THE SERVICE LINESECTION WAS REMOVED AND S | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2059 | 1998-04-07 | TX | other |  | BAY CITY MUNICIPAL GAS SYSTEM | OCCUPANT RENTED ROOM #36 OF THE FLAMINGO MOTEL AND ATTEMPTED TO COMMIT SUICIDEBY BLOCKING CEILING VENT WITH BATH TOWEL, CLOSING DOOR TO BATHROOM AND SEALINGDOOR WITH QUILT AND THEN ATTEMPTING TO REMOVE BATHROOM WALL HEATER WITHCRESENT WRENCH AND IN DOING | 5000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2060 | 1998-03-15 | CA | other |  | PACIFIC GAS & ELECTRIC CO | DRUNK DRIVER DROVE OFF U.S. 101, WENT THROUGH THE FREEWAY CHAIN LINK FENCE ANDHIT A GAS REGULATOR SET THAT WAS 30 FEET FROM THE DRY AND STRAIGHT ROADWAY.THE CAGE OVER THE SET WAS MOVED OFF BY THE VECHICLE. THE VEHICLE CONTINUEDANOTHER 5 FEET UNTIL IT WAS | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2061 | 1998-05-09 | VT | other | MANIFOLD SITE BUILT | VERMONT GAS SYSTEMS INC |  | 225000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2062 | 1998-05-01 | NC | other | DRESSER | PIEDMONT NATURAL GAS CO INC |  | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2063 | 1998-04-05 | AZ | other | RELIANCE | SOUTHWEST GAS CORP |  | 70000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2064 | 1998-03-31 | TN | other |  | SELMER NATURAL GAS SYSTEM |  | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2065 | 1998-04-14 | ME | ACCIDENTALLY CAUSED BY OPERATOR | PLEXCO | NORTHERN UTILITIES INC (ALLIED GAS DIV) |  | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2066 | 1998-04-24 | AK | other | PHILLIPS DRISCOPIPE | ENSTAR NATURAL GAS CO |  | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2067 | 1998-05-11 | IN | other |  | NEW HARMONY GAS DEPT, TOWN OF |  | 500000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2068 | 1998-05-16 | VA | other | PLEXCO | COLUMBIA GAS OF VIRGINIA INC | THE OWNER OF THE HOME AT 210 CHURCH STREET OR HIS REPRESENTATIVE DROVE A GROUND ROD THROUGH THE PLASTIC SERVICE LINE SERVING THE 210 CHURCH STREET ADDRESS. GAS ESCAPED FROM THE SERVICE LINE (AS A RESULT OF THE UNDERGROUND FACILITY DAMAGE), MIGRATED INTO | 120000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2069 | 1998-05-15 | MO | other |  | MISSOURI GAS ENERGY |  | 212641 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2070 | 1998-05-21 | IN | technical failure |  | KOKOMO GAS & FUEL CO |  | 500 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2071 | 1998-04-20 | PA | other | UNKNOWN | COLUMBIA GAS OF PENNSYLVANIA | THERE WERE NO INJURIES ASSOCIATED WITH THE EXPLOSION AND FIRE THAT CAUSEDDAMAGE IN EXCESS OF $50,000 WITH TOTAL DAMAGES ESTIMATED AT $200,000. THISFAILURE WAS A RESULT OF A LARGE MATURE TREE THAT COLLAPSED CAUSING COLUMBIA'S4-INCH BARE STEEL MEDIUM PRESS | 200000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2072 | 1998-05-20 | TN | other |  | NASHVILLE GAS CO | BYPASS LINE FOR ROUTINE MAIN REPAIR BECAME DISCONNECTED FROM UPSTREAM MACHINEAND GAS RELEASE WAS IGNITED BY WELDER'S TORCH. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2073 | 1998-06-15 | CO | other | ROCKWELL | PEOPLES NATURAL GAS CO | GAS REGULATOR WAS TAMPERED WITH AND DAMAGED BY CHILDREN CAUSING IT TO STICKOPEN AND OVERPRESSURE HOUSE PIPING SYSTEM. | 200000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2074 | 1998-05-27 | GA | other | UNKNOWN | ATLANTA GAS LIGHT CO | A CONTRACTOR RUPTURED A 6" STEEL NATURAL GAS MAIN WITH A TRACKHOE WHILEWIDENING THE HIGHWAY. | 55000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2075 | 1998-06-16 | NY | other | DRISCOPIPE | CONSOLIDATED EDISON CO OF NEW YORK | A CONTRACTOR, WORKING ON THE INSTALLATION OF A SPRINKLER SYSTEM SEVERED A 2"HIGH-PRESSURE SERVICE WITH A DITCH WITCH. THE SERVICE SUBSEQUENTLY IGNITED.THERE WAS NO MARKOUTS AS PER CODE 753. | 10000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2076 | 1998-06-03 | AZ | other | PHILLIPS | SOUTHWEST GAS CORP |  | 12915 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2077 | 1998-05-12 | TX | technical failure | UNKNOWN | LONE STAR GAS CO (DISTRIBUTION DIVISION) | A CONTRACTOR WAS IN THE PROCESS OF INSTALLINGA BAND CLAMP WHEN GAS IGNITED. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2078 | 1998-06-02 | NC | ACCIDENTALLY CAUSED BY OPERATOR | PLEXCO | GREENVILLE UTILITIES COMMISSION | DURING A ROUTINE PURGING OF AIR WITH GAS, IGNITION OF THE EXIT GASES OCCURREDBY UNKNOWN CAUSE. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2079 | 1998-06-02 | MD | other | AMERICAN | WASHINGTON GAS LIGHT CO |  | 250000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2080 | 1998-05-30 | SD | other |  | NORTHWESTERN PUBLIC SERVICE CO | TORNADO STRUCK SPENCER S.D. DESTROYING METER FITS. | 75000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2081 | 1998-06-23 | TX | other |  | ENTEX, A NORAM ENERGY COMPANY (FORM. DIV OF ARKLA | THIRD PARTY INSTALLING WATER LINE HIT & DAMAGED 2" IP PLASTIC MAIN CAUSING GASTO ESCAPE & IGNITE. | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2082 | 1998-07-01 | MA | other |  | BAY STATE GAS CO | THE HOMEOWNER ATTEMPTED SUICIDE BY TAKING A NIP AND CAP OFF AN INSIDE HOUSELINE AT THE FURNACE. THE HOUSE BLEW UP CAUSING HIS INJURIES AND THEDESTRUCTION OF HOUSE. | 115000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2083 | 1998-07-02 | TN | other |  | MEMPHIS LIGHT GAS & WATER DIVISION | PRIVATE VEHICLE LEFT THE ROADWAY AND STRUCK THE NORTWEST CORNER OF THERESIDENCE LOCATED AT 911 MCCLURE RD. THE COLLISION DESTROYED THE GAS METERCENTER, RELEASING AND IGNITING GAS UNDER AND AROUND THE HOUSE AT THE POINT OFIMPACT. THE FIRE DESTROYED THE V | 70000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2084 | 1998-06-16 | NC | other | KRALOY | NORTH CAROLINA NATURAL GAS CORP | SERVICE LINE WAS CUT BY MR. KEITH COLLINS WHILE DIGGING. GAS MIGRATED INTOTHE HOUSE AND WAS IGNITED. | 80000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2085 | 1998-06-18 | TN | other |  | UNITED CITIES GAS CO | THIS WAS NOT A REPORTABLE INCIDENT DUE TO NO PROPERTY DAMAGED OTHER THAN2'SECTION OF 2" PLASTIC MAIN. ALSO, NO INJURIES OCCURRED. THE CALL WAS MADEIN ORDER TO REPORT WITHIN TWO HOUR TIME LIMIT; OPERATOR WAS UNSURE OF EXTENTOF DAMAGE OR INJURIES AT THAT | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2086 | 1998-07-11 | PR | technical failure |  | SAN JUAN GAS CO |  | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2087 | 1998-07-11 | IN | other |  | INDIANA GAS CO INC | AN 1 -1/4 STEEL SERVICE WAS PULLED FROM A DRESSER COUPLING ALLOWING NATURALGAS TO INFILTRATE THE STORM SEWER AND ULTIMATELY THE STRUCTURE AT 310 COUNTYLINE RD IN ATLANTA, IN. THE GAS WAS IGNITED BY AN UNIDENTIFIED IGNITIONSOURCE, WHICH RESULTED IN A EXPL | 70000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2088 | 1998-07-15 | IN | other |  | INDIANA GAS CO INC | CUSTOMER FUEL LINE FOUND TO BE OPEN. ALL INDIANA GAS CO. FACILITIES OK. | 70000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2089 | 1998-07-23 | MD | ACCIDENTALLY CAUSED BY OPERATOR |  | BALTIMORE CITY, HOUSING AUTH OF | AT APPROXIMATELY 2320 HOURS WHILE REPLACING 1 1/4 TEE ON 16' CAST IRON MAINTHE GAS IGNITED. TWO POSSIBLE SOURCES OF IGNITION ARE BEING INVESTIGATED.ONE SOURCE IS A HALOGEN LIGHT USED BY THE CREW AND THE OTHER SOURCE IS STATICELECTRIC CHARGES FROM THE PLA | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2090 | 1998-08-05 | TX | other |  | NATGAS INC. | CUSTOMER SMELLED GAS IN HOUSE, OPENED WINDOW AND LIGHT LIGHTER TO FIND LEAK.HOUSE EXPLODED. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2091 | 1998-07-20 | NM | other |  | PUBLIC SERVICE COMPANY OF NEW MEXICO - GAS SVCS | THIRD PARTY OPERATING MAINTAINER GRADING BARDITCH CUT MAINLINE 8 MILESSOUTHEAST OF TUCUMCARI NEAR CANAL CROSSING. PNM GAS SERVICE'S SOLE NATURAL GASDISTRIBUTION PIPELINE SUPPLYING THE TOWN OF TUCUMCARI, NM, WAS DAMAGED BY ATHIRD PARTY APPROXIMATELY 8 MILE | 75000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2092 | 1998-08-12 | SC | other | PLEXCO | SOUTH CAROLINA ELECTRIC & GAS CO | A THIRD PARTY UTILITY CONTRACTOR DAMAGED A FOUR INCH PLASTIC DISTRIBUTION MAINWHILE INSTALLING A FIBER OPTIC TELEVISION CABLE. SCE&G'S RESPONDING EMPLOYEESATTEMPTED TO SLOW THE FLOW OF ESCAPING GAS BY INSTALLING A SPLIT SLEEVE/CLAMPOVER THE 2 1/2 BY 5 IN | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2093 | 1998-07-20 | TX | other |  | ENTEX, A NORAM ENERGY COMPANY (FORM. DIV OF ARKLA | THIRD PARTY CONTRACTOR PULLED A MARKED 1 1/4' L.P. STEEL SERVICE LINE, SERVING815 CENTER ST FROM A 2' L.P. STEEL MAIN LINE. GAS MIGRATED TO 816 CENTERWHERE AND EXPLOSION & FIRE OCCURRED. | 95000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2094 | 1998-07-08 | TX | other | UPONOR ALDYL | SIENERGY, LP | ACCORDING TO "NOTICE OF INTENT TO EXCAVATE" DIGGING WAS TO BEGIN 7//14/1998.ONE WEEK AFTER DAMAGE LINE LOCATION WAS SCHEDULED 7/13/1998. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2095 | 1998-07-29 | AZ | other |  | SOUTHWEST GAS CORP | A TRENCHER WAS EXCAVATING NEAR WENDEN, ARIZONA, WHEN IT DAMAGED A 2"HIGH-PRESSURE STEEL PIPELINE. THE EXCAVATOR WAS TRENCHING WITHOUT A LINELOCATE REQUEST. AS A RESULT OF THE DAMAGE, 439 CUSTOMERS WER TEMPORARILY OUTOF SERVICE. THE LINE IS MARKED WITH | 22928 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2096 | 1998-07-30 | TX | other | PLEXCO | LONE STAR GAS CO (DISTRIBUTION DIVISION) | A BACKHOE CUT INTO A 2 INCH POLY PIPE, RESULTING IN GAS IGNITION. THE BACKHOEDRIVER WAS INJURED AND THE BACKHOE WAS DAMAGED DUE TO THE FIRE. | 30000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2097 | 1998-07-31 | WA | other |  | PUGET SOUND ENERGY | ROAD IMPROVEMENT CONTRACTOR STRUCK 3/4" TEE ON A 8" SUPPLY MAIN (240 PSIG)WHILE REMOVING UNSUITABLE MATERIAL. CONTRACTOR THOUGHT LINE WAS ABANDONED,SIMILAR TO PIPE NEARBY. LINE WAS ACTIVE. REPAIR REQUIRED REDUCTION OFPRESSURE TO 150 PSIG. TEMPORARY CL | 51885 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2098 | 1998-08-19 | VA | other |  | VIRGINIA NATURAL GAS | FIRE AT A RESIDENTIAL TOWNHOUSE UNIT WAS CAUSED BY AN ELECTRICAL SHORT CIRCUITAT THE ELECTRICAL METER BASE WHICH SUBSEQUENTLY MELTED DOWN THE CUSTOMER'S GASMETER AND SERVICE REGULATOR. | 200000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2099 | 1998-08-22 | CT | other |  | CONNECTICUT NATURAL GAS CORP | ON AUGUST 22, 1998, AT APPROXIMATELY 2331 HOURS, CONNECTICUT NATURAL GAS CORP(CNG) RECEIVED NOTIFICATION FROM THE CITY OF NEW BRITAIN FIRE DEPARTMENT OF AHOUSE THAT WAS ON FIRE, APPARENTLY FROM AN EXPLOSION, AT 235 HIGH STREET. CNGRESPONDED AND HAD A REPR | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2100 | 1998-08-12 | KS | other |  | ONEOK SERVICES INC | THE COMPANY'S 4" STEEL PIPELINE WAS DAMAGED BY A THIRD PARTY CONTRACTOR WHILEAUGERING ACROSS A STREET WHICH RESULTED IN INTERRUPTION OF SERVICE TO 286CUSTOMERS. | 15000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2101 | 1998-08-20 | MO | other |  | LACLEDE GAS CO | A BACKHOE OPERATED BY THE CITY OF ST. ANN, MISSOURI, PULLED A TWO INCH COATEDAND CATHODICALLY PROTECTED STEEL MAIN FROM A COMPRESSION COUPLING WHILEEXCAVATING TO PERFORM A STORM SEWER REPAIR. | 75000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2102 | 1998-08-23 | NV | other |  | SOUTHWEST GAS CORP | A LEAK IN A 2" PVC GAS MAIN RESULTED IN GAS MIGRATING INTO A SINGLE FAMILYRESIDENCE (VACANT) AT 1320 DARTMOUTH STREET, LOVELOCK, NV. AN UNKNOWNIGNITION SOURCE CAUSED AN EXPLOSION WHICH RESULTED IN STRUCTURAL DAMAGE TO THEVACANT HOUSE. THE CAUSE OF THE L | 43898 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2103 | 1998-08-08 | NY | other |  | BROOKLYN UNION GAS CO | MARKETSPAN NATURAL GAS FACILITIES WERE NOT INVOLVED. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2104 | 1998-08-29 | CA | other |  | PALO ALTO, CITY OF | AT APPROXIMATELY 2230 HOURS ON AUGUST 29, 1998, THE PALO ALTO FIRE DEPARTMENTRESPONDED TO A REPORTED GARAGE FIRE AT 4103 WILKIE WAY, PALO ALTO, CA. UPONARRIVAL THE FIRE DEPARTMENT LOCATED AND EXTINGUISHED FLAMES IN THE GARAGE ANDTHE ATTIC AREA ABOVE THE | 200000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2105 | 1998-09-14 | CA | other | NIPAK | ISLAND ENERGY | THROUGH INVESTIGATION OF THE INCIDENT IT IS FOUND THAT THE CONTRACTOR, SSPORTSENVIRONMENTAL, HAD INEXPERIENCED BACK-HOE OPERATORS, AND/OR NO SPOTTERS ORFOREMAN ON THE SITE AT THE TIME. I HAVE TALKED TO PERSONNEL ABOUT THEEXCAVATION OF UTILITIES IN THE AR | 8000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2106 | 1998-09-15 | CA | other | NIPAK | ISLAND ENERGY |  | 8000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2107 | 1998-08-07 | AZ | other | PHILLIPS | SOUTHWEST GAS CORP | A CONTRACTOR WAS TRENCHING FOR CABLE INSTALLATION AND DAMAGED A 4"DISTRIBUTION MAIN. THE CONTRACTOR HAD REQUESTED BLUE STAKE AND THE LINE WASMARKED. AN OUTAGE OF APPROXIMATELY 1300 CUSTOMERS OCCURRED. REGARDING PARTB, 2(B): THE GAS MAIN WAS MARKED AT T | 40288 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2108 | 1998-09-07 | PA | maintenance | DRESSER | EQUITABLE RESOURCES (A.K.A EQUITABLE GAS CO) |  | 85000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2109 | 1998-08-31 | AZ | other | CSI | SOUTHWEST GAS CORP | A CAR COLLIDED WITH AN ABOVE GROUND BLOW OFF STACK, DAMAGING A 1/2" DIAMETERGAUGE TAP. THE TRANSMISSION PIPELINE WAS REMOVED FROM SERVICE TO MAKEPERMANENT REPAIRS. | 8481 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2110 | 1998-08-26 | NC | other | PLEXCO | PIEDMONT NATURAL GAS CO INC | AN EMPLOYEE OF ALLTEL COMMUNICATIONS EMPLOYEE WAS COATING A COMMUNICATIONSCABLE. THE COATING PROCESS REQUIRED THE USE OF A PROPANE TORCH. THE WORKERINADVERTENTLY EXPOSED THE POLYETHYLENE GAS PIPING TO THE TORCH FLAME. THEPIPE MELTED ALLOWING THE GAS TO | 1000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2111 | 1998-08-14 | OH | other | UNKNOWN | EAST OHIO GAS CO | SERVICE LINE WAS PULLED FROM CONNECTION AT HOUSE. THE PERSON OPERATING THEBACKHOW WAS THE SON OF THE BUILDING OWNER. NO ONE HAD CALLED OHIO UTILITIESPROTECTION TO HAVE LINE LOCATED. | 45000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2112 | 1998-08-31 | PA | other |  | PENNSYLVANIA GAS & WATER CO | CONTRACTOR WAS OPERATING A MOTORIZED MANLIFT NEXT TO THE GARAGE (GUEST HOUSE),LOST CONTROL OF HIS MACHINE AS HE TRIED TO STEER IT DOWN AN EMBANKMENT. ASTHE MANLIFT SLID DOWN THE HILL, IT HIT A METER SET (WHICH WAS AN AL425 WITH A1 1/4" RISER) SEVERING IT | 150000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2113 | 1998-08-27 | CA | other |  | PACIFIC GAS & ELECTRIC CO | THIS INCIDENT WAS CAUSED BY A CAR BEING RECKLESSLY DRIVEN BY THE PROPERTYOWNER, WHO RAN HER VEHICLE INTO THE GAS METER. THE GAS METER WAS LOCATED INAN AREA NOT NORMALLY ACCESSIBLE TO VEHICLES. THE INCIDENT IS STILL UNDERINVESTIGATION BY THE STOCKTON FIR | 51000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2114 | 1998-08-18 | CO | other |  | PUBLIC SERVICE CO OF COLORADO | 3RD PARTY MELTED P. E. D. MAIN WITH WELDING TORCH AND CAUSED FIRE. | 300000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2115 | 1998-09-30 | AK | other | DRISCOPIPE | ENSTAR NATURAL GAS CO | ON WEDNESDAY MORNING, SEPTEMBER 30, 1998 AT APPROXIMATELY 3:07 AM AST, ENSTARNATURAL GAS COMPANY RESPONDED TO A HOUSE FIRE AT TRACT C, NOLEN'S KNOLLSUBDIVISION, WASILLA, ALASKA. FIRE DEPARTMENT OFFICIALS REPORTED THE FIREORIGINATED FROM A CANDLE LIT BY A | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2116 | 1998-08-24 | AL | other | DRISCO | ALABAMA GAS CORP | GAS LINE MARKET INCORRECTLY. | 65000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2117 | 1998-09-01 | TX | other | DUPONT | LONE STAR GAS CO OF TEXAS, INC | A LONE STAR GAS CONTRACTOR (BUKEEN) LOCATED A GAS LINE ON THE WRONG SIDE OFTHE ROAD. RCA PLUMBING COMPANY CUT INTO A 2 INCH GAS LINE WHILE DIGGING ASEWER LINE IN THIS WORK AREA. A LONE STAR GAS EMPLOYEE, WHILE WORKING TO STOPTHE FLOW OF NATURAL GAS, WAS | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2118 | 1998-09-17 | GA | other |  | SUGAR HILL NATURAL GAS SYSTEM, CITY OF | GAS LINE MARKED PROPERLY. CONTRACTOR DID NOT POT HOLE BEFORE USING TRENCHER. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2119 | 1998-08-26 | MA | other |  | BOSTON GAS CO | ON AUGUST 26, 1998 AT 11:09 AM, AN EXPLOSION AND FIRE OCCURRED 8 ASHTONSTREET, DORCHESTER, BOSTON DEMOLISHING A THREE STORY, WOODEN, RESIDENTIALDWELLING. A SUBSEQUENT LEAK INVESTIGATION WAS CONDUCTED AND A SIX-INCH CASTIRON MAIN WAS FOUND TO BE CIRCUMFER | 750000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2120 | 1998-10-09 | AK | other | DRISCOPIPE | ENSTAR NATURAL GAS CO | ON FRIDAY EVENING, OCTOBER 9, 1998 AT APPROXIMATELY 8:10 PM AST, ENSTARNATURAL GAS COMPANY RESPONDED TO A 30 UNIT APARTMENT FIRE AT 3938 COPE STREET,ANCHORAGE, ALASKA. THE FIRE CONSUMED ENSTAR'S REGULATOR, METER AND RISER.THE POLYETHYLENE GAS SERVICE LIN | 500000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2121 | 1998-09-08 | TN | other |  | GIBSON COUNTY UTIL DIST | APPROXIMATELY 19:09 HRS, TUESDAY, SEPTEMBER 8,1998, RECEIVED A TELEPHONE CALLFROM CENTRAL CONTROL STATING THEIR HAD BEEN A GAS EXPLOSION AT GREEN ACRESAPARTMENTS LOCATED ON THE GIBSON ROAD INSIDE TRENTON CITY LIMITS. THEDISPATCHER ON DUTY STATED THAT ALL | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2122 | 1998-08-11 | CA | other |  | SAN DIEGO GAS & ELECTRIC CO | ON THE DAY OF THE INCIDENT, THE CONTRACTOR DID NOT EXPOSE THE GAS PIPE AT THECROSSING OF BORING OR REQUEST SDG&E STANDBY. | 138000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2123 | 1998-09-08 | KS | other | PLEXCO | KANSAS GAS SERVICE | A THIRD PARTY EXCAVATOR WAS OPERATING A TRENCHING MACHINE TO INSTALL ATELEPHONE CABLE. THE TRENCHING MACHINE OPERTOR SEVERED A 4" PLASTIC GAS MAINWHICH RESULTED IN THE IGNITION OF NATURAL GAS CAUSING INJURY TO THE MACHINEOPERATOR AND DAMAGE TO THE TRENCH | 60000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2124 | 1998-09-14 | TX | other |  | ENTEX, A NORAM ENERGY COMPANY (FORM. DIV OF ARKLA | HEAT FROM BURING HOUSE DAMAGED METER SET ASSEMBLY AND ESCAPING GAS IGNITED. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2125 | 1998-10-12 | AR | technical failure |  | NORTH LITTLE ROCK HOUSING AUTHORITY | THE SYSTEM OWNER/OPERATOR, THE HOUSING AUTHORITY OF THE CITY OF NORTH LITTLEROCK, ARKANSAS, CONTRACTED WITH SATTERFIELD PIPELINE, INC. TO INSTALL NEWUNDERGROUND GAS PIPING AT THREE FAMILY PUBLIC HOUSING DEVELOPMENTS ITOPERATES. THE NORTH LITTLE ROCK HOUS | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2126 | 1998-10-08 | NJ | ACCIDENTALLY CAUSED BY OPERATOR | DUPONT | SOUTH JERSEY GAS CO | WHILE EXCAVATING TO PINPOINT A GAS LEAK, AN EMPLOYEE USING A SMALL BACKHOEACCIDENTLY STRUCK AND PUNCTURED A 2" PLASTIC GAS MAIN OPERATING AT 40 PSIG.THE GAS IGNITED BY AN UNKNOWN SOURCE INJURING THE MACHINE OPERATOR AND CAUSINGSLIGHT DAMAGE TO A HOUSE AND | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2127 | 1998-10-04 | WV | other |  | HOPE GAS INC | AUTOMOBILE LEFT ROADWAY, FLIPPED OVER LANDING ON AND SHEARING OFF METER RISERSCAUSING RELEASE OF GAS FOLLOWED BY IGINTION. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2128 | 1998-10-20 | TX | other | CBOMANU | SPUR, CITY OF |  | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2129 | 1998-10-19 | MI | other | PHILLIPS | CONSUMERS POWER CO | AMERITECH EMPLOYEES WORKING IN EXCAVATION WITH TORCH MELTED PLASTIC GASSERVICE LINE AND IGNITED GAS CAUSING INJURIES. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2130 | 1998-10-07 | NY | maintenance |  | CONSOLIDATED EDISON CO OF NEW YORK | A CORRODED SECTION OF CUSTOMER OWNED HOUSE PIPING IN THE WALL OF APT 3A OF A 4STORY APARTMENT BUILDING, RESULTING IN A EXPLOSION IN APT 4A. ONE WOMANRECEIVE MINOR BURNS AND WAS TREATED AND RELEASED. WE ARE INVESTIGATING TODETERMINE WHETHER THE ACTIONS O | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2131 | 1998-10-11 | ID | other | RISER FIELD FABRICATION | WASHINGTON WATER POWER CO | ON OCTOBER 11, 1998, WASHINGTON WATER POWER, AN ELECTRIC AND NATURAL GASDISTRIBUTION UTLITY, RECEIVED NOTIFICATION BY THE FIRE DEPARTMENT THAT NATURALGAS WAS INVOLVED IN A RESIDENTIAL FIRE AT 6322 DISTRICT 2 RD. PRIVATE G,BONNERS FERRY, ID. DAVID W. KUHN | 150000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2132 | 1998-09-09 | OH | other | DRISCO | COLUMBIA GAS OF OHIO INC | CONTRACTOR WAS WORKING AROUND A 1-INCH EXPOSED SERVICE LINE. THE CONTRACTORSEVERED THE SERVICE LINE. A CONTRACTOR EMPLOYEE WAS BURNED WHEN THE BLOWINGGAS IGNITED. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2133 | 1998-10-09 | CA | other |  | PACIFIC GAS & ELECTRIC CO | EXCAVATOR NOTIFIED UNDERGROUND SERVICE ALERT (USA) TO MARK FACILITIES ON10/5/98. USA NOTIFIED OPERATOR ON 10/5/98 REGARDING REQUEST TO MARKFACILITIES. OPERATOR DID NOT MARK FACILITIES. FARMER RIPPING FARM LAND HITPIPELINE ON 10/9/98. | 55000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2134 | 1998-10-03 | NY | other |  | BROOKLYN UNION GAS CO | MARKETSPAN NATURAL GAS FACILITIES WERE NOT INVOLVED. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2135 | 1998-10-15 | AL | ACCIDENTALLY CAUSED BY OPERATOR | DRISCO | FULTONDALE GAS BOARD | A COMPANY SERVICE EMPLOYEE, MIKE HORSLEY, WAS IN THE PROCESS OF MAKING ASERVICE TAP. A 1' CROSS OVERLINE, UNDER PRESSURE 25#, WAS CUT IN ORDER TOMAKE THE TIE IN. A TEMPORARY ELECTRICAL SERVICE BOX LOCATED ABOUT THREE FEETFROM BELL HOLE WAS BEING USED BY | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2136 | 1998-10-24 | AK | other | DRISCOPIPE | ENSTAR NATURAL GAS CO | ON SATURDAY MORNING, OCTOBER 24, 1998, AT APPROXIMATELY 5:38 AM EST, ENSTARNATURAL GAS COMPANY WAS NOTIFIED OF AN EXPLOSION AND FIRE AT 1820 BELLEVUELOOP, ANCHORAGE, AK 99515. AN ENSTAR SERVICEMAN AND DUTY SUPERVISOR WEREDISPATCHED TO THE SCENE. UPON AR | 500000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2137 | 1998-10-13 | AZ | other | PHILLIPS | SOUTHWEST GAS CORP | A CONTRACTOR WAS EXCAVATING A TRENCH LINE WITH A BACKHOE AND UTLIZING A TRENCHBOX. THE BACKHOE DAMAGED A 4' PE MAIN, WHICH WAS ALREADY EXPOSED. ONE OF THECONTRACTOR'S EMPLOYEES WAS INJURED WHILE TRYING TO ESCAPE FROM THE TRENCH.THE EMPLOYEE WAS ADMITTED | 1150 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2138 | 1998-10-05 | CO | other |  | PUBLIC SERVICE CO OF COLORADO | ON OCTOBER 5, 1998 AT APPROXIMATELY 9:00 AM AN ELECTRICAL DISTRIBUTIONCONTRACTOR INSTALLING UNDERGROUND CONDUIT PULLED A 3/4' MW STEEL SERVICE LINETO 2804 3RD ST, BOULDER COLORADO. THE SERVICE LINE WAS BROKEN AND SEPARATEDAT 3/4" X 3/4" 90 DEGREE ELL AT | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2139 | 1998-10-10 | TX | other |  | LONE STAR GAS CO (DISTRIBUTION DIVISION) | THE PIPING IN A COMPRESSION COUPLING, ON THE SERVICE TAP FOR THE DWELLING AT1412 LACKLAND (ACROSS THE STREET FROM THE INCIDENT LOCATION), WAS PULLED OUTOF ITS FITTING, WITH A GAS LEAK ENSUING FROM THAT COMPRESSION COUPLING. THEOPERATOR BELIEVES THAT EART | 110000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2140 | 1998-10-30 | IL | other |  | PEOPLES GAS LIGHT & COKE CO | SEWER CONTRACTOR RUPTURED A 24" CAST IRON MEDIUM PRESSURE MAIN. ESCAPING GASIGNITED FROM UNKNOWN SOURCE AND FIRE DAMAGED AN ADJACENT BUILDING. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2141 | 1998-10-27 | TN | other | STUPP CORPORATION | MEMPHIS LIGHT GAS & WATER DIVISION | M & H CONSTRUCTION HIT 24" GAS LINE; THERE WAS NO LOCATE CALLED TO TENNESSEONE CALL. | 120000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2142 | 1998-11-09 | DE | other | CENTRAL PLASTICS | CHESAPEAKE UTILITY CORP | METER ASSEMBLY WAS STRUCK BY A PASSENGER VEHICLE. THE SERVICE RISER WASDAMAGED BELOW THE INLET VALVE. THE CAUSE OF THE INCIDENT WAS A VEHICULARACCIDENT. A PASSENGER VEHICLE STRUCK AND DAMAGED AN APARTMENT BUILDING ANDADJACENT NATURAL GAS METER SET. A R | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2143 | 1998-10-27 | OH | maintenance |  | CINCINNATI GAS & ELECTRIC CO |  | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2144 | 1998-11-10 | LA | other | PLEXCO | TRANS LOUISIANA GAS CO INC | 1" POLY PIPE WAS INSERTED INTO 4" PVC IN 1982 WHEN A MASTER TRAILER PARKREQUESTED INDIVIDUAL METERS. THE 4" PVC PIPE WAS CUT FOR EACH RISERINSTALLATION. A PARTIAL FRACTURE IN OR ADJACENT TO A FUSION JOINT OCCURREDPOSSIBLY FROM LONG TERM STRESS ON JOINT | 30000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2145 | 1998-11-22 | GA | other |  | QUITMAN GAS DEPT, CITY OF | ON OCTOBER 23, 1998 THE RESIDENT, JOSEPH GRIFFIN, WAS INFORMED BY THE CITYMETER READER DEPT THAT THEY WOULD NOT TURN HIS GAS METER ON BECAUSE THERE WASA GAS LEAK INSIDE HIS HOUSE. ON NOV. 22, 1998 THE QUITMAN FIRE DEPARTMENTRESPONDED TO A FIRE AT THE RES | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2146 | 1998-07-13 | LA | other |  | ARKLA, A NORAM ENERGY COMPANY | 2" POLY PIPE DEVELOPED CRACK. PIPE WAS INSTALLED BY CUSTOMER'S PLUMBER. | 120000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2147 | 1998-12-10 | NV | other | KRALOY | SOUTHWEST GAS CORP | A HOUSE, LOCATED AT 1402 E ST. LOUIS, WAS DAMAGED ON DECEMBER 10, 1998.ADDITIONAL RESIDENCES SUSTAINED DAMAGE THAT RANGED FROM EXTENSIVE STRUCTURALDAMAGE ON ONE HOUSE TO BROKEN WINDOWS ON A SECOND RESIDENCE. SOUTHWEST GASCORPORATION PERSONNEL RESPONDED T | 147825 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2148 | 1998-12-05 | TX | other |  | LONE STAR GAS CO (DISTRIBUTION DIVISION) | THE OPERATOR BELIEVES THAT EARTH MOVEMENT, SPECIFICALLY GROUND SHIFTING,CAUSED THE PIPING TO SEPARATE FROM THE COMPRESSION COUPLING OF A SERVICE TAP.THIS IS BELIEVED TO HAVE RESULTED IN A RELEASE OF GAS, WHICH MIGRATED INTO THEDWELLING AT 1305 DALE. IT R | 85000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2149 | 1998-12-04 | CA | other |  | SOUTHERN CALIFORNIA GAS CO | CONTRACTOR, USING TRACK MOUNTED TRENCHER HIT LINE, CUTTING THROUGH TOP OFMAIN. LINE WAS PROPERLY MARKED AND HAD BEEN EXPOSED AT POINT OF CONTACTBEFORE TRENCHING BEGAN. TOTAL LOSS IS EXPECTED TO BE APPROX. $55K. | 55000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2150 | 1998-11-30 | VA | other | LANCASTER | COLUMBIA GAS OF VIRGINIA INC | A VEHICLE PARKED IN AN APARTMENT COMPLEX PARKING LOT ADJACENT TO 4109 MALLARDLANDING CIRCLE, JUMPED A CONCRETE CURB AND TRAVELED APPROXIMATELY 27 FEETACROSS A GRASSY AREA, PRIOR TO STRIKING AN ABOVE GROUND METER SETTING. THEVEHICULAR DAMAGE TO THE METER | 250000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2151 | 1998-12-15 | MI | other |  | CONSUMERS POWER CO | BASED ON PRELIMINARY INVESTIGATION, GAS FROM A BROKEN MAIN MIGRATED INTOBUILDING AND WAS IGNITED BY UNKNOWN SOURCE CAUSING EXPLOSION AND FIRE. | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2152 | 1998-12-14 | AR | ACCIDENTALLY CAUSED BY OPERATOR |  | ASSOCIATED NATURAL GAS COMPANY | WHILE IN PROCESS OF DISCONTINUING PORTION OF 1 1/4 GAS LINE, EMPLOYEEINSTALLED A HYDRAULIC STEEL SQUEEZE-OFF MACHINE TO CURTAIL GAS FLOW. AFTERSEVERING GAS PIPE DOWN STREAM OF SQUEEZE-OFF, EMPLOYEE WAS IN PROCESS OFSEALING END OF PIPE BY ACETYLENE WELDIN | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2153 | 1998-12-11 | MN | other | DUPONT | NORTHERN STATES POWER CO | A UTILITY POLE ANCHOR, BEING INSTALLED BY A THIRD PARTY CONTRACTOR, CAME INTOCONTACT WITH THE POLYETHYLENE GAS SERVICE LINE FOR 29 COURT HOUSE SQUARE. THEANCHOR DAMAGED THE SERVICE LINE CAUSING GAS TO ESCAPE. GAS EXPLODED AFTERENTERING INTO THE ADJOININ | 5000000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2154 | 1998-12-03 | LA | other |  | LOUISIANA GAS SERVICE CO | MOST PROBABLE SCENARIO FOR EXPLOSION EVENT- FENCING CONTRACTOR WAS INSTALLINGA GATE. WHILE USING A JACKHAMMER TO BREAK THROUGH CONRETE ALONG SIDE THERESIDENCE, HE STRUCK AND BROKE THE 3/4' STEEL SERVICE LINE SERVING THE SUBJECTRESIDENCE. ESCAPING GAS EN | 150000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2155 | 1998-11-19 | MI | ACCIDENTALLY CAUSED BY OPERATOR | U S STEEL | CONSUMERS POWER CO | EXPLOSION & FIRE OCCURRED AT BLDG WHILE CO. CREW WAS REPLACING GAS SERVICERISER. EMPLOYEES DID NOT FOLLOW CO. WORK PROCEDURES TO LOCATE & CLOSE THESERVICE VALVE PRIOR TO EXCAVATION THE SERVICE RISER. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2156 | 1998-11-18 | TX | other | REYNOLDS | SOUTHERN UNION GAS CO | CONTRACT PAINTER HIRED BY PROPERTY OWNER WAS ALLEGEDLY ATTEMPTING TO TURN OFFWATER SERVICE TO THE RESIDENCE WHEN HE GAINED ACCESS TO A BELOW GROUND METERBOX SET AT A CURB NEAR THE RESIDENCE. THIS INDIVIDUAL MISTOOK THE GAS METERAND REGULATOR LOCATED IN T | 75000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2157 | 1998-12-07 | AK | other | DRISCOPIPE | ENSTAR NATURAL GAS CO | ON MONDAY EVENING, DECEMBER 7, 1998 AT APPROXIMATELY 7:25 PM AST, ENSTARNATURAL GAS COMPANY WAS ASKED TO RESPOND TO A HOUSE FIRE AT LOT 10 BLOCK 4,AURORA HILLS, SUBDIVISION, IN THE MATANUSKA SUSITNA BOROUGH NEAR PALMER,ALASKA. THE FIRE BURNED ENSTAR'S SE | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2158 | 1998-12-10 | AK | other | DRISCOPIPE | ENSTAR NATURAL GAS CO | ON THURSDAY MORNING, DECEMBER 10, 1998 AT APPROXIMATELY 6:12 AM AST, ENSTARNATURAL GAS COMPANY WAS ASKED TO RESPOND TO A HOUSE FIRE AT LOT 28 BLOCK 12,COTTONWOOD SHORES SUBDIVISION, IN THE MATANUSKA SUSITNA BOROUGH NEAR PALMER,ALASKA. THE FIRE BURNED ENS | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2159 | 1998-11-24 | MA | other |  | BOSTON GAS CO | ON NOVEMBER 24, 1998 AT APPROXIMATELY 7:16 AM, AN EXPLOSION AND FIRE OCCURREDAT 52 CANTERBURY STREET, HINGHAM, MA, DEMOLISHING A SINGLE FAMILY WOOD FRAME,RESIDENTIAL DWELLING. THE INCIDENT OCCURRED WHILE A THIRD-PARY EXCAVATOR,DIGGING WITH A LARGE TRACK | 250000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2160 | 1998-07-29 | OK | other |  | ARKLA, A NORAM ENERGY COMPANY | DUG INTO LINE COUNTY DEPT. | 5000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2161 | 1999-01-19 | LA | other |  | IBERVILLE PARISH NATURAL GAS SYSTEM |  | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2162 | 1999-01-22 | AR | other |  | ARKLA, A NORAM ENERGY COMPANY |  | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2163 | 1999-01-29 | WY | technical failure |  | CHEYENNE LIGHT FUEL & POWER |  | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2164 | 1999-01-15 | AZ | other |  | SOUTHWEST GAS CORP |  | 66500 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2165 | 1999-01-18 | LA | other |  | PLAQUEMINE, CITY OF |  | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2166 | 1999-01-07 | PA | maintenance | COUPLING SYS, INC | PENNSYLVANIA GAS & WATER CO |  | 105000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2167 | 1999-01-23 | OK | other |  | ARKLA, A NORAM ENERGY COMPANY |  | 5000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2168 | 1998-12-25 | MI | other |  | MICHIGAN CONSOLIDATED GAS CO (MICHCON) |  | 200000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2169 | 1998-12-27 | OK | technical failure | PHILLIPS | OKLAHOMA NATURAL GAS CO |  | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2170 | 1999-01-11 | GA | other |  | DOUGLAS GAS DEPT, CITY OF |  | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2171 | 1998-12-09 | TX | other |  | LONE STAR GAS CO (DISTRIBUTION DIVISION) |  | 40000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2172 | 1998-12-17 | CA | other |  | SOUTHERN CALIFORNIA GAS CO |  | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2173 | 1999-01-03 | VA | maintenance |  | UNITED CITIES GAS CO |  | 500000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2174 | 1998-05-28 | PA | other |  | PECO ENERGY DISTRIBUTION CO. | A CONTRACTOR WORKING FOR THE "CSX" WAS INSTALLING FIBER OPTIC CABLE PARALLELTO THE RAILROAD TRACKS IN CHESTER, PENNSYLVANIA. USING EARTH MOVING EQUIPMENT,AN 8-INCH WROUGHT IRON NATURAL GAS MAIN WAS STRUCK AND RUPTURED. THE UTILITYRIGHT-OF-WAY INTERSECTS | 70654 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2175 | 1999-01-19 | TX | maintenance |  | ENTEX, A NORAM ENERGY COMPANY (FORM. DIV OF ARKLA | AN EXPLOSION OCCURRED AT 5119 NORTHRIDGE. SEVERAL HOMES IN THE AREA WEREDAMAGED. THE SOURCE AND ORIGIN OF FUEL AND IGNITION SOURCE ARE UNDETERMINEDAT THIS TIME. OUR INVESTIGATION IS CONTINUING. | 75000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2176 | 1999-02-02 | NM | other | UNKNOWN | PUBLIC SERVICE COMPANY OF NEW MEXICO - GAS SVCS | ON FEBRUARY 2, 1999 AT1:40 PM, A.S.HORNER CALLED KYLE SAGER TO INFORM HIM THATTHEY HAD JUST HIT, AND BROKE, A GAS LINE. KYLE DISPATCHED A SERVICEMAN ANDHIS C&M CREW TO THE INCIDENT, WHICH WAS APPROXIMATELY 500 DEGREES SOUTH OF THEINTERSECTION OF US 285 A | 7500 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2177 | 1999-02-03 | IL | other | DRISOPIPE | NICOR GAS CO. | A FAULT OR SHORT ON AN ELECTRICAL SERVICE LINE MELTED THE PLASTIC GAS SERVICELINE RESULTING IN AN IGNITION AND FIRE. SIX UNIT BUILDING WAS EXTENSIVELYDAMAGED ALONG WITH PERSONAL PROPERTY/FURNITURE, AND NO PERSONAL INJURIES ORFATALITIES. | 25000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2178 | 1999-02-14 | IL | other | SPRAGUE | NICOR GAS CO. | EXTENSIVE FIRE DAMAGE TO THE BOILER BUILDING AND CONTENTS WITHIN THE BUILDING(I.E., GAS BOILERS AND AIR COMPRESSORS, CUSTOMER FUEL LINES) WERE OVERPRESSURIZED. THE SERVICE REGULATOR IS UNDER INVESTIGATION AS A POSSIBLE CAUSE. | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2179 | 1999-01-15 | MI | other |  | CONSUMERS POWER CO | BASED ON PRELIMINARY INVESTIGATION, GAS FROM A DAMAGED MAIN MIGRATED INTOBUILDING AND WAS IGNITED BY AN UNKNOWN SOURCE CAUSING AN EXPLOSION AND FIRE.MATTERS CONTAINED ON THIS PAGE OF THE FORM ARE STILL UNDER INVESTIGATION.WHEN CONCLUSIONS AS TO THE CAUSE | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2180 | 1999-02-07 | NY | other | UNIL | NEW YORK STATE ELECTRIC & GAS CORP | GAS (NATURAL) LEAK EMINATING FROM CRACKED 4" CAST IRON MAIN MIGRATED INTOBASEMENT OF DWELLING AT 13 CLIFFORD STREET. OCCUPANT IGNITED GAS BY SWITCHINGON LIGHT IN BASEMENT. RESULTING EXPLOSION DEMOLISHED DWELLING AND INJUREDOCCUPANT WHO WAS TREATED FOR B | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2181 | 1999-02-01 | TX | maintenance |  | LONE STAR GAS CO (DISTRIBUTION DIVISION) | CORROSION CAUSED A NATURAL GAS PIPE TO LEAK. THE OPERATOR BELIEVES THAT ANAPPARENT GAS ACCUMULATION AT THE SUBJECT RESIDENCE IGNITED. | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2182 | 1999-02-24 | MA | other | CONSOLIDATED PIPE CO | BAY STATE GAS CO | ON FEBRUARY 23, 1999 AT 10" BARE STEEL MAIN WAS BEING RETIRED IN CONJUCTIONWITH THE INSTALLATION OF A NEW 12" COATED STEEL MAIN ON PARK STREET, LAWRENCE,MA. THIS INVOLVED INSTALLING LINE STOPPERS AT TWO LOCATIONS TO ISOLATE THEMAIN BEING RETIRED. AFTER | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2183 | 1999-02-18 | MA | other |  | BAY STATE GAS CO | RESPOND TO A PUBLIC ODOR COMPLAINT AT #76 ASHLEY ST SPRINGFIELD. SERVICE TECHFOUND GAS IN HOUSE AND EVACUATED. LADY AT #79 CAME OUT OF HER HOUSE. TECHWENT IN AN FOUND FIRE AT ELECTRIC BOX AND EVACUATED. CHECKED OTHER HOUSES ANDEVACUATED 6 MORE HOUSES. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2184 | 1999-01-13 | NY | other |  | BROOKLYN UNION GAS CO | A FLASH FIRE OCCURRED FROM THE IGNITION OF A CRACKED 8" CAST IRON (0.25 PSIGOPERATING PRESSURE) GAS MAIN IN AN OPEN EXCAVATION. THREE BROOKLYN UNIONEMPLOYEES WERE INJURED, TAKEN TO THE HOSPITAL TREATED FOR BURNS, TWO ASINPATIENTS, ONE TREATED AND RELEASE | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2185 | 1999-02-09 | IN | other | UPONOR | NORTHERN INDIANA PUBLIC SERVICE CO | AT 6:01 AM ON TUESDAY, FEBRUARY 9, 1999, NORTHERN INDIANA PUBLIC SERVICECOMPANY (NIPSCO) WAS NOTIFIED OF A POTENTIAL NATURAL GAS LEAK ALONG CENTERSTREET NEAR THE COMPANY'S WHEATFIELD-SOUTH REGULATOR STATION IN THE TOWN OFWHEATFIELD, INDIANA. THE GAS SERV | 125000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2186 | 1998-03-20 | GA | other |  | ATLANTA GAS LIGHT CO | A 3/4" STEEL INSULATED UNION DOWNSTREAM OF THE NATURAL GAS METER WAS DAMAGEDBY LIGHTING. THE ESCAPING GAS IGNITED DAMAGING THE HOUSE. | 200000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2187 | 1999-02-09 | TX | other |  | RELIANT ENERGY - ARKLA | HOUSE FIRE THAT IS STILL UNDER INVESTIGATION. GAS IS NOT INVOLVED. CALL WASMADE DUE TO THE PROPERTY VALVE. | 200000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2188 | 1999-02-18 | TX | other |  | ENTEX, A NORAM ENERGY COMPANY (FORM. DIV OF ARKLA | THIRD PARTY DOING RECONSTRUCTION ROAD WORK DAMAGED A 6" IP PLASTIC MAIN ANDESCAPING GAS IGNITED. | 222850 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2189 | 1999-03-12 | FL | other | CONTINENTAL INDUSTRIES | PEOPLES GAS CO | TELEPHONE EMPLOYEE WAS USING A TORCH TO INSTALL A "SHRINK SLEEVE" AROUND ATELEPHONE CABLE IMMEDIATELY ADJACENT TO AND BELOW THE SERVICE LINE. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2190 | 1999-02-22 | MO | maintenance |  | LACLEDE GAS CO | VISUAL INSPECTION FOUND A CORROSION HOLE ON THE BODY OF THE COPPER SERVICELINE AT THE TEE CONNECTION TO THE MAIN SERVING 688 MERAMEC STATION ROAD. THISLOCATION WAS IN THE RIGHT-OF-WAY OF JEFFERSON AVENUE ADJACENT TO THE PROPERTYOF 688 MERAMEC STATION ROA | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2191 | 1999-03-15 | MI | ACCIDENTALLY CAUSED BY OPERATOR |  | MICHIGAN CONSOLIDATED GAS CO (MICHCON) | DISTRIBUTION EMPLOYEES WERE CUTTING AND CAPPING A SERVICE. THEY INADVERTENTLYBROKE OFF THE SERVICE TEE ON 12' CAST IRON MAIN AT 1/4# PRESSURE. THEY WEREIN THE PROCESS OF CLEANING OFF THE MAIN WHEN THE LEAKING NATURAL GAS IGNITED.THE SOURCE OF IGNITION I | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2192 | 1999-01-22 | AL | other |  | BRIDGEPORT UTILITIES BOARD | SERVICE LINE WAS PULLED BY EXCAVATOR'S BACKHOE. AS A RESULT THE SERVICE LINE(3/4" GALV.) WAS BROKEN UNDERGROUND AT THE RISER. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2193 | 1999-03-07 | PA | other |  | PHILADELPHIA GAS WORKS | THE FACTORS BELIEVED TO HAVE CONTRIBUTED TO THIS INCIDENT HAVE BEENINVESTIGATED BY THE PHILADELPHIA FIRE MARSHALLS' OFFICE AND THE PHILADELPHIAGAS WORKS (PGW). PGW FOUND A CIRCUMFERENTIAL BREAK ON A 6" CAST IRON MAIN ATTHE SERVICE TO 3587 GAUL AND LOCATE | 500000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2194 | 1999-03-06 | PA | other |  | PHILADELPHIA GAS WORKS | THE PHILADELPHIA FIRE MARSHALL'S OFFICE HAS CONCLUDED THAT THAT A FAILURE OFTHE 3/4" FLEXIBLE TUBING FOR THE WALL OVEN UNIT WAS THE CAUSE OF THEINCIDENT. THE INVESTIGATION FOUND THIS UNIT TO BE SEVERELY DAMAGED WITH THEEND CONNECTION VERY LOOSE. THE APP | 200000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2195 | 1999-03-08 | PA | other | UNKNOWN | UGI UTILITIES INC | ON MARCH 8, 1999, AT 8:05 HOURS, UGI UTILITIES, INC RECEIVED A CALL THATCONTRACTOR HIT THE GAS LINE AT 213 S. 3RD AVENUE, WEST READING. THECONTRACTOR, WEXCON, INC. HIT THE 3/4" XTC COATED STEEL MEDIUM PRESSURE SERVICELINE, FEEDING A SIX UNIT APARTMENT BU | 290000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2196 | 1999-03-01 | OH | other | DRISCO | EAST OHIO GAS CO | SEWER CONTRACTOR HIT 6" PLASTIC MAINLINE. CONTRACTOR FAILED TO OBSERVEPROPERLY MARKED PIPELINE (OUPS). LINE HAD OIL IN IT THAT SPRAYED ONTO PUBLICAND PRIVATE PROPERTY. OIL WAS TESTED FOR PCB. AREA WAS ENVIRONMENTALLYCLEANED UP. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2197 | 1999-03-11 | MN | other | FISHER | NORTHERN STATES POWER CO | WATER, ASSUMED TO BE FROM MELTING SNOW ON ROOF, FROZE AROUND A FISHER S254SERVICE REGULATOR, INCLUDING THE VENT OPENING WHICH WAS POINTING DOWN. EXCESSPRESSURE OCCUURED IN THE HOUSEPIPING. GAS ESCAPED FROM HOUSEPIPING AND WASIGNITED BY AN UNDETERMINED S | 70000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2198 | 1999-03-13 | MN | other | FISHER | NORTHERN STATES POWER CO | WATER, ASSUMED TO BE FROM MELTING SNOW ON ROOF, FROZE ON THE VENT SCREEN(POINTING DOWN) OF A FISHER S254-4 SERVICE REGULATOR. EXCESS PRESSUREOCCURRED IN THE HOUSEPIPING. GAS ESCAPED FROM HOUSEPIPING AND WAS IGNITED BYUNDETERMINED SOURCE OF IGNITION. | 60000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2199 | 1999-03-13 | OK | other |  | OKLAHOMA NATURAL GAS CO | ON SATURDAY, MARCH 13, 1999, A MONITOR REGULATOR STATION SERVING THE REPUBLICGYPSUM PLANT FROM OUR HIGH-PRESSURE DISTRIBUTION SYSTEM FAILED IN THE OPENEDPOSITION. THE MALFUNTION APPARENTLY WAS CAUSED BY AN APPARENT WATER VAPOR INTHE GAS STREAM FREEZING T | 59500 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2200 | 1999-03-16 | NV | other |  | SIERRA PACIFIC POWER CO | AN IGNITION OCCURRED DUE TO A RELEASE OF NATURAL GAS FROM A DAMAGED 3/4"WELDED X-TRU COAT PIPE. DAMAGE TO PIPE WAS CAUSED BY AN UNKNOWN 3RD PARTY. | 130000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2201 | 1999-03-19 | MI | other | PHILLIPS | CONSUMERS POWER CO | TWO BOLTS WERE REMOVED FROM FLANGE AT SERVICE VALVE IN WHAT APPEARS TO BESABOTAGE. APPARENTLY, GAS LEAKING FROM THE FLANGE IGNITED, CAUSING A FIREWHICH DESTROYED THE BUILDING (GREENHOUSE). | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2202 | 1998-12-05 | TX | other | UNKNOWN | LONE STAR GAS CO (DISTRIBUTION DIVISION) | THE OPERATOR BELIEVES THAT EARTH MOVEMENT, SPECIFICALLY GROUND SHIFTING,CAUSED THE PIPING TO SEPARATE FROM THE COMPRESSION COUPLING OF A SERVICE TAP.THIS IS BELIEVED TO HAVE RESULTED IN A RELEASE OF GAS, WHICH MIGRATED INTO THEDWELLING AT 1305 DALE. IT R | 85000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2203 | 1999-03-31 | NC | other | AMERICAN | PIEDMONT NATURAL GAS CO INC | CAR STRUCK METER SET. | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2204 | 1999-04-23 | CO | other |  | PUBLIC SERVICE CO OF COLORADO | DUE TO HEAVY SNOW A BRANCH FROM EVERGREEN TREE BROKE FROM THE TREE, FALLING ONMETER SET, PULLING FITTINGS FROM PUBLIC SERVICE GAS SERVICE PIPE AND HOUSEFUEL LINE. MOST LIKELY A FITTING INSIDE THE HOUSE ALSO PULLED AND CAUSED AGAS LEAK, WITH IGNITION FROM | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2205 | 1999-05-03 | CO | technical failure | PLEXCO | PUBLIC SERVICE CO OF COLORADO |  | 125000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2206 | 1999-04-29 | IL | other | PHILIP DRISCO | NICOR GAS CO. |  | 1500 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2207 | 1999-03-15 | FL | other |  | PEOPLES GAS SYSTEM INC |  | 80000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2208 | 1999-04-19 | TX | other | UNKNOWN | LONE STAR GAS CO (DISTRIBUTION DIVISION) |  | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2209 | 1999-05-19 | CO | other |  | PUBLIC SERVICE CO OF COLORADO |  | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2210 | 1999-05-01 | AL | other | POLY ARK | SOUTHEAST ALABAMA GAS DISTRICT |  | 90000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2211 | 1999-05-03 | OK | other |  | OKLAHOMA NATURAL GAS CO |  | 1000000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2212 | 1998-07-07 | VA | other | DRISCO PIPE | WASHINGTON GAS LIGHT CO |  | 380000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2213 | 1999-06-04 | KY | other |  | LOUISVILLE GAS & ELECTRIC CO | AT APPROXMATELY 10:00 A.M. ON 6/4/99, CSX EMPLOYEES WERE BACKING ELEVEN BOXCARS INTO THE DIXIE WAREHOUSE AT 2900 FERN VALLEY ROAD. THE ENGINEER WASVIRGIL BYBEE AND THE SWITCHMAN WAS LOUIS STARR. MR. STARR WAS COUNTING OFFCARS TO MR. BYBEE OVER A HAND H | 70000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2214 | 1999-06-03 | WV | other | DRESSER | MOUNTAINEER GAS CO | THE CITY OF CHARLESTON STREET DEPARTMENT CALLED MOUNTAINEER GAS COMPANY (MGC)ON JUNE 3, 1999 AT 11:21 A.M. TO REPORT DAMAGE TO A NATURAL GAS FACILITY. MGCFOUND AN 1 1/4" STEEL SERVICE LINE PULLED OUT OF A BOLTED DRESSER COUPLING,THE SEPARATION WAS CAUSED | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2215 | 1999-05-27 | NC | other |  | PIEDMONT NATURAL GAS CO INC | IN ATTEMPTING TO REPLACE A STEEL SERVICE LINE WITH PLASTIC, THERE WAS ACCIDENTAL IGNITION. THE PROBABLE SOURCE OF IGNITION WAS STATIC CHARGES ON THE PLASTIC. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2216 | 1999-06-25 | CO | ACCIDENTALLY CAUSED BY OPERATOR |  | PUBLIC SERVICE CO OF COLORADO | CONTRACTOR CT 3" PE GAS DISTRIBUTION MAIN. CONTRACTOR COMPLETING EXCAVATION CUT 3" PE GAS DISTRIBUTION. DUE TO GAS LEAK CHERRYSIDE DRIVE WAS CLOSED TO TRAFFIC FOR APPROXIMATELY 2 HOURS WHILE REPAIRS WERE MADE. CHERRYSIDE DRIVE IS NOT A MAIN ROAD. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2217 | 1999-06-15 | MI | technical failure |  | SEMCO ENERGY GAS COMPANY |  | 370000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2218 | 1999-06-29 | NM | other | LONE STAR STEEL | PUBLIC SERVICE COMPANY OF NEW MEXICO - GAS SVCS | AT APPROXIMATELY 1:25 A.M. ON JUNE 29, 1999, A D-10 CATERPILLAR BULLDOZER OWNED BY SEMA CONSTRUCTION AND OPERATED BY A PERSON NAMED MIKE MATHIAS HIT A 4" DISTRBUTION GAS MAIN IN A ROAD AT THE INTERSECTION OF ACCESS ROAD "B" AND GEORGE STREET SE IN ALBUQU | 525000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2219 | 1999-06-25 | MI | other | PHILLIPS | CONSUMERS POWER CO | CONTRACTOR INSTALLING TELEPHONE CABLE, STRUCK GAS MAIN. ESCAPING GAS ENTERED BUILDINGS AND IGNITED. | 500000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2220 | 1999-06-28 | AL | other |  | MOBILE GAS SERVICE CORP |  | 70000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2221 | 1999-07-15 | GA | other |  | CARTERSVILLE GAS DEPT, CITY OF | CONTRACTOR INSTALLING UNDERGROUND GASOLINE TANKS HIT NATURAL GAS LINE. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2222 | 1999-07-07 | MI | other |  | CONSUMERS POWER CO | SEWER CONTRACTOR HIT AND PULLED SERVICE, DAMAGING INSIDE PIPE. ESCAPING GAS IGNITED BY UNKNOWN SOURCE. | 90000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2223 | 1999-07-09 | PA | ACCIDENTALLY CAUSED BY OPERATOR |  | COLUMBIA GAS OF PENNSYLVANIA | EMPLOYEE INADVERTENTLY TURNED OFF SUPPLY PRESSURE TO CONTROLLERS PRIOR TO SHUTTING OFF THE DISTRIBUTION OUTLET VALVE. BOTH MONITOR AND CONTROL REGULATORS OPENED INTRODUCING 452 PSIG INTO A 175 PSIG MAOP SYSTEM. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2224 | 1999-07-06 | MD | other | AMERICAN | WASHINGTON GAS LIGHT CO | HOUSE FIRE WITH SECONDARY GAS INVOLVEMENT FROM OUTSIDE METER | 155000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2225 | 1999-07-22 | WA | other | PLEXCO | PUGET SOUND ENERGY | SEE COVER LETTER AND PARTS (3) AND D ON BACK OF FORM FOR ADDITIONAL INFORMATION. | 87447 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2226 | 1998-10-08 | OK | other |  | ARKLA, A NORAM ENERGY COMPANY | HIT METER BY CAR | 10000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2227 | 1999-08-07 | AK | other | DRISCOPE | ENSTAR NATURAL GAS CO | ON SATURDAY MORNING, AUGUST 7, 1999, AT APPROXIMATELY 12:55 AM AST, ENSTAR NATURAL GAS COMPANY WAS NOTIFIED OF A FIRE AT 801 TINA, NEAR PALMER, ALASKA. AN ENSTAR SERVICEMAN AND DISTRIBUTION CREW WAS DISPATCHED TO THE SCENE. UPON ARRIVAL THEY FOUND A SIN | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2228 | 1999-07-06 | MO | other | UNKNOWN | MISSOURI GAS ENERGY | SEE PART D AND ATTACHED NARRATIVE | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2229 | 1999-07-19 | NY | ACCIDENTALLY CAUSED BY OPERATOR |  | CONSOLIDATED EDISON CO OF NEW YORK | THE RESPONDING CREW FOUND A DOWNED ENERGIZED 13 KV FEEDER CABLE THAT IGNITED SMALL FIRES ALONG THE CURB LINE AND LAWN AREA TO THE ABOVE ADDRESS. ACCESS TO THE CURB VALVE WAS NOT AVALIABLE DUE TO THE FIRE. THE CREW WAS ABLE TO TURN OFF AND LOCK THE HEAD O | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2230 | 1999-08-10 | MD | other | DRISCO | BALTIMORE GAS & ELECTRIC CO | IT WAS APPARENT THAT THE FINAL GRADE HAD BEEN ESTABLISHED SHORTLY AFTER THE UTILITIES WERE INSTALLED IN 1992. THE 2" HIGH PRESSURE GAS LINE (99 PSIG) WAS LOCATED AND MARKED ON 7/27/99. THE GRADE HAD BEEN LOWERED SINCE THE ORIGINAL ESTABLISHED GRADE AND | 300000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2231 | 1999-08-03 | GA | other | UNKNOWN | AUSTELL NATURAL GAS SYSTEM, CITY OF |  | 175000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2232 | 1999-08-04 | PA | other | AMERICAN METER | PECO ENERGY CO |  | 800000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2233 | 1999-07-27 | SC | other | CBOMANU | SOUTH CAROLINA ELECTRIC & GAS CO | UPON COMPLETE INVESTIGATION IT WAS DETERMINED NATURAL GAS WAS NOT INVOLVED/INITIALLY REPORTED AS A NATURAL GAS EXPLOSION. THIS WAS HOUSE FIRE INITIALLY REPORTED TO BE CAUSED BY A GAS LEAK ON THE CUSOMTER'S COOK STOVE. AN EXPLOSION WAS ALSO REPORTED. FU | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2234 | 1999-08-02 | MI | other | CBOMANU | MICHIGAN CONSOLIDATED GAS CO (MICHCON) | LEAKING GAS FROM THE CUSTOMER'S FUEL LINE IGNITED FROM AN UKNOWN SOURCE. | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2235 | 1999-08-08 | NY | other |  | CENTRAL HUDSON GAS & ELECTRIC CORP |  | 10000000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2236 | 1999-07-31 | NJ | other | UNKNOWN | PUBLIC SERVICE ELECTRIC & GAS CO |  | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2237 | 1999-08-17 | NY | other | UNKNOWN | KEYSPAN ENERGY CORP |  | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2238 | 1999-08-06 | CA | ACCIDENTALLY CAUSED BY OPERATOR | DUPONT | PACIFIC GAS & ELECTRIC CO |  | 78000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2239 | 1999-08-13 | IL | other | UNKNOWN | ILLINOIS POWER CO |  | 150000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2240 | 1999-08-03 | CA | other |  | SOUTHERN CALIFORNIA GAS CO |  | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2241 | 1999-08-05 | NM | other | CHEVRON (PLEXCO) | PUBLIC SERVICE COMPANY OF NEW MEXICO - GAS SVCS |  | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2242 | 1999-07-26 | MO | other | UNKNOWN (ST LOUIS COUNTY) | LACLEDE GAS CO |  | 86554 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2243 | 1999-08-17 | OH | technical failure |  | COLUMBIA GAS OF OHIO INC |  | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2244 | 1999-07-26 | MO | other | UNKNOWN | MISSOURI GAS ENERGY | MATERIAL FAILURE | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2245 | 1999-09-04 | IL | other |  | NORTHERN ILLINOIS GAS CO | NATURAL GAS LEAK MIGRATED INTO A TELEPHONE MANHOLE. SEVERAL CHILDREN WERE PLAYING WITH MATCHES AND IGNITED THE GAS. ONE OF THE CHILDREN RECEIVED 1ST AND 2ND DEGREE BURNS TO HIS FACE & LEGS. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2246 | 1999-08-21 | OH | maintenance | UNKNOWN | EAST OHIO GAS CO | SEE PART D | 60000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2247 | 1999-08-26 | OK | other |  | RELIANT ENERGY - ARKLA |  | 378000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2248 | 1999-09-13 | TX | maintenance |  | ENERGAS CO | A GAS LEAK WAS DISCOVERED 18 FEET FROM RESIDENCE. CUSTOMER LIT CIGARETTE AND WAS BURNED FROM A FLASH FIRE. | 4000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2249 | 1999-08-31 | GA | other | UNKNOWN | ATLANTA GAS LIGHT CO | A 4" PLASTIC NATURAL GAS SERVICE WAS RUPTURED WHEN A CONTRACTOR WAS MAKING A DIRECTIONAL BORE WHILE INSTALLING CABLE TV. THE ESCAPING GAS IGNITED DESTROYING A TRENCHER AND A 10 UNIT APARTMENT BUILDING. | 1500000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2250 | 1999-09-08 | CA | other | AMERICAN METER | PACIFIC GAS & ELECTRIC CO | ACCORDING TO FRESNO FIRE DEPARTMENT INVESTIGATORS, KIDS PLAYING WITH MATCHES IGNITED A STRUCTURE FIRE IN A STORAGE ROOM OF AN APARTMENT BUILDING. THE STRUCTURE FIRE DAMAGED A 9 GAS METER MANIFOLD SET AND GAS IGNITED. | 179000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2251 | 1999-09-08 | KY | other | CBOMANU | LOUISVILLE GAS & ELECTRIC CO |  | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2252 | 1999-09-03 | KY | other |  | LOUISVILLE GAS & ELECTRIC CO | SEE ATTACHMENT | 60000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2253 | 1999-10-05 | OK | other | UNKNOWN (CANUTE COUNTY) | RELIANT ENERGY - ARKLA |  | 1807 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2254 | 1999-10-04 | MS | other | PLEXCO | MISSISSIPPI VALLEY GAS |  | 26000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2255 | 1999-09-20 | KY | other |  | LOUISVILLE GAS & ELECTRIC CO |  | 150000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2256 | 1999-09-20 | NY | other | UNKNOWN (ONONDAGA COUNTY) | NIAGARA MOHAWK POWER CORP | DAMAGE DIRECTLY RELATED TO INTERAL EXPLOSION AND FIRE NEAR CUSTOMERS APPLIANCES. | 30000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2257 | 1999-09-20 | NY | other | PHILLIPS DRISCOPIPE | NIAGARA MOHAWK POWER CORP |  | 45000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2258 | 1999-10-11 | NC | other | CBOMANU | PUBLIC SERVICE CO OF NORTH CAROLINA |  | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2259 | 1999-10-22 | AZ | other | UNKNOWN (COCONINO COUNTY) | CITIZENS UTILITY CO | VEHICLE LEFT ROADWAY AND EASEMENT. STRUCK GARGE AND METER LOGS. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2260 | 1999-10-25 | TX | other | NO DATA | TXU GAS DISTRIBUTION | A THIRD PARTY CONTRACTOR PERFORMED EXCAVATION WORK FOR THE HOMEOWNER. DURING THE COURSE OF THE EXCAVATION, THE REGULATOR WAS BURIED. THE BURIED REGULATOR FAILED, GAS IGNITED, AND THE RESIDENCE BURNED. | 55000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2261 | 1999-03-04 | PA | other | ROCKWELL | NATIONAL FUEL GAS DISTRIBUTION CORP |  | 200000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2262 | 1999-10-16 | IN | other | CBOMANU | NORTHERN INDIANA PUBLIC SERVICE CO |  | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2263 | 1999-11-05 | MS | other | PHILLIPS | MISSISSIPPI VALLEY GAS |  | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2264 | 1999-10-27 | MI | technical failure |  | MICHIGAN CONSOLIDATED GAS CO (MICHCON) |  | 75000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2265 | 1999-10-21 | CA | other | DUPONT | SOUTHERN CALIFORNIA GAS CO | ROOTS DAMAGED 1/2" PLASTIC SERVICE. MIGRATING GAS IGNITED GARAGE OF SINGLE FAMILY HOME. | 75000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2266 | 1999-10-27 | ID | other | DUPONT ALDY A | INTERMOUNTAIN GAS CO | ON OCTOBER 27, 1999 AT 101 SUNRISE IN SUN VALLEY, IDAHO A TREE REMOVAL SUBCONTRACTOR TO A LANDSCAPE CONTRACTOR SEVERED A 3/4 POLYETHYLENE NATURAL GAS SERVICE LINE WHILE IN THE PROCESS OF EXCAVATING A TREE. THE SEVERING OF THE SERVICE LINE APPARENTLY ALLO | 1000000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2267 | 1999-10-28 | MI | technical failure | PLEXCO | MICHIGAN CONSOLIDATED GAS CO (MICHCON) | CONTRACTOR USING POWER EQUIPMENT STRUCK AND CUT THE GAS MAIN. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2268 | 1999-11-17 | MS | other | DRISCO | FULTON MUNICIPAL GAS SYSTEM | THE MAN SAID HE LITE A CIGARETTE AND BLEW UP THE HOUSE. | 25000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2269 | 1999-10-30 | NC | other | SPRAGUE | NORTH CAROLINA GAS SERVICE |  | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2270 | 1999-11-15 | NJ | other |  | SOUTH JERSEY GAS CO | ON NOVEMBER 15, 1999, A FIRE OCCURRED AT 202 E. GREENFIELD AVE AS A RESULT OF A GAS LEAK ON THE CUSTOMERS HOUSE PIPING. ON THAT DAY, A SOUTH JERSEY GAS SERVICEMAN WAS COMPLETING AN APPLIANCE SERVICE CALL AT THIS ADDRESS WHEN THE CUSTOMER TOLD HIM SHE SMEL | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2271 | 1999-11-02 | MI | other | PHILLIPS | CONSUMERS POWER CO | LOCAL ELECTRIC COMPANY CREW, INSTALLING SHRINK SLEEVE ON ELECTRIC CABLE IN CLOSE PROXIMITY OF PLASTIC GAS SERVICE, MELTED GAS SERVICE, CAUSED FIRE, RESULTING IN BURNS TO TWO CREW MEMBERS. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2272 | 1999-11-04 | KY | ACCIDENTALLY CAUSED BY OPERATOR | CBOMANU | LOUISVILLE GAS & ELECTRIC CO |  | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2273 | 1999-11-05 | PA | technical failure | PLEXCO | U G I CORP |  | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2274 | 1999-11-16 | OH | other | UPONOR | COLUMBIA GAS OF OHIO INC |  | 750000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2275 | 1999-11-10 | MI | other | CBOMANU | CONSUMERS POWER CO |  | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2276 | 1999-11-29 | NJ | other |  | PUBLIC SERVICE ELECTRIC & GAS CO |  | 300000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2277 | 1999-11-24 | AZ | other |  | CITIZENS UTILITY CO | 2" HIGH PRESSURE GAS LINE WAS HIT BY VERMEER TRENCHER WHILE TRENCHING TO INSTALL NEW SEWER LINE IN DRY CREEK RD. DOT REPORT 506809 ALAN GRNEAU, ACC REPORT 990604 | 1500000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2278 | 1999-12-18 | CA | other | UNKNOWN (SAN DIEGO COUNTY) | SAN DIEGO GAS & ELECTRIC CO | ON THE DAY OF THE INCIDENT, THE CUSTOMER WAS PAINTING HIS APARTMENT KITCHEN. SO THAT HE COULD PAINT BEHIND THE GAS RANGE, HE CLOSED THE SHUT OFF VALVE AT THE METER SET AND REMOVED THE GAS RANGE. AFTER COMPLETING HIS PAINTING, THE CUSTOMER REOPENED THE S | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2279 | 1999-12-09 | NC | other | UNKNOWN | PIEDMONT NATURAL GAS CO INC | FAILURE OF THREADED PIPE IN THE METER SET ASSEMBLY. | 75000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2280 | 1999-12-14 | MA | other |  | BOSTON GAS CO | A 6" IRON MAIN, OPERATING AT AN MAOP OF 14" WATER COLUMN, WAS INSTALLED ON LIBBY ROAD IN 1927. IN 1969, A WATER MAIN WAS INSTALLED ABOVE THE CAST IRON GAS MAIN. WOOD BLOCKING WAS USED TO SUPPORT THE WATER MAIN ON TOP OF THE GAS MAIN. IN OCTOBER THROUGH | 30000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2281 | 2000-01-10 | AK | other | DRISCOPE | ENSTAR NATURAL GAS CO | ON MONDAY MORNING, JANUARY 10, 2000, AT APPROXIMATELY 7:30 AM AST, ENSTAR NATURAL GAS COMPANY WAS NOTIFIED OF A FIRE AT LOT 6, BLOCK 4 WINDRIDGE ESTATE II SUBDIVISION, KENAI, ALASKA. AN ENSTAR SERVICEMAN AND DISTRIBUTION CREW WAS DISPATCHED TO THE SCENE. | 75000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2282 | 1999-12-20 | CO | other | PLEXCO PE 3408 | K N ENERGY INC(KANSAS NEBRASKA GAS CO) (KMI) | PIPELINE WAS NOT PROPERLY MARKED | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2283 | 1999-12-25 | PA | other | INNER-TITE | PENNSYLVANIA GAS & WATER CO | FAILURE OF THE POSILOCK ADAPTER. | 350000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2284 | 1999-12-12 | TX | other | NIPAK | TXU GAS DISTRIBUTION | A CONTRACTOR WHO WAS REPLACING A SEWER MAIN FOR THE CITY OF BLUE RIDGE PULLED A 3/4 INCH POLY SERVICE OUT OF A DRESSER COUPLING CAUSING LEAKAGE. | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2285 | 2000-01-23 | PA | other |  | PFG GAS, INC | ON JANUARY 23, 2000, AT APPROXIMATELY 5PM THERE WAS AN EXPLOSION OF 825 MAIN STREET, STROUDSBURG, PA. UPON INVESTIGATION BY PFG GAS INC PERSONNEL, IT WAS DETERMINED THAT AT 2" BARE STEEL NATURAL GAS MAIN LOCATED ON MAIN STREET HAD FAILED. THE APPARENT C | 500000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2286 | 1999-11-23 | TX | other |  | ENTEX, A NORAM ENERGY COMPANY (FORM. DIV OF ARKLA | LIGHTENING STRUCK ELECTRICAL SERVICE, CAUSING FIRE TO GAS METER AND BUILDING. | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2287 | 1999-12-23 | TX | other |  | ENTEX, A NORAM ENERGY COMPANY (FORM. DIV OF ARKLA | NATURAL GAS FROM A 2" IP STEEL MAIN ACCUMALATED IN A HOUSE WHERE AN EXPLOSION & FIRE OCCURRED. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2288 | 1999-11-21 | PA | technical failure | DUPONT ALDYL A | NATIONAL FUEL GAS DISTRIBUTION CORP |  | 200000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2289 | 1999-12-30 | TX | other | UNKNOWN | SOUTHERN UNION GAS CO | ACCORDING TO THE ACCIDENT REPORT, A COLLISON BETWEEN SMALL CAR AND MINIVAN OCCURRED WHEN THE SMALL CAR MADE A LEFT TURN IN FRONT OF ONCOMING TRAFFIC. THE COLLISON RESULTED IN THE SMALL CAR LEAVING THE PAVED ROADWAY AND STRIKING A GAS METER SET. THE GAS | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2290 | 2000-01-27 | NE | other | PLEXCO | METROPOLITAN UTILITIES DISTRICT | LOCATING GAS SERVICE ERROR BY METROPOLITAN UTLITIES DISTRICT. | 2500 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2291 | 2000-01-03 | DE | technical failure | DRISCO | CHESAPEAKE UTILITY CORP | SEE PART D | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2292 | 2000-01-13 | MD | ACCIDENTALLY CAUSED BY OPERATOR | UNKNOWN | BALTIMORE GAS & ELECTRIC CO | ON 1/13/00, AT 1720 AN EXPLOSION OCCURRED AT 3122 BAKER ST. IN AN ATTEMPT TO RESOLVE A POOR GAS SUPPLY TO THIS RESIDENT THE 1 1/2" GAS SERVICE WAS IN THE PROCESS OF BEING CLEARED OF RUST. NATURAL GAS WAS RELEASED INTO THE BASEMENT AND APPARENTLY IGNITE | 150000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2293 | 2000-01-24 | TN | other | CBOMANU | TIPTON COUNTY, FIRST UTIL DIST OF | SEE PART D | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2294 | 1998-05-16 | CA | other | UNKNOWN (nan COUNTY) | PACIFIC GAS & ELECTRIC CO | AN EXPLOSION OCCURRED AT 2010 HOURS ON SATURDAY MAY 16, 1998. THE ENSUING FIRE DESTOYED A THREE STORY BUILDING AND DAMAGED ADJACENT BUILDINGS. THE CAUSE OF THE INCIDENT WAS IDENTIFIED AS IGNITION OF FIREWORKS INSIDE THE BUILDING. | 500000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2295 | 2000-01-13 | MI | maintenance | AMERICAN METER | CONSUMERS POWER CO | PRELIMINARY INDICATIONS ARE THE SERVICE REGULATOR MAY HAVE FAILED TO FUNCTION PROPERLY, COUPLED WITH DOWNSTREAM FAILURE OF CUSTOMER EQUIPMENT. GAS ESCAPED FROM CUSTOMER EQUIPMENT AND WAS IGNITED BY UNKNOWN SOURCE. THIS ANALYSIS TO FURTHER INVESTIGATION | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2296 | 2000-01-26 | MD | other | UNKNOWN | BALTIMORE GAS & ELECTRIC CO | WE RECEIVED A GAS LEAK CALL AT 826 N LINWOOD AVE. WE FOUND A PROBLEM WITH THE GAS FURNACE AT THIS HOUSE AND PLACED A DEFECTIVE APPLIANCE TAG ON THE EQUIPMENT. THE MECHANIC PERFORMED A FRONT WALL INSPECTION AND PICKED UP A READING ON HIS METER. HE PROCE | 100 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2297 | 2000-01-26 | AK | other |  | ENSTAR NATURAL GAS CO | ON WEDNESDAY, JANUARY 26, 2000, AT APPROXIMATELY 3:15 PM AST, ENSTAR RECEIVED NOTICE THAT A GAS MAIN AT THE INTERSECTION OF TUDOR ROAD AND ARTIC BLVD. IN ANCHORAGE, ALASKA, HAD BEEN DAMAGED AND LEAKING NATURAL GAS. UPON ARRIVAL, ENSTAR CREWS FOUND AN AU | 75000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2298 | 2000-01-25 | GA |  | UNKNOWN | TALLAPOOSA GAS DEPT, CITY OF | NATURAL GAS MIGRATED INTO MANHOLE AND SEWER LINE. NATURAL GAS ENTERED DWELLING THROUGH IMPROPER INSTALLED SEWER CONNECTION. SOURCE OF IGNITION UNKNOWN. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2299 | 2000-01-27 | LA | other | UKNOWN | NEW ORLEANS PUBLIC SERVICE INC | AT APPROXIMATELY 12:40 A.M. ON 1/28/00, THE NEW ORLEANS FIRE DEPARTMENT NOTIFIED THE ENTERGY OIC THAT GAS WAS INVOLVED IN A FIRE. THE GAS SERVICE MAN ON DUTY WAS NOTIFIED BY THE OIC. AT APPROXIMATELY 1:20 A.M., THE GAS SERVICE MAN ARRIVED ON THE SCENE, | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2300 | 2000-01-22 | NJ | technical failure | INNER-TITE | ELIZABETHTOWN GAS CO | A MECHANICAL COMPRESSION FITTING THE POLYETHYLENE GAS SERVICE LINE TO THE GAS MAIN WAS IMPROPERLY INSTALLED. THE CONNECTION SEPARATED ALLOWING NATURAL GAS TO MIGRATE INTO THE BASEMENT OF THE PREMISES | 200000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2301 | 2000-01-29 | GA | other | AMERICAN METER | ATLANTA GAS LIGHT CO | DUE TO OUTSIDE WEATHER CONDITIONS REGULATOR HAD FROZEN (ICE IN VENT) IN THE OPEN POSITION. THIS CONDITION ALLOWED 12 POUNDS OF PRESSURE TO BE PUT ON CUSTOMERS FUEL LINE. THIS RESULTED IN A FIRE AT THE WATER HEATER IN THE GARAGE AREA OF THE RESIDENCE. | 150000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2302 | 2000-01-27 | TN | other | CBOMANU | NASHVILLE GAS CO | HOUSE FIRE MOST LIKELY RESULTED FROM NATURAL GAS LEAKING FROM THE CUSTOMER OWNED UNDERGROUND FUEL LINE TO A POOL HEATER. NASHVILLE GAS FACILITIES SERVING THIS ADDRESS DID NOT HAVE ANY LEAKAGE AND DID NOT CONTRIBUTE TO THIS HOUSE FIRE. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2303 | 2000-01-14 | TX |  | PLEXCO | TXU GAS DISTRIBUTION | A LEAK OCCURRED ON THE MAIN AT A FUSION POINT. GAS MIGRATED UNDER THE STRUCTURE AND THE GAS IGNITED. THE CAUSE OF THE LEAK IS STILL UNDER INVESTIGATION AND A SUPPLEMENTAL REPORT WILL BE FILED ONCE AN ENGINEERING LABORATORY ANALYSIS OF THE PIPE IS COMPLETE | 150000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2304 | 2000-01-19 | TX | other |  | TXU GAS DISTRIBUTION | A VEHICLE BACKED INTO A VACANT RISER KNOCKING THE STOPCOCK OFF. A BUILDING WAS EVACUATED AND TXU GAS DISTRIBUTION HAS UNCONFIRMED INFORMATION THAT AN EVACUEE WAS HOSPITALIZED. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2305 | 2000-02-04 | DC | other |  | WASHINGTON GAS LIGHT CO | HOUSE FIRE IN PROGRESS, CAUSE UNDETERMINED BY FIRE DEPT. METER AND PIPING EXPOSED TO FIRE. SERVICE WAS UNCOVERED IN SIDEWALK THEN CUT AND PLUGGED. | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2306 | 2000-02-02 | VA | other | PHILLIPS | WASHINGTON GAS LIGHT CO | A PLUMBER FROM COMMONWEALTH PLUMBING RESTED THE PIPE HE WAS SOLDERING DIRECTLY ON OUR 3/4" HIGH PRESSURE PLASTIC SERVICE. PENETRATION TO THE SERVICE OCCURRED CAUSING A FIRE AND SIGNIFICANT PROPERTY DAMAGE. | 750000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2307 | 2000-03-06 | FL | other | PLEXCO | GAINESVILLE REGIONAL UTIL GAS DEPT | A BELL SOUTH EMPLOYEE WAS WORKING IN A BELLHOLE WITH A TORCH AND APPARENTLY BURNED A HOLE IN A 5/8" GAS SERVICE LINE. THE ESCAPING GAS WAS IGNITED BY THE TORCH. | 3500 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2308 | 2000-02-23 | AZ | ACCIDENTALLY CAUSED BY OPERATOR | FISHER | COPPER MARKET INC | PILOT ACCURATOR FAILURE ON MONITORING REGULATOR. MAINTENANCE PERSONS FAILURE TO REARM VERBATIM ALARM SYSTEM. | 11608 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2309 | 2000-02-07 | MO | other | PHILLIPS | LACLEDE GAS CO |  | 150000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2310 | 2000-03-01 | KS | other | CBOMANU | WINFIELD GAS DEPT, CITY OF | APPEARS THAT IGNITER ON GAS DRYER OF PRINTING PRESS FAILED TO ARC. GAS ACCUMULATION CAUSED EXPLOSION. NO FIRE | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2311 | 2000-02-13 | TX | other | CBOMANU | ENTEX, A NORAM ENERGY COMPANY (FORM. DIV OF ARKLA | FLASH FIRE AT SOUTHWESTERN BELL MOBILE | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2312 | 2000-02-25 | WI | other | PLEXCO | MADISON GAS & ELECTRIC CO |  | 200000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2313 | 2000-02-23 | MS | other | UNKNOWN (LOWNDES COUNTY) | MISSISSIPPI VALLEY GAS |  | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2314 | 2000-02-20 | KY | other | CBOMANU | LOUISVILLE GAS & ELECTRIC CO | AT APPROXIMATELY 5:05 AM ON SUNDAY FEB.20,2000 THE LG&E ELECTRIC SERVICE BOARD RECEIVED A CALL FROM THE WEST POINT FIRE DEPARTMENT STATING THAT THERE HAD BEEN AN EXPLOSION INSIDE THE RESIDENTIAL DWELLING AT 903 ELM ST CAUSING NATURAL GAS TO BE DISCHARGE T | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2315 | 2000-02-17 | OK | technical failure | UNKNOWN (BECKHAM COUNTY) | OKLAHOMA NATURAL GAS CO | GAS MIGRATED UNDER PAVEMENT FROM COLD FUSED POLYTHYLENE PIPE JOINT THROUGH A SEWER CONNECTION TO A PORTABLE BUILDING BEING USED AS A FIELD OFFICE. THE GAS IGNITED WHEN AN ELECTRICAL SWITCH WAS TURNED ON BY AN EMPLOYEE. THE EMPLOYEE WAS INJURED AND HOSPITA | 12000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2316 | 2000-02-23 | CA | other |  | SOUTHERN CALIFORNIA GAS CO | EXPLOSION OCCURRED WHEN CUSTOMER ATTEMPTED TO LIGHT A WALL FURNANCE. FURTHER INVESTIGATION FOUND A LEAKING 1/2 PLASTIC SERVICE AT ADJACENT PROPERTY. CAUSE OF LEAK UNDER INVESTIGATION. | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2317 | 2000-02-29 | CA | other |  | SOUTHERN CALIFORNIA GAS CO | BACKHOE OPERATOR PULLED BRANCH SERVICE. LEAKING GAS WAS IGNITED BY WATER HEATER. | 60000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2318 | 2000-03-07 | FL | other | PLEXCO | PENSACOLA, ENERGY SERVICES OF | TIME WARNER CABLE COMPANY EMPLOYEE DAMAGED 5/8" P.E. SERVICE LINE BY USING PROPANE TORCH TO APPLY SHRINK WRAP COATING TO CABLE REPAIR. TORCH HEAD WEAKENED OR MELTED SERVICE LINE AND LEAKING GAS IGNITED, BURNING TIME WARNER EMPLOYEE ON FACE AND UPPER TORS | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2319 | 2000-03-13 | OK | other | ROCKWELL | RELIANT ENERGY FIELD SERVICES CORP |  | 15400 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2320 | 2000-02-22 | VA | other | DRISCO PIPE | RICHMOND DEPT OF PUBLIC UTILITIES, CITY OF |  | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2321 | 2000-03-17 | AL | other |  | ALABAMA GAS CORP (EX. MARENGO CORP PROPERTY) |  | 400000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2322 | 2000-03-20 | AZ | other | MOONEY | SOUTHWEST GAS CORPORATION | SEE PART D | 129322 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2323 | 2000-03-23 | NJ | maintenance |  | PUBLIC SERVICE ELECTRIC & GAS CO |  | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2324 | 2000-03-19 | MS | other |  | MISSISSIPPI VALLEY GAS | CONTRACTOR PULLED 3/4 SERVICE LINE OUT OF 3/4" DRESSER ELL AT SERVICE TIE-IN TO 2" STEEL MAIN. GAS MIGRATED TO SANITARY SEWER AND INTO HOUSES FROM LEAKS IN SEWER PIPES IN HOMES. GAS IGNITED FROM WATER HEATER. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2325 | 2000-03-15 | IN | other |  | NORTHERN INDIANA PUBLIC SERVICE CO | THE LOCATION OF THE GAS INCIDENT IS NEAR A LIQUEFIED NATURAL GAS (LNG) REFUELING STATION, OWNED AND OPERATED BY THE CITY OF GARY TRANSPORTATION CENTER. BOIL-OFF FROM THE LNG TANK IS COLLECTED, METERED AND INJECTED INTO NIPSCOS GAS DISTRIBUTION SYSTEM IN | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2326 | 2000-02-12 | OH | other |  | CINCINNATI GAS & ELECTRIC CO | A CRACK IN A 4" CAST IRON MAIN | 180000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2327 | 2000-03-22 | PA | other | UNKNOWN (WESTMORELAND COUNTY) | PEOPLES NATURAL GAS CO | THIRD PARTY CONTRACTOR BORED THROUGH 12 INCH NATURAL GAS DISTRIBUTION LINE. | 300000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2328 | 2000-03-22 | PA | other | PLEXCO | PEOPLES NATURAL GAS CO | THIRD PARTY CONTRACTOR DAMAGED MAINLINE WHILE INSTALLING TELEPHONE POLES. | 150000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2329 | 2000-03-30 | MD | other | LTV | WASHINGTON GAS LIGHT CO |  | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2330 | 2000-04-01 | OH | other | CBOMANU | CINCINNATI GAS & ELECTRIC CO | EXPLOSION STILL UNDER INVESTIGATION. INCIDENT STILL UNDER INVESTIGATION. VARIOUS FACTOS POSSIBLY CONTRIBUTED TO THE CAUSE OF THE RISER FAILURE AND INSPECTION TESTING AND REVIEW OF RECORDS AVAILABLE TO CG&E TO DATE FAIL TO DETERMINE THE SPECFIC CONTRIBUT | 250000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2331 | 2000-03-25 | MO | maintenance | UNKNOWN (ST FRANCOIS COUNTY) | LACLEDE GAS CO |  | 20000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2332 | 2000-04-08 | MD | other | PLEXCO | WASHINGTON GAS LIGHT CO | MULTIPLE FACILITIES (METER, RISERS) EXPOSED IN CONSECUTIVE HOUSE FIRES. SERVICES WERE ABANDONED AT THE MAIN. CAUSE UNDETERMINED BY FIRE DEPARTMENT. GAS SECONDARY, PRIMARY CAUSE STILL UNDER INVESTIGATION. | 370000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2333 | 2000-03-04 | AZ | other | UNKNOWN (MARICOPA COUNTY) | SOUTHWEST GAS CORP | A CONTRACTOR WAS BORING ALONG 15TH AVENUE AND STRUCK A 6" STEEL DISTRIBUTION MAIN. THE MAIN WAS PROPERLY MARKED AND HAD BEEN POT HOLED BY THE BORING CONTRACTOR. THE DAMAGED CAUSED AN OUTAGE OF 1,250 ACCOUNTS. THIS OUTAGE CAUSED THE LOSS TO EXCEED $50,000, | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2334 | 2000-05-09 | FL | other |  | TECO PEOPLES GAS LP OPERATIONS | 4 INCH MAIN CUT BY MIXER ON NEW ROAD PROJECT. | 11711 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2335 | 2000-05-13 | AK | other | DRISCOPIPE | ENSTAR NATURAL GAS CO | ON SATURDAY AFTERNOON, MAY 13, 2000, AT APPROXIMATELY 12:43 PM AST, ENSTAR NATURAL GAS CO WAS NOTIFIED OF A FIRE AT TAX PARCEL C9, SECTION 26, ON WYOMING DRIVE ( NO HOUSE NUMBER) IN THE MATANUSKA SUSITNA BOROUGH. AN ENSTAR SERVICEMAN AND DISTRIBUTION CRE | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2336 | 2000-04-13 | OH | maintenance | UNKNOWN | COLUMBIA GAS OF OHIO INC |  | 200000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2337 | 2000-04-14 | CA | other |  | SOUTHERN CALIFORNIA GAS CO | HIGH PRESSURE GAS MAIN HIT BY BORING MACHINE. STREET AND RAILROAD CLOSURE BY FIRE DEPARTMENT. CONTRACTOR DID NOT POT HOLE BEFORE BORING. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2338 | 2000-04-21 | IL |  | UNKNOWN (COOK COUNTY) | NORTHERN ILLINOIS GAS CO |  | 150000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2339 | 2000-04-12 | NE | other | PLEXCO | PEOPLES NATURAL GAS | SEWER CONTRACTOR WAS BLIND BORING AND HIT OUR GAS LINE. HE ALSO HIT THE SEWER LINE TO THE SAME ADDRESS. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2340 | 2000-05-09 | AL | other | AMERICAN | MARSHALL COUNTY GAS DISTRICT |  | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2341 | 2000-04-28 | TX | other | UNKNOWN | ENTEX, A NORAM ENERGY COMPANY (FORM. DIV OF ARKLA | THIRD PARTY USING A DRILLING AUGER DAMAGED A 8 I.P. STL. MAIN | 40000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2342 | 2000-05-18 | RI | other | UNKNOWN | PROVIDENCE GAS CO |  | 250000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2343 | 2000-05-08 | VA | other |  | RICHMOND DEPT OF PUBLIC UTILITIES, CITY OF | LEAK SITE ON GAS SERVICE PIPE INSIDE HOUSE, DOWNSTREAM OF METER. BEYOND THE CONTROL OF THE GAS COMPANY | 200000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2344 | 2000-05-12 | MA | other | AMERICAN | ESSEX COUNTY GAS CO | SEE PART D- OTHER BRIEF DESCRIPTION: (ON REVERSE SIDE) | 500000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2345 | 2000-06-06 | AK | other | DRISCOPIPE | ENSTAR NATURAL GAS CO |  | 1000000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2346 | 2000-05-07 | NY | other | CBOMANU | KEYSPAN ENERGY CORP | SEE PART D ON BACK OF THIS REPORT. ALSO SUPPLEMENTAL A & B* | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2347 | 2000-05-15 | MA | other | UNKNOWN (NORFOLK COUNTY) | BOSTON GAS CO | CONTRACTOR STRUCK SERVICE TO HOME WITH A LARGE EXCAVATOR. SERVICE WAS PULLED AT POINT OF CONTACT, BUT NOT BROKEN. SERVICE BROKE INSIDE OF STRUCTURE, CAUSING STRUCTURE TO FILL WITH GAS. THIRD PART DID NOT NOTIFY DIG SAFE AS REQUIRED BY COMMONWEALTH OF MASS | 250000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2348 | 2000-05-19 | NY | other | NO DATA | KEYSPAN ENERGY CORP | S.I. INDUSTRIES HIT 3/4 H.P. STEEL SERIVCE. THIS CAUSED HOUSE TO FILL UP WITH GAS AND EXPLODE. THEY WERE DIGGING TO MAKE AN EXTENSION FOR THE HOUSE. IT WAS MARKED OUT CORRECTLY CASE #1360017. ONE PERSON INJURIED BY FLYING DEBRIS AND TAKEN TO THE NORTH SHO | 400000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2349 | 2000-03-20 | TX | other |  | SAN ANTONIO, CITY PUBLIC SERVICE BOARD OF | CONTRACTOR HIT SUPPLY LINE WITH ROCK SAW. | 72183 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2350 | 2000-05-17 | CA | other | UNKNOWN (ORANGE COUNTY) | SOUTHERN CALIFORNIA GAS CO | PLUMBER WAS USING TORCH TO WORK ON WATER LINE AND CONTACTED EXPOSED PLASTIC MAIN, CAUSING LEAKAGE AND IGNITION. PLUMBER RECEIVED 1ST AND 2ND DEGREE BURNS. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2351 | 2000-06-02 | DC | other |  | WASHINGTON GAS LIGHT CO | SEE PART D | 61600 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2352 | 2000-05-30 | VA | other | PLEXCO | VIRGINIA NATURAL GAS | AN EMPLOYEE OF ANOTHER UTILITY COMPANY COX COMMUNICATIONS WAS PERFORMING WORK IN AN OPEN EXCAVATION WHERE THE GAS LINE WAS EXPOSED. THE WORKER WAS USING A PROPANE TORCH TO HEAT A CABLE REPAIR DEVICE AND ACCIDENTLY MELTED THE PLASTIC GAS SERVICE LINE, RUPT | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2353 | 2000-06-07 | CA | technical failure | UNKNOWN (LOS ANGELES COUNTY) | SOUTHERN CALIFORNIA GAS CO | GAS COMPANY EMPLOYEE OVERCOME WHILE ATTEMPTING TO PUT CLAMP ON DAMAGED 3" PE MAIN. HOSPITALIZED FOR 3 DAYS. CURRENTLY RECOVERING AT HOME. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2354 | 2000-06-12 | FL | technical failure | PLEXCO | PENSACOLA, ENERGY SERVICES OF | THE OPERATOR WAS ATTEMPTING TO INSTALL A 5/8" SERVICE ONTO AN 1 1/4 MAIN. IT APPEARS THAT THE OPERATOR OVERHEATED THE FUSION ON THE SADDLE TO THE MAIN. THIS ACTION CAUSED THE FUSION TO FAIL, RELEASING NATURAL GAS IN THE ATMOSPHERE. STATIC ELECTRICITY T | 4000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2355 | 2000-06-16 | LA | other | HACKNEY | DYNEGY MIDSTREAM SERVICES, L.P. | UNKNOWN OUTSIDE FORCE | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2356 | 2000-07-04 | CA | other | UNKNOWN (SANTA CLARA COUNTY) | PACIFIC GAS & ELECTRIC CO | VEHICLE STRUCK GAS METER SET LOCATED IN A METER CABINET RECESSED IN THE FRONT WALL OF THE BUILDING. LEAKING GAS CAUGHT FIRE. EXTENSIVE DAMAGE TO RESIDENCE, DUE TO FIRE. | 76500 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2357 | 2000-07-14 | MN | other | NORDSTROM | HUTCHINSON UTILITIES COMMISSION | SEE PART D | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2358 | 2000-06-12 | NY | other | PHILLIPS | NIAGARA MOHAWK POWER CORP |  | 450000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2359 | 2000-07-07 | IN | other | DUPONT | NORTHERN INDIANA PUBLIC SERVICE CO | SEE ATTACHED | 60000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2360 | 2000-07-17 | OK | ACCIDENTALLY CAUSED BY OPERATOR |  | OKLAHOMA NATURAL GAS CO | EMPLOYEE RECEIVED 2ND DEGREE BURNS WHEN GAS WAS IGNITED BY STATIC ELECTRICITY DURING PURGING OF PLASTIC PIPE FOLLOWING REPAIR OF A CUT LINE. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2361 | 2000-07-03 | MO | other | CBOMANU | MISSOURI GAS ENERGY | RILEY CONSTRUCTION COMPANY WAS WORKING WITH A TRACK HOE LOWERING AN EXISTING FIBER OPTIC CABLE. THEY WERE EXCAVATING IN CLOSE PROXIMITY TO TWO OF OUR GAS LINES (8 INCH STEEL 55 POUND SYSTEM AND 4 INCH PLASTIC 25 POUND SYSTEM). THEY HAD LOCATES AND THE L | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2362 | 2000-08-03 | AL | other | CBOMANU | ALABAMA GAS CORP (EX. MARENGO CORP PROPERTY) | THE CAUSE OF THE INCIDENT HAS NOT BEEN DETERMINED. A POST-INCIDENT INVESTIGATION REVEALED A LEAK IN THE 2 1/4 CAST IRON MAIN LOCATED 45 FEET FROM THE HOUSE. THE WALL THICKNESS OF THE UNDERGROUND MAIN IS .25 INCHES. ALABAMA GAS CORPORATION HOPES TO DETE | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2363 | 2000-08-15 | AK | other | DRISCOPIPE | ENSTAR NATURAL GAS CO | SEE ATTACHED SHEET | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2364 | 2000-07-27 | GA | other | DRISCOPIPE | LAWRENCEVILLE, CITY OF | DEVELOPER WAS CUTTING A ROAD INTO A SMALL SUBDIVISION. THE ROAD WAS FOLLOWING AN EXISTING DRIVEWAY WHICH HAD A 2" PE GAS SERVICE RUNNING ALONG THE EDGE. THE LINE HAD BEEN LOCATED AND SPOTTED BY POT HOLES. THE MOTOR GRADER OPERATOR GOT TO CLOSE THE LINE. G | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2365 | 2000-07-30 | OH | other |  | COLUMBIA GAS OF OHIO INC | AT APPROXIMATELY 0217 SUNDAY JULY 30, 2000 DAVE L. WORKMAN, AGE 33, 2143 ARROW RAOD, CARROLLTON, OH 44615 WAS SOUTHBOUND ON SR 43 AT THE SOUTH CARROLLTON VILLAGE CORPORATION LIMIT IN A 1989 FORD AREOSTAR. THE DRIVER LOST CONTROL ON A CURVE TO THE LEFT GOI | 150000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2366 | 2000-07-21 | VA | other | CBOMANU | RICHMOND DEPT OF PUBLIC UTILITIES, CITY OF | OLD 6" CAST IRON JOINT LEAKED OVER TIME FROM AGAING AND SOIL SUBSIDENCE. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2367 | 2000-08-02 | IA | technical failure | CBOMANU | MIDAMERICAN ENERGY COMPANY |  | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2368 | 2000-07-24 | MO | other | DRISCO | MISSOURI GAS ENERGY | CONSTRUCTION COMPANY DID BORING WORK PRIOR TO LINES BEING LOCATED. THEY HIT OUR GAS LINE AND A SEWER LINE ALLOWING GAS TO ENTER HOME THRU SEWER PIPE. | 40000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2369 | 2000-08-01 | KS | other | FISHER | GREELEY GAS CO | UNKNOWN VEHICLE STRUCK REGULATOR. CAUSING RELEASE OF HIGH PRESSURE GAS INTO BUILDING. THE GAS IGNITED AND CAUSED A SMALL FIRE. MOST DAMAGED WAS CAUSED BY FIRE DEPT. AND SPRINKLER SYSTEM. | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2370 | 2000-08-07 | MI | other | UNKNOWN | MICHIGAN CONSOLIDATED GAS CO (MICHCON) | DUE TO HOSPITALIZATION OF 2 PERSONS AND EXTENSIVE NEWS COVERAGE, THE INCIDENT WAS TELEPHONICALLY REPORTED. | 300000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2371 | 2000-08-08 | MI | other | UNKNOWN (WAYNE COUNTY) | MICHIGAN CONSOLIDATED GAS CO (MICHCON) | DUE TO TWO FATALITIES AND EXTENSIVE MEDIA COVERAGE, THE INCIDENT WAS TELEPHONICALLY REPORTED. | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2372 | 2000-08-08 | MO | ACCIDENTALLY CAUSED BY OPERATOR | UNKNOWN | MISSOURI GAS ENERGY | WHILE IN THE PROCESS OF CONDUCTING A SERVICE REPLACEMENT, CONTRACTOR WAS PREPARING ACTIVE SERVICE FOR RETIREMENT WHEN A SUDDEN RELEASE OF GAS OCCURRED RESULTING IN IMMEDIATE IGNITION WHICH CAUSED INJURIES TO TWO CONTRACT EMPLOYEES. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2373 | 2000-07-06 | PA | other |  | COLUMBIA GAS OF PENNSYLVANIA | THE RELEASE OF GAS WAS CAUSED BY A THIRD PARTY CONTRACTOR, ELLES BROTHERS, OPERATING A DRILLING RIG, WHILE CONSTRUCTING A RETAINING WALL NEAR COLUMBIA FACILITIES AT THE INTERSECTION OF TRANSPORT AND GLENBURY STREETS, PITTSBURGH, PENNSYLVANIA. | 96000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2374 | 2000-08-16 | AL | other |  | CHILDERSBURG GAS BOARD | A 4 INCH DIAMETER CAST IRON GAS MAIN WAS IGNITED BY TWO INDIVIDUALS ON THE RIGHT OF WAY OF US HWY 280. A DETAILED REPORT IS ATTACHED. | 500 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2375 | 2000-08-11 | WV | other |  | MOUNTAINEER GAS CO |  | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2376 | 2000-09-01 | LA | other |  | LOUISIANA GAS SERVICE CO | MOST PROBABLE SCENARIO FOR EXPLOSION EVENT- INTERIOR HOUSE PIPING CONNECTION WAS UNCAPPED LEADING TO AN UNDETERMINED AMOUNT OF NATURAL GAS WITHIN AN UNATTACHED POOL CABANA BUILDING NEXT TO THE MAIN PROPERTY. THE ESCAPING NATURAL GAS ON THE INTERIOR OF TH | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2377 | 2000-08-01 | TX | other |  | ENTEX, A NORAM ENERGY COMPANY (FORM. DIV OF ARKLA | AT THIS TIME IT IS BELIEVED THAT GAS FROM BELOW GROUND RISER LEAK ENTERED THE RESIDENCE @ 5811 LYDNHURST & WAS IGNITED BY SPARK CAUSING EXPLOSION AND FIRE. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2378 | 2000-08-02 | TX | technical failure |  | TXU GAS DISTRIBUTION | A METER WAS OVER PRESSURED WHILE BEING PLACED BACK IN SERVICE. THE METER CAME APART AND A PARK OF THE METER STRUCK THE TECHNICIAN IN THE SIDE. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2379 | 2000-08-11 | CA | other | UPNOR | PACIFIC GAS & ELECTRIC CO |  | 205000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2380 | 2000-08-17 | OH | other | CENTRAL (UNCONFIRMED) | HAMILTON GAS DEPT, CITY OF | SUSPICIOUS ORIGIN NOT RELATED TO CIVIL DISTURBANCE (IGNITION FACTOR 21). CIRCUMSTANCES OF EXPLOSION UNDER INVESTIGATION BY FIRE INVESTIGATOR. METER TAKEN FOR EVIDENCE. | 60000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2381 | 2000-08-16 | PA | other |  | COLUMBIA GAS OF PENNSYLVANIA | THE RELEASE OF NATURAL GAS APPEARS TO HAVE BEEN CAUSED BY ADDITIONAL EXTERNAL LOADING OVER A BURIED 12" STEEL GAS PIPELINE LOCATED WITHIN COLUMBIAS RIGHT OF WAY. COLUMBIA BELIEVES THIS LOADING CAUSED THE PIPELINE COUPLING FAILURE AND RELEASE OF GAS. REF | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2382 | 2000-08-25 | VA | other |  | WASHINGTON GAS LIGHT CO | THESE TWO BUILDINGS WERE UNDER CONSTRUCTION AT THE TIME OF THE FIRE. THE GAS METERS HAD NOT YET BEEN INSTALLED. DURING THE FIRE, DEBRIS FROM THE BURNING BUILDINGS FELL ON TOP OF ONE OF THE RISERS, DAMAGING THE STOPCOCK ON THE RISER AND ALLOWING SOME GAS | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2383 | 2000-09-05 | AZ | other | PHILLIPS | SOUTHWEST GAS CORP | SEE PART D | 105498 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2384 | 2000-09-16 | PA | other |  | COLUMBIA GAS OF PENNSYLVANIA | THE EMPLOYEE ENTERED THE EXCAVATION WITH A SHOVEL TO CLEAR ADDITIONAL MATERIAL FROM THE EXCAVATION. NO INDICATION/ODOR OF GAS AT THAT TIME, HOWEVER, UPON ENTRY, A FLASH FIRE OCCURRED, AND THE EMPLOYEE IMMEDIATELY EXITED THE EXCAVATION, WHILE ANOTHER EMPL | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2385 | 2000-08-24 | MS | other |  | MOSS POINT MUNICIPAL GAS SYSTEM, CITY OF | UNDETERMINED AT THIS TIME STILL UNDER INVESTIGATION. | 90000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2386 | 2000-09-16 | TX | other | UNKNOWN | SOUTHERN UNION GAS CO | A CAR, TRAVELING AT A HIGH RATE OF SPEED, STRUCK A VAN CAUSING THE DRIVER OF THE CAR TO LOSE CONTROL RESULTING IN CAR LEAVING THE ROADWAY. THE CAR THEN STRUCK NUMEROUS OBSTICLES INCLUDING A RESIDENTIAL GAS METER SET. THE GAS RISER TO THE METER SET WAS D | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2387 | 2000-10-14 | AK | other | DRISCOPIPE | ENSTAR NATURAL GAS CO | ON SUNDAY MORNING, OCTOBER 14, 2000, AT APPROXIMATELY 3:20 AM AST, ENSTAR NATURAL GAS COMPANY WAS NOTIFIED OF A MOBILE HOME FIRE AT 3751 W 74TH AVE ANCHORAGE, AK. AN ENSTAR SERVICEMAN AND DISTRIBUTION CREW WAS DISPATCHED TO THE SCENE. UPON ARRIVAL THEY | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2388 | 2000-09-28 | AL | other |  | MARSHALL COUNTY GAS DISTRICT |  | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2389 | 2000-10-02 | AL | other | PHILLIPS DRISCO PIPE | ALABAMA GAS CORP (EX. MARENGO CORP PROPERTY) | D&L CONSTRUCTION COMPANY, INCS BACKHOE OPERATOR EXCAVATED INTO ALABAMA GAS CORPS 4" PLASTIC MAIN WHILE WORKING TO INSTALL TELECOMMUNICATIONS CABLE. PIPELINE HAD BEEN ACCURATELY LOCATED AND MARKED BY AGCS THIRD PARTY LOCATING COMPANY | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2390 | 2000-09-13 | CA | other | UNKNOWN | SAN DIEGO GAS & ELECTRIC CO | TRUCK (WITHOUT DRIVER) ROLLED DOWN THE STREET INTO AN ATTACHED GARAGE AND CONNECTED GAS METER SET ASSEMBLY. THE GAS SERVICE LINE WAS BROKEN AT THE NIPPLE BETWEEN THE SHUT OFF VALVE AND THE REGULATOR. A FIRE OCCURRED RESULTING IN DAMAGE TO THE TRUCK AND | 51500 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2391 | 2000-10-04 | SD | other | PLEXCO | MIDAMERICAN ENERGY COMPANY |  | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2392 | 2000-09-29 | OH | technical failure | PHILLIPS DRISCO PIPE | EAST OHIO GAS CO | METER MANIFOLD WAS RELOCATED BECAUSE OF CONSTRUCTION MODIFICATION TO FRONT OF HOUSE. SERVICE LINE HAD GAS IN IT AND WAS STUBBED OFF WITH PERMASET FITTING. PLUMBER THEN CUT THROUGH SERVICE LINE WITHOUT CHECKING FOR GAS. GAS LEAKED OUT AND WAS IGNITED BY | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2393 | 2000-08-16 | TX | ACCIDENTALLY CAUSED BY OPERATOR | UPONOR | NAVASOTA, CITY OF | ON OR ABOUT 17:30 HOURS ON AUGUST 16, 2000, AN INCIDENT INVOLVING THE RELEASE AND SUBSEQUENT IGNITION OF NATURAL GAS OCCURRED AT THE SOUTHWEST CORNER OF INTERSTATE DRIVE AND STATE HIGHWAY 379 WHICH IS IMMEDIATELY SOUTH OF NAVASOTA, TEXAS. TWO CONTRACT WO | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2394 | 2000-09-11 | TX | technical failure | PHILLIPS | SAN ANTONIO, CITY PUBLIC SERVICE BOARD OF | WHILE CPS PERSONNEL WERE MAKING REPAIRS TO A 2" PLASTIC SERVICE, EMPLOYEE APPARENTLY STRUCK FLINT ROCK WITH A SHOVEL, RESULTING IN AN IGNITION. THE CPS EMPLOYEE RECEIVED 2ND DEGREE BURNS TO HIS FOREARM AND WAS TRANSPORTED TO UNIVERSITY HOSPITAL. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2395 | 2000-09-25 | CA | other | UPONOR | PACIFIC GAS & ELECTRIC CO | CONTRACTOR, HENNING BROTHERS, WAS DRILLING FOR A STREETLIGHT POLE BASE AND STRUCK A 2-IN PLASTIC GAS MAIN. GAS ESCAPED IGNITED, CAUSING FIRST AND SECOND DEGREE BURNS TO THE EQUIPMENT OPERATOR, AND SERIOUSLY DAMAGING THE DRILLING RIG. THE INJURED OPERATO | 45000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2396 | 2000-10-09 | PA | other |  | NATIONAL FUEL GAS DISTRIBUTION CORP | THIS WAS A NON-REPORTABLE INCIDENT. FAILURE WAS ON CUSTOMER HOUSELINE. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2397 | 2000-10-06 | KY | other | NATIONAL TUBE | UNION LIGHT HEAT & POWER CO | WATER ENTERED A 8" COATED STEEL GAS MAIN AND TRAVELED THROUGHOUT THE GAS SYSTEM. | 5000000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2398 | 2000-10-12 | IN | other | KEROTEST | INDIANA GAS CO INC | CAUSE OF INCIDENT APPEARS TO BE A GROUND FAULT PROBLEM WITH ELECTRIC WIRES OVERHEAD. THIS APPARENTLY CAUSED AN ELECTRIC SURGE TO GROUND TO THE PIPELINE WHICH IN TURN CAUSED FAILURE OF AN INSULATOR ALLOWING 335 PSIG TO ESCAPE TO ATMOSPHERE. IGNITION SOUR | 161700 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2399 | 2000-09-06 | NM | other |  | LAS VEGAS, CITY OF, HOUSING AUTH OF | 1" PVC SERVICE LINE MELTED AND RUPTURED, CAUSED BY STREET PERSONNEL USING A CUTTING TORCH TOO CLOSE TO THE SERVICE LINE. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2400 | 2000-10-05 | TX | other | PLEXCO | TXU GAS DISTRIBUTION | A TRENCHER CUT A 3 INCH POLY MAIN. GAS IGNITED AND THE TRENCHER BURNED. | 300000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2401 | 2000-10-24 | WY | other | DRISCO | CHEYENNE LIGHT FUEL & POWER | CONTRACTOR DAMAGED MAIN IN THE PROCESS OF INSTALLING FIBER OPTIC CABLE. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2402 | 2000-10-15 | OK | maintenance |  | WESTERN RESOURCES INC (AKA KPL CO. OR GAS SERVICE) | RECORDS ACQUIRED FROM FORMER OPERATORS DID NOT SHOW EXISTENCE OF THIS SHORT SECTION (40 FEET) OF 2-INCH BARE STEEL PIPE. | 35000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2403 | 2000-11-01 | AL | other | KEROTEST | ALABAMA GAS CORP (EX. MARENGO CORP PROPERTY) | SEE PART D | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2404 | 2000-10-21 | PA | other |  | PECO ENERGY CO | SEE PART D - OTHER | 300000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2405 | 2000-11-06 | AZ | other | MOONEY | SOUTHWEST GAS CORP | SEE PART D | 120000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2406 | 2000-10-26 | NV | other | KRALOY | SOUTHWEST GAS CORP | SEE PART D | 451884 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2407 | 2000-10-23 | VA | other | PLEXCO | COLUMBIA GAS OF VIRGINIA INC | A PLUMBING CONTRACTOR (CAPITAL PLUMBING AND AIR) FAILED TO NOTIFY THE ONE CALL NOTIFICATION CENTER (MISS UTILITY) OF THE INTENT TO EXCAVATE AND SUBSEQUENTLY STRUCK AND UNMARKED 2" MEDIUM PRESSURE PLASTIC MAIN. | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2408 | 2000-07-11 | NY | other |  | KEYSPAN ENERGY-WEST |  | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2409 | 2000-10-31 | CA | other |  | SOUTHERN CALIFORNIA GAS CO | CONTRACTOR PULLED SERVICE OFF OF 6" STEEL MAIN. FACILITY HAD BEEN PROPERLY LOCATED. REPORTED DUE TO LOSS OVER $50,000. LOSS DUE TO BUSINESS OUT OF GAS AND REPAIRS. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2410 | 2000-10-31 | AZ | other | PHILLIPS | SOUTHWEST GAS CORP | THE CAUSE OF THE LEAK IS UNDER INVESTIGATION BY A THIRD PARTY LABORATORY. A SUPPLEMENTAL REPORT WILL BE SUBMITTED BASED ON THE RESULTS OF THE LABORATORY TESTS. SUPPLEMENTAL REPORT: THE CAUSE OF THE LEAK STRESS-RUPTURE DUE TO EXCESSIVE COMPRESSION LOADING | 95000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2411 | 2000-10-26 | NY | other | CBOMANU | NIAGARA MOHAWK POWER CORP | AT 12:45PM ON OCTOBER 26, 2000 NIAGARA MOHAWK SYSTEM OPERATIONAL DISPATCH RECEIVED A CALL FROM THE ONONDAGA COUNTY 911 CENTER REQUESTING RESPONSE TO AN EXPLOSION AT 219 PRIMROSE AVENUE. THE FOLLOWING IS A SUMMARY OF THE RESPONSE TO THIS INCIDENT:12:46 SYS | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2412 | 2000-11-03 | NY | other | DRISCOPIPE | CONSOLIDATED EDISON CO OF NEW YORK | PRELIMINARY ANALYSIS INDICATED AN ELECTRIC BURNOUT SUBSEQUENTLY MELTED AND IGNITED 4" LOW-PRESSURE PLASTIC GAS MAIN EXPOSED IN AN OPEN CONTRACTORS EXCAVATION. CONTRACTOR ACTIVITY IN THE AREA PRIOR TO INCIDENT. THE NEW YORK CITY FIRE DEPARTMENT EVACUATED | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2413 | 2000-11-03 | IN | other | UNKNOWN (PORTER COUNTY) | NORTHERN INDIANA PUBLIC SERVICE CO | ON FRIDAY, NOVEMBER 3, 2000, AT APPROXIMATELY 7:15PM CST, A COMBUSTIBLE GAS MIXTURE BUILT UP AND IGNITED IN A HOUSE LOCATED AT 461 GROVE AVENUE IN VALPARAISO, INDIANA. THERE WERE NO OCCUPANTS IN THE HOUSE AT THE TIME OF THE EXPLOSION AND NO INJURIES RESUL | 300000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2414 | 2000-11-18 | AZ | ACCIDENTALLY CAUSED BY OPERATOR | UNKNOWN (MARICOPA COUNTY) | MESA MUNICIPAL SYSTEM, CITY OF | ABOUT 9:00 AM ON NOVEMBER 18, 2000, WHILE EXCAVATING FOR A DEVELOPMENT SERVICES PROJECT FOR THE CITY OF MESA, ARIZONA, ARCHON, INC., A GENERAL CONTRACTOR, DUG-IN TO AND SEVERED A FOUR (4") INCH HIGH PRESSURE (HP) NATURAL GAS MAIN. THE MAIN WAS OPERATING A | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2415 | 2000-11-02 | TX | other | NO DATA | ENTEX, A NORAM ENERGY COMPANY (FORM. DIV OF ARKLA | THIRD PARTY DAMAGED A 2" I.P. PLA. MAIN WITH A BORING TOOL. ESCAPING GAS ENTERED DAMAGED SEWER MAIN AND SUBSEQUENTLY ENTERED HOME WHERE AN EXPLOSION AND FIRE OCCURRED. | 200000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2416 | 2000-10-29 | TX |  | UNKNOWN (DENTON COUNTY) | TXU GAS DISTRIBUTION | A LEAK OCCURRED AT A SERVICE SADDLE. GAS MIGRATED UNDER THE STRUCTURE AND THE GAS IGNITED. THE CAUSE OF THE LEAK IS STILL UNDER INVESTIGATION AND A SUPPLEMENTAL REPORT WILL BE FILED ONCE AN ENGINEERING LABORATORY ANALYSIS OF THE PIPE IS COMPLETED. | 80000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2417 | 2000-11-16 | MN | other | PLEXCO | NORTHERN STATES POWER CO | POLYETHYLENE PLASTIC GAS MAIN WAS DAMAGED DURING THE CLEANING OF THE SANITARY SEWER SERVICE BY A THIRD PARTY FROM WITHIN THE HOUSE AT 1415 BERKELEY AVENUE. GAS ESCAPED INTO THE HOUSE, PRESUMABLY THROUGH THE SANITARY SEWER SERVICE, AND WAS IGNITED BY AN UN | 130000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2418 | 2000-12-07 | AK | other | DRISCOPIPE | ENSTAR NATURAL GAS CO | ON THRUSDAY EVENING, DECEMBER 7,2000, AT APPROXIMATELY 11:44 PM AST, ENSTAR NATURAL GAS COMPANY WAS NOTIFIED OF A STRUCTURE FIRE AT 7745 PALMER WASILLA HIGHWAY, WASILLA, AK. AN ENSTAR SERVICEMAN AND DISTRIBUTION PERSON WERE DISPATCHED TO THE SCENE. UPON A | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2419 | 2000-11-16 | CA | other | DRISCOPIPE | PACIFIC GAS & ELECTRIC CO | ESCAPING GAS FROM A LEAK AT A BUTT FUSION FAILURE MIGRATED INTO LOWER UNIT OF TWO-STORY DUPLEX. GAS WAS IGNITED AND EXPLOSION AND HOUSE FIRE RESULTED. NO REPORTS OF GAS ODOR WERE MADE PRIOR TO INCIDENT. HOWEVER, FIRE DEPARTMENT REPORTED STRONG GAS ODOR AF | 252000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2420 | 2000-11-27 | MN | ACCIDENTALLY CAUSED BY OPERATOR | UNKNOWN (AITKIN COUNTY) | NORTHERN MINNESOTA UTILITIES | NORTHERN PIPELINE CONSTRUCTION CO.(NPL), AN INDEPENDENT CONTRACTOR WORKING FOR NORTHERN MINNESOTA UTILITIES (NMU), DAMAGED 4" STEEL LINE THAT SERVES THE COMMUNITY OF AITKIN. THIS DAMAGE RESULTED IN LOSS OF SERVICE TO THE ENTIRE COMMUNITY OF 756 CUSTOMERS. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2421 | 2000-11-03 | RI | other | UNKNOWN (nan COUNTY) | PROVIDENCE GAS CO | PROVIDENCE GAS COMPANY IS FILING THIS FORM AT THE REQUEST OF MR. DON LEDVERSIS OF THE RHODE ISLAND DIVISION OF PUBLIC UTILITIES EVEN THOUGH IT BELIEVES THAT IT IS NOT NECESSARY OR APPROPRIATE FOR IT TO DO SO. ON FRIDAY, NOVEMBER 3, 2000 AT APPROXIMATELY 1 | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2422 | 2000-11-22 | OR | other | UNKNOWN (MULTNOMAH COUNTY) | NORTHWEST NATURAL GAS CO | AN INDIVIDUAL LOST CONTROL OF A VEHICLE, DRIVING INTO THE SIDE OF A BUILDING AND DAMAGING THE RISER. RELEASED GAS WAS IGNITED BY DOWN POWER LINES. BUILDING WAS ASSESSED AS A COMPLETE LOSS, DUE TO THE FIRE. | 125000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2423 | 2000-11-11 | TX | other | UNKNOWN (BEXAR COUNTY) | SAN ANTONIO, CITY PUBLIC SERVICE BOARD OF | 12-INCH STEEL MAIN WAS HIT BY ADB UTILITY (CONTRACTOR) BORING FOR FIBER OPTIC CABLE. | 53380 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2424 | 2000-11-28 | NJ | other | PLEXCO | PUBLIC SERVICE ELECTRIC & GAS CO | ON THE DAY IN QUESTION THE COMPANY RECEIVED A CALL FROM THE SOUTH BRUNSWICK POLICE DEPARTMENT REPORTING THAT WHILE CARUSO CONTRACTING CO., OF PO BOX 2043, OCEAN, NJ 07712 WAS EXCAVATING TO INSTALL WATER AND SEWER MAINS THEY STRUCK AND DAMAGED A 6" DIAMETE | 300000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2425 | 2000-01-18 | MA | other |  | FALL RIVER GAS CO |  | 41948 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2426 | 2000-11-29 | MA | other |  | KEYSPAN ENERGY DELIVERY | ON NOVEMBER 29, 2000 AT APPROXIMATELY 7:39 A.M., A PAVEMENT GRINDER OPERATED BY NOCELLA CONSTRUCTION AND OWNED BY FITZGERALD GRADING, INC., STRUCK A 16" INTERMEDIATE PRESSURE STEEL GAS LINE. THE MALDEN FIRE DEPARTMENT AND KEYSPAN EMPLOYEES RESPONDED IMMED | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2427 | 2000-11-24 | OH |  | CBOMANU | CINCINNATI GAS & ELECTRIC CO | A CRACK WAS FOUND IN A 4" CAST IRON MAIN RUNNING ADJACENT TO THE PROPERTY. | 85000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2428 | 2000-12-25 | AK | other | DRISCOPIPE | ENSTAR NATURAL GAS CO | ON CHRISTMAS DAY, MONDAY, DECEMBER 25, 2000, AT APPROXIMATELY 6:54 AM AST, ENSTAR NATURAL GAS COMPANY WAS NOTIFIED OF A STRUCTURE FIRE AT 15825 E. SHAWN DR., IN THE MATANUSKA SUSITNA BOROUGH (NEAR PALMER, AK). AN ENSTAR SERVICEMAN AND DISTRIBUTION PERSON | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2429 | 2000-10-18 | TX | other | UNKNOWN (WILLIAMSON COUNTY) | TXU GAS DISTRIBUTION | A THIRD PARTY CONTRACTOR CUT A SIX INCH POLY MAIN. GAS IGNITED WHEN A TXU GAS DISTRIBUTION TRUCK BACKFIRED NEAR THE BLOWING GAS LEAK. THE TRUCK WAS ALSO DESTROYED IN THE FIRE. | 160000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2430 | 2000-12-11 | MT | other | UNKNOWN (FLATHEAD COUNTY) | MONTANA POWER CO | PIPELINE EXPERIENCED A RAPID SEPARATION RESULTING FROM TENSILE STRESS FROM THERMAL CONTRACTION AT A STRESS RISER CAUSED BY PAST EXCAVATION (A SEWER LINE CROSSES DIRECTLY BELOW THE GAS LINE AT THE POINT OF FAILURE). | 60000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2431 | 2000-12-07 | IA | other | REPUBLIC, OR JONES & LAUGHLIN | I E S UTILITIES, INC. | 2-INCH STEEL MAIN FAILURE APPEARS TO BE DUE TO STRESS CRACKING. THE MAIN WAS LOCATED IN A GRAVEL ALLEY WAY THAT WAS USED BY SEMITRAILERS. THE PIPE APPEARED TO BE BENT DOWNWARD, WAS IN A SAND BACKFILL AREA,, WAS WRAPPED AND CATHODICALLY PROTECTED. AT TH | 1000000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2432 | 2000-12-16 | OH | other | CBOMANU | COLUMBIA GAS OF OHIO INC | CAUSE NOT YET DETERMINED. OBSERVED LEAKAGE AT THE RISER PORTION OF THE CUSTOMER OWNED SERVICE LINE AT THE SITE. THE CONDITION OF THE RISER WILL BE INVESTIGATED BY FURTHER EXAMINATION AND TESTING IN A LABORATORY SETTING. | 400000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2433 | 2000-12-16 | WI | other | FISHER | MADISON GAS & ELECTRIC CO | A FIRE OCCURRED INSIDE ON UNIT OF AN EIGHT-UNIT APARTMENT BUILDING. THE OUTSIDE GAS METER AND REGULATOR WERE COVERED WITH AN EXCESSIVE LAYER OF ICE. THE ICE FORMED AS A RESULT OF WATER THAT DRIPPED OFF THE BUILDING EAVES OVERHEAD. THE BUILDUP OF ICE OV | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2434 | 2000-12-20 | WY | other | PLEXCO | MONTANA - DAKOTA UTILITIES CO |  | 25000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2435 | 2000-12-22 | PA | other |  | PHILADELPHIA GAS WORKS |  | 1200000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2436 | 2000-12-19 | GA | other | AMERICAN | ATLANTA GAS LIGHT CO | WATER DRAINING FROM A ROOF FROZE ONTO THE SERVICE REGULATOR, CAUSING AN ICICLE TO FORM OVER THE VENT TO THE INTERNAL RELIEF OF THE REGULATOR. THE VACUUM CREATED BY THE STOPPED VENT CAUSED THE REGULATOR TO LOCK OPEN, EMITTING EXCESS GAS INTO THE RESIDENCE | 48500 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2437 | 2000-12-25 | CA | other |  | PACIFIC GAS & ELECTRIC CO | VEHICLE STRUCK GAS METER SET CAUSING STRUCTURE FIRE. | 52500 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2438 | 2001-01-06 | MS | other |  | MISSISSIPPI VALLEY GAS | 2" CAST IRON MAIN BROKE AT JOINT FITTING APPROXIMATELY 20 FEET IN FRONT OF HOUSE. MAIN BROKE AS RESULT OF EXTERNAL LOADING CAUSING BY SOIL SHIFTING. GAS APPEARED TO MIGRATE INTO CINDER BLOCK WALLS OF HOUSE ALONG FRACTURE IN SOIL OR SERVICE LINE UNDER FR | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2439 | 2000-12-21 | TX | other | UNKNOWN (HARRIS COUNTY) | ENTEX, A NORAM ENERGY COMPANY (FORM. DIV OF ARKLA | PIPE CRACKED FROM THIRD PARTY DAMAGE WHICH OCCURRED AT SOME UNKNOWN RIOR TIME. | 8000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2440 | 2001-01-05 | TX | other | UNKNOWN (HARRISON COUNTY) | RELIANT ENERGY FIELD SERVICES CORP | TRUCK HIT APARTMENT BUILDING AND METER LOOP. | 40000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2441 | 2001-01-06 | MI | other | TAYLOR MANUFACTURING | MICHIGAN CONSOLIDATED GAS CO (MICHCON) | NATURAL GAS BEING DRIED IN A DEHYDRATION LOOP WAS OVERHEATED. A 180 DEGREE STEEL FITTING FAILED AND THE THEN LEAKING FROM THE BURNER PILOT CAUSING DAMAGE. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2442 | 2000-12-17 | PA | other | UNKNOWN | PPL GAS UTILITIES CORP | APPARENT CAUSE OF ACCIDENT WAS THIRD PARTY DAMAGE. INVESTIGATION IS ONGOING. | 250000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2443 | 2000-11-06 | AR | other | UNKNOWN | ARKLA, A NORAM ENERGY COMPANY | THE HOME AT 223 ELBERTA APPEARS TO HAVE HAD AN ADDITION BUILT ON TO THE SIDE OF THE HOUSE. THE ORIGINAL, 1-INCH STEEL SERVICE LINE WOULD HAVE BEEN LOCATED UNDER THE NEW ADDITION. A 1.25-INCH PE 3406 PLASTIC SERVICE LINE WAS INSTALLED TO REROUTE THE SERVIC | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2444 | 2001-01-14 | IL | other |  | NORTHERN ILLINOIS GAS CO | OUTSIDE METER SET WAS DAMAGED FROM FALLING ICE. CUSTOMER WAS INVESTIGATING THE DAMAGES WHEN THE GAS IGNITED. (CAUSE UNKNOWN) CUSTOMER RECEIVED BURNS TO THE FACE AND HANDS TAKEN TO HOSPITAL. | 5000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2445 | 2000-11-25 | TX |  | NIPAK | TXU GAS DISTRIBUTION | A LEAK OCCURRED AT A REDUCER. GAS MIGRATED UNDER THE STRUCTURE AND IGNITED. THE CAUSE OF THE LEAK IS STILL UNDER INVESTIGATION AND A SUPPLEMENTAL REPORT WILL BE FILED ONCE AN ENGINEERING ANALYSIS IS COMPLETED. | 40000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2446 | 2001-01-03 | AR | other | UNKNOWN | ARKLA, A NORAM ENERGY COMPANY | 2 INCH STEEL PIPE DEVELOPED AN APPROXIMATE 60% PLUS TRANSVERSE CRACK FROM AN OUTSIDE FORCE. METALURGICAL EXAMINATION IS BEING PERFORMED THROUGH THE APSC TO DETERMINE FAILURE MODE. | 350000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2447 | 2001-01-16 | NM | other | UNKNOWN | PUBLIC SERVICE COMPANY OF NEW MEXICO - GAS SVCS | CABLE CONTRACTOR BORED INTO HIGH PRESSURE 16-INCH DISTRIBUTION LINE. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2448 | 2001-01-14 | NM | other |  | PUBLIC SERVICE COMPANY OF NEW MEXICO - GAS SVCS | VEHICLE CRASHED INTO BUILDING AND METER SET, BREAKING METER SET AT RISER. | 80000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2449 | 2001-01-09 | AL | technical failure |  | ALABAMA GAS CORP (EX. MARENGO CORP PROPERTY) | WHILE INSTALLING A MAIN BY DIRECTIONALLY BORING, A CONTRACTOR DAMAGED TWO WATER LINES AND A LOW PRESSURE CAST IRON GAS MAIN. WATER FILLED PORTIONS OF THE DISTRIBUTION SYSTEM THUS CAUSING THE LOSS OF SERVICE TO 209 HOUSES. | 83000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2450 | 2001-01-16 | TX | other | VARIOUS | ENTEX, A NORAM ENERGY COMPANY (FORM. DIV OF ARKLA | A STRUCRTURE FIRE CAUSED THE METER SET ASSEMBLY TO MELT THAT CAUSED GAS TO ESCAPE AND IGNITE. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2451 | 2001-01-12 | MO | other | UNKNOWN (ST FRANCOIS COUNTY) | LACLEDE GAS CO |  | 75000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2452 | 2001-02-02 | CA | other | NO DATA | SOUTHERN CALIFORNIA GAS CO | FARMER STRUCK TRANSMISSION LINE #8109 WHILE RIPPING FIELDS WITH BULLDOZER. | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2453 | 2001-01-29 | WV | maintenance | UNKNOWN (WOOD COUNTY) | HOPE GAS INC | A WATER BOARD EMPLOYEE ENTERED AN UNDERGROUND VAULT BELONGING TO THE PARKERSBURG WATER BOARD WITH THE INTENTION OF INSTALLING A DEHUMIDIFIER. THE EMPLOYEE PLUGGED THE DEHUMIDIFIER INTO AN ELECTRICAL OUTLET. AS THE SWITCH ON THE DEHUMIDIFIER WAS TURNED ON | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2454 | 2001-01-31 | CO | other | DRESSER | PUBLIC SERVICE CO OF COLORADO | CONTRACTORS EQUIPMENT SHAGGED 1" MW SERVICE PULLING PIPE OUT OF COMPRESSION COUPLING & CRACKING ELL. | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2455 | 2001-02-03 | WI | other | PLEXCO | WISCONSIN GAS CO |  | 185000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2456 | 2001-02-18 | MS | maintenance | UNKNOWN (HINDS COUNTY) | MISSISSIPPI VALLEY GAS | ABOVE GROUND CORROSION LEAK ON 1" SERVICE RISER IN VACANT LOT NEXT TO 1212 WOOD STREET.A 1" STEEL SERVICE LINE TO A VACANT LOT HAD A CORROSION LEAK ON A PORTION OF PIPE EXTENDING ABOVE GROUND LEVEL. AN EMERGENCY MEDICAL UNIT RESPONDED ON FEBRUARY 18, 2001 | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2457 | 2001-01-18 | MO | other | UNKNOWN | MISSOURI GAS ENERGY | HOMELESS PERSONS HAD BUILT A FIRE UNDER THE EXPOSED 12" PIPELINE NEAR A FLANGE UP UNDER A BRIDGE FOR HEAT DURING SEVERE COLD WEATHER. | 600000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2458 | 2001-02-06 | KS | other | UNKNOWN (WILSON COUNTY) | NEODESHA GAS DEPT, CITY OF | ON TUESDAY, FEBRUARY 6, 2001 AT 3:50 P.M., JERRY LOUR CALLED ON THE RADIO THAT THERE HAD BEEN AN EXPLOSION AT 1103 N. 6TH. DARRELL CLARK, BRENT WHEELER AND LEON REEDY ARRIVED ON SITE AT 4:00 P.M. LEON SHUT OFF THE GAS METER. DARRELL AND BRENT WENT INSIDE | 1200 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2459 | 2001-02-01 | CA | other | UNKNOWN (RIVERSIDE COUNTY) | SOUTHERN CALIFORNIA GAS CO | KENKO INC. STRUCK A 2" STEEL SERVICE LINE WHILE INSTALLING A SEWER LINE. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2460 | 2001-01-10 | MI | other | UNKNOWN (WAYNE COUNTY) | MICHIGAN CONSOLIDATED GAS CO (MICHCON) | BORING CONTRACTOR STRUCK GAS MAIN UNDER INTERSECTION. EXTENSIVE WORK REQUIRED TO CONTROL GAS LEAK AND REPAIR THE PIPELINE. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2461 | 2001-02-13 | PA | other | PLEXCO | PECO ENERGY CO |  | 200000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2462 | 2001-02-19 | CO | other | UPONOR | PUBLIC SERVICE CO OF COLORADO | THIRD PARTY EXCAVATING CONTRACTOR DIGGING WITH BACKHOE REMOVING FROST FOR DRIVEWAY CONCRETE POUR PUNCTURED 1.25" P.E. GAS MAIN. BLOWING GAS ENTERED STRUCTURE. GAS IGNITED FROM UNKNOWN SOURCE DAMAGING STRUCTURE. | 360000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2463 | 2001-02-26 | SD | other | UNIVERSAL CONTROLS | NORTHWESTERN PUBLIC SERVICE CO | A SNOW REMOVAL CONTRACTOR WAS REMOVING SNOW BEHIND THE BUILDING AT THE HURON VISION CENTER LOCATED AT THE ABOVE REFERENCED LOCATION. THE SNOW REMOVAL TOOK PLACE BETWEEN 10:00 & 10:30 PM ON THE EVENING OF FEBRUARY 25, 2001. AN EMPLOYEE OF THE CLINIC ARRIVE | 55000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2464 | 2001-02-20 | TX | ACCIDENTALLY CAUSED BY OPERATOR | UNKNOWN (HARRIS COUNTY) | ENTEX, A NORAM ENERGY COMPANY (FORM. DIV OF ARKLA | DURING A CUSTOMER METER INSPECTION AN EMPLOYEE CAUSED AN ACCIDENTIAL OVER PRESSURE OF A CUSTOMER HOUSELINE RESULTING IN A FIRE. | 35000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2465 | 2001-02-13 | MS | other | UNKNOWN (BOLIVAR COUNTY) | MISSISSIPPI VALLEY GAS | BROKEN 2" C.I. LINE NEXT DOOR (1008 NORTH YALE STREET) ALLOWED GAS TO MIGRATE INTO THE SEWER & RESIDENCE. | 90000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2466 | 2001-01-26 | CA | other | UNKNOWN | PACIFIC GAS & ELECTRIC CO | A LARGE DIAMETER SEWER LINE WAS INSTALLED PARALLEL AND TEN FEET AWAY FROM A 4-INCH GAS MAIN. IT IS LIKELY THAT THE CONTRACTOR STRUCK THE CROSSING 3/4 INCH GAS SERVICE. A LEAK DID NOT OCCUR IN THE SEWER TRENCH LINE. FORCES EXERTED ON THE GAS SERVICE LINE C | 102000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2467 | 2001-02-26 | TX | technical failure | UNKNOWN (GRAYSON COUNTY) | TXU GAS DISTRIBUTION | A CONTRACTOR WORKING FOR TXU REPLACING A GAS MAIN BORED INTO THE GAS MAIN AS WELL AS A WATER MAIN. WATER ENTERED THE LOW PRESSURE GAS SYSTEM FILLING THE GAS MAINS AND SERVICE WITH WATER. | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2468 | 2000-10-23 | MN | technical failure | PLEXCO | PEOPLES NATURAL GAS | GAS LEAKED FROM AN INCOMPLETE PIPE FUSION INTO THE HOUSE AT 1645 OAKBROOKE DRIVE. AN UNKNOWN SOURCE OF IGNITION, INSIDE THE HOUSE, CAUSED AN EXPLOSION INJURYING ONE PERSON AND DAMAGING THIS HOUSE AND TWO ADJACENT HOUSES. | 1000000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2469 | 2001-03-08 | TX | other | UNKNOWN (HOWARD COUNTY) | ENERGAS CO | THIRD PARTY HIT GAS LINE AND PULLED THE LINE APART AT A COUPLING 80 FT AWAY. SUBSEQUENTLY TO STOPPING GAS FLOW, A FLASH OCCURED IN THE BUILDING AT 804 N BELL. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2470 | 2001-02-23 | NJ | other | UNKNOWN (HUDSON COUNTY) | PUBLIC SERVICE ELECTRIC & GAS CO | ON FRIDAY, FEBRUARY 23, 2001, AT APPROXIMATELY 9:30 AM AN EMPLOYEE WAS DISPATCHED TO GAIL PLACE, SECAUCUS, TO PERFORM AN EMERGENCY MARKOUT FOR THE UNITED WATER COMPANY. THE EMPLOYEE OBTAINED FROM THE DISTRICT HEADQUARTERS THE INFORMATION AS TO THE SERVICE | 300000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2471 | 2001-03-01 | NC | other | PERFECTION | NORTH CAROLINA NATURAL GAS CORP | HOUSE FIRE. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2472 | 2001-03-15 | IA | other | UNKNOWN (POLK COUNTY) | MIDAMERICAN ENERGY COMPANY | CONTRACTOR INSTALLING COMMUNICATIONS CONDUIT MADE A DIRECTIONAL BORE. CONTRACTOR HAD REQUESTED AND RECEIVED LOCATES FOR THE GAS FACILITIES AND DRILLED A "LOCATE" HOLE TO FIND THE TOP OF THE 16" GAS LINE. CONTRACTOR INDICATED THEY HAD SUCCESSFULLY MADE THE | 52000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2473 | 2001-03-20 | OK | ACCIDENTALLY CAUSED BY OPERATOR | PLEXCO | OKLAHOMA NATURAL GAS CO |  | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2474 | 2001-03-25 | MO | other | PHILIPS | LACLEDE GAS CO | HOME OWNER PIERCED THE SERVICE WITH A FOREIGN OBJECT, POSSIBLY A 1/2 INCH BY 36 INCH PIECE OF STEEL REINFORCING BAR. THE NATURAL GAS MIGRATED INTO THE RESIDENCE AND WAS IGNITED BY AN UNKNOWN SOURCE. | 350000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2475 | 2001-03-29 | OH | other | UPONOR | VECTREN ENERGY DELIVERY OF OHIO | CONTRACTOR (FOUSS CONSTRUCTION) DUG-IN TO A MEDIUM PRESSURE PLASTIC DISTRIBUTION LINE RESULTING IN A FIRE, INJURING THE TRENCHER OPERATOR. THE LOCATING CONTRACTOR (RELIANT SERVICES) PERFORMED AN INCOMPLETE LOCATE OF ALL MAIN IN THE AREA. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2476 | 2001-04-06 | LA | other | UPNOR | GULF STATES UTILITIES CO |  | 150000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2477 | 2001-04-04 | TX | other |  | TXU GAS DISTRIBUTION | A THIRD PARTY CONTRACTOR USING AN AUGER TRUCK CUT A GAS MAIN. THE AUGER TRUCK CAUGHT FIRE. | 250000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2478 | 2001-04-25 | NM | maintenance | UNKNOWN | PUBLIC SERVICE COMPANY OF NEW MEXICO - GAS SVCS | AT APPROXIMATELY 2:15 PM ON APRIL 25, 2001 THE NORTHERN INSURANCE COMPANY BUILDING LOCATED AT 851 CERRILLOS ROAD IN SANTA FE, NEW MEXICO EXPLODED. TWO WOMEN WERE INJURED IN THE INCIDENT AND WERE HOSPITALIZED. (A) ESTIMATED PRESSURE AT POINT AND TIME OF IN | 180000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2479 | 2001-05-04 | NM | other | SPRAQUE | DEMING GAS SYSTEM | VEHICLE RAN OVER GAS METER, ESCAPING GAS IGNITED. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2480 | 2001-05-01 | PA |  | UNKNOWN (MCKEAN COUNTY) | GASCO DISTRIBUTION SYSTEMS, INC. | THE FIRE MARSHALL SAID THAT A FAULTY HOT WATER HEATER OVERHEATED, WHICH WAS THE CAUSE OF THE FIRE. THE FIRE MARSHALL SAID THERE WAS A SMALL LEAK AT THE WATER HEATER, WHERE THE FLEX CONNECTOR SCREWED INTO THE WATER HEATER CONTROL VALVE. THE FIRE MARSHALL S | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2481 | 2001-01-01 | MN | other | CBOMANU | MINNEGASCO INC |  | 1000000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2482 | 2001-03-14 | AZ | other | UNKNOWN (PINAL COUNTY) | MESA MUNICIPAL SYSTEM, CITY OF | FARMER HIT THE 4" GAS MAIN WHILE PLOWING HIS FIELD TO PLANT CROPS. CITY OF MESA LINE MARKERS WERE IN PLACE | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2483 | 2001-04-24 | MN | other | UNKNOWN (RICE COUNTY) | NORTHERN STATES POWER CO | THE SUSPECTED SOURCE OF THE GAS THAT CAUSED THE EXPLOSION IS A LEAK ON THE CUSTOMER OWNED GAS PIPING INSIDE THE HOUSE AT 605 CARTER DRIVE. THE HOUSE FIRE THAT FOLLOWED THE EXPLOSION MELTED THE SERVICE REGULATOR AND THE GAS METER. THE FIRE ALSO DAMAGED THE | 250000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2484 | 2001-05-02 | NC | other | DRISCOPIPE | PUBLIC SERVICE CO OF NORTH CAROLINA | THIRD PARTY, CABLEVISION, IN PROCESS OF REPAIRING CABLE EXPOSED 3/4" PLASTIC SERVICE LINE. CABLEVISION REPAIRMAN MELTED PLASTIC SERVICE WITH A TORCH WHILE INSTALLING HEAT SHRINK SLEEVE ON CABLE SPLICE. REPAIRMAN WAS BURNED WHEN GAS IGNITED & WAS TAKEN TO | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2485 | 2001-04-25 | TX | other | CBOMANU | ENTEX, A NORAM ENERGY COMPANY (FORM. DIV OF ARKLA | VEHICLE STRUCK GAS METER. IGNITION OCCURRED. | 115000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2486 | 2001-04-25 | OH | other | UPONOR | COLUMBIA GAS OF OHIO INC | THIRD PARTY CONTRACTOR ERRONEOUSLY STRUCK AND INITIALLY DAMAGED A "6 PLASTIC MEDIUM DENSITY PIPELINE OPERATING AT APPROXIMATELY 42 PSIG. COLUMBIA GAS OF OHIO, INC EMPLOYEES WERE ATTEMPTING TO MAKE REPAIRS ON DAMAGED LINE, WHEN UNKNOWN IGNITION SOURCE IGNI | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2487 | 2001-05-02 | TX | other | UNK | ENTEX, A NORAM ENERGY COMPANY (FORM. DIV OF ARKLA | THIRD PARTY DAMAGED A .75 INCH IP PLA. SERVICE LINE WITH A BORING TOOL AND ESCAPING GAS WAS IGNITED. | 200000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2488 | 2001-05-19 | TX | other | DUPONT | ENTEX, A NORAM ENERGY COMPANY (FORM. DIV OF ARKLA | CONTRACTOR DAMAGED A 2" POLYETHYLENE GAS MAIN WHILE TRENCHING. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2489 | 2001-05-09 | CA | other | UNKNOWN (LOS ANGELES COUNTY) | SOUTHERN CALIFORNIA GAS CO | DURING PLANNED BLOWDOWN TO TRANSMISSION LINE, ODORANT WAS SMELLED AT JR HIGH SCHOOL APPOXIMATE 11/2 AWAY. SCHOOL WAS EVACUATED, 9 STUDENTS AND 1 ADULT WERE TRANSPORTED TO HOSPITAL WITH NAUSEA AND DIZZINESS. ALL TREATED AND RELEASED. SCHOOL RE-OPENED. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2490 | 2001-05-19 | TX | other | UNKNOWN (TRAVIS COUNTY) | SOUTHERN UNION GAS CO | UNOCCUPIED VEHICLE ROLLED DOWN HILL, OVER A CURB AND THROUGH RESIDENTIAL CARPORT STRIKING A RESIDENTIAL GAS METER SET AT THE STRUCTURE CAUSING LEAKAGE WHICH RESULTED IN A RESPONSE BY THE LOCAL FIRE DEPARTMENT. WHILE FIREFIGHTERS WERE ATTEMPTING TO SHUT OF | 75000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2491 | 2001-06-04 | MN | technical failure | PLEXCO | BAGLEY NATURAL GAS, CITY OF | 2" BRANCH OFF OF A 4" MAIN. THE 4" MAIN WAS LOCATED, BUT THE 2" MAIN WAS NOT. | 3000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2492 | 2001-05-19 | TX | other | UNK | ENTEX, A NORAM ENERGY COMPANY (FORM. DIV OF ARKLA | AN EMPTY WAREHOUSE ON FIRE, WALL COLLAPSED ON VACANT RISER AND ESCAPING GAS WAS IGNITED. | 1500000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2493 | 2001-05-25 | OK | other |  | OKLAHOMA NATURAL GAS CO | THIRD PARTY CONTRACTOR HIT A 12" MP MAIN IN THE NORTH CANADIAN RIVER. | 125000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2494 | 2001-06-04 | PA | other |  | COLUMBIA GAS OF PENNSYLVANIA | CONTRACTOR WAS MAKING REPAIRS TO NEWLY INSTALLED SEWER SYSTEM WHEN THEY HIT A MEDIUM PRESSURE TAP ON A 2" STEEL MAIN. GAS ENTERED HOME AT BOX 307 FRONT STREET AND IS THOUGHT TO HAVE IGNITED AT A SPACE HEATER IN THE BASEMENT. ELDERLY RESIDENT WAS ASSISTE | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2495 | 2001-05-21 | CO | other |  | KINDER MORGAN ENERGY PARTNERS, L.P. | THE CONTRACTOR HAS BEEN WORKING FOR OVER A YEAR IN THE AREA., PARALLELING THE PIPELINE, CONSTRUCTING A NEW HIGHWAY. THE CONTRACTOR CALLED IN TO REQUEST A LOCATE, AND A LOCATE WAS PROVIDED. A POTHOLE, WHICH WAS NOT DUG DEEP ENOUGH BY THIS CONTRACTOR, DI | 80000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2496 | 2001-05-30 | NM | ACCIDENTALLY CAUSED BY OPERATOR | UNKNOWN | PUBLIC SERVICE COMPANY OF NEW MEXICO - GAS SVCS | ON MAY 30, 2001 A CREW FROM J & D CONTRUCTION WAS RETIRING A SERVICE LINE LOCATED AT 1034 HICKOX STREET IN SANTA FE, NEW MEXICO. AT APPROXIMATELY 2:00 PM A PNM EMPLOYEE AND TWO CONTRACTOR EMPLOYEES FROM J & D CONTRUCTION WERE BURNED. THE SERVICE LINE THEY | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2497 | 2001-06-04 | TX | other | UNK. | ENTEX, A NORAM ENERGY COMPANY (FORM. DIV OF ARKLA | THIRD PARTY DAMAGED A 1 1/4" H.P. STL. SERVICELINE WITH A TRACKHOE WHILE INSTALLING SANITARY SEWER LINES. | 7500 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2498 | 2001-06-03 | MA | other | FISHER | BERKSHIRE GAS CO | THE FOLLOWING PRESENTS INFORMATION RELATED TO THE RECENT INCIDENT EXPERIENCE BY THE BERKSHIRE GAS COMPANY ("BERKSHIRE") WITH REGARDS TO THE OVER-PRESSURIZATION OF ITS PITTSFIELD LOW PRESSURE DISTRIBUTION SYSTEM ON SUNDAY, JUNE 3, 2001. BASED ON BERKSHIRES | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2499 | 2001-06-07 | NV | other | CHEVRON PHILLIPS CHEMICAL CO | SOUTHWEST GAS CORP | WHILE AN OPERATOR FOR R.P. WEDDELL & SONS WAS TRENCHING FOR SEWER IMPROVEMENTS, HE STRUCK AND DAMAGED A 4" P.E. GAS MAIN. THE CONTRACTOR HAD A CURRENT USA ONE-CALL TICKET, BUT THE LOCATE WAS INCORRECT. THE INCIDENT RESULTED IN 2,568 THERMS OF LOST GAS AND | 489169 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2500 | 2001-06-04 | TX | other | UNKNOWN (HARRIS COUNTY) | ENTEX, A NORAM ENERGY COMPANY (FORM. DIV OF ARKLA | A CARPORT STRUCTURE COLLAPSED DUE TO FIRE, DAMAGING METER SET ASSEMBLY AND ESCAPING GAS WAS IGNITED. | 60000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2501 | 2001-05-29 | MO | other | KAISER STEEL CO. | LACLEDE GAS CO | WHILE ATTEMPTING TO MOVE AND SCOOP EARTH FROM OVER THE STEEL GAS PIPELINE WHICH WAS MARKED FOR ANOTHER CONTRACTOR, THE DAMAGING CONTRACTOR STRUCK THE MAIN WITH A BUCKET TOOTH FROM A HI-LIFT DOZER (CAT963C). NO ATTEMPT WAS MADE BY THE CONTRACTOR TO EXPOSE | 49000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2502 | 2001-06-25 | WY | other | CBOMANU | FRANNIE - DEAVER UTILITIES | HIGH WINDS CAUSED A LIMB TO FALL SOME 20 TO 30 FEET AND STRUCK THE SPRING HOUSING OF THE GAS REGULATOR AND SHEARED IT OFF. THE REGULATOR FAILED IN THE OPEN POSITION AND GAS ENTERED THE HOUSE THROUGH THE GAS PIPING. THE PILOT LIGHT WAS SNUFFED OUT WHEN THE | 40000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2503 | 2001-06-15 | TX | other | UNK | ENTEX, A NORAM ENERGY COMPANY (FORM. DIV OF ARKLA | THIRD PARTY DAMAGED A 4" I.P./ STEEL RELIEF VALVE STACK WITH HIS TRUCK. | 58000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2504 | 2001-06-21 | FL | ACCIDENTALLY CAUSED BY OPERATOR | UNK | DEFUNIAK SPRINGS NATURAL GAS SYSTEM, CITY OF | THE INCIDENT OCCURRED DURING THE SECOND CUT TO REMOVE A ONE FOOT SECTION OF AN EXISTING 3/4" GALVANIZED GAS SERVICE LINE. THE BELL HOLE HAD BEEN EVACUATED AND THE GAS LINE TAP HAD BEEN CLOSED AND JUMPER CABLES HAD BEEN INSTALLED SPANNING THE AERA TO BE CU | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2505 | 2001-06-18 | VA | other | CBOMANU | RICHMOND DEPT OF PUBLIC UTILITIES, CITY OF | VACATED HOUSE (BOARDED UP) VANDALIZED BY REMOVING APPROXIMATELY 20 FEET OF 1 1/4" COPPER SERVICE LINE CAUSING GAS RELEASE IN CRAWL SPACE. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2506 | 2001-07-04 | AZ | other | DUPONT | SOUTHWEST GAS CORP | SOUTHWEST GAS WAS NOTIFIED OF A FIRE AT 2938 E. PRESIDIO ROAD AT 2332 HOURS ON JULY 4, 2001. ONCE THE FIRE WAS EXTINGUISHED, NATURAL GAS LEAKAGE WAS DETECTED. THE LEAKING GAS WAS SHUT DOWN AT 0131 HOURS ON JULY 5 BY SQUEEZING THE SERVICE AT THE PROPERTY L | 85000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2507 | 2001-06-22 | IL | ACCIDENTALLY CAUSED BY OPERATOR | UNKNOWN (KNOX COUNTY) | ILLINOIS POWER CO | ON JUNE 22, 2001, A TWO-MAN GAS CREW WAS REPLACING THE RISER AT 1135 GRAND AVENUE IN GALESBURG, ILLINOIS. THIS WORK WAS BEING DONE DUE TO A COMPRESSION FITTING FOUND BELOW GROUND AT THE RISER. THE SERVICE HAD BEEN EXPOSED BETWEEN 1131 AND 1135 GRAND AVENU | 65000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2508 | 2001-06-27 | GA | other |  | ATLANTA GAS LIGHT CO | DRIVER OF A PASSENGER VEHICLE LOST CONTROL, JUMPED A CURB AND STRUCK GAS METER SET. THIS CAUSED THE 1 1/4" NIPPLE TO CRACK BELOW THE PRIMARY REGULATOR. THE ESCAPING GAS IGNITED CAUSING DAMAGE TO AUTOMOBILE AND THREE BUSINESSES. THE DRIVER OF THE VEHICL | 200000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2509 | 2001-07-07 | IL | other |  | NORTH SHORE GAS CO | LIGHTNING STREAK THE ROOF OF A HOME AND CAUSED A FIRE THAT DAMAGED NORTH SHORES METER SET. | 500000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2510 | 2001-07-09 | PA | other | UNKNOWN (ALLEGHENY COUNTY) | COLUMBIA GAS OF PENNSYLVANIA | INITIAL INVESTIGATION SHOWED METHANE ACCUMULATION IN A WATER WELL LOCATED IN THE BASEMENT. IGNITION OCCURED WHEN PUMP RELAY ENERGIZED CAUSING AN EXPLOSION. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2511 | 2001-07-12 | TX | other |  | ENTEX, A NORAM ENERGY COMPANY (FORM. DIV OF ARKLA | GARAGE FIRE SPREAD TO HOUSE AND HEAT MELTED INSULATING BUSHING ON METER SET ASSEMBLY AND ESCAPING GAS WAS IGNITED. | 70000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2512 | 2001-07-30 | AR | other | DUPONT | ARKANSAS OKLAHOMA GAS CORP | OPERATORS 2" PLASTIC MAIN STRUCK BY TV CABLE CREW. MAIN HAD BEEN PROPERLY MARKED IN ADVANCE. GAS WAS IGNITED AT SITE OF BREAK BY UNKNOWN CAUSE RESULTING IN OVERNIGHT HOSPITALIZATION OF ONE OF OPERATORS EMPLOYEES | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2513 | 2001-07-21 | MT | other | UNKNOWN | MONTANA POWER CO | PIPELINE EXPERIENCED A SHEARING STRESS FROM EARTH MOVEMENT WHICH RESULTING FROM OUTSIDE CONTRACTOR EXCAVATION TAKING PLACE NEXT TO GAS MAIN. | 70000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2514 | 2001-08-15 | AR | other | UPONOR-ALDYL | ARKANSAS WESTERN GAS CO | PRIVATE CONTRACTOR WAS EXPOSING 2" PLASTIC GAS MAIN WITH BACKHOE AND STRUCK TOP OF MAIN CAUSING A RELEASE OF GAS. COMPANY CREW RESPONSED TO MAKE REPAIRS ON MAIN (HAD TWO-WAY FEED). ONE SIDE WAS SQUEEZED OFF - SECOND SIDE IGNITED AT SQUEEZE OFF ATTEMPT B | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2515 | 2001-08-16 | TX | other | VARIOUS | ENTEX, A NORAM ENERGY COMPANY (FORM. DIV OF ARKLA | A FIRE WHICH ORIGINATED INSIDE A GARAGE SPREAD TO AND DAMAGED A METER SET ASSEMBLY. THE ESCAPING GAS WAS IGNITED. | 70000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2516 | 2001-07-24 | MI | other | UNKNOWN (KENT COUNTY) | MICHIGAN CONSOLIDATED GAS CO (MICHCON) | EXCAVATING CONTRACTOR DAMAGED VAULT AND FALLING CONCRETE BROKE FITTING FOR PRESSURE TEST VALVE. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2517 | 2001-08-02 | PA | maintenance |  | NATIONAL FUEL GAS DISTRIBUTION CORP | NATURAL GAS, LEAKING FROM A CORROSION PIT FAILURE IN A 10" GAS MAIN, MIGRATED INTO THE BASEMENT OF A RESIDENTIAL HOME. IGNITION OF THE SUBSEQUENT NATURAL GAS BUILDUP RESULTED IN A EXPLOSION AND FIRE. | 160000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2518 | 2001-08-18 | MN | other |  | MINNEGASCO INC | CRACK IN 1 1/4" AA PLASTIC MAIN FOUND IN FRONT OF RESIDENCE. CAUSE OF EXPLOSION STILL UNDER INVESTIGATION. | 400000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2519 | 2001-08-16 | TX | other | UPONOR | ARKLA, A NORAM ENERGY COMPANY | BRICK WALL OF COMMERICAL BUILDING FELL ON METER SET ASSEMBLY BREAKING RISER AT GROUND IGNITING GAS. ORIGIN OF FIRE UNRELATED TO NATURAL GAS. | 300 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2520 | 2001-08-20 | AK | other | UNKNOWN (nan COUNTY) | ENSTAR NATURAL GAS CO | ON MONDAY EVENING, AUGUST 20, 2001, AT 9:00 PM ADT, ENSTAR NATURAL GAS COMPANY WAS NOTIFIED BY A CUSTOMER OF A GAS MAIN BLOWING AT THE CORNER OF E STREET AND THE ALLEY BETWEEN 10TH AND 11TH STREETS, IN ANCHORAGE, ALASKA. AN ENSTAR SERVICE TECHNICIAN WAS D | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2521 | 2001-09-10 | AK | other | DRISCOPIPE | ENSTAR NATURAL GAS CO | ON MONDAY MORNING, SEPTEMBER 13, 2001, AT APPROXIMATELY 2:15 AM AST, ENSTAR NATURAL GAS COMPANY WAS NOTIFIED BY THE MATANUSKA VALLEY FIRE DEPARTMENT OF A FIRE AT 3830 N GREENTREE ST NORTHEAST OF WASILLA, ALASKA. AN ENSTAR SERVICEMAN WAS DISPATCHED TO THE | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2522 | 2001-08-30 | AZ | other | MUELLER | SOUTHWEST GAS CORP | SEE PART D | 269000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2523 | 2001-08-25 | NC | other | UNKNOWN (WAKE COUNTY) | PUBLIC SERVICE CO OF NORTH CAROLINA | HOME OWNER HIT GAS METER WITH RIDING MOWER. | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2524 | 2001-08-17 | TX | other | UNKNOWN (MORRIS COUNTY) | RELIANT ENERGY FIELD SERVICES CORP | LIGHTNING STRUCK TREE AND TRAVELED THROUGH ROOTS TO BURN HOLE IN GAS SERVICE LINE. | 500 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2525 | 2001-08-29 | IL | other | UNKNOWN (WINNEBAGO COUNTY) | NORTHERN ILLINOIS GAS CO | LAWN MOWER HIT FARM TAP (1ST STAGE REGULATOR). 1" HIGH-PRESSURE VALVE WAS BROKEN OFF THE RISER. NATURAL GAS IGNITED AND COUNTY WORKER WAS BURNED OVER 20% OF BODY. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2526 | 2001-09-06 | NY | other |  | KEYSPAN ENERGY CORP |  | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2527 | 2001-09-08 | VA | other | AMERICAN METER | WASHINGTON GAS LIGHT CO | WG METER AND REGULATOR ASSEMBLY WERE DAMAGED AND NATURAL GAS WAS RELEASED FOLLOWING AN EXPLOSION AND FIRE IN THIS HOUSE. SOURCE OF FIRE IS BELIEVED TO BE THE WATER HEATER. | 200000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2528 | 2001-09-30 | GA | other | UNKNOWN | ATLANTA GAS LIGHT CO | MARIETTA POWER TECHNICIAN WAS INSTALLING A SHRINK SLEEVE TO POWER CABLE LOCATED UNDERNEATH 5/8" PLASTIC GAS SERVICE LINE. APPARENTLY, THE HEAT FROM THE TORCH BEING USED BY THE TECHNICIAN TO INSTALL THE SLEEVE MELTED THE 5/8" PLASTIC GAS LINE, RESULTING IN | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2529 | 2001-09-06 | TX | other | UNKNOWN (KAUFMAN COUNTY) | TXU GAS DISTRIBUTION | A THIRD PARTY BORING CONTRACTOR BORED IN TO A GAS MAIN AS WELL AS A SEWER MAIN. THE HIGHER PRESSURE GAS ENTERED THE SEWER MAIN CAUSING DAMAGE WITHIN A HOUSE. | 10000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2530 | 2001-09-25 | CO | technical failure | UPONOR | COLORADO SPRINGS, CITY OF | CONTRACTOR EMPLOYEES WERE PERFORMING A PURGE ON A NEW TWO-INCH POLYETHYLENE GAS MAIN. THE EMPLOYEES PLACED A SQUEEZE TOOL ON THE LINE TO CONTROL THE FLOW OF PURGE GAS, BELIEVING THAT THE SQUEEZE TOOL SUFFICIENTLY COMPRESSED THE PIPE TO PREVENT ANY GAS FLO | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2531 | 2001-10-21 | VA | other | UNKNOWN | RICHMOND DEPT OF PUBLIC UTILITIES, CITY OF | UNKNOWN AT THIS TIME/INVESTIGATION CONTINUES | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2532 | 2001-10-02 | PA | other | UNKNOWN (PHILADELPHIA COUNTY) | PHILADELPHIA GAS WORKS | THE PHILADELPHIA FIRE DEPARTMENT AND PHILADELPHIA GAS WORKS HAVE INVESTIGATED THIS INCIDENT. TO DATE THE FIRE MARSHALLS OFFICE HAS NOT RELEASED ITS FINDINGS. PGW HAS CONCLUDED ITS INVESTIGATION AND HAS DETERMINED THAT NATURAL GAS WAS A FUEL IN THIS FIRE A | 75000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2533 | 2001-10-05 | AZ | other | NORDSTROM | SOUTHWEST GAS CORP | ON OCTOBER 5, 2001 AT 2324 HOURS AN ALARM WAS RECEIVED FROM A REMOTE PRESSURE MONITORING DEVICE, INDICATING AN OVERPRESSURE CONDITION ON THE DISTRIBUTION SYSTEM FED FROM REGULATOR STATION #575. UPON VERIFICATION OF THE ALARM AT 2326 HOURS, FIELD PERSONNEL | 8750 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2534 | 2001-10-06 | AZ | other | AMERICAN METER | SOUTHWEST GAS CORP | ON OCTOBER 6, 2001 AT 0831 HOURS WE BEGAN RECEIVING TELEPHONE CALLS FROM CUSTOMER REPORTING INOPERABLE APPLIANCES. AT 1005 HOURS IT WAS DETERMINED THAT THE REGULATOR STATION SERVING THE DISTRIBUTION SYSTEM IN THE VICINITY OF SPEEDWAY BLVD. AND HOUGHTON RD | 8750 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2535 | 2001-10-06 | AZ | other | NORDSTROM | SOUTHWEST GAS CORP | ON OCTOBER 6, 2001 AT 1650 HOURS A SPECIAL REGULATOR STATION INSPECTION IDENTIFIED 72 PSIG ON THE OUTLET OF THE STATION. THE LOCK FOR THE ABOVE GROUD BYPASS VALVE HAD BEEN REMOVED AND THE VALVE HAD BEEN PARTIALLY OPENED, RESULTING IN AN OVERPRESSURE CONDI | 8750 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2536 | 2001-10-07 | AZ | other | FISHER | SOUTHWEST GAS CORP | ON OCTOBER 7, 2001 AT 1409 HOURS A SPECIAL REGULATOR STATION INSPECTION IDENTIFIED 70 PSIG ON THE OUTLET OF THE STATION. THE ADJUSTMENT SCREWS FOR THE WORKER AND MONITOR REGULATORS HAD BEEN TAMPERED WITH, RESULTING IN AN OVERPRESSURE CONDITION. THE DISTRI | 8750 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2537 | 2001-10-07 | AZ | other | AMERICAN METER | SOUTHWEST GAS CORP | ON OCTOBER 7, 2001 AT 1524 HOURS A SPECIAL REGULATOR STATION INSPECTION IDENTIFIED THAT THE REGULATOR STATION HAD BEEN TAMPERED WITH. THE LOCK SECURING THE GATE FOR THE FENCED ENCLOSURE HAD BEEN REMOVED AND THE ADJUSTMENT SCREWS FOR THE WORKER AND MONITOR | 8750 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2538 | 2001-10-08 | AZ | other | FISHER | SOUTHWEST GAS CORP | ON OCTOBER 8, 2001 AT 1025 HOURS A SPECIAL REGULATOR STATION INSPECTION IDENTIFIED 73 PSIG ON THE OUTLET OF THE STATION. THE ADJUSTMENT SCREWS ON THE WORKER AND MONITOR REGULATORS HAD BEEN TAMPERED WITH RESULTING IN AN OVERPRESSURE CONDITION. THE DISTRIB | 8750 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2539 | 2001-10-08 | AZ | other | NORDSTROM | SOUTHWEST GAS CORP | ON OCTOBER 8, 2001 AT 1400 HOURS A SPECIAL REGULATOR STATION INSPECTION IDENTIFIED THAT THE REGULATOR STATION HAD BEEN TAMPERED WITH. THE LOCK SECURING THE GATE FOR THE FENCED ENCLOSURE HAD BEEN REMOVED AND THE ABOVE GROUND INLET VALVE TURNED OFF. ALTHOUG | 70000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2540 | 2001-10-12 | AZ | other | NORDSTROM | SOUTHWEST GAS CORP | ON OCTOBER 12, 2001 AT 1040 HOURS A SPECIAL REGULATOR STATION INSPECTION IDENTIFIED THAT THE REGULLATOR STATION HAD BEEN TAMPERED WITH. THE ABOVE GROUND INLET VALVE WAS TURNED OFF AND THE ADJUSTMENT SCREW ON THE MONITOR REGULATOR HAD BEEN TAMPERED WITH. A | 8750 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2541 | 2001-10-30 | AL | other |  | FULTONDALE GAS BOARD | ON OCTOBER 30, 2001, SOUTHEASTERN CONSTRUCTION (PHONE NUMBER 865-470-7777), ADDRESS: 8605 AMBLECOTE ROAD, KNOXVILLE, TENNESSEE 37923) WAS CLEARING RIGHT-OF-WAY FOR ALABAMA POWER ON COALBURG ROAD, JEFFERSON COUNTY, ALABAMA. THEY WERE CLEARING RIGHT-OF-WAY | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2542 | 2001-11-03 | AZ | other |  | SOUTHWEST GAS CORP |  | 150000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2543 | 2001-11-20 | CT | other |  | CONNECTICUT NATURAL GAS CORP | VEHICLE CAUGHT ON FIRE IN GARAGE, SET OTHER VEHICLES ON FIRE, SPREAD TO GARAGE STRUCTURE AND ADJACENT CONDOMINUMS AND GARAGE. | 750000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2544 | 2001-12-16 | OH | other |  | COLUMBIA GAS OF OHIO INC |  | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2545 | 2001-12-26 | AK | other | DRISCOPIPE | ENSTAR NATURAL GAS CO | ON FRIDAY EVENING, DECEMBER 21, 2001 AT APPROXIMATELY 7:00 PM AST, ENSTAR NATURAL GAS COMPANY WAS NOTIFIED BY THE ANCHORAGE FIRE DEPARTMENT OF A FIRE AT 101 E. WHITNEY ROAD, ANCHORAGE, ALASKA. AN ENSTAR SERVICE WAS DISPATCHED TO THE SCENE. UPON ARRIVAL TH | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2546 | 2001-11-20 | TX | other | UPONOR | ENTEX, A NORAM ENERGY COMPANY (FORM. DIV OF ARKLA | THIRD PARTY DAMAGED A .75 INCH I.P. SERVICE LINE WITH A TORCH WHILE REPAIRING A TELEPHONE CABLE. THE ESCAPING GAS WAS IGNITED AND THIRD PARTY EMPLOYEE WENT TO HOSPITAL WITH SECOND DEGREE BURNS TO HANDS AND FACE. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2547 | 2001-10-16 | NC | other | PLEXCO | PUBLIC SERVICE CO OF NORTH CAROLINA | 9:03 PM A PSNC ENERGY SERVICE EMPLOYEE IS MONITORING A POLICE SCANNER AND IS MADE AWARE OF A GAS LEAK ON FRANKLIN STREET, CHAPEL HILL, NC. HE DECIDES TO DRIVE TO THE LOCATION TO SEE IF IT IS A NATURAL GAS LEAK. 9:10 PM THE CUSTOMER CARE CENTER (CCC) RECEI | 20000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2548 | 2001-12-20 | NV | other | KRALOY | SOUTHWEST GAS CORP | WHILE IN THE PROCESS OF REPLACING A TILTING SERVICE RISER AT 300 E. TROPICANA AVE. SPACE 11, A GAS LEAK IGNITED CAUSING A SWG CREWMEMBER TO RAPIDLY EXIT THE AREA, INJURING HIS LEG. IT WAS LATER DETERMINED THAT AN EXCAVATION FOR A WATER LEAK HAD CAUSED THE | 21598 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2549 | 2001-10-15 | NC | other | UNKNOWN | PUBLIC SERVICE CO OF NORTH CAROLINA | 6:28 PM PSNC ENERGY CCC RECEIVES A CALL FROM DURHAM COUNTY 911 STATING THERE HAS BEEN AN ACCIDENT ON HIGHWAY 147 AND A GAS MAIN HAS BEEN RUPTURED AND IS BLOWING. POLICE ARE ON SITE AND BLOCKING TRAFFIC, AND FIRE IS IN ROUTE. 6:35 PM CCC PAGES THE SERVICEM | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2550 | 2001-12-23 | OH | other |  | CINCINNATI GAS & ELECTRIC CO | EXPLOSION STILL UNDER INVESTIGATION. 4-16-04 NATURAL GAS FROM A BREAK IN THE GAS MAIN MIGRATED TO THE RESIDENCE LOCATED AT 3149 TIMBERVIEW DRIVE AND WAS IGNITED. | 170000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2551 | 2001-12-21 | CA | other | DUPONT | SOUTHERN CALIFORNIA GAS CO | STRESS CHECK ON 3" PE FITTINGS CAUSED LEAK THAT MIGRATED TO TELEPHONE SWITCHING FACILITY, RESULTING IN EXPLOSION. | 1000000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2552 | 2001-10-09 | OK | other | UNKNOWN (WASHITA COUNTY) | OKLAHOMA NATURAL GAS CO | APPROXIMATELY 125 DOMESTIC GAS METER SETTINGS AND SOME ASSOCIATED PIPELINE AND REGULATOR SETTINGS WERE DESTROYED OR DAMAGED BY A TORNADO THAT STRUCK CORDELL, OK. | 75000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2553 | 2001-11-29 | NC | ACCIDENTALLY CAUSED BY OPERATOR | DRISCO PIPE | KINGS MOUNTAIN NATURAL GAS SYSTEM | ON NOVEMBER 29, 2001 TWO CITY EMPLOYEES WERE ASSIGNED TO INSTALL A 3/4 INCH SERVICE LINE AT A LOCATION ACROSS THE STREET FROM 146 PERSIMMON CREEK ROAD. AFTER COMPLETING THE EXCAVATION AND ROAD BORE THE EMPLOYEE ENTERED THE BELL HOLE TO INSTALL THE SERVICE | 12865 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2554 | 2001-09-13 | NY | other | UNKNOWN | CONSOLIDATED EDISON CO OF NEW YORK | A TERRORIST ATTACK TO THE WTC ON 9/11/01 CAUSED DAMAGE TO THE GAS DISTRIBUTION SYSTEM SUPPLYING LOWER MANHATTAN. A STRONG GAS ODOR WAS REPORTED AT THE ABOVE LOCATION AND WE FOUND ON OUR ARRIVAL THAT THE GAS HAD IGNITED. COMPANY CREWS SHUT ONE MAIN VALVE A | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2555 | 2001-12-29 | AK | other | DRISCOPIPE | ENSTAR NATURAL GAS CO | ON SATURDAY EVENING, DECEMBER 29, 2001 AT APPROXIMATELY 8:55 PM AST, ENSTAR NATURAL GAS COMPANY WAS NOTIFIED BY THE ANCHORAGE FIRE DEPARTMENT OF A FIRE AT 8133 PARKRIDGE CIRCLE, ANCHORAGE, ALASKA. AN ENSTAR SERVICEMAN AND DUTY SUPERVISOR WERE DISPATCHED T | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2556 | 2001-10-09 | IL | other | UNKNOWN | PEOPLES GAS LIGHT & COKE CO | BUILDING CAUGHT ON FIRE DUE TO THE IGNITION OF LEAKING NATURAL GAS IN THE BASEMENT. GAS LEAK WAS CAUSED BY PERSONS TAMPERING WITH OUR FACILITIES (GAS METERS) WITH THE INTENT TO STEAL GAS. GAS METERS HAD PREVIOUSLY BEEN TURNED OFF AND LOCKED FOR NON-PAYMEN | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2557 | 2001-12-07 | NM | other | UNKNOWN | PUBLIC SERVICE COMPANY OF NEW MEXICO - GAS SVCS | 13 YEAR OLD DRIVING CHEVY TAHOE HIT GAS METER AND HOUSE WHICH IGNITED; FLAMES DESTROYED BOTH THE VEHICLE AND HOUSE. | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2558 | 2002-01-17 | AK | other | YELLOWSTRIPE HDPE | ENSTAR NATURAL GAS CO | ON THURSDAY MORNING, JANUARY 17, 2002 AT APPROXIMATELY 1:25 AM ADT, ENSTAR NATURAL GAS COMPANY WAS NOTIFIED BY THE ELMENDORF AIR FORCE BASE FIRE DEPARTMENT OF A FIRE AT 3711 FAUST CT, ELMENDORF AIR FORCE BASE, ANCHORAGE, ALASKA. AN ENSTAR SERVICEMAN AND | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2559 | 2001-12-18 | MI | other |  | CONSUMERS POWER CO | HOUSE EXPLOSION DUE TO GAS LEADAGE INSIDE THE RESIDENCE. UNKNOWN REASON FOR INCIDENT. NO GAS WAS FOUND IN THE GROUND ADJACENT TO THE HOUSE AND THE SERVICE LINE WAS PRESSURE TESTED WITH NO LEAKAGE FOUND. ON-GOING INVESTIVATION OF THE METER AND REGULATOR MA | 200000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2560 | 2001-10-11 | OH | maintenance | UNKNOWN (LUCAS COUNTY) | COLUMBIA GAS OF OHIO INC | DURING RECONSTRUCTION OF THE WATER MAIN IN THIS AREA, A CONSTRUCTION WORKER ENTERED A MANHOLE TO PURGE THE NEW WATER LINE. DURING THIS PROCESS, THERE WAS AN ACCIDENTAL IGNITION INSIDE THE MANHOLE. SUBSEQUENT INVESTIGATION REVEALED THAT BOTH THE CONTRACTOR | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2561 | 2001-12-10 | MO | other | UNKNOWN | MISSOURI GAS ENERGY | OCCURRENCE UNDER INVESTIGATION. MINUTE PRESENCE OF NATURAL GAS DOES NOT SUPPORT THE POWERFUL FLASH THAT REPORTABLY OCCURRED. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2562 | 2002-01-10 | CA | other | SHINHO STEEL | ISLAND ENERGY | WORK FORCE FOR XKT ENGINEERING WAS LIFTING BOOM FOR CRANE, SHIFTED BOOM TOWARD METER SET ASSY AND DESTROYED METER AND COMPENSATOR METER IS A 3175CDB3 05521-0212 INST DRIVE ROOTS GAS ROTERY METER ME-6000 EDFCV METRETEK FLOW COMPUTER, TEMP & PRESS CORRECTOR | 3022 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2563 | 2001-12-15 | IL | other | UNKN | NORTH SHORE GAS CO | A MOTOR VEHICLE LEFT THE ROADWAY, CROSSED THE CUSTOMERS LAWN AND STRUCK THE METER SET ASSEMBLY INSTALLED OUTSIDE OF THE PREMISE. THE IMPACT SEVERED A PIPE NIPPLE OF THE METER SET ASSEMBLY. THE VEHICLE CAME TO REST ON THE METER SET ASSEMBLY WITH THE ENGINE | 75000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2564 | 2002-01-18 | LA | other | UNKNOWN (nan COUNTY) | GULF STATES UTILITIES CO |  | 15000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2565 | 2001-12-28 | TN | other | UNKNOWN (ROBERTSON COUNTY) | NASHVILLE GAS CO | OUTSIDE PARTY DAMAGED RESIDENTIAL NATURAL GAS SERVICE LINE WHILE EXCAVATING TO REPAIR BROKEN WATER LINE. LEAKING NATURAL GAS MIGRATED THROUGH SEWER DITCH LINE TO SMALL HOUSE. IGNITION OCCURRED WHICH RESULTED IN DAMAGE TO THE HOUSE AND INJURIES TO THOSE PE | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2566 | 2002-01-29 | AZ | other | UNKNOWN (MARICOPA COUNTY) | SOUTHWEST GAS CORP | ARIZONA CORPORATION COMMISSION INCIDENT: PL NUMBER 2002-0089 THE 2" STEEL PIPE APPEARS TO HAVE BEEN DAMAGED BY AN UNKNOWN 3RD PARTY, WHICH CAUSED THE EVENTUAL PIPELINE LEAK. SOUTHWEST IS INVESTIGATING TO DETERMINE WHO CAUSED THE ORIGINAL DAMAGE AND WHEN I | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2567 | 2002-01-22 | MI | other | DRISCOPIPE 6500 | CONSUMERS POWER CO | A CONSTRUCTION COMPANY DAMAGED A 2" PLASTIC PIPELINE WHILE INSTALLING COMMUNICATIONS CABLE UTILIZING DIRECTIONAL BORING PROCEDURES. THE DAMAGE RESULTED IN A SUBSURFACE LEAK WITH GAS FILTERING THROUGH THE GROUND AROUND THE DAMAGED AREA. A DISTRIBUTION CREW | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2568 | 2002-02-09 | UT | other | UNKNOWN (UTAH COUNTY) | QUESTAR GAS COMPANY | A CAR WAS PARKED ACROSS THE STREET AND LEFT UNATTENDED (WHILE RUNNING) WHEN IT ROLLED OUT OF THE PARKING LOT, WENT ACROSS THE STREET, OVER THE CURB AND STRUCK THE NATURAL GAS METER (THE GAS METER LOCATED APPROXIMATELY 20 FEET OFF THE CURB). THE IMPACT OF | 550000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2569 | 2002-01-25 | TX | other | UNKNOWN (DALLAS COUNTY) | TXU GAS DISTRIBUTION | A LEAK OCCURRED BELOW GROUND NEAR THE INLET RISER SERVING 3209 SANDERS. GAS MIGRATED UNDER THE SLAB AT 3213 SANDERS AND WAS IGNITED BY AN UNDETERMINED SOURCE. | 75000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2570 | 2002-02-19 | AR | other | UNKNOWN (GARLAND COUNTY) | RELIANT ENERGY ARKLA, DIV OF RELIANT ENERGY RESOUR | A REGULATOR STATION SERVING APPROXIMATELY 120 CUSTOMERS WAS RUN OVER BY AN ALLEGED DRUNK DRIVER. THE DRIVER WAS TAKEN TO THE HOSPITAL AND TREATED FOR INJURIES ASSOCIATED WITH THE VEHICLE ACCIDENT. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2571 | 2002-02-07 | NV | other | UNKNOWN (WASHOE COUNTY) | SIERRA PACIFIC POWER CO | MOBILE HOME FIRE CAUSED SUBSEQUENT DAMAGE TO TWO METER MANIFOLD AND REGULATOR. DAMAGE TO METERS AND REGULATOR RESULTED IN A RELEASE OF GAS WHICH IGNITED CAUSING FURTHER DAMAGE TO METERS AND REGULATOR. | 84000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2572 | 2002-02-05 | IN | other | UPONOR | NORTHERN INDIANA PUBLIC SERVICE CO | THIRD PARTY CONTRACTOR EXCAVATING ALONG OUTSIDE PERIMETER OF HOUSE STRUCK PLASTIC GAS SERVICE LINE CAUSING IT TO LEAK. GAS IGNITED AND BURNED PORTION OF THE STRUCTURE. NO INJURIES RESULTED. LOCATES WERE NOT REQUESTED PRIOR TO INCIDENT. | 75000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2573 | 2002-02-19 | VA | other | CENTRAL PLASTICS | COLUMBIA GAS OF VIRGINIA INC | AN UNINTENTIONAL RELEASE OF NATURAL GAS AND SUBSEQUENT IGNITION CONSUMED A PLASTIC PIPELINE FACILITY AND APPURTENANCES PRESENT DURING TIE-IN AND BYPASS OPERATIONS ASSOCIATED TO THE RELOCATION OF AN EXISTING 6" PLASTIC MAIN. THE RELEASE OF GAS OCCURRED AF | 120000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2574 | 2002-03-08 | AK | other | M 8000 HDPE | ENSTAR NATURAL GAS CO | ON FRIDAY MORNING, MARCH 8, 2002, AT APPROXIMATELY 2:07 AM ADT, ENSTAR NATURAL GAS COMPANY WAS NOTIFIEDBY THE WASILLA FIRE DEPARTMENT OF A FIRE AT 271 E PARK AVE, WASILLA, AK. AN ENSTAR SERVICEMAN WAS DISPATCHED TO THE SCENE. UPON ARRIVAL THE SERVICEMAN | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2575 | 2002-03-01 | CA | other |  | SOUTHERN CALIFORNIA GAS CO | CONTRACTOR STRUCK STEEL SERVICE WHILE CUTTING CONCRETE, WHICH IGNITED, DAMAGING BUILDING AND CONTENTS. | 1000000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2576 | 2002-01-11 | PA | other | UNKNOWN | U G I CORP | NATURAL GAS LEAKING FROM A CRACKED FOUR-INCH (4") BARE STEEL MAIN APPARENTLY FOLLOWED THE SANITARY SEWER TRENCH AND MIGRATED INTO HOUSE 2802 NORTHAMPTON STREET. PALMER TOWNSHIP. UNKNOWN IGNITION SOURCE CAUSED AND EXPLOSION. THE CAUSE OF THE CRACK REMAI | 150000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2577 | 2002-03-03 | PA | other | PLEXCO | PECO ENERGY CO |  | 150000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2578 | 2002-03-09 | PA | other | PLEXCO | PECO ENERGY CO |  | 200000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2579 | 2002-02-20 | TX | other | UNKNOWN (WILLIAMSON COUNTY) | TXU GAS DISTRIBUTION | A NON-ONCOR EXCAVATOR DAMAGED A GAS MAIN. THE ESCAPING GAS IGNITED AND THE BULLDOZER BURNED. | 250000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2580 | 2002-02-26 | IL | other | UNKNOWN (COOK COUNTY) | PEOPLES GAS LIGHT & COKE CO | ON FEBRUARY 26, 2002, EMPLOYEES OF THE CITY OF CHICAGOS SEWER DEPARTMENT WERE PERFORMING WORK IN THE PARKWAY IN FRONT OF 3140 W. 107TH STREET. IN THE COURSE OF THEIR WORK, THE SEWER DEPARTMENT CREW DUG AN EXCAVATION IN THE PARKWAY AND EXPOSED A 6-INCH CAS | 200000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2581 | 2002-03-11 | OH | other | UNKNOWN (CUYAHOGA COUNTY) | DOMINION EAST OHIO | THE CAUSE OF THE INCIDENT WAS A CONTRACTOR WORKING ON THE INSTALLATION OF A SEWER LINE AT THE INTERSECTION OF LEE AND LIBBY ROADS IN MAPLE HEIGHTS, OHIO. DURING THE CONSTRUCTION PHASE OF EXCAVATION A 6 INCH VALVE AND FLANGE ATTACHED TO A 24 INCH 90 PSIG W | 1000000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2582 | 2002-04-09 | AK | other | 8000 HDPE | ENSTAR NATURAL GAS CO | ON TUESDAY MORNING, APRIL 9, 2002 AT APPROXIMATELY 3:20 AM AST, ENSTAR NATURAL GAS COMPANY WAS NOTIFIED BY THE ANCHORAGE FIRE DEPARTMENT OF A FIRE AT 108 E 8TH STREET, ANCHORAGE, ALASKA. AN ENSTAR SERVICEMAN AND DUTY SUPERVISOR WERE DISPATCHED TO THE SCE | 4000000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2583 | 2001-01-04 | PA | other |  | EQUITABLE RESOURCES (A.K.A EQUITABLE GAS CO) | ON THURSDAY, JANUARY 4, 2001, AN EXPLOSION OCCURRED AT A CAR WASH AT 831 HARRISON CITY ROAD, LEVEL GREEN, WESTMORELAND COUNTY, PA AT 8:45 PM. INITIALLY, THE EXPLOSION WAS REPORTED TO THE PENNSYLVANIA PUBLIC UTILITY COMMISSION GAS SAFETY DIVISION VIA A "C | 95104 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2584 | 2002-03-21 | PA | other | DU PONT | PECO ENERGY CO | CONTRACTOR CALLED FOR A PRIVATE PROPERTY, LOCATE IN NOVEMBER OF 2001. CONTRACTOR HAD CALLED FOR ANOTHER LOCATE (FOR EXCAVATION IN PAVING) ON 3/19/02 AND WAS NOT TO BEGIN EXCAVATING UNTIL 3/22/02 AFTER 1:30PM (72 HOURS AFTER THE CALL). THE DAMAGE OCCURRE | 5000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2585 | 2002-03-20 | IN | other | RW LYALL | VECTREN ENERGY DELIVERY OF OHIO |  | 60000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2586 | 2002-04-03 | PA | other | EQUIMETER | PENNSYLVANIA GAS & WATER CO | AN INDIVIDUAL DRIVING A TOYOTA PICKUP TRUCK, WHILE UNDER THE INFLUENCE OF ALCOHOL, LEFT THE ROAD AND HIT A MULTIPLE FAMILY DWELLING INCLUDING A MULTIPLE METER SET DESTORYING BOTH METERS AND ASSOCIATED PIPING (AFTER THE REGULATOR) CAUSING THE RELEASE OF GA | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2587 | 2002-03-20 | TX | other |  | DUMAS, CITY OF | FRONTEND LOADER PICKING UP DEBRIS AND TRASH IN THE ALLEY, HIT REGULATOR AND KNOCKED OFF METER SET. | 55000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2588 | 2002-04-04 | OH | other | UNKNOWN | COLUMBIA GAS OF OHIO INC | A PERSON WITH A HISTORY OF SEIZURES LOST CONTROL OF HIS VEHICLE, TRAVELED OFF THE MAIN ROAD, TRAVELED ACROSS A FIELD, AND HIT THE FENCED METER SETTING LOCATED AT 29150 GLENWOOD ROAD IN PERRYSBURG, OH, WHICH RESULTED IN GAS ESCAPING FROM THE DAMAGED METER | 500000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2589 | 2002-02-13 | MN | other | PLEXCO | PEOPLES NATURAL GAS |  | 140000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2590 | 2002-04-06 | OH | technical failure | UNKNOWN (BUTLER COUNTY) | CINCINNATI GAS & ELECTRIC CO | EXPLOSION STILL UNDER INVESTIGATION. 5-31-02 GAS SERVICE FAILED INSIDE THE HOUSE DUE TO EXCESSIVE INTERNAL STRESS ON THE PIPE. THE FILL HAD NOT BEEN SUITABLY COMPACTED AND IT SETTLED UNDER THE LOAD OF THE OVERLYING FILL. | 75000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2591 | 2002-04-13 | AK | other | DRISCOPIPE | ENSTAR NATURAL GAS CO | ON SATURDAY EVENING, APRIL 13, 2002, AT APPROXIMATELY 11:07 PM ADT, ENSTAR NATURAL GAS COMPANY WAS NOTIFIED BY THE BIG LAKE FIRE DEPARTMENT OF A FIRE ON GODIN DRIVE, NEAR BEAVER LAKE (NE 1/4 SECTION 17, T17NRSW) ALASKA. AN ENSTAR SERVICEMAN WAS DISPATCHE | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2592 | 2002-04-16 | MI | other |  | MICHIGAN CONSOLIDATED GAS CO (MICHCON) |  | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2593 | 2002-05-18 | AK | other | UNKNOWN | ENSTAR NATURAL GAS CO | ON SATURDAY MORNING, MAY 18, 2002 AT APPROXIMATELY 6:47 AM ADT, ENSTAR NATURAL GAS COMPANY WAS ASKED TO RESPOND TO A HOUSE FIRE AT 8311 KIP COURT, ANCHORAGE, AK. THE FIRE BURNED ENSTARS SERVICE LINE RISER. THE POLYETHYLENE GAS SERVICE LINE INSIDE THE ST | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2594 | 2002-05-24 | MA | ACCIDENTALLY CAUSED BY OPERATOR |  | NSTAR ELECTRIC GAS | AT APPROXIMATELY 08:21 AM ON MAY 24, 2002 A BACKHOE OPERATOR EMPLOYED BY PIPELINE CONSTRUCTION, A CONTRACTOR FOR NSTAR GAS, INADVERTENTLY PULLED A 1" STEEL SERVICE TO 9 BONITO DRIVE, FRAMINGHAM. THE CONTRACT CREW WAS EXCAVATING TO PERFORM A SERVICE TIE-O | 150000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2595 | 2002-06-01 | MT | other | UNKNOWN | NORTHWESTERN ENERGY LLC | STRUCTURE DEMOLITION RECENTLY AT AN ADJACENT PROPERTY MAY HAVE CAUSED UNANTICIPATED LOADS ON THE CURB BOX. WEATHER CONDITIONS WERE ALSO VERY WET. | 10000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2596 | 2002-05-22 | UT | other | LANCASTER | QUESTAR GAS COMPANY | AS A RESULT OF ARSON THE INTENSE HEAT FROM THE BUILDING FIRE CAUSED THE QUESTAR OWNED SERVICE REGULATOR TO FAIL AND RELEASE GAS. WITH THIS RELEASE OF GAS, THERE WAS A SECONDARY IGNITION AT THE REGULATOR. | 92000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2597 | 2002-05-26 | AK | other |  | ENSTAR NATURAL GAS CO | ON SATURDAY MORNING, MARCH 26, 2002, AT APPROXIMATELY 4:07 AM ADT, ENSTAR NATURAL GAS COMPANY WAS NOTIFIED BY THE ANCHORAGE FIRE DEPARTMENT OF A FIRE AT 2875 INTERNATIONAL AIRPORT RD, ANCHORAGE, AK. AN ENSTAR SERVICEMAN WAS DISPATCHED TO THE SCENE. UPON | 350000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2598 | 2002-05-20 | NE | other |  | K N ENERGY INC(KANSAS NEBRASKA GAS CO) (KMI) | INCIDENT IS BEING INVESTIGATED BY THE STATE FIRE MARSHALLS OFFICE. THE CUSTOMER ALLEGEDLY LOOSENED A NATURAL GAS FITTING INSIDE THE HOUSE AND SUPPLIED IGNITION FOR A GAS EXPLOSION. HOUSE WAS DESTOYED BY THE EXPLOSION AND THE CUSTOMER WAS TAKEN TO A HOSP | 60000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2599 | 2002-05-15 | MI | other | PHILLIPS | CONSUMERS POWER CO | CONTRACTOR HIT 1 1/4 INCH PLASTIC PIPELINE DURING DIRECTIONAL BORING OPERATIONS. ESCAPING GAS IGNITED AND DESTROYED A SINGLE WIDE TRAILER AND CONTENTS. | 55000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2600 | 2002-06-07 | NC | technical failure | PERFORMANCE | PIEDMONT NATURAL GAS CO INC | GAS ESCAPED BACKFLOWING THROUGH BYPASS TAPPING TEE. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2601 | 2002-06-06 | KY | technical failure |  | UNION LIGHT HEAT & POWER CO | WHILE REPLACING A DEFECTIVE VALVE ON A METER SET, GAS IGNITED CAUSING AN EXPLOSION AND BURN INJURIES TO TWO (2) COMPANY EMPLOYEES. | 2000000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2602 | 2002-06-04 | AK | other | M 8000 HDPE | ENSTAR NATURAL GAS CO | ON TUESDAY AFTERNOON JUNE 4, 2002, A SMALL CAR RAN INTO AN AL 800 GAS METER SET ASSEMBLY SERVING A 30 UNIT CONDOMINUM COMPLEX AT 1405 W 27TH AVENUE, ANCHORAGE, AK 99519. THE REGULATOR BROKE OFF THE RISER CAUSING A RELEASE OF NATURAL GAS. THE DRIVER OF T | 250000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2603 | 2002-06-19 | AK | other | UNKNOWN (nan COUNTY) | ENSTAR NATURAL GAS CO | ON WEDNESDAY EVENING, JUNE 19, 2002 A FIRE DAMAGED A SINGLE FAMILY RESIDENCE AT 19026 KLONDIKE, EAGLE RIVER, AK. ENSTAR WAS NOT NOTIFIED OF THE FIRE. ON THURSDAY, JUNE 20, 2002, ENSTAR WAS CALLED BY THE OWNER OF THE HOME REPORTING A GAS ODOR. ENSTAR RES | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2604 | 2002-06-07 | AK | other |  | ENSTAR NATURAL GAS CO | ON 6/7/02, A STRUCTURE FIRE DESTROYED A HOME/SHOP AND BURNED UP THE METER SET. THE RISER MELTED AND RELEASED GAS FROM OUR FACILITY. A SERVICE CREW EXCAVATED THE SERVICE AND CUT AND CAPPED THE SERVICE. THERE HAS BEEN NO INDICATION OF GAS INVOLVEMENT AS | 75000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2605 | 2002-06-18 | NY | ACCIDENTALLY CAUSED BY OPERATOR |  | NIAGARA MOHAWK POWER CORP | FACILITIES EMPLOYEE DAMAGE 1" STEEL TEST POINT WHILE MOWING | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2606 | 2002-06-21 | CA | other |  | PACIFIC GAS & ELECTRIC CO | FIRE DEPT SAID FIRE STARTED IN TRASHCAN ON SIDE OF HOUSE, WHICH MELTED THE GAS METER, CAUSING GAS TO ESCAPE. THE ESCAPING GAS PROVIDED MORE FUEL TO THE FIRE. AN ACETYLENE TANK INSIDE THE GARAGE ALSO ADDED FUEL TO THE FIRE. GAS DID NOT CAUSE THIS INCIDEN | 151000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2607 | 2002-06-14 | MN | other |  | NORTHERN MINNESOTA UTILITIES | OUR INVESTIGATION SUGGESTS AN EXPLOSION WAS CAUSED BY A MECHANICAL FAILURE AT A INDUSTRIAL WATER HEATER WHICH CAUSED $300,000 IN DAMAGES TO THE TURKEY PLANT. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2608 | 2002-07-07 | AK | other |  | ENSTAR NATURAL GAS CO | ON SUNDAY MORNING, JULY 7, 2002, TWO TEENAGERS WERE RACING CARS AND LOST CONTROL OF THEIR VEHICLES. ONE OF THE CARS HIT A BLOCK BUILDING AT 341 E 77TH ANCHORAGE. THE SECOND CAR HIT THE GAS METER ATTACHED TO THE BLOCK BUILDING AND ALSO AN ELECTRIC TRANSF | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2609 | 2002-07-24 | MA | other | UNKNOWN (MIDDLESEX COUNTY) | NSTAR ELECTRIC GAS | AT 01:49A.M. NSTAR GAS RECEIVED A CALL FROM THE HOPKINTON FIRE DEPARTMENT THAT THERE WAS A HOUSE EXPLOSION AND BUILDING COLLAPSE AT 65 MAIN ST., HOPKINTON AND FOUR PERSONS WERE INJURED. IT WAS ALSO REPORTED THAT ONE CHILD WAS STILL IN THE BUILDING. NSTAR | 400000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2610 | 2002-06-12 | TX | other |  | ENTEX, A NORAM ENERGY COMPANY (FORM. DIV OF ARKLA | DUE TO A HOUSE FIRE METER SET ASSEMBLY WAS DAMAGED AND THE ESCAPING GAS IGNITED. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2611 | 2002-07-12 | IL | other | PLEXCO | ILLINOIS POWER CO |  | 350000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2612 | 2002-08-03 | CA | other | UNKNOWN (IMPERIAL COUNTY) | SOUTHERN CALIFORNIA GAS CO | DRIVER LOST CONTROL OF VEHICLE, TRAVELLED OUT OF ROADWAY, ACROSS SIDEWALK, THROUGH STEEL & CONCRETE POSTS ADD STRUCK MSA; IGNITING. DRIVER DIED FROM BURN INJURIES. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2613 | 2002-08-13 | CT | other |  | SOUTHERN CONNECTICUT GAS CO | THE SOUTHERN CONNECTICUT GAS COMPANY (SCG) WAS NOTIFIED OF A FIRE AND EXPLOSION AT THE ORCHARD HILL RESIDENTIAL CONDOMINIUM COMPLEX, 309 TERRACE AVENUE, WEST HAVEN, CONNECTICUT AT 3:50 AM ON AUGUST 13, 2002. THE CALL CAME TO THE SCG DISPATCH CENTER FROM | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2614 | 2002-08-13 | CA | other | UNKNOWN (LOS ANGELES COUNTY) | SOUTHERN CALIFORNIA GAS CO | EXPLOSION RELATED TO ESCAPING NATURAL GAS COLLECTING UNDER FUMIGATION TENT AND IGNITING. | 1000000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2615 | 2002-09-12 | UT | other | UNKNOWN (UTAH COUNTY) | SANTAQUIN CITY | RAIN STORM CAUSED A MUD SLIDE WHICH PUSHED A VEHICLE. THE VEHICLE PULLED M.S.A AWAY FROM STRUCTURE AND 1/2 SERVICE LINE. | 500 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2616 | 2002-08-22 | CT | other | NO DATA | YANKEE GAS SERVICES CO | OCCUPANT WAS USING A FLAMMABLE LIQUID TO CLEAN THE BASEMENT FLOOR AND WALLS WHICH IGNITED. THE FIRE DAMAGED THE METER SET, MELTING THE INSULATED COUPLING AND THE METER INDEX. A SMALL AMOUNT OF NATURAL GAS WAS RELEASED INTO THE FIRE. | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2617 | 2002-09-08 | AR | other | UNKNOWN (SEBASTIAN COUNTY) | ARKANSAS OKLAHOMA GAS CORP | AN AUTO RAN OFF BURNHAM ROAD, JUMPED THE DITCH, EJECTING A PASSENGER AND CAUSING HER DEATH. THE CAR CONTINUED ON, RUNNING THROUGH A FENCE, HITTING A GAS METER SET, SEVERING THE METER SET ABOVE THE SHUT-OFF VALVE, AND CAUSING A RELEASE OF NATURAL GAS. THE | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2618 | 2002-08-21 | AR | ACCIDENTALLY CAUSED BY OPERATOR | UNKNOWN (JEFFERSON COUNTY) | RELIANT ENERGY ARKLA, DIV OF RELIANT ENERGY RESOUR | ELECTRIC SAW WAS USED TO CUT PIPE WHILE GAS WAS IN LINE. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2619 | 2002-08-27 | MI | ACCIDENTALLY CAUSED BY OPERATOR | UNKNOWN (KENT COUNTY) | MICHIGAN CONSOLIDATED GAS CO (MICHCON) | ALL CLEAR WAS GIVEN IN ERROR BY MICHCON STAKER | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2620 | 2002-08-26 | TX | other | UNKNOWN (BOWIE COUNTY) | RELIANT ENERGY ARKLA, DIV OF RELIANT ENERGY RESOUR | CONTRACTOR DID NOT ATTEMPT TO NOTIFY UTILITIES FOR UNDERGROUND LOCATES BEFORE OPERATING ASPHALT RECLAIMER | 90000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2621 | 2002-08-27 | MD | other | AMERICAN | WASHINGTON GAS LIGHT CO | FIRE AND EXPLOSION TO SINGLE FAMILY HOME, WHICH CAUSED FAILURE TO METER FACE PLATE AND REGULATOR DIAPHRAM. INCIDENT IS UNDER INVESTIGATION BY THE PRINCE GEORGES COUNTY FIRE DEPARTMENT. | 250000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2622 | 2002-08-23 | VA | other | QUANEX | WASHINGTON GAS LIGHT CO | INCIDENT (GAS EXPLOSION W/FIRE) OCCURRED DUE TO GROUND SETTLEMENT ALONG BUILDING WALL, WHICH CAUSED STRESS ON PIPE THREADS (1 STEEL SCH 40) AND CAUSED A BREAK AT BEGINNING EDGE OF A 90 DEGREE ELBOW IN THE UTILITY CLOSET. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2623 | 2002-09-16 | PA | ACCIDENTALLY CAUSED BY OPERATOR | UNKNOWN (JEFFERSON COUNTY) | T W PHILLIPS GAS & OIL CO | EMPLOYEE WERE EXECUTING A 2-INCH HOT TAP INTO 4-INCH STEEL PIPELINE. DURING THE TAPPING PROCEDURE, GAS WAS EXITING A PLASTIC TRANSITION FITTING AND IGNITED. INCIDENT UNDER INVESTIGATION, HOWEVER, STATIC ELECTRICITY WAS THE APPARENT IGNITION SOURCE. TWO EM | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2624 | 2002-08-27 | WY | other | CBOMANU | MONTANA - DAKOTA UTILITIES CO | FLASH FLOOD CAUSED BY 7 INCH RAINFALL WITHIN 1 HR PERIOD. | 15000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2625 | 2002-07-16 | MI | other |  | MICHIGAN CONSOLIDATED GAS CO (MICHCON) |  | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2626 | 2002-06-28 | MI | other | UNKNOWN (KENT COUNTY) | MICHIGAN CONSOLIDATED GAS CO (MICHCON) | CONTRACTOR DAMAGED MICHCON FACILITIES. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2627 | 2001-11-30 | MI | other | UNKNOWN (WAYNE COUNTY) | MICHIGAN CONSOLIDATED GAS CO (MICHCON) | EXCAVATION BY CITY OF DETROIT WATER DEPARTMENT. | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2628 | 2002-09-08 | MI | other | UNKNOWN (WAYNE COUNTY) | MICHIGAN CONSOLIDATED GAS CO (MICHCON) | RELEASE OF GAS CAUSED BY LEAK IN CUSTOMERS FUEL LINE. THIS RELEASE OF GAS WAS IGNITED BY TWO SEPARATE AND UNRELATED FIRES BURNING WITHIN THE DWELLING. | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2629 | 2002-09-12 | PA | other | ALLIED | PECO ENERGY CO |  | 200000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2630 | 2002-09-20 | PA | other | AMERICAN | COLUMBIA GAS OF PENNSYLVANIA | SINGLE VEHICLE ACCIDENT WHERE CAR LEFT ROADWAY AND CRASHED INTO RESIDENCE. THE GAS METER SERVICING THIS CUSTOMER (558 BECKS RUN ROAD) WAS DAMAGED THAT RESULTED IN BLOWING GAS (NO IGNITION) AND DEATH OF THE DRIVER. | 75000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2631 | 2002-09-29 | CA | other | UNKNOWN (nan COUNTY) | SOUTHERN CALIFORNIA GAS CO | VEHICLE STRUCK ANOTHER VEHICLE INSIDE GARAGE, PUSHING VEHICLE THROUGH REAR WALL OF GARAGE AND STRIKING METER SET, WHICH IGNITED. | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2632 | 2002-10-11 | PA | other | UNKNOWN (YORK COUNTY) | COLUMBIA GAS OF PENNSYLVANIA | ELECTRICAL FIRE STARTED ON THE 2ND FLOOR OF 316 EAST PRINCESS STREET. NOTE!! INCIDENT WAS NOT CAUSED BY NATURAL GAS. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2633 | 2002-10-02 | KS | other | UNKNOWN (SALINE COUNTY) | WESTERN RESOURCES INC (AKA KPL CO. OR GAS SERVICE) |  | 750000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2634 | 2002-10-14 | AZ | ACCIDENTALLY CAUSED BY OPERATOR | AMERICAN AC250 | SOUTHWEST GAS CORP | SEE PART D | 120000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2635 | 2002-10-06 | OH | other | UNKNOWN (BUTLER COUNTY) | CINCINNATI GAS & ELECTRIC CO | VARIOUS FACTORS POSSIBLY CONTRIBUTED TO THE CAUSE OF THE INCIDENT. INSPECTION, TESTING, AND REVIEW OF RECORDS AVAILABLE TO CG&E TO DATE FAIL TO IDENTIFY THE SPECIFIC CONTRIBUTING FACTORS. | 300000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2636 | 2002-10-29 | AK | other | DRISCOPIPE M 8000 HDPE | ENSTAR NATURAL GAS CO | ON TUESDAY MORNING, OCTOBER 29, 2002, AT APPROXIMATELY 3:43 AM AST, ENSTAR NATURAL GAS COMPANY WAS NOTIFIED BY THE ALASKA STATE TROOPERS OF A FIRE AT 51819 RUT AVE, NIKISKI, AK 99635. AN ENSTAR SERVICEMAN WAS DISPATCHED TO THE SCENE. UPON ARRIVAL HE FOU | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2637 | 2002-10-23 | CA | technical failure | NIPAC | ISLAND ENERGY | CONTRACTOR DEMOLISHING BUILDING | 3000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2638 | 2002-10-17 | VA | other | UNKNOWN (nan COUNTY) | COLUMBIA GAS OF VIRGINIA INC |  | 273103 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2639 | 2002-09-25 | MO | other | UPONOR | SPRINGFIELD, CITY UTILITIES OF |  | 24979 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2640 | 2002-10-21 | MD | other | UNKNOWN (ALLEGANY COUNTY) | COLUMBIA GAS OF MARYLAND INC | CONTROL ON CUSTOMERS SPACE HEATER. | 80000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2641 | 2002-10-16 | TN | other | UNKNOWN (HAMILTON COUNTY) | CHATTANOOGA GAS CO | A 16" CAST IRON NATURAL GAS MAIN WAS RUPTURED WHILE A CONTRACTOR WAS EXCAVATING TO PLUG A SEWER LINE. THE ESCAPING GAS IGNITED INJURING THREE WORKERS AND HOSPITALIZING ONE. | 25000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2642 | 2002-11-07 | IN | other | UNKNOWN (DEARBORN COUNTY) | LAWRENCEBURG GAS CO | A GEOTHERMAL WELL DRILLING CONTRACTOR PENETRATED THE STORAGE FIELD THAT WE UTILIZE TO STORE NATURAL GAS. | 56598 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2643 | 2002-10-30 | NY | other | UNKNOWN (ONEIDA COUNTY) | NIAGARA MOHAWK POWER CORP |  | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2644 | 2002-11-05 | CO | other | UNKNOWN (JEFFERSON COUNTY) | PUBLIC SERVICE CO OF COLORADO |  | 300000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2645 | 2001-05-24 | TX | other | UNKNOWN (DALLAS COUNTY) | TXU GAS DISTRIBUTION | A CONTRACTOR WORKING FOR THE CITY OF DALLAS DAMAGED A SERVICE LINE. THE CONTRACTOR FAILED TO REPORT THE DAMAGE. GAS SUBSEQUENTLY ESCAPED FROM THE DAMAGED SERVICE LINE AND ENTERED A STORM SEWER. THE GAS IN THE STORM SEWER WAS IGNITED BY A CIGARETTE LIGHTER | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2646 | 2002-11-20 | PA | other | DUPONT | PECO ENERGY CO | SEE PART D | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2647 | 2002-09-01 | MD | maintenance | UNKNOWN (WORCESTER COUNTY) | EASTERN SHORE GAS CO |  | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2648 | 2002-12-02 | CA | other | UPONOR | SOUTHERN CALIFORNIA GAS CO | CONTRACTOR STRUCK 2" PE GAS MAIN, WHILE TRENCHING FOR CONDUITS. ESCAPING GAS IGNITED WHILE GAS COMPANY CREW WAS ATTEMPTING REPAIRS. TWO GAS COMPANY EMPLOYEES INJURED. | 75000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2649 | 2002-12-04 | VA | other | MOONEY | COLUMBIA GAS OF VIRGINIA INC | IT IS SUSPECTED THAT A COMBINATION OF LOW AMBIENT AIR TEMPERATURES, HIGH FLOW RATE (GAS VOLUMES) AND INSUFFICIENT HEAT OBTAINED FROM THE WATER BATH HEATER, ALLOWED HYDRATES TO FREEZE IN THE DISCHARGE PORT(S) OF ONE OF THE PILOT REGULATORS UPSTREAM OF THE | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2650 | 2002-12-12 | AK | other |  | ENSTAR NATURAL GAS CO | ON THURSDAY EVENING, DECEMBER 12, 2002 AT APPROXIMATELY 10:12 PM AST, ENSTAR NATURAL GAS COMPANY WAS NOTIFIED BY THE EAGLE RIVER FIRE DEPARTMENT OF A FIRE AT 2900 SUN VALLEY RD, EAGLE RIVER, ALASKA. AN ENSTAR SERVICEMAN AND DUTY SUPERVISOR WERE DISPATCHE | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2651 | 2002-11-27 | IN | other | DUPONT | INDIANA GAS CO INC | THIRD PARTY CONTRACTOR CONDUCTING BORING BY HORIZONTAL DIRECTIONAL DRILLING PIERCED 4-INCH PLASTIC GAS MAIN. GAS ESCAPING FROM MAIN ENTERED NEARBY SEWER SYSTEM. FOUR RESIDENTIAL STRUCTURES INOVOLVED IN EXPLOSION(S). | 350000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2652 | 2002-12-10 | GA | other |  | ATLANTA GAS LIGHT CO | A 4" PLASTIC NATURAL GAS MAIN WAS RUPTURED WHEN A CONTRACTOR WAS MAKING A DIRECTIONAL BORE WHILE INSTALLING FIBER OPTIC CABLE. THE ESCAPING GAS MIGRATED INTO A SEWER LATERAL WHICH HAD ALSO BEEN DAMAGED BY THE CONTRACTOR. GAS ENTERED HOUSE AND WAS IGNITI | 300000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2653 | 2002-12-03 | AZ | other | PHILLIPS | SOUTHWEST GAS CORP | A LEAK RESULTED FROM AN APPARENT FAILURE AT THE PIPE TO RISER CONNECTION. IGNITION OCCURRED RESULTING IN A FIRE AND SUBSEQUENT DAMAGE TO THE THE GARAGE AT THIS ADDRESS. THE CAUSE OF THE FAILURE IS CURRENTLY UNDER INVESTIGATION. A SUPPLEMENTAL REPORT WIL | 80000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2654 | 2002-11-30 | IA | other | AMERICAN | MIDAMERICAN ENERGY COMPANY | DAMAGE WAS CAUSED BY A CAR THAT STRUCK A HOUSE AND ITS GAS METER. THE INCIDENT CAUSED A FIRE. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2655 | 2002-12-11 | MI | ACCIDENTALLY CAUSED BY OPERATOR |  | MICHIGAN CONSOLIDATED GAS CO (MICHCON) | COMPANY EMPLOYEES CHANGE GAS VALVE WITH GAS FLOWING. IGNITION OF GAS OCCURRED AND EMPLOYEES RECEIVED FLASH BURNS AND TRANSPORTED TO AREA HOSPITAL FOR TREATMENT. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2656 | 2002-12-09 | KY | technical failure |  | WESTERN KENTUCKY GAS CO | A GIRTH WELD ON A 4" STEEL LINE OPERATING AT 45 PSIG CRACKED, ALLOWING GAS TO MIGRATE UNDERGROUND TO AN ASPHALT PLANT QC LAB BUILDING (NO GAS SERVICE). GAS IGNITION IN THE BUILDING DESTROYED THE LAB & TEST EQUIPMENT. VALUE OF CONTENTS WAS REPORTED TODAY | 78000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2657 | 2002-12-19 | PA | ACCIDENTALLY CAUSED BY OPERATOR |  | EQUITABLE RESOURCES (A.K.A EQUITABLE GAS CO) | A 4-MAN CREW WAS ASSIGNED TO INSTALL A LARGE METER SET AT THE CAPA BUILDING AT 111 9TH STREET, PITTSBURGH, PA ON DECEMBER 19, 2002. WHEN THE CREW ARRIVED AT APPROXIMATELY 10:00 AM, THEY FAILED TO ENSURE THAT THE INLET VALVE ON THE 6-INCH STEEL SERVICE LI | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2658 | 2002-12-17 | GA | maintenance |  | ATMOS ENERGY |  | 60000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2659 | 2002-12-20 | WV | other |  | MOUNTAINEER GAS CO | CAR BACKED OVER METER SET ASSEMBLY. | 3000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2660 | 2002-11-26 | SC | other | NORDSTROM | YORK COUNTY NATURAL GAS AUTH | AT APPROXIMATELY 10:00 ON NOVEMBER 26, 2002, YORK COUNTY NATURAL GAS AUTHORITY WAS NOTIFIED OF A STRONG ODOR OF GAS IN THE VICINITY OF 489 S HERLONG AVENUE, HERLONG PLAZA. THE CAUSE OF THE ODOR WAS DETERMINED TO BE A 4" UNDERGROUND VALVE (FIG. 143 NORDST | 120000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2661 | 2002-12-27 | IA | other | PLEXCO | GILMORE CITY MUNICIPAL GAS SYSTEM INC |  | 130000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2662 | 2003-01-02 | AZ | other | SWANSON | SOUTHWEST GAS CORP | SEE PART D | 200000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2663 | 2003-01-08 | MI | other |  | MICHIGAN CONSOLIDATED GAS CO (MICHCON) | METER SWIVELS HAD BEEN DELIBERATELY LOOSENED ALLOWING RELEASE OF GAS RESULTING IN AN EXPLOSIION, FIRE AND COLLAPSE. | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2664 | 2002-11-04 | IL | other |  | NORTHERN ILLINOIS GAS CO | FIRE AT ABOVE ADDRESS, PRELIMINARY VERBAL REPORT FROM FIRE MARSHALL INDICIATED THAT THE LEFT SIDE OF HOUSE HAD FALLEN ON METER SET AND CAUSED RELEASE OF GAS, WHICH IGNITED. THE RELEASE WAS MADE SAFE BY CUTTING AND CAPPING THE 1" PE SERVICE LINE. | 1500000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2665 | 2002-12-12 | PA | other | PLEXCO | PECO ENERGY CO | SEE PART D | 20000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2666 | 2002-10-20 | TX | other |  | WEST TEXAS GAS INC | EITHER TEJAS FEEDERS, EMPLOYEES OR CONTRACTOR HAD REPAIRED THEIR SERVICE LINES AT AN UNKNOWN DATE WITH UNACCEPTABLE PLASTIC (PVC) PIPE REPAIR PROCEDURES. TWO OF THESE REPAIRS WERE FOUND. ONE REPAIR WAS MADE BY GLUEING A SPLIT SECTION OF PVC PIPE TO THE | 205000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2667 | 2003-01-19 | IN | other | UKNOWN | NORTHERN INDIANA PUBLIC SERVICE CO | AUTOMOBILE VEERED OFF ROAD AND STRUCK SERVICE LINE AND METER CAUSING GAS TO LEAK. GAS IGNITED AND BURNED HOUSE AND AUTOMOBILE. AUTOMOBILE DRIVER KILLED. THE HOUSE WAS NOT OCCUPIED AT THE TIME OF THE INCIDENT. | 70000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2668 | 2002-12-31 | OK | other | PHILLIPS | KANSAS GAS SERVICE | SEE PART D - OTHER | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2669 | 2002-12-31 | AZ | ACCIDENTALLY CAUSED BY OPERATOR | MUELLER | SOUTHWEST GAS CORP | SEE PART D | 70000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2670 | 2003-01-02 | AR | ACCIDENTALLY CAUSED BY OPERATOR | UNKNOWN | RELIANT ENERGY ARKLA, DIV OF RELIANT ENERGY RESOUR | GAS IGNITION CAUSED BY CIGARETTE LIGHTER USE DURING A MAIN LEAK REPAIR. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2671 | 2002-09-20 | CO | other |  | K N ENERGY INC(KANSAS NEBRASKA GAS CO) (KMI) |  | 3500000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2672 | 2003-01-17 | PA | other | CRANE | EQUITABLE RESOURCES (A.K.A EQUITABLE GAS CO) | EQUITABLE GAS HAS DETERMINED A CONTRIBUTING FACTOR TO BE LEAKAGE FROM A CRACK ON A 12" MAIN LINE VALVE LOCATED APPROXIMATELY 100 FEET FROM THE CORNER OF THE BUILDING AT 2146 RHINE STREET. | 500000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2673 | 2003-02-05 | AK | other |  | ENSTAR NATURAL GAS CO | ON TUESDAY EVENING, FEBRUARY 4, 2003 AT APPROXIMATELY 10:50 PM AST, ENSTAR NATURAL GAS COMPANY WAS NOTIFIED BY THE BUTTE FIRE DEPARTMENT OF A FIRE AT 1676 BODENBURG LOOP, EAST OF PALMER ALASKA. AN ENSTAR SERVICEMAN WAS DISPATCHED TO THE SCENE. UPON ARRI | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2674 | 2003-01-23 | MN | other | CONTINENTAL IND | GREAT PLAINS NATURAL GAS CO | THE APPARENT CAUSE OF THIS INCIDENT WAS FAILURE OF A ROCKWELL 143 VALVE BODY POSSIBLY DUE TO STRESSES CAUSED FROM SETTLEMENT/FROST OR OTHER PIPE MOVEMENT IN CONJUNCTION WITH SUB-ZERO TEMPERATURES. THE VALVE WAS CAST IRON AND HOUSED IN A VALVE BOX IN AN A | 500000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2675 | 2003-01-27 | WV | other | UNKNOWN | BLUEFIELD GAS CO | BLUEFIELD GAS COMPANY IS SERVED BY 2 HIGH-PRESSURE GAS MAINS FROM ITS PRICENTON, WV GATE STATION WITH COLUMBIA GAS. THE TWO LINES COME TOGETHER AND GAS IS CARRIED BY A ONE 10-INCH GAS MAIN APPROXIMATELY 1 1/2 MILES LONG. FURTHER DOWNSTREAM THIS 10-INCH | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2676 | 2003-02-02 | VT | other | US MANUFACTURER | VERMONT GAS SYSTEMS INC | A LARGE SEGMENT OF ICE/SNOW SLID OFF THE ROOF OF A TWO STORY BUILDING. IT STRUCK A SING METER SET AND SHEARED A THREADED PIPE NIPPLE ON THE RISER BETWEEN THE SHUT-OFF VALVE AND REGULATOR. THE ESCAPING GAS IGNITED FROM AN UNKNOWN IGNITION SOURCE AND THE | 175000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2677 | 2003-01-16 | PA | other | MAVERICK | DOMINION PEOPLES | THE INLET LINE TO REGULATOR STATION (XS-320) BECAME FROZEN AND BLOCKED OFF, THIS RESULTED IN A SERVICE OUTAGE TO 3,217 CUSTOMERS. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2678 | 2003-01-26 | NC | other |  | PUBLIC SERVICE CO OF NORTH CAROLINA | DRIVER LOST CONTROL OF VEHICLE, RAN OFF STREET, AND CRASHED INTO SIDE OF SINGLE FAMILY DWELLING DAMAGING DOMESTIC METER SET AND CAUSING FIRE. | 175000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2679 | 2003-01-18 | MN | other | UNKNOWN (OLMSTED COUNTY) | PEOPLES NATURAL GAS | 2 INCH STEEL MAIN HAD BEEN HIT, GOUGED, AND BURIED DURING SUMMER SEWER AND WATER CONSTRUCTION CAUSING A STRESS AREA ON THE PIPE. WINTER FROST CONDITIONS CAUSED THE PIPE TO CRACK IN THE GOUGE AND SEPARATE CAUSING A NATURAL GAS LEAK. | 30000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2680 | 2003-01-28 | OH | other | OIL CREEK | COLUMBIA GAS OF OHIO INC | AMERICAN ELECTRIC POWER (AEP) WAS INSTALLING A SHRINK WRAP WHILE REPAIRING AN ELECTRIC LINE WHEN THEY BURNED THROUGH THE CUSTOMERS GAS SERVICE LINE WITH A PROPANE TORCH, CAUSING AN IGNITION AND FIRE. THE ELECTRIC LINE REQUIRED REPAIR BECAUSE A COLUMBIA GA | 55000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2681 | 2003-02-04 | TX | other | UPONOR | ENTEX, A NORAM ENERGY COMPANY (FORM. DIV OF ARKLA | THIRD PARTY DAMAGED .5 INCH I.P. POLY SERVICE LINE WITH A TRENCHER. ESCAPING GAS WAS IGNITED, DAMAGING TRENCHER AND A NEW HOUSE. | 107810 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2682 | 2003-01-30 | IL | other | UNKNOWN | NORTH SHORE GAS CO | WATER SERVICE CONTRACTOR HIT PROPERLY MARKED AND EXPOSED GAS SERVICE SEPARATING IT FROM THREADED RISER FITTING. | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2683 | 2003-02-05 | GA | other | UNKNOWN | ATLANTA GAS LIGHT CO | AN EXCAVATOR RUPTURED A 12" HP STEEL NATURAL GAS MAIN WHILE BORING A 24" CASING UNDERNEATH HWY 9 FOR A FUTURE WATER LINE. LOCATE MARKINGS WERE PRESENT AND WITHIN THE LOCATE TOLERANCE ZONE (24"). THE GAS MAIN WAS NOT SPOTTED BY THE EXCAVATOR AND THERE WA | 99158 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2684 | 2003-02-04 | PA | other |  | PHILADELPHIA GAS WORKS | ON FEBRUARY 4, 2003 AT 1617HR A NATURAL GAS EXPLOSION OCCURRED AT THE RESIDENTIAL HOME OF 1200 LONGSHORE AVENUE, PHILADELPHIA, PA. PHILADELPHIA FIRE DEPARTMENT (PFD), IN RESPONSE TO AN ODOR COMPLAINT, ARRIVED ON SCENE SHORTLY BEFORE PGW EMPLOYEES AND EVA | 200000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2685 | 2003-02-20 | NE | other |  | METROPOLITAN UTILITIES DISTRICT | NONE | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2686 | 2003-02-12 | PA | other | UNKNOWN (YORK COUNTY) | COLUMBIA GAS OF PENNSYLVANIA | THIS INCIDENT RESULTED IN THE INJURY TO THREE PEOPLE, TWO ADULTS AND ONE CHILD, WHO RECEIVED FIRST AND SECOND DEGREE BURNS TO THE HANDS, ARMS, AND CHEST ON THE AFOREMENTIONED DATE. THEY WERE TAKEN TO JOHN HOPKINS BAYVIEW MEDICAL BURN UNIT FOR TREATMENT. N | 250000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2687 | 2003-02-09 | RI | other |  | NEW ENGLAND GAS COMPANY | A MAIN FAILURE OCCURRED FROM POSSIBLE SOIL SUBSIDENCE RESULTING IN GAS MIGRATION INTO A BUILDING, PROBABLY THROUGH A FRENCH DRAIN, WITH GAS IGNITION FROM AN UNKNOWN SOURCE. | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2688 | 2003-01-21 | OR | technical failure | UNKNOWN | AVISTA UTILITIES | AN AVISTA CREW WAS REPAIRING A LEAKING 3/4" SERVICE TEE ON A 2" STEEL MAIN. WHEN IT WAS DETERMINED THAT THE TAPPER IN THE TEE WAS NOT FUNCTIONAL AND AFTER ATTEMPTING UNSUCCESSFULLY TO CONTROL THE LEAKS BY ARC WELDING THE TEE, THE CREW DECIDED TO REDIRECT | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2689 | 2003-02-01 | TX | other | UPONOR | ENTEX, A NORAM ENERGY COMPANY (FORM. DIV OF ARKLA | THIRD PARTY DAMAGED 2" I.P. POLY MAIN WITH A TRENCHING MACHINE AND ESCAPING GAS WAS IGNITED. DAMAGING NEW HOUSE AND TRENCHER. | 45000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2690 | 2003-02-22 | MD | other | UNKNOWN (nan COUNTY) | BALTIMORE GAS & ELECTRIC CO | BALTIMORE CITY FIRE DEPARTMENT REPORTED EXPLOSION AT 2739 EAST CHASE STREET AT 23:32. METERS WERE OFF BY THE TIME THE OPERATORS FIRST RESPONDERS ARRIVED ON-SCENE (15 MINUTES LATER). SERVICE TO 2739 COMES FROM 6" LOW PRESSURE GAS MAIN LOCATED APPROXIMATELY | 150000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2691 | 2003-02-13 | MA | other | PERFECTION | BERKSHIRE GAS CO | ON THURSDAY, FEBRUARY 13TH AT APPROXIMATELY 1:50 A.M., BERKSHIRE GAS DISPATCH CENTER RECEIVED A CALL FROM THE TURNERS FALLS POLICE DEPARTMENT REPORTING A FIRE AND EXPLOSION AT THE ABOVE REFERENCED LOCATION. BERKSHIRE IMMEDIATELY DISPATCHED "ON-CALL" PERSO | 450000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2692 | 2003-02-25 | GA | other | UNKNOWN | ATLANTA GAS LIGHT CO | AN EXCAVATOR RUPTURED A 6" HP STEEL NATURAL GAS MAIN WITH A TRACK HOE WHILE CLEANING OUT A RETENTION POND. THE ESCAPING GAS DID NOT IGNITE. | 62277 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2693 | 2003-02-27 | NJ | other | UNKNOWN (MIDDLESEX COUNTY) | ELIZABETHTOWN GAS CO | A FEW MINUTES BEFORE 3:00 A.M. AN AUTOMOBILE WAS DRIVEN INTO A HIGH PRESSURE METER SET THAT FED A FIRST FLOOR LAUNDROMAT IN A 3-STORY BUILDING CAUSING A GAS LEAK. PERTH AMBOY POLICE AND FIRE DEPARTMENTS RESPONDED AND EVACUATED 13 BUILDING TENANTS AT THE I | 1000000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2694 | 2003-02-28 | MI |  |  | MICHIGAN CONSOLIDATED GAS CO (MICHCON) | PRIMARY IGNITION OF MIGRATING NATURAL GAS EMANATING FROM SERVICE LINE AS A RESULT OF DAMAGE DURING INSTALLATION, | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2695 | 2003-03-16 | MI | other | UNKNOWN (WAYNE COUNTY) | MICHIGAN CONSOLIDATED GAS CO (MICHCON) | PRIMARY IGNITION OF NATURAL GAS AS A RESULT OF MAIN BREAK | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2696 | 2003-03-11 | PA | other | UNKNOWN (ARMSTRONG COUNTY) | EQUITABLE RESOURCES (A.K.A EQUITABLE GAS CO) | A PRODUCTION WELL, NOT OWNED BY EQUITABLE, HAD A CASING LEAK. MIGRATING GAS FROM THE CASING WAS A CONTRIBUTING FACTOR TO THE INCIDENT. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2697 | 2003-03-14 | OR | other |  | NORTHWEST NATURAL GAS CO | A PORTLAND GENERAL ELETRIC (PGE) CREW WAS WORKING IN THE APPALOOSA COURT AREA PRIOR TO THE INCIDENT DUE TO A POWER OUTAGE THAT OCCURRED AT ABOUT MIDNIGHT. SHORTLY BEFORE THE INCIDENT, A NEARBY RESIDENT NOTIFIED THE PGE CREW THAT HE SMELLED NATURAL GAS. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2698 | 2003-03-03 | PA | other |  | COLUMBIA GAS OF PENNSYLVANIA | THE REGULATOR AT THE EMIGSVILLE TAKE STATION FROZE UP, CAUSING DOWN STREAM LOSS OF PRESSURE TO RED LION, DALLASTOWN, YOE, AND WINDSOR IN YORK COUNTY. APPROX. 7000 CUSTOMERS WERE AFFECTED. THE COMPANY IS CURRENTLY WORKING WITH THE PUBLIC UTILITY COMMISSI | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2699 | 2003-03-16 | AZ | other | DUPONT | SOUTHWEST GAS CORP | SEE PART D | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2700 | 2003-03-09 | MO | other | UNKNOWN | MISSOURI GAS ENERGY | THIRD PARTY ACTIVITY REMOVED SUPPORT FROM BENEATH A SIX INCH CAST IRON MAIN. A HOLE FILLED WITH GRAVEL AND SAND ALLOWED GAS TO MIGRATE. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2701 | 2003-03-17 | CA | other | UNKNOWN (LOS ANGELES COUNTY) | SOUTHERN CALIFORNIA GAS CO | VEHICLE LEFT RUNNING AND UNATTENDED. VEHICLE TRAVELED ACROSS DRIVEWAY, OVER CURB, AND STRUCK RISER WALL IN CARPORT, CAUSING GAS ESCAPE. VEHICLE AND CARPORT CAUGHT FIRE. EIGHTY TWO YEAR OLD MALE ENTERED BURNING VEHICLE FROM THE REAR DRIVER-SIDE DOOR, WA | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2702 | 2003-03-14 | AK | other | DRISCOPIPE | ENSTAR NATURAL GAS CO | ON FRIDAY MORNING, MARCH 14, 2003 AT APPROX 0106 HOURS AST, ENSTAR NATURAL GAS COMPANY WAS NOTIFIED BY THE PALMER FIRE DEPARTMENT OF A FIRE AT 533 E. DOLPHIN AVE; PALMER, AK. AN ENSTAR SERVICEMAN AND DUTY SUPERVISOR WERE DISPATCHED TO THE SCENE. UPON AR | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2703 | 2003-02-19 | PA | other | UNKNOWN (MONTGOMERY COUNTY) | PECO ENERGY CO | SEE PART D | 2000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2704 | 2003-04-03 | AK | other | UNKNOWN (nan COUNTY) | ENSTAR NATURAL GAS CO | ON THURSDAY AFTERNOON, APRIL 3, 2003 AT APPROXIMATELY 2:25 PM AST, AN ENSTAR NATURAL GAS COMPANY SERVICE TECHNICIAN NOTICED SMOKE IN THE AIR FROM A STRUCTURE FIRE. UPON INVESTIGATION, THE SERVICE TECHNICIAN FOUND LOCAL FIRE FIGHTERS FIGHTING A RESIDENTIA | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2705 | 2003-04-07 | AK | other | UNKNOWN (nan COUNTY) | ENSTAR NATURAL GAS CO | SEE PART D | 150000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2706 | 2003-04-09 | CA | other | UNKNOWN (SOLANO COUNTY) | ISLAND ENERGY | CONTRACTOR TRENCHING ACROSS GAS LINE FOR IRRIGATION (WATER) LINE. | 3000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2707 | 2003-03-23 | OK | other | PHILLIPS | OKLAHOMA NATURAL GAS CO |  | 90000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2708 | 2003-03-19 | KS | other | UNKNOWN (SEDGWICK COUNTY) | CHENEY MUNICIPAL UTILITY | A 1" DIAMETER SERVICE LINE PIPE BROKE ABOUT 3/4THS THE WAY THROUGH. PIPE WAS ABOUT 4 FOOT DEEP. THE CITY HAD EXPERIENCE HEAVY RAIN FOR 3 DAYS PRIOR TO THE BREAK. THE 1" PIPE HAD BEEN STRUCK BY CONSTRUCTION EQUIPMENT PROBABLY AROUND 1961 OR 1962. THE A | 175000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2709 | 2003-03-16 | MI | other | ECLIPS | CONSUMERS ENERGY CO | ON 3/16/03 AT 0652 HOURS. A PASSERBY HEARD HISSING COMING FROM THE METER LOCATION AT 5966 HORTON ROAD IN JACKSON, MI. A CONSUMERS ENERGY GAS SERVICE WORKER (GSW) WAS DISPATCHED TO THE ADDRESS. UPON ARRIVAL, THE GSW ATTEMPTED TO NOTIFY THE HOMEOWNER THAT | 200000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2710 | 2003-04-12 | MI | other | UNKNOWN (ROSCOMMON COUNTY) | MICHIGAN CONSOLIDATED GAS CO (MICHCON) | APPLIANCE VALVE FOR GAS FIRED CLOTHES DRYER FOUND IN OPEN POSITION PROVIDING NATURAL GAS RESULTING IN AN EXPLOSION AND RESULTING IN A FIRE. | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2711 | 2003-04-03 | VA | other | DRISCO 6500 | COLUMBIA GAS OF VIRGINIA INC |  | 200000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2712 | 2003-04-12 | WA | other | N/R | PUGET SOUND ENERGY | ELECTRIC FAULT CURRENT ENERGIZED STEEL GAS MAIN AND COPPER WATER SERVICE "WELDING" THEM TOGETHER AT POINT WHERE WATER CONTACTED GAS MAIN. WATER FLOWED INTO GAS SYSTEM CAUSING LOSS OF SERVICE TO ABOUT 360 CUSTOMERS. COST TO CLEAN SYSTEM, SERVICES, AND ME | 125683 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2713 | 2003-03-31 | LA | other | UPONOR | ENTEX, A NORAM ENERGY COMPANY (FORM. DIV OF ARKLA | TRENCHING WITHOUT CALLING LA ONE CALL FOR A UTILITY LINE LOCATE. | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2714 | 2003-04-23 | IL | other |  | NORTHERN ILLINOIS GAS CO | PLUMBING CONTRACTOR WAS EXCAVATING TO INSTALL WATER AND SEWER SERVICE LINES TO A HOME UNDER CONSTRUCTION. 2" STEEL MAIN WAS DAMAGED, CAUSING A LEAK DOWNSTREAM OF THE DAMAGE. GAS MIGRATED ACROSS THE STREET AND CAUSED EXPLOSION. | 3000000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2715 | 2003-04-27 | NC | other |  | PUBLIC SERVICE CO OF NORTH CAROLINA | DRIVER LOST CONTROL OF VEHICLE, RAN OFF ROAD AND INTO RESIDENTIAL DUPLEX DWELLING DAMAGING DOMESTIC METER SET AND IGNITING THE LEAKING GAS. VEHICLE AND RESIDENTIAL STRUCTURE DAMAGED BY FIRE. | 90000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2716 | 2003-05-03 | PA | other |  | EQUITABLE RESOURCES (A.K.A EQUITABLE GAS CO) | THE RESULTS OF EXTENSIVE TESTING OF EQUITABLE GAS FACILITIES IN THE INCIDENT AREA INDICATE EQUITABLE GAS FACILITIES WERE NOT A CONTRIBUTING FACTOR. A PRODUCTION WELL, NOT OWNED BY EQUITABLE GAS, IS CURRENTLY UNDER INVESTIGATION AS A POSSIBLE CONTRIBUTING | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2717 | 2003-04-28 | SD | other | UNIVERSAL CONTROLS | NORTHWESTERN PUBLIC SERVICE CO | THE FIRE REPORTS INDICATES AT 9:15 AM JOHN BERGER AT 207 GRANT STREET NOTIFIED THE CLARK FIRE DEPARTMENT OF A FIRE AT 205 GRANT STREET. THE HOMEOWNERS, JERI AND LEE TERVEEN, OF 205 GRANT STREET WERE NOT HOME AT THE TIME OF THE INCIDENT. EMERGENCY CREWS | 68500 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2718 | 2003-05-13 | GA | other | UNKNOWN | ATLANTA GAS LIGHT CO | AN EXCAVATOR RUPTURED A 2.5" HP STEEL NATURAL GAS MAIN WITH A LOADER WHILE DEMOLISHING AN OLD BUILDING. THE ESCAPING GAS DID NOT IGNITE. THIS RESULTED IN THE LOSS OF GAS SERVICE TO 1100 CUSTOMERS. | 148616 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2719 | 2003-05-09 | OK | other |  | OKLAHOMA NATURAL GAS CO | ON MAY 9, 2003, AT APPROXIMATELY 9:30 P.M. THROUGH 11:30 P.M., A STORM THAT GENERATED TORNADO STRUCK CENTRAL OKLAHOMA, AND MOST OF THE DAMAGE WAS LIMITED TO OKLAHOMA CITY, OKLAHOMA AND SURROUNDING SUBURBS. COMPLETE DEVASTATION OCCURRED TO SOME STRUCTURES | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2720 | 2003-05-08 | OK | other |  | OKLAHOMA NATURAL GAS CO | ON MAY 8, 2003, AT APPROXIMATELY 5:30 P.M., A STORM THAT GENERATED TORNADOS STRUCK CENTRAL OKLAHOMA, AND MOST OF THE DAMAGE WAS LIMITED TO MOORE, OKLAHOMA. COMPLETE DEVASTATION OCCURRED TO SOME STRUCTURES, WHILE MANY OTHERS SUSTAINED ONLY MINOR DAMAGE. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2721 | 2003-05-05 | OH | other |  | COLUMBIA GAS OF OHIO INC | INTIAL INVESTIGATION HAS REVEALED THAT THE CAUSE OF FIRE AND EXPLOSION AT THE REFERENCED ADDRESS WAS LIKELY THE RELEASE OF NATURAL GAS; HOWEVER THE INCIDENT IS UNDER INVESTIGATION AND AS OF THE DATE OF THIS REPORT, IT IS UNKNOWN WHETHER THE SOURCE OF THE | 200000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2722 | 2003-02-15 | MI | other | PLEXCO | MICHIGAN GAS UTILITIES CO |  | 110000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2723 | 2003-05-07 | CA | other | UKNOWN | PACIFIC GAS & ELECTRIC CO | DIRECTIONAL BORING SYSTEMS INC BORED INTO A TWO-INCH PLASTIC GAS MAIN AT APPROXIMATELY 1350 HOURS ON MAY 7, 2003. LEAKING GAS ACCUMULATED IN THE ADJACENT HOME AND IT EXPLODED AT 1438 HOURS. | 415000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2724 | 2003-05-16 | MA | other |  | KEYSPAN ENERGY DELIVERY | INVESTIGATION IS ONGOING. FIRE MARSHALLS OFFICE DISCOVERED THAT A CAP WAS REMOVED FROM THE DRIP PIPE OF THE BOILER. TOOLS WERE ALSO FOUND AT THE SCENE. SERVICE LINE PASSED PRESSURE TEST BY MASSACHUSETTS DTE. DTE ALSO PLANS TO TEST REGULATORS. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2725 | 2003-05-17 | PA | maintenance | UNKNOWN | PECO ENERGY CO | SEE PART D | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2726 | 2003-05-22 | PA | other | DUPONT | PECO ENERGY CO | SEE PART D | 81000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2727 | 2003-05-05 | NM | other | UNKNOWN | PUBLIC SERVICE COMPANY OF NEW MEXICO - GAS SVCS | CAUSE OF FIRE IS CURRENTLY UNDER INVESTIGATION BY LOCAL FIRE DEPARTMENT. ARSON IS SUSPECTED DUE TO LOCATION OF POSSIBLE IGNITION FROM STACKS OF CARDBOARD BOXES ON CORNER OF BUILDING. CARDBOARD BOXES WERE LOCATED NEXT TO THE RISER AND GAS METER. THE FIR | 125000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2728 | 2003-04-14 | PA | other | UNKNOWN (LANCASTER COUNTY) | U G I CORP | TRACKHOE OPERATOR FOR BRIDGE CONTRACTOR HIT AND PUNCTURED 6" STEEL NATURAL GAS PIPELINE. OPERATOR WAS EXCAVATING FOR STORM WATER PIPE SYSTEM LOCATED ADJACENT TO GAS PIPELINE. GAS FACILITIES WERE PROPERLY MARKED. | 70598 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2729 | 2003-06-12 | TN | other | POLYPIPE | LEBANON GAS DEPT, CITY OF |  | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2730 | 2003-06-03 | LA | other |  | LOUISIANA GAS SERVICE CO | TOWN OF NORTH HODGE CONTRACTOR HIT GAS COMPANY FACILITIES CAUSING INCIDENT. | 3000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2731 | 2003-05-27 | WI | other | PLEXCO | ALLIANT ENERGY - WISCONSIN POWER & LIGHT CO | A SEWER CONTRACTOR WAS INSTALLING A NEW SANITARY LINE NEAR A NATURAL GAS PLASTIC DISTRIBUTION SYSTEM. WHILE SCRAPING OFF A LAYER OF DIRT ABOVE THE NATURAL GAS MAIN WITH A BACKHOE, THE CONTRACTOR SEVERED THE 2-INCH PLASTIC MAIN. TWO MEN ENTERED THE TRENC | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2732 | 2003-06-20 | CA | other |  | SOUTHERN CALIFORNIA GAS CO | CONTRACTOR STRUCK TWO FOOT LONG, THREE INCH STEEL STUB WHILE EXCAVATING ON BRIDGE JOB. PINCHING MAIN LINE RESULTED IN APPROXIMATELY 1000 OUTAGES. STUB WAS NOT IDENTIFIED ON ATLAS SHEET, NOT LOCATED AND MARKED. | 75000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2733 | 2003-06-28 | FL | other | LTV | TECO PEOPLES GAS LP OPERATIONS | A ROAD MIXER WAS BEING USED TO STABILIZE ROAD SUB-GRADE MATERIAL OVER A 6" (NPS) STEEL GAS MAIN. DURING THE OPERATION THE MIXER HIT THE GAS LINE, RUPTURING IT. GAS ESCAPING UNDER 50 PSIG ENGULFED THE EQUIPMENT AND OPERATOR, AND THEN IGNITED. THE OPERAT | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2734 | 2003-06-16 | AZ | technical failure | PHILLIPS DRISCO | SOUTHWEST GAS CORP | SEE PART D | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2735 | 2003-06-12 | MN | other | PLEXCO | MINNEGASCO INC |  | 18000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2736 | 2003-06-10 | IN | other | UNKNOWN | CITIZENS GAS & COKE UTILITY | CONTRACTOR WAS ATTEMPTING TO COMPACT SOIL IN AREA FOR INTERSTATE I74 RESTORATION PROJECT. CONTRACTOR APPEARS TO HAVE MADE ERROR IN MEASURING MAIN DEPTH AND BELIEVED THEY HAD SUFFICIENT CLEARANCE BUT DID NOT. THIS IS THE PRIMARY FACTOR IN THE MAIN BEING | 435000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2737 | 2003-06-16 | NM | other | UNKNOWN | PUBLIC SERVICE COMPANY OF NEW MEXICO - GAS SVCS | PNM IS PROVIDING A FOLLOW-UP WRITTEN NOTIFICATION TO THE INITIAL TELEPHONIC NOTIFICATION MADE ON JUNE 17, 2003, OF THE FATAL SINGLE CAR ACCIDENT WHICH OCCURRED ON JUNE 16, 2003, AT 47190 HWY 187 IN DERRY, NM. THE SOLE OCCUPANT OF THE VEHICLE WAS A TWENTY | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2738 | 2003-06-18 | NM | other | UNKNOWN | PUBLIC SERVICE COMPANY OF NEW MEXICO - GAS SVCS | ON JUNE 18, 2003, DURING A ROUTINE REGULATOR INSPECTION AT THE PORTALES SOUTH BORDER STATION, A GAS MEASUREMENT TECHNICIAN WAS USING A GAUGE IN A "PETES PLUG" LOCATED ON THE OUTLET VALVE SET TO MONITOR PRESSURES WHILE WORKING ON THE REGULATORS. THE GAUGE | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2739 | 2003-06-17 | UT | other | UNKNOWN (UINTAH COUNTY) | QUESTAR GAS COMPANY | THIRD PARTY CONTRACTOR HIT AND PULLED A 3/4" STEEL SERVICE LINE. A LEAK OCCURRED FURTHER DOWNSTREAM ON THE SERVICE LINE AT A COMPRESSION TYPE FITTING. THE SERVICE LINE WAS PULLED OUT OF THE COMPRESSION TYPE FITTING. THE LEAKING GAS MIGRATED INTO THE CR | 60000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2740 | 2003-06-25 | CA | other |  | PACIFIC GAS & ELECTRIC CO | A VEHICLE DRIVEN BY A THIRD PARTY VEERED OFF OF THE STREET AND SHEERED THE METER SET FROM THE RISER, CAUSING GAS TO ESCAPE. THE ESCAPING GAS IGNITED AND BURNED PART OF THE HOUSE AND TWO VEHICLES. | 360000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2741 | 2003-07-07 | MI | other |  | MICHIGAN CONSOLIDATED GAS CO (MICHCON) | CONTRACTOR STRUCK AND RUPTURED AN 8" XTC 150 PSIG NATURAL GAS MAIN. A 2" EXTRA HEAVY NIPPLE USED FOR PURGING WAS DAMAGED BY A BACKHOE. | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2742 | 2003-07-02 | DE | other | UNKNOWN | CONECTIV | INITIAL INVESTIGATION, UNDER THE DIRECTION OF NTSB, INDICATES A CONTRACTOR REPLACING CURBS AND SIDEWALK FOR THE CITY OF WILMINGTON HIT A GAS SERVICE LINE CAUSING GAS TO LEAK. AN EXPLOSION AND FIRE RESULTED. THE CONTRACTOR HAD NOT NOTIFIED THE OPERATOR T | 300000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2743 | 2003-07-03 | CA | other | DRISCO | PACIFIC GAS & ELECTRIC CO | AT 1655 HOURS ON 7/3/03, PG&E DETERMINED THAT THE PROPERTY LOSS WOULD EXCEED $50,000, AND THE INCIDENT BECAME REPORTABLE AT THAT TIME. | 105000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2744 | 2003-07-03 | KS | other | DUPONT | ATMOS ENERGY CORPORATION | EXCAVATOR WAS TILLING ROADWAY BASE ON A PUBLIC IMPROVEMENT PROJECT. EQUIPMENT WAS TURNING AROUND SOUTH OF THE ROADWAY AND CONTACTED MAIN. | 300000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2745 | 2003-06-18 | MO | other |  | SPRINGFIELD, CITY UTILITIES OF | AT APPROXIMATELY 12:08 PM ON JUNE 18, 2003 THERE WAS AN EXPLOSION AT THE FRISCO BUILDING ON THE OZARK EMPIRE FAIRGROUNDS AT 1001 W NORTON ROAD. THERE WAS ONE FATALITY. CITY UTILITIES PROCEDURES FOR NATURAL GAS EMERGENCIES WERE FOLLOWED AND THE MISSOURI | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2746 | 2003-07-18 | TX | other | UKNOWN | ENTEX, A NORAM ENERGY COMPANY (FORM. DIV OF ARKLA | THIRD PARTY DAMAGED A 1" STEEL D. R. S. WITH A VEHICLE, DAMAGING INLET RISER AND ESCAPING GAS WAS IGNITED. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2747 | 2003-01-22 | MA | other |  | KEYSPAN ENERGY DELIVERY | OUTSIDE PRESSURE FROM FROST CAUSED A CRACK IN GAS MAIN. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2748 | 2003-08-06 | VA | other |  | RICHMOND DEPT OF PUBLIC UTILITIES, CITY OF | INDIVIDUAL WAS DRIVING A PICK-UP TRUCK THE WRONG WAY DOWN ONE-WAY STREETS (FLOYD & BERRINGTON) TRAVELING SEVERAL BLOCKS. HE CROSSED A FOUR LANE DIVIDED HIGHWAY, LEFT THE RIGHT-OF-WAY OF THE ROAD, WENT APPROXIMATELY 300 FT THROUGH THE YARD, AND STRUCK A T | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2749 | 2003-07-23 | MO | other |  | PERRYVILLE MUNICIPAL SYSTEM, CITY OF |  | 59117 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2750 | 2003-07-28 | CA | other | UNKNOWN | PACIFIC GAS & ELECTRIC CO | A TREE BRANCH BROKE AND FELL, STRIKING AND DAMAGING THE GAS METER CREATING A LEAK. A STRUCTURE FIRE ALSO RESULTED FROM DAMAGE CAUSED BY THE FALLING BRANCH. THE SOURCE OF IGNITION OF THE FIRE IS UNKNOWN. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2751 | 2003-08-06 | GA | other | DRISCOPLEX | ATLANTA GAS LIGHT CO | PLUMBING CONTRACTOR WAS SWEATING A FITTING ON A 2" COPPER WATER SERVICE WITH A PROPANE TORCH IN A DITCH WITH THE 1 1/4" PLASTIC NATURAL GAS SERVICE EXPOSED. THE PLUMBER INADVERTENTLY BROUGHT THE TORCH TOO CLOSE TO THE NATURAL GAS SERVICE THUS MELTING AND | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2752 | 2003-08-12 | NM | other | UNKNOWN | PUBLIC SERVICE COMPANY OF NEW MEXICO - GAS SVCS | DRIVER OF A SOUTHBOUND VEHICLE SWERVED TO MISS A DOG AND LOST CONTROL OF VEHICLE. VEHICLE LEFT ROAD AND HIT A SINGLE LOOP GAS METER. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2753 | 2003-08-13 | AZ | other | CABOT PIPING SYSTEM | UNISOURCE ENERGY SERVICES | PLUMBER PROPANE WELDING IN BOTTOM OF BELL HOLE WITH NATURAL GAS SERVICE LINE LOCATED ABOVE. HEAT FROM PROPANE WELDING BURNED HOLE IN PVC SERVICE LINE RESULTING IN NATURAL GAS IGNITION AND FLASH BURN TO PLUMBER. PLUMBER WAS TREATED AND RELEASED FROM LOCA | 1500 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2754 | 2003-07-31 | PA | other |  | COLUMBIA GAS OF PENNSYLVANIA | THIRD PARTY CONTRACTOR, KUKURIN CONSTRUCTION, WHILE WORKING ON INSTALLING SEWER LINE, SEVERED AND PULLED THE 1 1/4" STEEL NATURAL GAS SERVICE LINE TO 156 SHAFFER DRIVE, WHICH IN TURN PULLED THE SERVICE LINE COUPLING AT THE METER APART, AND WHICH ALSO PULL | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2755 | 2003-08-11 | NC | other | EQUIMETER | PUBLIC SERVICE CO OF NORTH CAROLINA | THE METER WAS DAMAGED WHEN AN UNOCCUPIED VEHICLE ROLLED INTO THE METER SET BREAKING THE SERVICE BELOW THE SERVICE SHUT-OFF. THE ESCAPING GAS WAS IGNITED CAUSING THE VEHICLE TO BURN AND IGNITING THE SIDE OF THE BUILDING. THE VEHICLE WAS A TOTAL LOSS AND | 116000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2756 | 2003-09-02 | AK | other | DRISCOPIPE | ENSTAR NATURAL GAS CO | ON TUESDAY AFTERNOON, SEPTEMBER 2, 2003 AT APPROXIMATELY 12:50 PM ADT, ENSTAR NATURAL GAS COMPANY WAS NOTIFIED BY THE ANCHORAGE FIRE DEPARTMENT (AFD) OF A GAS MAIN BREAK AND FIRE AT THE CORNER OF DENALI STREET AND BENSON BLVD IN ANCHORAGE, ALASKA. SERVIC | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2757 | 2003-05-14 | MI | other |  | MICHIGAN CONSOLIDATED GAS CO (MICHCON) | CONTRACTOR STRUCK AND RUPTURED 6" STEEL NATURAL GAS MAIN # 150 PSIG. | 69000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2758 | 2003-08-04 | NJ |  | X-TRU | PUBLIC SERVICE ELECTRIC & GAS CO | ON MONDAY, AUGUST 4, 2003, AT APPROXIMATELY 2:10 PM THE COMPANY RECEIVED A CALL FROM THE HILLSBOROUGH POLICE DEPARTMENT REPORTING A WORKING STRUCTURE FIRE AT 432 ROYCEFIELD ROAD, AND DOWNED POWER LINES BETWEEN 173 AND 175 VALLEY ROAD, HILLSBOROUGH, NJ. A | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2759 | 2003-08-23 | PA | other | US STEEL | U G I CORP | PRIOR TO THE INCIDENT, UGI ATTENDED 4 SITE MEETINGS (JUNE 4TH, JULY 11TH, JULY 24TH, AND AUGUST 12TH 2003), ALL OF WHICH WERE ATTENDED BY A REPRESENTATIVE OF THE BUILDER (JAINDL) AND TWO OF WHICH WERE ATTENDED BY A REPRESENTATIVE OF THE EXCAVATOR (LIVENGO | 135000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2760 | 2003-08-01 | TX | other | DRISCOPLEX | TXU GAS DISTRIBUTION | A NON-ONCOR CONTRACTOR INSTALLING A SPRINKLER SYSTEM CUT A SERVICE LINE. THE ESCAPING GAS IGNITED. THE TRENCHER WAS DESTROYED IN THE FIRE AND A HOUSE WAS DAMAGED, | 103000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2761 | 2003-08-06 | TX | other |  | ENERGAS CO | CUSTOMERS COPPER TUBING TO THE WATER HEATER WAS CUT, RELEASING GAS INTO THE RESIDENCE. THE RELEASED GAS IGNITED RESULTING IN A EXPLOSION. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2762 | 2003-08-11 | TX | other |  | ENERGAS CO | COPPER GAS LINE SOLDER JOINT BROKE ALLOWING GAS TO ESCAPE UNDER AND INTO THE HOUSE. ACCUMLATED GAS IGNITED CAUSING AN EXPLOSION AND SUBSEQUENT FIRE. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2763 | 2003-08-28 | IL | other |  | NORTHERN ILLINOIS GAS CO | FIRE DAMAGED 2 METER SETS. NATURAL GAS IGNITED. UNITS WERE MODELS FOR NEW SUBDIVISION. CAUSE OF FIRE UNKNOWN. | 800000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2764 | 2003-09-13 | IL | other |  | NORTHERN ILLINOIS GAS CO | DRIVER LOST CONTROL OF VEHICLE STRIKING A HOUSE AND THE METER SET. THE METER SET WAS DAMAGED. NATURAL GAS WAS RELEASED BUT THERE WAS NO IGNITION. FATALITY RESULTED FROM THE IMPACT OF THE VEHICLE ACCIDENT AND WAS NOT RELATED TO THE RELEASE OF THE NATURA | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2765 | 2003-09-13 | LA | other | UNKNOWN (EAST BATON ROUGE COUNTY) | GULF STATES UTILITIES CO | PUBLIC STRUCK METER SET WITH VEHICLE (FLED SCENE) | 150000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2766 | 2003-10-06 | AL | other | UNKNOWN | MOBILE GAS SERVICE CORP |  | 2000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2767 | 2003-09-15 | NJ | other |  | PUBLIC SERVICE ELECTRIC & GAS CO | ON MONDAY, SEPTEMBER 15, 2003, AT APPROXIMATELY 2:48 PM THE COMPANY RECEIVED A CALL FROM THE CHATHAM FIRE DEPARTMENT REPORTING A DAMAGED GAS MAIN AT RIVER ROAD NEAR BRIDGE AVENUE, CHATHAM, NJ. A DISTRIBUTION SUPERVISOR WAS IMMEDIATELY DISPATCHED, ARRIVED | 95000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2768 | 2003-09-26 | MD | other |  | BALTIMORE GAS & ELECTRIC CO |  | 250000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2769 | 2003-09-24 | IL | other |  | NORTHERN ILLINOIS GAS CO | FIRE DAMAGED TWO METER SETS. NATURAL GAS IGNITED. COMPANY INVESTIGATION INDICATES INCIDENT RESULTED FROM A BROKEN BELOW GROUND CUSTOMER OWNED FUEL LINE FEEDING A GAS GRILL. SOURCE OF IGNITION IS UNKNOWN. | 500000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2770 | 2003-10-11 | AK | other | DRISCOPLEX HDPE | ENSTAR NATURAL GAS CO | ON SATURDAY MORNING, OCTOBER 11, 2003 AT APPROXIMATELY 1:30 AM ADT, ENSTAR NATURAL GAS COMPANY WAS NOTIFIED OF A STRUCTURE FIRE AT LOT 9, BLOCK 5 MOOSE RANGE MEADOW, ON KEYSTONE DRIVE NEAR SOLDOTNA, ALASKA. AN ENSTAR SERVICEMAN WAS DISPATCHED TO THE SCEN | 150000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2771 | 2003-10-07 | DC | other | UNKNOWN | WASHINGTON GAS LIGHT CO | A DEMOLITION CONTRACTOR WAS EXCAVATING AT 901 23RD STREET NW AND STRUCK A THREE INCH GAS PIPELINE CAUSING A LEAK. A VEHICLE DRIVING NORTH ON 23RD STREET BROKE DOWN (STALLED ENGINE) IN THE VICINITY OF THE GAS LEAK. SEVERAL PEOPLE, INCLUDING THE PERSONNE | 10000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2772 | 2003-10-18 | MI | other |  | MICHIGAN CONSOLIDATED GAS CO (MICHCON) | CUSTOMER EXCAVATING STRUCK AND RUPTURED NATURAL GAS SERVICE LINE. THERE WAS A RELEASE AND IGNITION OF NATURAL GAS WITH FIRE RESULTING. MISS DIG WAS NOT CALLED. | 65000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2773 | 2003-10-22 | TX | other | UNKNOWN | TEXAS GAS SERVICE COMPANY | A SUB-CONTRACTOR WORKING FOR HARRIS CONSTRUCTION WAS EXCAVATING PARALLEL TO AN EXISTING 14-INCH MAIN AS PART OF A MAIN REPLACEMENT PROJECT WHEN THE WALL OF THE TRENCH SHIFTED RESULTING IN THE MOVEMENT OF THE EXISTING MAIN. A DRESSER FITTING LOCATED ON TH | 55009 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2774 | 2003-10-23 | MI | other |  | MICHIGAN CONSOLIDATED GAS CO (MICHCON) | CAUSE OF EXPLOSION UNKNOWN. STILL UNDER INVESTIGATION. SCENE SPOILED DUE TO FIRE DEPARTMENT ORDERED DOZER WITH FRONT-END LOADER TO KNOCK DOWN REMAINING WALLS. | 150000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2775 | 2003-10-22 | NY | other |  | CENTRAL HUDSON GAS & ELECTRIC CORP | ARGENIO BROTHERS, A NEWBURGH, NY CONTRACTOR WORKING FOR THE TOWN OF CORNWALL NEAR THE CURB LINE ON FIRTH STREET, STRUCK 3/4" GALVANIZED STEEL NATURAL GAS SERVICE PIPE FEEDING 20 HIGHLAND AVENUE. THE 30 PSIG MAOP SERVICE LINE WAS PULLED THROUGH THE BASEME | 300000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2776 | 2003-10-30 | AK | other |  | ENSTAR NATURAL GAS CO | ON THURSDAY MORNING, OCTOBER 30, 2003 AT APPROXIMATELY 8:38 AM AST, ENSTAR NATURAL GAS COMPANY WAS NOTIFIED OF A STRUCTURE FIRE AT LOT 3, BLOCK 1 GOLD RUSH ESTATES, ON LUCKY SHOT LANE NEAR WASILLA, ALASKA. AN ENSTAR SERVICEMAN WAS DISPATCHED TO THE SCENE | 150000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2777 | 2001-08-30 | DC | other | UNKNOWN | WASHINGTON GAS LIGHT CO | CAPITAL PAVING COMPANY PLOWED OVER APPROXIMATELY 150 FEET OF 4-INCH CAST IRON MAIN WITH A HOE RAM WHILE IN THE PROCESS OF BREAKING CONCRETE FOR A CURB AND GUTTER REPLACEMENT. THERE WAS NO MISS UTILITY TICKET NOR WERE THERE ANY MARKS INDICATING THE LOCATI | 51000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2778 | 2003-11-19 | AL | other | DRISCOPIPE | ALABAMA GAS CORP (EX. MARENGO CORP PROPERTY) | C&M CONSTRUCTION, A CABLE TELEVISION CONTRACTOR, MAKING A DIRECTIONAL DRILL IN ASH GROVE LANE DRILLED INTO ALABAMA GAS 4" PLASTIC MAIN LOCATED IN FOREST GLENN BLVD. SUBSEQUENTLY, ALABAMA GAS WORK FORCES WERE DISPATCHED TO THE LEAK AREA. WHILE ALABAMA GA | 4565 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2779 | 2003-11-19 | VA | other | PERMASERT | VIRGINIA GAS DISTRIBUTION CO. |  | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2780 | 2003-11-01 | PA | other |  | COLUMBIA GAS OF PENNSYLVANIA | MOLLY FITZGERALD WAS DRIVING AN ATV (PLATE #40309) ON COLUMBIA GAS PRIVATE PROPERTY, WITH TWO PASSENGERS LINDSAY GASPER & ABBY PERZA. THE ATV STRUCK AN ABOVE GROUND 4 INCH GATE VALVE THAT WAS STICKING OUT OF THE GROUND 3 FEET, CAUSING A LEAKAGE TO VALVE | 10000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2781 | 2003-11-02 | MD | other |  | BALTIMORE GAS & ELECTRIC CO | BALTIMORE CITY FIRE DEPARTMENT CALLED FOR ASSISTANCE WITH STRONG ODOR OF GAS AT 557 CHALCOT SQUARE AT 17:23. THEY CALLED BACK AT 17:30 TO REPORT AN EXPLOSION AT THE SAME ADDRESS WITH TWO FIREMEN TRAPPED IN THE RUBBLE. THE OPERATORS FIRST RESPONDER ARRIV | 150000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2782 | 2003-11-17 | AZ | technical failure | UNKNOWN | SOUTHWEST GAS CORP | SEE PART D | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2783 | 2003-11-09 | CA | other |  | SAN DIEGO GAS & ELECTRIC CO | CUSTOMER BACKING VEHICLE FROM BACK YARD TO SIDE OF HOUSE STRUCK METER, CAUSING BLOWING GAS. GAS IGNITED, CAUSING FIRE THAT DAMAGED ATTACHED GARAGE. NO INJURIES. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2784 | 2003-11-03 | NY | other | UNKNOWN | NIAGARA MOHAWK POWER CORP | ON 11/3/03 AT 10:12 AM, A THIRD PARTY DAMAGED A 1" CONTROL LINE IN FRONT OF THE VLIET ST. GRS #523 IN COHOES, NEW YORK. THE DAMAGE CAUSED THE STATION REGULATOR TO FAIL WIDE OPEN. AS A RESULT, THE LOW PRESSURE DISTRIBUTION SYSTEM IN COHOES WAS OVER PRESS | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2785 | 2003-11-13 | MI | other |  | MICHIGAN CONSOLIDATED GAS CO (MICHCON) |  | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2786 | 2003-11-12 | MD | other | UNKNOWN | WASHINGTON GAS LIGHT CO | UPON ARRIVAL AT THE ABOVE ADDRESS, THE FIRE WAS IN PROGRESS AND WASHINGTON GAS CUT THE GAS OFF AT THE STOPCOCK IN THE FRONT YARD. THE FIRE DEPARTMENT HAS NOT DETERMINED THE ORIGIN AND CAUSE OF THE FIRE. THE HOUSE ITSELF WAS CONSUMED BY THE FIRE AND THE | 400000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2787 | 2003-11-13 | MD | other | UNKNOWN | WASHINGTON GAS LIGHT CO | WASHINGTON GAS RECEIVED A CALL FROM THE MONTGOMERY COUNTY FIRE BOARD THAT AN ABOVE GROUND ELECTRIC LINE SPARKED A GAS LINE AND A FIRE WAS IN PROGRESS AT THIS ADDRESS. STRONG WINDS CAUSED THE ELECTRIC LINE TO SEPARATE FROM A POLE, DROP TO GROUND AND DISCHA | 170000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2788 | 2003-10-16 | IA | other | PLEXCO | MIDAMERICAN ENERGY COMPANY | THE HEAT FROM A FIRE CAUSED BY AN ELECTRICAL MALFUNCTION RESULTED IN THE PLASTIC PIPE IN THE SERVICES RISER TO MELT AND A SECONDARY GAS FIRE. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2789 | 2003-11-13 | GA | other | UNKNOWN | ATLANTA GAS LIGHT CO | AN EXCAVATOR SEVERED A 4" HP STEEL NATURAL GAS MAIN WITH A GRADING PAN WHILE REMOVING EARTH FROM A HILL ON A COMMERICAL BUILDING SITE. THE ESCAPING GAS IGNITED DESTROYING THE GRADING PAN. ALSO, A SECOND GRADER MANUVERED OUT OF CONTROL DUE TO THE INCIDENT | 875000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2790 | 2003-11-20 | FL | other |  | TECO PEOPLES GAS LP OPERATIONS |  | 500000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2791 | 2003-11-13 | MN | other | QUAIL PIPING PRODUCTS | MINNEGASCO INC |  | 52000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2792 | 2003-11-20 | NC | other | UNKNOWN (WAKE COUNTY) | PUBLIC SERVICE CO OF NORTH CAROLINA | PRIOR TO THE INCIDENT, A CONTRACTOR INSTALLING ELECTRICAL CONDUITS DISTRUBED THE COMPACTED SOIL AROUND A 6" CAST IRON GAS PIPE. THE INSTALLATION OF THE ELECTRICAL CONDUIT ALLOWED EXTERNAL STRESS FROM HEAVY STREET TRAFFIC TO BE TRANSMITTED TO THE CAST IRO | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2793 | 2003-11-11 | CA | other | UNKNOWN (CONTRA COSTA COUNTY) | PACIFIC GAS & ELECTRIC CO | THIS WAS AN ARSON FIRE AT THE WALNUT CREEK MIDDLE SCHOOL. THE FIRE STARTED IN THE DUMPSTER AND SPREAD TO THE BUILDING. THE HEAT FROM THE BURNING BUILDING MELTED SOME OF THE GAS FACILITIES, WHICH LED TO THE BLOWING GAS FLAME. THE OVERALL DAMAGE TO THE F | 750000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2794 | 2003-11-21 | MA | other |  | NSTAR GAS COMPANY | ON NOVEMBER 21, 2003 AT APPROXIMATELY 0745 HOURS NSTAR GAS RECEIVED NOTIFICATION FROM THE NEW BEDFORD FIRE DEPARTMENT OF AN EXPLOSION IN A HOUSE LOCATED AT 533 SOUTH SECOND STREET IN NEW BEDFORD. GAS DISTRIBUTION SERVICE AND SUPPLY CREWS WERE DISPATCHED | 320000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2795 | 2003-11-27 | IL | other | UNKNOWN | PEOPLES GAS LIGHT & COKE CO | DRIVER OF STOLEN CAR HIT ABOVE GROUND METER SET INSTALLATION, RISER BROKE BELOW SHUT OFF. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2796 | 2003-10-20 | CA | other |  | SOUTHERN CALIFORNIA GAS CO | CONTRACTOR REMOVING PAVEMENT WITH HEAVY EQUIPMENT, STRUCK ABANDONED SERVICE FITTING ON TOP OF MAIN. ESCAPING GAS IGNITED. SEVERELY BURNING OPERATOR. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2797 | 2003-11-28 | VA | other | UNKNOWN | WASHINGTON GAS LIGHT CO | A FIRE BEGAN IN THE REAR STORAGE AREA OF THE BUSINESS AND SPREAD TO THE GAS METER, WHERE IT MELTED THE INDEX OFF, CAUSING GAS TO LEAK. THE REGULATOR GASKET MELTED, CAUSING THE REGULATOR TO FAIL AND THE RELIEF VALVE TO VENT OUTSIDE. THE LEAKING AND BLOWI | 500000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2798 | 2003-11-29 | UT | other | REG:FISHER/METER:ROCKWELL | QUESTAR GAS COMPANY | QUESTAR PERSONNEL WERE NOTIFIED BY THE FIRE DEPARTMENT OF A RESIDENTIAL HOUSE FIRE IN PROGRESS. WHEN QUESTAR PERSONNEL ARRIVE ON SCENE THE FIRE HAD COMPLETELY INCINERATED THE METER AND HAD MELTED THE REGULATOR. THIS RESULTED IN A RELEASE OF NATURAL GAS. | 102000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2799 | 2003-12-08 | MD | other |  | BALTIMORE GAS & ELECTRIC CO | ODOR CALL RECEIVED FOR 7123 ROLLING BEND ROAD AT 8:28 AM. GAS MECHANIC WAS DISPATCHED AT 0830 AM AND ARRIVED 0853 TO FIND 7119, 7121, & 7123 INVOLVED IN MAJOR FIRE. METER CLOSETS IN ALL THREE BUILDINGS WERE DAMAGED AT THE TIME, BUT FIRE WAS BEGINNING TO | 300000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2800 | 2003-11-26 | CA | ACCIDENTALLY CAUSED BY OPERATOR | DUPONT | PACIFIC GAS & ELECTRIC CO | WHILE CREW WAS PERFORMING EMERGENCY EXCAVATION TO REPAIR GAS LEAK, DISTURBED SOIL RESULTED IN LEAK FROM SECOND, DEFECTIVELY FUSED FITTING ESCAPING GAS IGNITED. RESULTING FIRE DAMAGED BACKHOE. | 90000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2801 | 2003-12-11 | CA | other | PHILLIPS DRISCO | PACIFIC GAS & ELECTRIC CO | CONTRACTOR INSTALLING CABLE TELEVISION CONDUIT STRUCK A DISTRIBUTION SERVICE WITH A TRENCHER BECAUSE THE SERVICE WAS NOT MARKED ACCURATELY. GAS IGNITED AND TRENCHER EQUIPMENT WAS DESTROYED BY FIRE. | 130000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2802 | 2003-12-17 | PA | other | PLEXCO | PECO ENERGY CO |  | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2803 | 2003-12-11 | MO | other | CONTINENTAL | LACLEDE GAS CO | AN ASH TREE WAS PLANTED OVER THE NATURAL GAS SERVICE LINE TEE CONNECTION TO THE MAIN AT THIS LOCATION, APPARENTLY SHORTLY AFTER THE INSTALLATION OF THE SERVICE LINE. THE LARGE ROOT BALL GROWTH FROM THIS TREE CREATED A STRESS THAT PUSHED DOWN ON THE MAIN | 285000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2804 | 2003-12-05 | CT | other | FISHER GOVERNOR | CONNECTICUT NATURAL GAS CORP | ON DECEMBER 5, 2003 AT 2126 HOURS, CONNECTICUT NATURAL GAS CORPORATION (CNG) RECEIVED NOTIFICATION FROM THE TOWN OF GREENWICH FIRE DEPARTMENT OF AN ACTIVE HOUSE FIRE AT 312 DAVIS AVENUE. THERE WAS A HEAVY SNOWSTORM IN GREENWICH DURING THE INCIDENT. A CO | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2805 | 2003-12-23 | PA | other |  | COLUMBIA GAS OF PENNSYLVANIA | TERESA DUMBAUGH WAS FOUND DECEASED 12/23/2003. THERE WAS A RELEASE OF GAS FROM THE NON-JURISDICTIONAL PIPING INSIDE BUILDING AT RANGE BURNER DOWNSTREAM OF METER. NO FIRE OR EXPLOSION. CAUSE OF DEATH IS UNKNOWN. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2806 | 2004-01-20 | AL | other |  | ALABAMA GAS CORP (EX. MARENGO CORP PROPERTY) | A NATURAL BREAK IN THE BODY OF THE MAIN. | 125000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2807 | 2003-03-11 | CT | other | A. Y. MCDONALD | YANKEE GAS SERVICES CO | A VEHICLE OPERATED BY AN OCCUPANT OF THE BUILDING STRUCK EQUIPMENT STORED IN FRONT OF THE GAS METER SET. EQUIPMENT DAMAGED THE SERVICE, CAUSING A LEAK. DRIVER INJURED BY CRASH. DRIVERS HUSBAND INJURED BY THE FOLLOWING CRASH. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2808 | 2004-01-12 | ME | other | UNKNOWN | NORTHERN UTILITIES INC (ME) | AT APPROXIMATELY 4:00 PM ON 1/12/04 AN EXPLOSION OCCURRED, APPARENTLY INSIDE A BUILDING LOCATED AT 95 MAIN ST. THE FUEL WHICH EXPLODED IS NOW UNKNOWN. NORTHERN UTILITIES PERSONNEL WERE IMMEDIATELY DISPATCHED TO THIS AREA. THEY FOUND NO SIGNIFICANT GAS | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2809 | 2004-01-11 | PA | technical failure | PERFECTION | PECO ENERGY CO | A PLASTIC MECHANICAL TEE BECAME UNSEALED FROM THE MAIN RESULTING IN A RELEASE OF GAS. | 300000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2810 | 2004-01-17 | TX | other | UNKNOWN | ENTEX, A NORAM ENERGY COMPANY (FORM. DIV OF ARKLA | DAMAGED FROM OUTSIDE FORCES CAUSED DRESSER COUPLING ON A 3/4" SERVICE LINE AT 502 GARETT TO LEAK. GAS MIGRATED THROUGH PREVIOUSLY DAMAGED CUSTOMER OWNED SEWER LINE DROP. ON 1/17/04 GAS WAS IGNITED WHILE THRID PARTY CONTRACTOR WAS REPLACING SEWER LINE AT | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2811 | 2004-02-03 | RI | other | UNKNOWN (PROVIDENCE COUNTY) | NEW ENGLAND GAS COMPANY | UNUSUALLY LONG PERIODS OF EXTREME COLD TEMPERATURES GENERATED FROST CONDITIONS REACHING THE MAINS DEPTH OF APPROXIMATELY 4.5 FEET, PRESUMABLY CAUSING EARTH MOVEMENT AND RESULTING PIPE FRACTURE. | 18000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2812 | 2004-01-31 | VA | other | UNKNOWN | WASHINGTON GAS LIGHT CO | THE ROOF GUTTER ON THE HOUSE, WHICH WAS FILLED WITH ICE, FELL OFF AND SEVERED THE COPPER LINE THAT ENTERED THE HOUSE FROM THE METER BUILD UP. THE SEVERED LINE CAUSED GAS TO RELEASE WHICH WAS IDENTIFIED AS A SECONDARY CONTRIBUTOR TO THIS INCIDENT. THE OR | 400000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2813 | 2004-02-06 | AL | other | MAVERICK | ALABAMA GAS CORP (EX. MARENGO CORP PROPERTY) | SUDDEN HEAVY RAINS OF 4-5" FELL THEREBY CAUSING A RECENTLY CONSTRUCTED STATE HWY. ROADBED TO SOFTEN AND SLIDE INTO ALABAMA GAS 4" STEEL MAIN, WHICH WAS LOCATED NEAR THE TOE OF THE SLOPE. | 65000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2814 | 2004-01-23 | OH | other | CENTRAL | COLUMBIA GAS OF OHIO INC | A THIRD PARTY CONTRACTOR WAS INSTALLING WATER LINES WHEN THEY STRUCK A NATURAL GAS SERVICE TEE ON AN 8" PLASTIC MAIN LINE. A COLUMBIA GAS OF OHIO, INC. CREW RESPONDED TO THE SCENE AND SQUEEZED OFF THE 8" PLASTIC MAIN RESULTING IN AN OUTAGE TO APPROXIMATE | 85000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2815 | 2004-01-19 | NJ | other |  | ELIZABETHTOWN GAS CO | HOUSE FIRE. CAUSE UNDER INVESTIGATION. PARTS BELOW ARE NOT APPLICABLE | 150000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2816 | 2004-02-18 | SC | other | UNKNOWN | PIEDMONT NATURAL GAS CO INC | PLEASE SEE PART B | 1000000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2817 | 2004-01-26 | AL | other | UNKNOWN | MOBILE GAS SERVICE CORP | VEHICLE LEFT ROADWAY AND DAMAGED PIPE AT RISER WHERE PIPELINE TRANSITIONS FROM UNDERGROUND TO ABOVEGROUND TO TRAVERSE THE BRIDGE. | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2818 | 2004-02-07 | RI | other | UNKNOWN | NEW ENGLAND GAS COMPANY | UNUSUALLY LONG PERIODS OF EXTREME COLD TEMPERATURES GENERATED FROST CONDITIONS REACHING THE MAINS DEPTH OF APPROXIMATELY 4.5 FEET, PRESUMABLY CAUSING EARTH MOVEMENT AND RESULTING PIPE FRACTURE. | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2819 | 2004-01-31 | IL | technical failure | UNKNOWN | NORTHERN ILLINOIS GAS CO | GAS FROM LEAK ON 6" STELL MAIN MIGRATED ACROSS THE STREET CAUSING A SMALL EXPLOSION AND SUBSEQUENT FIRE. NO INJURIES, NO FATALITIES. NOTE: THIS INCIDENT WAS ORIGINALLY REPORTED BY PHONE TO THE NRC AS 306 FARRELL ROAD, LOCKPORT | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2820 | 2004-02-02 | AZ | technical failure | PHILLIPS | SOUTHWEST GAS CORP | SEE PART D | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2821 | 2004-01-25 | PA | other | UNKNOWN | EQUITABLE RESOURCES (A.K.A EQUITABLE GAS CO) | THE INCIDENT IS CURRENTLY UNDER INVESTIGATION TO DETERMINE IF EQUITABLE GAS FACILITIES WERE A CONTRIBUTING FACTOR. | 60000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2822 | 2004-01-13 | PA | other |  | PHILADELPHIA GAS WORKS | ON FEBRUARY 12, 2004 AT 2355, THE PHILADELPHIA WATER DEPARTMENT DISPATCHER (KING) NOTIFIED PHILADELPHIA GAS WORKS DISPATCHER (R. ROSAS) OF A BROKEN WATER MAIN AT OLNEY AND OGONTZ AVENUE. AT 1:00 AM ON FEBRUARY 13, 2004, A GAS WORKS CREW LEAD BY WILLIAM W | 75000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2823 | 2004-02-06 | MD | other |  | WASHINGTON GAS LIGHT CO | INCIDENT WAS BELIEVED TO BE DUE TO FAULTY WIRING IN THE KITCHEN AREA OF THE HOME. AS FIRE CONSUMED HOME, DAMAGE WAS DONE TO THE GAS METER LOCATED IN THE BASEMENT (BELOW KITCHEN). ESCAPING GAS PROVIDED A SECONDARY SOURCE OF EMISSION FOR THE FIRE. | 400000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2824 | 2004-01-13 | MN | other | DUPONT | NORTHERN STATES POWER CO | THE SUSPECTED SOURCE OF THE GAS THAT CAUSED THE EXPLOSION IS A LEAK ON THE GAS SERVICE TO 715 STATE HIGHWAY 10. THIS SERVICE RUNS BETWEEN 709 AND 711 BIRCH STREET TO SERVE GENES REPAIR, A COMMERCIAL BUSINESS LOCATED BEHIND 711 BIRCH. THE LEAK IN THE SER | 200000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2825 | 2004-02-03 | IL | other |  | NORTHERN ILLINOIS GAS CO | FIRE, WHICH STARTED INSIDE THE HOUSE NEAR GARAGE, CONSUMED THE ENTIRE STRUCTURE ALSO CAUSING DAMAGE TO THE METER SET ASSEMBLY. METER SET ASSEMBLY WAS LOCATED ON OPPOSITE SIDE OF LOCATION WHERE FIRE STARTED. NO INJURIES, NO FATALITIES. | 750000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2826 | 2004-02-04 | IN | other | UNKNOWN | CITIZENS GAS & COKE UTILITY | HOUSE AT 373 S RITTER EXPLODED AT APPROXIMATELY 2:40 AM ON THE MORNING OF 02/04/04. NO CAUSE HAS BEEN DETERMINED AT THIS TIME AND THERE IS NO INDICATION FROM OUR INVESTIGATION THAT THE CAUSE WAS RELATED TO PIPING OWNED AND OPERATED BY CITIZENS GAS. THE | 900000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2827 | 2004-02-13 | CT | other | UNKNOWN | YANKEE GAS SERVICES CO | WHILE GAS EMPLOYEE WAS REPAIRING GAS MAIN, EMPLOYEE WAS OVERCOME BY OXYGEN DISPLACEMENT. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2828 | 2004-02-26 | FL | other | UNKNOWN | TECO PEOPLES GAS LP OPERATIONS | CONTRACTOR HIT MAIN WHILE PERFORMING DIRECTIONAL BORING. TECO PEOPLES GAS EMPLOYEE WAS INJURED WHILE IN THE PROCESS OF REPAIRING DAMAGED MAIN. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2829 | 2004-03-02 | AK | other | UNKNOWN | ENSTAR NATURAL GAS CO | ON TUESDAY MORNING, MARCH 2, 2004 AT APPROXIMATELY 10:57 AM AST, ENSTAR NATRUAL GAS COMPANY WAS NOTIFIED OF A STRUCTURE FIRE AT 1101 ROBINS SONG AVE, WASILLA, ALASKA. AN ENSTAR SERVICEMAN WAS DISPATCHED TO THE SCENE. UPON ARRIVAL THE SERVICEMAN FOUND A | 150000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2830 | 2004-02-19 | MN | other | ORANGEBERG | CENTERPOINT ENERGY MINNEGASCO | THE SERVICE LINE MATERIAL PULLED OUT OF MECHANICAL FITTING. THIS FITTING AND STIFFENER COMBINATION DID NOT HAVE ADEQUATE TENSILE RESTRAINT TO COUNTER SOIL EFFECTS AND TEMPERTURE CONTRACTION EFFECTS OF THIS SERVICE. 6-16-05 MATERIALS: SERVICE MATERIAL IS | 198000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2831 | 2004-02-16 | MD | other |  | BALTIMORE GAS & ELECTRIC CO | BALTIMORE COUTY FIRE DEPT. (BCFD) REQUESTED OUR ASSISTANCE TO TURN OFF NATURAL GAS. A GAS MECHANIC WAS DISPATCHED AT 2051 AND ARRIVED AT 2111. THE METER/REGULATOR INSTALLATION HAD BEEN DAMAGED BY THE HEAT OF THE FIRE CREATING A RESTRICTED MP GAS FIRE AT | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2832 | 2004-03-21 | AL | other | UNKNOWN | ALABAMA GAS CORP (EX. MARENGO CORP PROPERTY) | A VEHICLE ROLLED APPOX. 300 IN REVERSE FROM 512 WEST CREST ESTATES STRIKING A RESIDENTIAL GAS METER ASSEMBLY, RESIDENTIAL ELECTRICAL HOOKUP AND A MOBILE HOME. A FIRE RESULTED IN THE DEATH OF THE DRIVER OF THE VEHICLE. LATITUDE 33459 LONGITUDE -8700 | 18500 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2833 | 2004-02-24 | TX | other |  | TXU GAS COMPANY | A GAS LEAK OCCURRED AT DRESSERS CONNECTING A SERVICE LINE TO THE MAIN. GAS MIGRATED UNDER A SLAB AND INTO AN INTERIOR WALL. THE GAS IGNITION WAS SPARKED WHEN A WALL SWITCH WAS FLIPPED FROM THE "ON" POSITION TO THE "OFF" POSITION. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2834 | 2004-02-27 | MT | technical failure | PERFORMANCE PIPE | NORTHWESTERN ENERGY LLC | THIRD PARTY WAS DIGGING IN THE BACKYARD AND HIT A 1/2 PLASTIC GAS SERIVCE SERVING A HAIR STYLING BUSINESS LOCATED IN THE OWNERS HOME. GAS IMMIGRATED INTO THE FOUNDATION AND AN EXPLOSION OCCURED CAUSING STRUCTURAL DAMAGE TO THE RESIDENCE. | 51000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2835 | 2004-01-22 | WI | other | UNKNOWN | WE ENERGIES | ON JANUARY 22, 2004, AT ABOUT 0750 HOURS IN THE MORNING, TERA HEIL, WHILE DRIVING A FORD TAURUS VEHICLE (MODEL YEAR 2000) ON SMITH STREET IN NEENAH WISCONSIN, LOST CONTROL OF HER VEHICLE. THE VEHICLE LEFT THE HIGHWAY, TRAVELED ACROSS A LAWN, AND STRUCK T | 63856 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2836 | 2004-04-06 | MI | technical failure |  | MICHIGAN CONSOLIDATED GAS CO (MICHCON) | CONTRACTOR, CORDESS CONSTRUCTION, DOING PUBLIC IMPROVEMENT WORK GRINDING ASPHALT ROAD, HIT 1-1/8" PLASTIC 60 LB SERVICE WHICH CAUSED A FIRE AND BURNT TRUCK AND EQUIPMENT. | 435000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2837 | 2004-04-27 | GA | other | USS | ATLANTA GAS LIGHT CO | A CONTRACTOR INSTALLING STORM DRAINS RUPTURED A 12" HIGH PRESSURE STEEL GAS MAIN WITH A TRACK HOE WHILE EXCAVATING. | 948000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2838 | 2004-01-13 | LA | other | CBOMANU | ENTERGY GULF STATES INC | N/A NOT GAS RELATED | 60000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2839 | 2004-06-29 | PA | other |  | PECO ENERGY CO | FATAL VEHICLE ACCIDENT - VEHICLE STRUCK UTILITY POLE AND THEN STRUCK RESIDENTIAL GAS METER RESULTING IN RELEASE OF NATURAL GAS.. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2840 | 2004-07-25 | CA | other | UNKNOWN (SAN BERNADINO COUNTY) | PACIFIC GAS & ELECTRIC CO | SEARLESS VALLEY MINERALS OPERATING A BACKHOE STRUCK AND PUNCTURED A 3" STEEL GAS MAIN ON 7/25/04 CAUSING SERVICE LOSS TO APPROX 779 CUSTOMERS. AT THE TIME OF THE INCIDENT, THE PROPERTY DAMAGE WAS ESTIMATED TO BE LESS THAN 50,000. HOWEVER, DUE TO THE REM | 90500 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data