## incident_gas_transmission_gathe
| Date | State | Cause of Loss | Name of Installation | Name of Owner | Text | Loss Estimated ($) | Link
0 | 1984-08-07 | TX | other | HARRIS | UNITED TEXAS TRANSMISSION CO | COUNTY EMPLOYEE HIT EXPOSED PIPE IN DITCH WHILE MOWING. EMPLOYEE WAS DRIVING A FORD TRACTOR WITH RUBBER TIRES AND A SIDE BOOM CUTTER. | 4060 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1 | 1984-05-22 | TX | maintenance | COLLIN | TEXAS UTILITIES FUEL CO | TUFCO LEAK NO. LT-9-84 | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
2 | 1984-05-23 | TX | maintenance | LIMESTONE | TEXAS UTILITIES FUEL CO | TUFCO LEAK CONTROL NUMBER LT-7-84 | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
3 | 1984-05-25 | TX | maintenance | FREESTONE | TEXAS UTILITIES FUEL CO | TUFCO LEAK CONTROL NUMBER LG-1-84 | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
4 | 1984-06-07 | CO | other | GARFIELD | NORTHWEST PIPELINE CORP | DAMAGE BY OUTSIDE FORCE. (LANDSLIDE/WASHOUT) | 175000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
5 | 1984-06-14 | WY | other | CONVERSE | PHILLIPS PETROLEUM CO | FAILURE OF 3/4" THREADED NIPPLE CAUSED GAS LEAK IN COMPRESSOR ROOM. ENGINE IGNITION SYSTEM BELIEVED TO HAVE STARTED FIRE. | 800000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
6 | 1984-06-17 | MI | maintenance | ALLEGAN | ANR PIPELINE CO (AMERICAN NATURAL RESOURCE) | DAMAGE DUE TO CORROSION. | 84000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
7 | 1984-06-19 | MD | other | MONTGOMERY | WASHINGTON GAS LIGHT CO | CONTRACTOR (D.A.FOSTER) AND WASHINGTON GAS LIGHT EMPLOYEES WERE OFFSETTING A 22": WRAPPED STEEL MAIN, DUE TO ROAD CONSTRUCTION. THEY WERE REMOVING A 60' SECTION OF PIPE THAT WAS TO BE RELOCATED. TWO CUTS WERE BEING MADE. THE WEST END BEING CUT WITH REED | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
8 | 1984-06-24 | LA | technical failure | CADDO | J - W OPERATING CO | DAMAGE DUE TO CONSTRUCTION/MATERIAL DEFECT. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
9 | 1984-06-25 | KY | other | LAUREL | DELTA NATURAL GAS CO INC | A LAUREL COUNTY HIGHWAY DEPARTMENT ROADGRADER CAUSED A TEAR IN THE 6" STEEL PIPELINE WHILE CLEANING DITCHES ON BURNETT ROAD, NEAR HWY. 229 IN LAUREL COUNTY, KENTUCKY. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
10 | 1984-06-28 | TX | other | CHAMBERS | AMOCO GAS CO | ON JUNE 26, THE DRAGLINE THAT PUNCTURED OUR PIPELINE WAS DISCOVERED BY OUR AIR PATROL. HIS FOREMAN WAS NOTIFIED BY AMOCO GAS. IMMEDIATELY, HE WENT TO LOCATION AND TOLD HIS DRAGLINE OPERATOR NOT TO DIG OVER PIPELINE. THE NEXT DAY, AMOCO GAS HAD AN INSPE | 22000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
11 | 1984-06-29 | TX | maintenance | UPSHUR | ARKANSAS LOUISIANA GAS CO (ARKLA GAS CO) | LINE BLEW OUT IN BANK OF CREEK. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
12 | 1984-07-19 | ND | other | MERCER | NORTHERN PLAINS NATURAL GAS COMPANY | ON THE DAY OF THE INCIDENT, OPERATOR PERSONNEL WERE IN THE PROCESS OF PERFORMING SEVERAL TASKS IN ORDER TO PREPARE THIS NEW METER STATION, OWNED BY GREAT PLAINS COAL GASIFICATION ASSOCIATES, FOR ACCEPTING THE FIRST DELIVERIES OF SYNTHETIC GAS FROM THE PLA | 230000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
13 | 1984-07-13 | GA | other | CLAYTON | SOUTHERN NATURAL GAS CO | CONTRACTOR CLEARING LOT FOR RESIDENTIAL CONSTRUCTION PUNCTURED LINE WITH FRONT END LOADER WHILE DIGGING HOLE TO BURY TRASH AT REAR OF LOT.DEPTH OF PIPELINE - 43" | 18607 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
14 | 1984-07-15 | FL | other | DADE | FLORIDA GAS TRANSMISSION CO | SOMEONE SHOT A HOLE (APPROX. 5/16") IN 90 DEGREE ELL FITTING IN 4" PIPELINE WHERE IT IS EXPOSED TO CROSS A POWER PLANT DRAIN CANAL. POLICE ARE INVESTIGATING.OUTSIDE PARTY SHOT HOLE IN 4" ELBOW WITH HIGH-POWERED RIFLE (APPEARS TO HAVE USED ARMOR-PIERCING | 1500 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
15 | 1984-08-15 | TX | other | HARRIS | UNITED TEXAS TRANSMISSION CO | 1" TAP VALVE WAS KNOCKED OFF PIPELINE BY COMPANY PERSONNEL DIGGING IN VICINITY. | 1635 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
16 | 1984-08-21 | WI | other | SAUK | NORTHERN NATURAL GAS CO | GAS THAT HAD BEEN VENTED TO ATMOSPHERE DURING PURGING OF REGULATOR PIPING WAS IGNITED RESULTING IN A FLASH FIRE. THE SOURCE OF IGNITION IS BELIEVED TO HAVE BEEN A PILOT ON AN INDIRECT FIRED GAS HEATER. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
17 | 1984-07-09 | TX | maintenance | LIMESTONE | TEXAS UTILITIES FUEL CO |  | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
18 | 1984-08-28 | TX | other | HUTCHINSON | MAPCO.,INC | LINE WAS DAMAGED BY ROCKS SETTLING ON TOP OF LINE.SOIL AND ROCK SETTLED ON LINE CAUSING PLASTIC PIPE TO BREAK. REPLACED WITH 33'STEEL PIPE. THIS LINE WAS NOT IN OPERATION WHEN LEAK WAS DISCOVERED WHILE WALKING LINE FOR INSPECTION. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
19 | 1984-08-28 | TX | other | RUNNELS | LONE STAR GAS CO | LINE HIT BY AUGER DRILLING FOR FENCE POST. | 2697 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
20 | 1984-08-29 | TX | other | COLLIN | LONE STAR GAS CO | 10" PIPELINE WAS HIT BY BACKHOE BUCKET TEETH WHILE DIGGING OUT FOR RETAINING WALL FOR A BRIDGE BEING CONSTRUCTED. GOUGES LEFT FROM TEETH WERE DEEP ENOUGH TO REQUIRE REPAIRING. | 1419 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
21 | 1984-09-20 | LA | other | CADDO | J - W OPERATING CO | LINE BROKEN BY OUTSIDE CONTRACTOR'S BACKHOE. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
22 | 1984-07-30 | TX | maintenance | MIDLAND | PHILLIPS PIPELINE CO |  | 5000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
23 | 1984-09-16 | TX | maintenance | LIMESTONE | TEXAS UTILITIES FUEL CO | LT-16-84 & LT-17-84 | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
24 | 1984-09-06 | TX | maintenance | NANANO | TEXAS UTILITIES FUEL CO | DAMAGE WAS CAUSED BY CORROSION ON TRANSMISSION SYSTEM. LEAK CALLED IN BY FLOYD HENDERSON. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
25 | 1984-09-03 | TX | technical failure | HENDERSON | TEXAS UTILITIES FUEL CO | PIPELINE IN STRAIN WHERE LINE WAS WELDED TO NEW PIPE AT CREEK CROSSING, LEAK JUST BACK OF MOLD ON OLD PIPE. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
26 | 1984-08-23 | NY | technical failure | WESTCHESTER | CONSOLIDATED EDISON COMPANY, NEW YORK | TENNESSEE GAS CO, RELIEF VALVE RELEASED GAS TO ATMOSPHERE. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
27 | 1984-10-22 | LA | other | BOSSIER | ARKANSAS LOUISIANA GAS CO (ARKLA GAS CO) | EXTENDED RAINY WEATHER WITH EXTREMELY HEAVY RAINS CAUSED EARTH MOVEMENT IN CREEK BOTTOM ALLOWING PIPE TO PULL OUT OF MECHANICAL COUPLING. | 34220 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
28 | 1984-09-17 | AR | technical failure | CLARK | ARKANSAS LOUISIANA GAS CO (ARKLA GAS CO) | 35' SECTION OF 20" O.D. PIPE RUPTURED ADJACENT TO LONGITUDINAL SEAM ALONG HEAT-AFFECTED ZONE. RUPTURE OCCURED ADJACENT TO LONGITUDINAL WELD SEAM BUT NOT ON WELD SEAM, APPARENTLY IN ZONE AFFECTED BY HEAT FROM LONGITUDINAL WELD. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
29 | 1984-09-05 | TX | maintenance | KARNES | VALERO INTERSTATE TRANSMISSION CO | DAMAGE DUE TO CORROSION ON TRANSMISSION SYSTEM. FAILURE OCCURRED ON WELD (LONGI-TUDINAL). | 335000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
30 | 1984-09-21 | TX | technical failure | ZAPATA | ZAPATA GATHERING CO. | 35,000 MCFD BEING DELIVERED TO NATURAL GAS PIPELINE COMPANY OF AMERICA WAS SHUTIN TEMPORARILY, CAUSING PRESSURES TO RISE, HIGH LOW VALVES AT WELLS FAILED TO SHUT IN WELLS WHEN PRESSURES EXCEEDED MAOP OF PIPELINE.PIPE SPLIT IN AND ALONG THE ERW SEAM, TOTAL | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
31 | 1984-09-27 | WV | maintenance | MONONGALIA | COLUMBIA GAS TRANSMISSION CORP | A SEGMENT OF PIPE RUPTURED AND BLEW OUT OF THE GROUND, APPARTENTLY DUE TO CORROS | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
32 | 1984-08-05 | TX | other | CHAMBERS | ARCO PIPE LINE COMPANY | STATIC ELECTRICITYWHILE DEPRESSING A METER CAVITY IN ORDER TO REMOVE AN ORIFICE PLATE AND UPON INITIAL OPENING OF THE BLEEDER VALVE, AN APPARENT STATIC ELECTRICAL CHARGE IGNITEDTHE ETHYLENE. | 52 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
33 | 1984-07-28 | KS | maintenance | RENO | PANHANDLE EASTERN PIPELINE CO |  | 105000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
34 | 1984-09-09 | LA | maintenance |  | UNITED GAS PIPELINE CO | LEAK WAS DISCOVERED DURING REPRESSURING OF THE LINE AFTER ELECTRONIC PIGGING OPE | 200000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
35 | 1984-09-27 | WY | technical failure | LINCOLN | NORTHWEST PIPELINE CORP | A CRACK INITIATED FROM TOE OF FILLET WELD THAT JOINED A REINFORCING SADDLE TO PIEP; CRACK PROPAGATED THROUGH PIPE WALL. | 85000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
36 | 1984-09-17 | NV | other | CLARK | SOUTHWEST GAS CORP | T A COMPRESSOR STATION. APPARENTLY, THE CONTROL VALVE TO THIS 16" VALVE HAD A MECHANICAL FAILURE. GAS AT 500 PSIG ENTERED A CENTAUR COMPRESSOR, DAMAGED IT AND VENTED OUT A 6" BLOW DOWN VALVE. THE ESD VALVES AT THE STATION CLOSED AT 0830HRS. THE NEXT DA | 500000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
37 | 1984-09-20 | TX | other | FORT BEND | UNITED TEXAS TRANSMISSION CO | LEAK OCCURRED WHEN A FARMER HIT THE LINE WHILE CLEANING OUT DITCHES WITH A MAINTAINER. | 2304 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
38 | 1984-05-22 | CO | other | GARFIELD | ROCKY MOUNTAIN NATURAL GAS CO INC | MUD SLIDE DAMAGED PIPE. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
39 | 1984-10-11 | TX | other | ECTOR | WESTAR TRANSMISSION CO |  | 9100 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
40 | 1984-10-12 | TX | other | SCHLEICHER | ADOBE GAS CO. | THE PIPELINE WAS SHOT WITH A RIFLE OR PISTOL PUNCTURING IT. WAS NOT DAMAGED BYEXCAVATION. IT WAS DONE BY GUNFIRE. | 2500 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
41 | 1984-10-12 | TX | other | TAYLOR | LONE STAR GAS CO | A LARGE CASE TRACTOR WITH A SUBSOILER ATTACHMENT STRUCK 8" LINE KCMI. THIS RESULTED IN A 3" X 1 1/2" RECTANGULAR SHAPED HOLE IN THE PIPE AT STATION #93 + 30. | 2941 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
42 | 1984-09-23 | TX | maintenance | BROWN | EL PASO HYDROCARBONS COMPANY | EXCESSIVE INTERNAL WEAR ON INSIDE OF PIPE DOWNSTREAM OF RIVER CROSSING. | 6000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
43 | 1984-10-04 | NE | other | DAWES | KN ENERGY INC (KANSAS NEBRASKA NATURAL GAS CO INC) |  | 110000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
44 | 1984-10-14 | TX | other | NOLAN | LONE STAR GAS CO | A DITCHING MACHINE OPERATED BY TOMBUR CONSTRUCTION HIT LINE KCRA-12" GOUGING ITBUT NOT RUPTURING IT. THE OPERATOR'S HELPER REMOVED THE MARKER SHOWING THE LOCATION AND DEPTH. THE DAMAGED PORTION WILL BE REPLACED.PERMANENT MARKER 67', TEMPORARY MARKER ON | 5000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
45 | 1984-10-09 | TX | maintenance | NANANO | TEXAS UTILITIES FUEL CO | MR. ROGER THRALE CALLED IN LEAK ON 6" LINE. | 5000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
46 | 1984-10-11 | MO | technical failure | BOLLINGER | NATURAL GAS PIPELINE CO OF AMERICA | A 3/8" LONG CRACK BEGAN NEAR A GIRTH WELD THAT PROGRESSED LONGITUDINALLY INTO THE CARRIER PIPE. | 75000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
47 | 1984-08-29 | TX | maintenance | FREESTONE | TEXAS UTILITIES FUEL CO | PROPERTY OWNER RICKY SHARP REPORTED GAS LEAK. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
48 | 1984-12-01 | TX | other |  | ENERGY GATHERING, INC. | BULLDOZER DRAGGING ROCK RIPER WAS RIPING GROUND FOR GRAVEL PIT. | 3500 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
49 | 1984-12-15 | LA | maintenance | WEST BATON ROUGE | MONTEREY PIPELINE CO. | SMALL ACCUMULATION OF LIQUIDS IN THE LOWER PART OF THE DRIP RESERVOIR BARREL OVER AN EXTENDED PERIOD CONTRIBUTED TO AN INTERNAL CORROSION PROBLEM. DROP OUT TYPE LINE DRIP - ATTACHED TO BOTTOM OF TRANSMISSION LINE. | 80000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
50 | 1984-11-22 | TX | technical failure | CAMERON | RIO GRANDE VALLEY GAS CO | IT IS SUSPECTED THAT A RELOCATION TIE-IN 50' FROM THE LEAK WHICH WAS PERFORMED THREE WEEKS PRIOR TO THIS INCIDENT MAY HAVE WEAKENED THE WELD DUE TO MOVEMENT. | 7800 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
51 | 1984-08-30 | TX | technical failure | LIMESTONE | TEXAS UTILITIES FUEL CO | LONGITUDINAL WELD SEAMS WERE ALIGNED WITHIN 1" OF THE AFFECTED PIPE JOINTS IN THE LOWER QUADRANT OF THE PIPE. FAILURE OCCURRED ALONG THE LONGITUDINAL WELD SEAM WHERE INADEQUATE FUSION IS BELIEVED TO HAVE BEEN PRESENT. | 21500 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
52 | 1984-09-10 | TX | technical failure | JACK | TEXAS UTILITIES FUEL CO | PROPERTY OWNER REPORTED LEAK. HYDROSTATIC TEST PRESSURES OF THIS PIPELINE EXCEEDED, IN ALL CASES, THE REQUIREMENTS OF ASA CODE B 31.8, 1958. CRACK APPEARS TOBE AT EDGE OF GIRTH WELD ADJACENT TO PARENT PIPE MATERIAL AND RESULTED IN THIS REPORTED LEAK. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
53 | 1984-01-13 | TX | other | HARRIS | AIR PRODUCTS & CHEMICALS, INC. | DUCTILE FAILURE BELIEVED TO HAVE BEEN CAUSED BY DREDGING OVERBURDEN COMPRESSINGSUBSTRATA RESULTING IN UNDERGROUND PIPE MOVEMENT. | 20000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
54 | 1984-08-20 | TX | maintenance | NUECES | DELHI GAS PIPELINE CORP |  | 2000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
55 | 1984-07-16 | TX | other | HOOD | LONE STAR GAS CO | A ROAD CROSSING JOB WHEN THE COUPLING BLEW OUT. | 7668 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
56 | 1984-09-15 | TX | other | RUNNELS | LONE STAR GAS CO | LINE HIT BY TRACTOR PULLING MOWBOARD PLOW WHICH TORE A 3" X 2" GASH IN THE PIPEL | 1717 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
57 | 1984-12-03 | TX | other | COLLIN | LONE STAR GAS CO | TRACTOR PULLING CULTIVATOR CUT INTO LINE, CUTTING LINE IN HALF. | 10400 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
58 | 1984-12-02 | TX | technical failure |  | TRANSCO GAS PIPELINE CORP | A LEAK IN BODY OF FITTING OCCURED IN A CONNECTOR JOINING TWO 20" PIPE SEGMENTS INSTALLED DURING JUNE OF 1983. | 1600000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
59 | 1984-12-03 | LA | other | POINTE COUPEE | TRANSCO GAS PIPELINE CORP | A RUPTURE AND FIRE ON A 30" TRANSMISSION LINE ON TH PIPELINE SYSTEM OF TRANSCONTINENTAL GAS PIPELINE OCCURED ON DECEMBER 3, 1984. THIS INCIDENT WAS REPORTED BY TELEPHONE TO THE DEPARTMENT OF TRANSPORTATION'S OFFICE IN WASHINGTON, D.C. ON DECENBER 3, 1984. | 400000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
60 | 1984-10-28 | AR | technical failure | CRAWFORD | ARKANSAS OKLAHOMA GAS CORPORATION | RUPTURE OCCURRED IN PIPE DUE TO WET SOIL CONDITIONS, AGE & TYPE OF STEEL AND PRESSURE AT TIME OF INCIDENT.PART C.4 : SPECIFICATION UNDER WHICH THE PIPE WAS MADE ARE NOT KNOWN, HOWEVER THE PIPE DID HAVE A BUTT WELDED SEAM. | 10000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
61 | 1984-10-27 | LA | maintenance |  | NATURAL GAS PIPELINE CO OF AMERICA | LEAK WAS CAUSED BY INTERNAL CORROSION IN THE PIPE AND WAS REPAIRED BY INSTALLING A PLIDCO LEAK CLAMP. | 250000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
62 | 1984-11-09 | TX | maintenance | EASTLAND | LONE STAR GAS CO | LINE 2ND KC-12" WAS BEING LOADED FOR RETURE TO SERVICE WHEN THE PIPE SEPARATED AT STATION #439+11 APPARENTLY THE RESULT OF TEMPERATURE CHANGE AND STRESS. THE LINE WAS ISOLATED FROM THE PLANT #4 GATE TO CANYON ROAD, APPROXIMATELY 8.81 MILES. REPAIRS WERE M | 3072 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
63 | 1984-11-09 | TX | other | EASTLAND | LONE STAR GAS CO | C.B. FRAILEY, OPERATOR II AT HILL LAKE STORAGE, CALLED CINDY SNYDER, OPERATOR II AT PUEBLO, AT 12:14 PM, 11/9/84 AND SAID THAT THERE WAS A PRESSURE DROP ON LINE KC. THE PRESSURE WAS CHECKED AT THE PUEBLO PLANT AND THE VALVE CLOSED ON KC EAST. CINDY CONTAC | 8032 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
64 | 1984-10-28 | TX | other | JEFFERSON | TEXACO CHEMICAL CO.,ADIVISION OF TEXACO INC. | AND GREASE FITTING ON 8 INCH ETHYLENE VALVE. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
65 | 1984-06-10 | KS | other | POTTAWATOMIE | KANSAS POWER & LIGHT CO |  | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
66 | 1984-07-03 | KS | technical failure | STAFFORD | KANSAS POWER & LIGHT CO | PART C: EARTH SETTLEMENT TROUGHOUT THE YEARS CREATE MISALIGMENT OF A MECHANICALDRESSER COUPLING, THEREFORE, COAUSED A RUBBER GASKET TO FAIL. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
67 | 1984-06-27 | KS | maintenance | COWLEY | ARKANSAS LOUISIANA GAS CO (ARKLA GAS CO) | LEAK ORIGINALLY REPORTED BY FARMER WHO SAID LINE WAS COMPLETELY SEVERED. INVESTIGATION REVEALED A SMALL CORROSION PIT HOLE ONLY. GAS SERVICE WAS NOT INTERRUPTED | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
68 | 1984-07-15 | KS | maintenance | COWLEY | ARKANSAS LOUISIANA GAS CO (ARKLA GAS CO) | SMALL LEAK DUE TO CORROSION PIT HOLE IGNITED WHILE FARMER WAS BURNING FIELD. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
69 | 1984-11-25 | LA | other | WEST FELICIANA | TEXAS EASTERN GAS PIPELINE CO | 4 TO GAS SERVICE FOLLOWING CONSTRUCTION ACTIVITIES INVOLVING AN ADJACENT SECTION OF PIPE. THE CAUSE OF THE INCIDENT IS CURRENTLY UNDER INVESTIGATION. | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
70 | 1984-11-30 | ND | other | MCKENZIE | MONTANA-DAKOTA UTILITIES COMPANY | DUE TO VIBRATION. ESCAPING GAS WAS IGNITED , PROBABLY BY THE ENGINE'S IGNITION SYSTEM. THE RESULTING EXPLOSION DESTROYED THE CMPRESSOR BUILDING. MACHINES WERE NOT DAMAGED, NO ONE WAS INJURED. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
71 | 1984-12-11 | TX | maintenance | EASTLAND | EL PASO HYDROCARBONS COMPANY | LINE WAS PRESSURE TESTED AT TIME OF CONSTRUCTION IN 1972, CONSTRUCTION OR MATERIAL WAS NOT CAUSE OF RUPTURE. | 13000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
72 | 1984-12-10 | TX | other | DALLAS | LONE STAR GAS CO | WHILE INSTALLING SEWER LINE UNDER GAS PIPELINE, BACKHOE OPERATOR STRUCK GAS PIPELINE WITH TOOTH ON BACKHOE BUCKET CAUSING SPLIT IN SIDE OF PIPELINE APPROX. 1 INCH IN SIZE. LINE HAD BEEN LOCATED AND FLAGGED PRIOR TO INCIDENT BUT COMPANY WASNOT NOTIFIED CON | 2642 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
73 | 1984-11-26 | TX | maintenance | LEON | TEXAS UTILITIES FUEL CO |  | 500 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
74 | 1984-12-12 | TX | other |  | ANR PIPELINE CO (AMERICAN NATURAL RESOURCE) | ANCHOR CABLE DAMAGE OF 2" PURGE LINE. | 250000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
75 | 1984-12-16 | KY | other | WHITLEY | DELTA NATURAL GAS CO INC | GAS ON THE SUCTION SIDE OF THE UNIT. A FAULTY RELIEF VALVE VENTED GAS INTO THE COMPRESSOR BUILDING. TWO HOURS LATER, GAS HAD MIGRATED OUT OF THE BUILDING AND WAS IGNITED BY AN OPEN FLAME OF A DEHYDRATION UNIT. | 25000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
76 | 1984-12-22 | LA | other |  | STINGRAY PIPELINE CO | PART 3: LEAK WAS DISCOVERED BY PHI PILOT T-53 & REPORTED TO MARK BREAUX AT W.C.509, DIVISION WAS CONTRACTED(A.E.FAWCETT), AUTHORIZATION WAS GIVEN TO SHUT IN LINE AT W.C. 536, DIVER SHUT IN VALVE AT 8:00 AM ON 12/24/84.PART C: SHRIMPING NET WAS FOUND ENTAN | 300000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
77 | 1984-12-18 | OR | other | MORROW | PACIFIC GAS TRANSMISSION CO. | L PUMP DISCHARGE LINE, DEVELOPED A CRACK IN THE THREADS WHICH ALLOWED LUBE OIL TO SPRAY ON THE HOT SECTION OF THE UNIT REACTION TURBINE AND SUBSEQUENTLY IGNITED, RESULTING IN A FIRE WHICH CAUSED SOME EQUIPMENT DAMAGE. THERE WAS NO GAS INVOLVED AND NO THRE | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
78 | 1984-12-28 | WY | other | CONVERSE | PHILLIPS PETROLEUM CO |  | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
79 | 1985-01-03 | TX | other | LUBBOCK | ADOBE GAS CO. |  | 400 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
80 | 1985-01-05 | TX | other | TAYLOR | LONE STAR GAS CO | A 12" WELD CRACKED APPROX. 14" LONG, CAUSED THE LEAK. A SET OF 12" WELDOVER SLEEVES WERE INSTALLED OVER THE GIRTH WELD, WHICH CAUSED PERMANENT REPAIR. | 2580 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
81 | 1985-01-17 | TX | other | DALLAS | LONE STAR GAS CO | LINE FLAGGED TO STA. 70+01 OPERATOR DID NOT CALL TO GO PASS STA. 70+01. OPERTORWAS DIGGING 44" DEEP. INFORMED US HE WAS ONLY DIGGING 30" DEEP. | 2050 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
82 | 1985-01-04 | TX | other | GALVESTON | BLACK MARLIN PIPELINE CO |  | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
83 | 1985-01-25 | TX | other | HALE | WESTAR TRANSMISSION CO | 10 3/4" O.D. PIPELINE WAS DAMAGED BY OUTSIDE FORCES WITHUT THE KNOWLEDGE OG THEPIPELINE OPERATOR. DATE OF THE DAMAGE IS UNKNOWN. | 18000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
84 | 1985-01-29 | TX | maintenance | CHAMBERS | WINNIE PIPELINE CO | INTERNAL CORROSION & DEFECTIVE WELD WERE CONTRIBUTING FACTORS AS THE CORROSION ATTACHED A DEFECTIVE WELD LOCATED AT A LOW POINT NEAR AN OVERHEAD DRAINAGE DITCHCROSSING. | 10000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
85 | 1985-01-23 | TX | maintenance | JEFFERSON | WINNIE PIPELINE CO | PART 3: INTERNAL CORROSION DUE TO NO INTERNAL CHEMICAL TREATMENT UNTIL 1979.PART A: THIS PIPELINE IS CURRENTLY BEING TREATED INTERNALLY WITH CORROSION INHIBITOR; HOWEVER, THE PIPELINE WAS OPERATED FROM 1965 UNTIL 1978 WITHOUT BEING TREA | 1000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
86 | 1985-02-16 | NM | other | SANTA FE | GAS COMPANY OF NEW MEXICO | TRANSMISSION LINE WAS HIT AND PUNCTURED BY PRIVATE INDIVIDUAL USING A RENTED FRONT-END. | 37000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
87 | 1985-01-29 | TX | maintenance | LA SALLE | R K G ENGINEERING INC | VALERO TRANSMISSION CO. SHUT SALES LINE IN UNKOWN TO R.K.G.ENGINEERING,INC. COMPRESSOR HOLE IN LINE IN CORRODED AREA. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
88 | 1985-02-08 | MO | other | MARION | PANHANDLE EASTERN PIPELINE CO | LMYRA #1 M&R STATION. A SHARP PRESSURE PILLDOWN RESULTED FROM THE STARTUP OF A CUSTOMER POWER PLANT ENGINE. THIS PROBABLY LED TO VIOLENT LEVER ARM MOVEMENT OF THE REGULATOR AND THE SUBSEQUENT DROPPING OG THE WEIGHTS. THIS CLOSED THE REGULATOR VALVES. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
89 | 1985-01-18 | TX | maintenance |  | NATURAL GAS PIPELINE CO OF AMERICA | ART A: CORRODED AREA WAS APPROXIMATELY ANE-HALF INCH IN DIAMETER WITH ONE SMALLPIN HOLE NEAR THE CENTER. LEAK LOCATED 69'-10" FROM THE 8" VALVE (SIDE TAP) AT THE SEVEN O'CLOCK POSITION LOOKING AGAINST THE FLOW.PART 3: LEAK WAS CAUSED BY INTERNAL CORROSION | 250000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
90 | 1985-01-24 | TX | other | CRANE | EL PASO HYDROCARBONS COMPANY | PART B: INFRACTION WAS FOUND DUE TO PIPELINE SURVEY APPROXIMATELY 3 YEARS EARLIE | 2000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
91 | 1985-01-03 | TX | maintenance | NAVARRO | TEXAS UTILITIES FUEL CO |  | 9068 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
92 | 1985-01-28 | TX | other | FAYETTE | VALERO TRANSMISSION CO | LINE WAS STRUCK BY DITCHING MACHINE OPERATED BY CONTRACTOR INSTALLING ANOTHER COMPANY'S PIPELINE. | 5000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
93 | 1985-01-26 | TX | other | ZAVALA | VALERO TRANSMISSION CO | RISER WAS HIT BY MOVING VEHICLE WHICH CAUSED A LEAK IN THE PIPE. | 2000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
94 | 1985-02-10 | WV | other | FAYETTE | CABOT CORPORATION | FACTORS CONTRIBUTING TO THIS PROBLEM CAN BE ASSOCIATED TO EXTREME WEATHER CONDITIONS EXPERIENCED IN THIS AREA. EARTH MOVEMENT ASSOCIATED WITH EXPANSION AND CONTRACTION OF THE PIPELINE WERE PRESENT. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
95 | 1985-02-12 | KS | other | RICE | NORTHERN NATURAL GAS CO | RAL GAS WAS BEING USED, WITHOUT MONITORING PRESSURE, TO PURGE LIQUIDS FROM THE VESSEL. THE ENGAGED VESSEL CAP CONNECTION DEVICE FAILED, ALLOWING THE SEPARATION OF THE CAP FROM THE VESSEL. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
96 | 1985-01-26 | TX | maintenance |  | RIO GRANDE VALLEY GAS CO | NO COMMENTS GIVEN. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
97 | 1985-01-25 | MO | maintenance |  | PANHANDLE EASTERN PIPELINE CO | THE CAUSE IS CURRENTLY UNKNOWN. THE COMPANY IS PERFORMING A COMPLETE METALLURGICAL ANALYSIS OF THE FAILED PIPE TO DETERMINE CAUSE. NO EVIDENCE FOUND THUS FAR POINTS TO ANY SPECIFIC CAUSE.*/! CAUS CHANGED TO CORROSION AS PER SUPPLEMENTAL REPORT. | 54000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
98 | 1984-11-25 | TX | maintenance | DIMMIT | R K G ENGINEERING INC | HIGH LINE PRESSURE CAUSED VALVE TO LEAK IN CORRODED AREA. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
99 | 1984-12-17 | TX | technical failure |  | NORTHERN NATURAL GAS CO | FLANGED END CONNECTOR DID NOT SEAT PROPERLY AFTER FIELD FORGING; AND, GASKET RINGS LEAKED ON MISALIGNMENT FLANGE. | 1800000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
100 | 1985-01-04 | LA | other | LINCOLN | MISSISSIPPI RIVER TRANS. CO. | TED AT A FLAW IN A WRINKLE BEND. | 55000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
101 | 1985-02-14 | TX | other | JEFFERSON | UNITED TEXAS TRANSMISSION CO | OF HYDRATES FREEZING INSIDE THE PIPELINE, THUS CREATING A LINE BLOCKAGE AND SUBSEQUENT PRESSURE BUILD-UP. THE PRESSURE INCREASE REACHED 108% OF MAOP BEFORE THE PIPE RUPTURED IN A LOCATION WHERE ATMOSPHERIC CORROSION WAS EVIDENT. | 8150 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
102 | 1985-01-22 | TX | other | REAGAN | BIG LAKE GAS DEPT, CITY OF |  | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
103 | 1985-02-10 | TX | other | JASPER | TRANSCO GAS PIPELINE CORP | T TAP CONNECTION AT A BLOCK VALVE ASSEMBLY. CAUSE UNKNOWN. | 68000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
104 | 1985-02-28 | LA | other | CADDO | J - W OPERATING CO | NO COMMENTS GIVEN | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
105 | 1985-02-09 | TX | technical failure | BASTROP | VALERO TRANSMISSION CO | SEAM FAILURE | 30000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
106 | 1985-02-08 | TX | maintenance | GALVESTON | AMOCO GAS CO | INTERNAL CORROSION ON BOTTOM OF PIPE IN LOW AREA OF DITCH CROSSING. | 1250 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
107 | 1985-02-14 | MS | other | ALCORN | COLUMBIA GULF TRANSMISSION CO | EZING THIS VALVE IS ABOVE GROUND, AND WAS SUBJECTED TO BELOW ZERO AMBIENT TEMPERATURES. SINCE THE VALVE WAS CLOSED, ICE COULD NOT ESCAPE PAST THE SEAT, THUS FORCING THE GATE UPWARD. THIS CAUSED THE SNAP RING TO FAIL AND VALVE TO SEPARATE. | 65000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
108 | 1985-02-18 | TX | technical failure | WILSON | VALERO TRANSMISSION CO | A 4" X 20" WELD SADDLE DEVELOPED A CRACK IN THE FILLET WELD. | 40000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
109 | 1985-02-22 | TX | other | CHAMBERS | WINNIE PIPELINE CO | BURN. PIG WAS BEING RAN WITH AIR, A STEEL PLATE LEFT INSIDE PIPELINE SPARKED ANDIGNITED PIG WAS BEING RUN WITH AIR, A STEEL PLATE LEFT INSIDE THE BELLHOLE WHEN THE PIG CAME OUT OF THE PIPELINE THROUGH AN OPEN VALVE. | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
110 | 1984-04-16 | OK | other | CUSTER | TRANSOK PIPELINE CO. |  | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
111 | 1985-02-22 | WV | other | WETZEL | CONSOLIDATED GAS SUPPLY CORPORATION | 1/2" NIPPLE BROKE IN THREADS. CONTROL LINE FROM MAIN 24" PIPELINE TO VALVE SETTING. | 55000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
112 | 1985-02-09 | TX | other | BROWN | EL PASO HYDROCARBONS COMPANY |  | 11878 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
113 | 1985-02-11 | TX | other | CASTRO | WESTAR TRANSMISSION CO | PIPE WAS HIT SOMETIME IN THE PAST (TIME UNKNOWN). PIPE HAS LARGE DENT AND GOUGE. PIPE PULLED APART AT GOUGE. PIPE SEPERATED AT THE GOUGE AND CRACKED THREE-QUARTERS OF THE CIRCUMFERENCE OF THE PIPE. | 1500 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
114 | 1985-02-09 | TX | other | BROWN | EL PASO HYDROCARBONS COMPANY |  | 18654 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
115 | 1985-02-14 | TX | other | MATAGORDA | BAY CITY MUNICIPAL GAS SYSTEM | PART B : THIRD PARTY DAMAGE OCCURED ABOVE GROUND. | 1500 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
116 | 1985-02-27 | TX | other | DALLAS | LONE STAR GAS CO | PART B: P/L MARKER WAS DIRECTLY ABOVE WHERE PIPE WAS HIT. CONTRACTOR REMOVED PRIOR TO DAMAGING PIPELINE.LINE HIT BY BACK HOE. | 10750 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
117 | 1985-03-18 | TX | maintenance | WALLER | PHILLIPS OIL CO. | PART A : THIS LINE WAS DEPRESSURED AND APPROXIMATELY 15 FEET OF THE LINE WAS REPPART 3 : BREAKDOWN OF CATHODIC PROTECTION. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
118 | 1985-03-16 | TX | technical failure | GONZALES | TIPPERARY CORPORATION | APPEARED THAT WELD PARTED. | 500 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
119 | 1985-03-04 | TX | maintenance | KLEBERG | HOUSTON PIPELINE CO |  | 5000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
120 | 1985-02-27 | MI | technical failure | CLARE | MICHIGAN GAS STORAGE CO. | PART 3 - 2" BLOWDOWN APPROX 12" UPSTREAM OF FAILED VALVE HAD BEEN OPENED TO CLEAR HYDRATES FROM 4" LATERAL. FAILED VALVE HAD BEEN CLOSED PRIOR TO OPENING 2" BLOWDOWN. AFTER APPROX 1 MINUTE OF BLOWING, VALVE FAILED, BLOWING DIRT OUT OF GROUND. WHEN ADDITIO | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
121 | 1985-03-25 | TX | technical failure |  | TRUNKLINE GAS CO | PART C - LEAK IN FLANGE JOINT AND RING IN RING JOINT FLANGE. | 60000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
122 | 1984-12-04 | WY | other | PARK | RALSTON PROCESSING ASSOC. INC. | D LEAKING AT THREADS; IT GRADUALLY PARTED. THE HIGH PRESSURE (400#) GAS STREAM WAS IGNITED BY FRICTION OF GAS FLOW ON CONCRETE FLOOR, OR SOME OTHER SOURCE. | 80000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
123 | 1985-03-18 | NC | other | BEAUFORT | NORTH CAROLINA NATURAL GAS CORPORATION | CATERPILLAR 225 HYDRALIC TRACK HOE HIT 4" GAS LINE WHILE DIGGING SAND PIT.FOREMAN - R.B. INGRAM HOE OPERATOR - PERRY ROUSE | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
124 | 1985-03-08 | TX | other |  | EL PASO HYDROCARBONS COMPANY | RUPTURE WAS NOT CAUSED FROM CONSTRUCTION OR MATERIAL DEFECTS | 20012 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
125 | 1985-03-18 | TX | other | DIMMIT | VALERO TRANSMISSION CO | DUE TO A LEAKING REPAIR CLAMP. A 21' SECTION OF PIPE WAS INSTALLED TO REPAIR THIS LEAK. | 4000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
126 | 1985-03-29 | TX | other | SAN PATRICIO | VALERO TRANSMISSION CO | CONSTRUNCTION CONTRACTOR HIT 8" ABOVEGROUD RISER WITH A BULLDOZER ON MARCH 29. THE REPAIR WORK WAS DONE ON APRIL 2. THERE WAS NO BREAKAGE OR RUPTURE WHICH REPAIRED EMERGENCY ACTION. | 70000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
127 | 1985-04-01 | TX | other | TRAVIS | VALERO TRANSMISSION CO | PART 2 - DRIVER LOST CONTROL OF VEHICLE LEAVING PUBLIC ROADWAY AND RAN INTO FANCE AND METER STATION ON MONTOPOLIS DRIVE, AUSTIN, TEXAS.PART B.3 - VEHICLE RAN INTO METER STATION #551-124. METER STATION WAS ENCLOSED BY ALLIED FENCING AND MARKED WITH METER S | 4500 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
128 | 1985-04-03 | TX | technical failure | FRIO | VALERO TRANSMISSION CO |  | 2400 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
129 | 1985-03-26 | TX | other |  | LONE STAR GAS CO | LINE HIT BY DOZER | 3417 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
130 | 1985-04-30 | NM | other | SANDOVAL | GAS CO OF NEW MEXICO | LANDSLIDE DUE TO PREVIOUS HIGHWAY CONSTRUCTION; APPARENTLY CAUSED BY WATER SEEPAGE AND INSUFFICIENT COMPACTION. | 10000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
131 | 1985-04-20 | TX | other | PARMER | WESTAR TRANSMISSION CO | SHALLOW PIPE - DEEP PLOWING. FARMER PLOWING FIELD, PLOWHIT PIPELINE CAUSING 2.5" X 2" HOLE IN PIPE BODY. | 500 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
132 | 1985-04-22 | CO | other | WASHINGTON | KN ENERGY INC (KANSAS NEBRASKA NATURAL GAS CO INC) | THE ATTACHED LEAK REPORT COVERS A NATURAL GAS LEAK THAT OCCURED ON K N ENERGY, INC.'S ('KN') 6-INCH TOP-OF-GROUND TRANSMISSION PIPELINE IN WASHINGTON COUNTY, COLORADO ON APRIL 22, 1985. IGNITION DID NOT OCCUR, HOWEVER, SERVICE WAS INTERUPTED TO THREE DOME | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
133 | 1985-04-25 | TX | other |  | ANR PIPELINE CO (AMERICAN NATURAL RESOURCE) | AM OF PLATFORM BLOCK VALVE. | 200000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
134 | 1985-04-15 | TX | other | WALLER | TEXAS SOUTHEASTERN GAS CO | PIPELINE HIT BY FARMER WITH MOLD-BOARD PLOW. | 1000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
135 | 1985-04-12 | LA | other |  | SOUTHERN NATURAL GAS CO | MUDSLIDE ON OCEAN FLOOR INDUCED TENSION ON 10" PPELINE CAUSING A LOAD LIMITING CONNECTOR TO SEPARATE AT UNDERWATER TIE-IN. (DEVICE FUNCTIONED AS DESIGNED) | 600000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
136 | 1985-04-10 | AL | technical failure | MARENGO | SOUTHERN NATURAL GAS CO |  | 25 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
137 | 1985-05-06 | MI | maintenance | MASON | DOW CHEMICAL USA |  | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
138 | 1985-04-27 | KY | other | METCALFE | TEXAS EASTERN GAS PIPELINE CO | AY #90. THE CAUSE OF THE INCIDENT IS CURRENTLY UNDER INVESTIGATION. | 742000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
139 | 1985-05-21 | LA | other | ASCENSION | ACADIAN GAS PIPELINE SYSTEM |  | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
140 | 1985-04-30 | OK | other | PITTSBURG | ARKANSAS LOUISIANA GAS CO (ARKLA GAS CO) | LIGHTNING STRUCK ON OR NEAR THE WELLHEAD DAMGING THE GASKETS ABOVE THE MAIL WELLHEAD VALVE. GAS LEAKAGE FROM DAMAGED GASKET IGNITED. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
141 | 1985-05-02 | KY | other | CLAY | SOMERSET GAS SERVICE | LATE IN THE AFTERNOON OF THURSDAY, MAY 2ND, THE HOME OF JAMES FIELDS, LOCATED TEN MILES EAST OF MANCHESTER ON KY HWY 11 NEAR THE COMMUNIT OF LITTLE WLDCAT, EXPLODED AND BURNED TO THE GROUND. MR. FIELDS, HIS WIFE, ANGIA AND SON, JAMES FIELDS, JR. WERE INJU | 40000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
142 | 1985-05-03 | TX | other | PECOS | VALERO TRANSMISSION CO | PART 3 - EMPLOYEE CLEANING UNIT WITH SOLVENT. SOLVENT IGNITED CAUSING FIRE. FIRE EXTINGUSHED WITHIN 10 MINUTES. | 13000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
143 | 1984-11-16 | WY | other | CONVERSE | MONTANA-DAKOTA UTILITIES COMPANY | VER VIBRATIONS AT THE ENGINE RELIEF VALUE. THIS VIBRATION RUPTURED THE RELIEF VALVE INLET FLANGE GASKET ALLOWING LIQUID TO ESCAPE, SPRAY ON THE EXHAUST MANIFOLD, AN IGNITE. | 150000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
144 | 1985-03-25 | FL | technical failure | INDIAN RIVER | FLORIDA GAS TRANSMISSION CO | PIPE SAMPLES CONTAINING THE BREAK AREA HAVE BEEN SENT TO A METALLURGICAL LAB FOR EVALUATION. THE VALVE SECTION CONTAINING THIS FAILURE HAS BEEN RETESTED (FOLLOWING THE BREAK) TO 1192 PSIG WITH ADDITIONAL FAILURES. | 300000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
145 | 1984-11-18 | FL | maintenance | WASHINGTON | FLORIDA GAS TRANSMISSION CO | PART A.6 - BATTELLE MADE FIELD INVESTIGATION. PRELIMINARY INDICATION IS THAT FAILURE IS DUE TO STRESS CORROSION. SAMPLES HAVE BEEN SENT TO LAB FOR ANALYSIS ANDPART3 - IT APPEARS THAT THE FAILURE WAS DUE TO STRESS CORROSION CRACKING. | 275000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
146 | 1985-02-25 | AL | maintenance | MOBILE | FLORIDA GAS TRANSMISSION CO | PART A.6 - BATELLE MADE FIELD INVESTIGATION. PRELIMINARY INDICATION IS THAT FAILURE IS DUE TO STRESS CORROSION. SAMPLES HAVE BEEN SENT TO LAB FOR ANALYSIS AND REPORT. | 510000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
147 | 1985-06-03 | TX | maintenance | LA SALLE | VALERO TRANSMISSION CO | PART A.6 - THE REASON THIS LINE WAS NOT UNDER ADEQUTE PROTECTION WAS DUE TO ONERECTIFIER BEING OUT. THIS UNIT IS SCHEDULED FOR REPLACEMENT AND TWO ADDITIONAL UNITS BE BUILT THIS YEAR. | 9000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
148 | 1985-05-28 | TX | other | MATAGORDA | CHANNEL INDUSTRIES GAS CO. |  | 300 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
149 | 1985-05-21 | MT | other | MISSOULA | MONTANA POWER CO | A RIPPER PULLED BY A D-8 TRACTOR TORE A LARGE HOLE IN THE PIPE RESULTING IN A VERY RAPID LOSS OF GAS TO THE ATMOSPHERE | 36000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
150 | 1985-05-24 | UT | other | SAN JUAN | EL PASO NATURAL GAS CO | AN EXPLOSION OCCURED ON THE MAIN STARTING AIR HEADER. SOURCE OF IGNITION AND CAUSE OF RUPTURE HAS NOT BEEN DETERMINED AT THIS TIME.PART 4.1 - STARTING AIR SYSTEM 4.2 - BODY OF PIPE, VALVE, FITTING | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
151 | 1985-05-16 | TX | other | MADISON | LONE STAR GAS CO | OUTSIDE FORCES DAMAGED 3-INCH LINE WHILE LAYING TELEPHONE LINE AND DID NOT REPORT DAMAGE UNTIL LATER. LINE BEGAN LEAKING 5/16/85 | 3800 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
152 | 1985-06-11 | NJ | other | ESSEX | PUBLIC SERVICE ELECTRIC AND GAS COMPANY | AT SOMETIME PREVIOUS AND UNKNOWN TO THIS COMPANY THE PIPE WAS DAMAGED BY EXCAVATING EQUIPMENT AS VERIFIED BY INDENTATINS ON THE PIPE. RUPTURE, HOWEVER, DID NOTOCCUR UNTIL THIS DATE. | 80000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
153 | 1985-05-20 | TX | other | ELLIS | INDUSTRIAL GAS TRANS. CO. | CITY OF WAXAHACHIE, TEXAS WATER DEPARTMENT WAS EXCAVATING FOR INSTALLATION OF SEWER AND STRUCK IGT 6" LINE SEVERAL TIMES WITH CASE BACKHOE BUCKET BLADE. | 1590 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
154 | 1985-06-06 | TX | maintenance | NAVARRO | TEXAS UTILITIES FUEL CO | PITTED FROM THE INSIDE OUT FROM CORROSION. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
155 | 1985-06-09 | AR | other | SALINE | ARKANSAS LOUISIANA GAS CO (ARKLA GAS CO) | OPERATOR OF D-9 DOZER FOR ALCOA MINING BECAME STUCK ON R.O.W. HE LOWERED RIPPERFOOT AND CUT INTO LINE AM-25. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
156 | 1985-05-31 | MI | maintenance | CLARE | MICHIGAN GAS STORAGE CO. | DURING ROUTINE SURVEILLANCE, OBSERVED SAND HUMPED UP AND BLOWING IN WELLLEAK LOCATED APPROX. 250' SOUTH OF WELL. LINE COATED WITH #7 WAX WRAPPER.REPLACED APPROX. 8' OF PIPE AND COATED WITH TAPECOAT #20.PART A - METALLURGY LABORATORY IS PERFORMING AN ANALY | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
157 | 1985-06-11 | TX | maintenance | GALVESTON | BLACK MARLIN PIPELINE CO |  | 250000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
158 | 1985-06-14 | KY | other | BELL | DELTA NATURAL GAS CO INC | PINEVILLE, KY, DELTA NATURAL GAS COMPANY, INC., WAS REQUIRED TO RELOCATE ITS EXISTING LINES AND TOWN BORDER STATION. SOME OF THE WORK WAS COMPLETED IN 1983 ANDTHE REMAINING WORK WAS SCHEDULED TO BE COMPLETED IN 1985. WORK COMMENCEDON APRIL 30, 1985, CASIN | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
159 | 1985-06-26 | TX | other | CALDWELL | INTRATEX GAS COMPANY OPERATOR FOR OASIS PIPE COMPA | COMPRESSOR WAS BEING STARTED. THE SEPARATED LINE DISCHARGED GAS INTO THE COMPRESSOR BUILDING AND THE GAS WAS IGNITED, CAUSING A FIRE WHICH WAS EXTINGUISHED WITHIN 1 1/2 MINUTES BY THE ACTIVATION OF THE ESD SYSTEM. | 5000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
160 | 1985-07-05 | TX | other | YOAKUM | WESTAR TRANSMISSION CO | MABEE PETROLEUM CORP. HIRED WEST ENGINEERING OUT OF HOBBS TO SURVEY WELL LOCATION, THEN IN TURN HIRED BUTCH'S RAT HOLE AND ANCHOR SERVICE TO DRILL RAT HOLE, WHILE DRILLING RAT HOLE - PUNCTURED CABOT'S (WESTAR) 12" FROM SHELL WASSON TO LEVELLAND. | 11000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
161 | 1985-06-17 | SD | other | KINGSBURY | NORTHERN NATURAL GAS CO |  | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
162 | 1985-06-28 | MN | other | STEVENS | NORTHERN NATURAL GAS CO |  | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
163 | 1985-06-09 | TX | maintenance | NUECES | VALERO TRANSMISSION CO | THIS INCIDENT WAS DUE TO A LEAK ON OUR REFERENCED PIPELINE BETWEEN I.H. 37 AND THE ACCESS ROAD NEAR CORPUS CHRISTI. WE HAVE NOT RECEIVED APPROVAL FROM THE TEXAS HOGHWAY DEPARTMENT TO EXCAVATE IN THEIR RIGHT-OF-WAY, SO WE HAVE NOT BEEN ABLETO DETERMINE THE | 10000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
164 | 1985-06-15 | TX | maintenance | ARANSAS | VALERO TRANSMISSION CO | PART A - CATHODIC PROTECTION INSTALLED PRIOR TO 1969. WE DO NOT HAVE RECORDS FOR THIS LINE BEFORE 1969. | 3000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
165 | 1985-06-17 | TX | technical failure | HARRIS | HOUSTON PIPELINE CO | PART C - AN ORIGINAL ACETYLENE BUTT WELD LEAKED. | 1000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
166 | 1985-06-24 | TX | other | KERR | LONE STAR GAS CO | LINE HIT BY FRONT-END LOADER. | 7941 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
167 | 1985-06-19 | TX | maintenance | NAVARRO | TEXAS UTILITIES FUEL CO | BLOW-OUT ON 6" LINE NORTH MILE MARKER K-9 ABOUT 6,000 FEET BETWEEN TO LEAKS REPAIRED AND WEEK BEFORE. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
168 | 1985-06-07 | MI | technical failure | OAKLAND | MICHIGAN CONSOLIDATED GAS CO (MICHCON) | A 1" DRAIN CONNECTION ON A COMPRESSOR DISCHARGE BOTTLE FAILED IN THE THREAD AREA OF A PIPE NIPPLE. THE BUILDING FILLED WITH GAS AND AN EXPLOSION ESUED. CAUSE OF IGNITION UNKNOWN. | 940000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
169 | 1985-06-29 | FL | other | BROWARD | FLORIDA GAS TRANSMISSION CO | CONTRACTOR EMPLOYEE WORKING TOO CLOSE TO PIPELINE WITH LARGE RUBBER-TIRED FRONTEND LOADER. BELIEVED TO BE BACKFILLING AROUND 48" STORM DRAIN WHICH CROSSED UNDERNEATH OUR PIPELINE. APPARENTLY GOT TOO CLOSE AND TRAILER FELL IN ON OUR EXPOSED PIPELINE. | 90000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
170 | 1985-06-25 | TX | maintenance |  | ANR PIPELINE CO (AMERICAN NATURAL RESOURCE) | PART A - CORROSION OCCURED ON CAD WELD OF ANODE TO PIPELINE, SUSPECTED DAMAGE OCCURED DURING CONSTRUCTION LAY OR BURY OPERATIONS. | 130000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
171 | 1985-07-09 | TX | other | RANDALL | WESTAR TRANSMISSION CO | ROD BUILDING CONTRACTOR HIT 20" PIPELINE INSIDE A 26" CASING, RIPPING CASING AND CREASING 20" PIPE, CAUSING SMALL LEAK. CASING WAS INSTALLED TO HIGWAY STANDARDS , BUT A MISTAKE ON GRADES CAUSED DITCH TO BE DUG TOO DEEP. HIGHWAY DEPT. ACCEPTED RESPONSIBILI | 10000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
172 | 1985-07-14 | TX | technical failure | FORT BEND | HOUSTON PIPELINE CO | PART C - THE THREADS OF THE VALVE LEAKED. THE VALVE IS OWNED BY THE SUBCNTRACTOR WHO WAS PERFORMING THE STOPPEL AND BYPASS ON THE PIPELINE. | 10000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
173 | 1985-06-27 | TX | other | BURLESON | FERGUSON CROSSING PIPELINE COMPANY | N PIPE IGNITED CAUSING GRASS TO IGNITE. | 100 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
174 | 1985-07-26 | TX | other | EASTLAND | SOUTHWESTERN GAS PIPELINE INC | PART B - THE THIRD PARTY IS ON THE OPERATORS LIST OF EXCAVATORS FOR ANNUAL NOTIFICATION TO CALL BEFORE DIGGING WHERE PIPELINE ARE PREVALENT. THE THIRDS PARTY DID NOT NOTIFY OPERATOR BEFORE EXCAVATING.PART 3 - DOZER, OPERATOR FAILED TO CALL BEFORE BEGINNIN | 3500 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
175 | 1985-07-05 | TX | maintenance | GLASSCOCK | EL PASO NATURAL GAS CO | AN EL PASO NATURAL GAS (EPNG) EMPLOYEE WAS OPERATING A BACKHOE, MAKING FINAL PASSES TO CLEAN OUT THE BOTTOM OF THE BELL HOLE WHEN COMPACTED DIRT UNDERNEATH THEPIPE CRUMBLED AWAY, ALLOWING A CORRODED SEGMENT APPROXIMATELY 3" X 6" TO FALL FROM THE BOTTOM OF | 42415 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
176 | 1985-07-03 | TX | other | COLLINGSWORTH | LONE STAR GAS CO | PART 3 - LINE HIT BY PLOW.PART B - PERMANENT MARKER WAS 50 FEET FROM WHERE LINE 72-6" WAS HIT BY PLOW. | 2300 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
177 | 1985-08-07 | LA | other | ASSUMPTION | ACADIAN GAS PIPELINE SYSTEM |  | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
178 | 1985-08-12 | IL | maintenance | MORGAN | PANHANDLE EASTERN PIPELINE CO |  | 75000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
179 | 1985-01-28 | WV | other | KANAWHA | FMC CORP. INDUSTRIAL CHEM. GROUP, SPECIALTY CHEM. | T. TWO FAILURES WERE FOUND ABOUT 6 FEET APART IN THE 3-INCH LINE APPROXIMATELY 200 FEET SOUTH OF ROUTE 60 BETWEEN THE MAIN OFFICE AND BUILDING 316. THE FAILURES WERE CAUSED BY WATER FREEZING IN THE 3-INCH LINE, WHICH APPARENTLY HAD NOT BEEN TRANSPORTING H | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
180 | 1985-08-20 | TX | other | ZAPATA | ZAPATA GATHERING CO. | LANDOWNER WAS ROOT PLOWING IN BRUSH AREA, PULLING ROOT PLOW INTO SIDE OF 16" TOP OF LINE. LOCATION WAS IN A NATURAL ARROYO - EROSION HAD REDUCED COVER TO APPROXIMATELY 24". | 10000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
181 | 1985-08-14 | MI | maintenance | MASON | DOW CHEMICAL USA |  | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
182 | 1985-08-26 | OK | other | OKLAHOMA | MOBIL OIL CORPORATION | CIMARRON CONSTRUCTION WAS CONSTRUCTED BY CONOCO TO INSTALL A GATHERING SYSTEM FOR SEVERAL TXO WELLS IN THE AREA. MOBIL WAS NOTIFIED OF THE INSTALLATION AND HADFLAGGED THEIR LINES. CIMARRON CONSTRUCTION DUG A TRENCH AND UNCOVERED SEVERAL OF MOBIL'S LINES. | 106500 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
183 | 1985-09-17 | PA | other | CHESTER | TEXAS EASTERN GAS PIPELINE CO | DE A METALLIC BUILDING USED TO ODORIZE TRANSMISSION GAS IN ACCORDANCE WITH NEW JERSEY STATE REQUIREMENTS. THE FIRE TOTALLY DESTROYED THE BUILDING AND ITS ONTENTS WHICH INCLUDED ODORIZATION EQUIPMENT, DATA ACQUISITION EQUIPMENT AND OFFICE FIXTURES. NO INFO | 175500 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
184 | 1985-09-09 | LA | other |  | NATURAL GAS PIPELINE CO OF AMERICA |  | 600000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
185 | 1985-09-07 | AK | other |  | ALASKA PIPELINE CO. | WILDER CONSTRUCTION WAS BUILDING ROAD ADJACENT TO 12" LINE - LEFT WORK EQUIPMENT PARKED ON SIDE OF ROAD. AT APPROX. 4:30AM THE FOLLOWING MORNING SOMEONE STARTED A LARGE BACKHOE-DUG SEVERAL HOLES AND ON THE 4TH HOLE STRUCK THE GAS LINE.PART B - OPERATOR OF | 20000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
186 | 1985-08-30 | LA | other | OFFSHORE | SOUTHERN NATURAL GAS CO |  | 2000000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
187 | 1985-09-01 | TX | technical failure |  | SEA ROBIN PIPELINE CO | AFTER INSTALLING A 16" X 36" HYDROTECT HOTTAP FITTING, A LEAK DEVELOPED OUT OFTHE NORTH PACKING FLANGE. TAP WAS INSTALLED ON OCS-1907, INDEX 700, VERMILLIONAREA COORDINATES, X=1, 728,572.61; Y=216,644.68 | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
188 | 1985-09-18 | NM | other |  | BENSON-MONTIN-GREER DRILLING CORP. BRAZOS GAS TRAN |  | 7531 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
189 | 1985-10-16 | LA | other |  | SEA ROBIN PIPELINE CO | LEAK WAS VERIFIED AS BELONGING TO SEA ROBIN AT 0700 OCTOBER 17, 1985. LEAK APPEARED TO BE CAUSED BY SHRIMP NETS FOULING THE 2-INCH TAP. | 180000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
190 | 1985-10-09 | LA | technical failure | JEFFERSON DAVIS | LOUISIANA GAS SYSTEM INC | A LEAK WAS DETECTED ON A LOUISIANA GAS SYSTEM PIPELINE APPROXIMATELY TWO (2) MILES SOUTH OF HAYES, LOUISIANA AT APPROXIMATELY 10:50 A.M. ON OCTOBER 9, 1985. THE LEAK WAS CAUSED WHEN A BONNET DISLOGED FROM A VALVE WHICH CONNECTED A 4" GATHERING LATERAL TO | 4000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
191 | 1985-10-08 | LA | maintenance | VERMILLION | ANR PIPELINE CO (AMERICAN NATURAL RESOURCE) | FAILURE OCCURRED ON 4" PIPE EXTENDING FROM 8" BURIED CATHODICALLY PROTECTED PIPELINE TO AN ABOVEGRADE VALVE LOCATED IN A REMOTE MARSH. CORROSION AND FAILURE OCCURRED IN VICINITY OF GROUND LEVEL. BURIED PIPE HAS BEEN UNDER CATHODIC PROTECTION SINCE INSTALL | 60000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
192 | 1985-10-27 | LA | other |  | TRUNKLINE GAS CO | WINDS & WAVES CAUSED BY HURRICANE JUAN COMPLETELY DESTROYED ODECO'S PRODUCTION PLATFORM ON WHICH WE HAD AN 8" SINGLE METER MEASURING STATION #319B-2721-P AND A10" LINE #319B-2700 TIED INTO PLATFORM. | 750000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
193 | 1985-11-01 | PA | maintenance | LANCASTER | COLUMBIA GAS TRANSMISSION CORP | AT APPROXIMATELY 4:00 A.M. ON NOVEMBER 1, 1985, COLUMBIA GAS TRANSMISSION'S PIPELINE 1804 RUPTURED NEAR MARIETTA, PA. COLUMBIA'S GAS CONTROL CENTER AT BETHEL PARK NEAR PITTSBURGH, PA OBSERVED A SIGNIFICANT PRESSURE DROP IN LINE 1804 AT APPROXIMATELY 4:10 | 250000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
194 | 1985-10-22 | WV | maintenance | KANAWHA | AJAX PIPELINE CO | GAS MIGRATED FROM LEAK TO BASEMENT OF HOUSE VIA A SEPARATED DRAIN LINE THAT WASINSTALLED OVER THE GAS LINE. | 30000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
195 | 1985-10-26 | KY | other | FLEMING | TEXAS EASTERN GAS PIPELINE CO |  | 817000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
196 | 1985-09-23 | RI | other | PROVIDENCE | TENNESSEE GAS PIPELINE CO | PUNTURED BY OUTSIDE CONTRACTOR BUILDING ACCESS ROAD FOR NEW ENGLAND POWER CO. D8L CAT. DOZER PUT A 4" X 16" HOLE IN THE LINE. | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
197 | 1985-11-04 | TX | other |  | ANR PIPELINE CO (AMERICAN NATURAL RESOURCE) |  | 85000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
198 | 1985-11-06 | AR | maintenance | WHITE | NATURAL GAS PIPELINE CO OF AMERICA | THE HEAT EXCHANGER TEST SAMPLE SHOWED EVIDENCE OF INTERGRANULAR CORROSION DAMAGE IN THE 3003 ALUMINUM FIN SHEET | 200000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
199 | 1985-11-15 | MO | other | PLATTE | NORTHWEST CENTRAL PIPELINE CORP |  | 64500 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
200 | 1985-11-29 | IN | maintenance | PIKE | MIDWESTERN GAS TRANSMISSION CO | RUPTURE WAS CAUSED BY BACTERIAL CORROSION. NO OUTSIDE FORCES WERE INVOLVED. PIPE AT POINT OF RUPTURE WAS LYING ON COAL. | 1100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
201 | 1985-11-29 | WV | technical failure | LEWIS | CONSOLIDATED GAS TRANSMISSION CORP | THE FAILURE OCCURED AT AN INCOMPLETE WELD BETWEEN TWO JOINTS AND WAS APPARENTLYCAUSED BY A STRESS WHICH WAS PUT ON THE LINE BY A NEARBY SLIP IN THE LAND. | 35350 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
202 | 1985-12-13 | LA | other |  | EXXON CO USA | FIRES AND NO INJURIES. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
203 | 1985-11-28 | KS | maintenance | STAFFORD | NORTHERN NATURAL GAS CO |  | 80000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
204 | 1985-12-02 | AR | technical failure | CLARK | ARKANSAS LOUISIANA GAS CO (ARKLA GAS CO) | THERE ARE SEVERAL CRACKS IN THE HEAT AFFECTED ZONE NEAR THE LONGITUDINAL SEAM. EVEN AFTER EXTENSIVE FIRE EXPOSURE THERE ARE ENOUGH CHEVRON MARKS TO SOMEWHAT ISOLATE THE ORIGIN ON THE FAILURE. IT APPEARS THAT THE FAILURE BEGAN IN THE SEAM, PROPAGATED IN TH | 308000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
205 | 1985-12-07 | KS | other | RICE | NORTHERN NATURAL GAS CO | A CRACK DEVELOPED IN A MODEL G-3301-D, INGERSOLL-RAND COMPRESSOR CYLINDER.THE CAUSE OF THE CRACK HAS NOT YET BEEN DETERMINED. | 500000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
206 | 1985-12-23 | LA | other | PLAQUEMINES | SOUTHERN NATURAL GAS CO | PIPLINE APPERENTLY RUPTURED IN THE MISSISSIPPI RIVER. DUE TO HIGH WATER ANDSTRONG CURRENT, A DIVING INVESTIGATION TO DETERMINED THE CAUSE CANNOT BEACCOMPLISHED AT THIS TIME. A SUPPLIMENTAL REPORT WILL BE FILLED AT A LATERDATE. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
207 | 1985-11-12 | MS | other | MARSHALL | TENNESSEE GAS PIPELINE CO |  | 75000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
208 | 1985-12-15 | PA | technical failure | POTTER | CONSOLIDATED GAS TRANSMISSION CORP | SALT BATH HEATER - THE WELD ON THE CAP WHERE IT WAS WELDED TO THE TUBE SHEETRUPTURED CAUSING A CRACK 14 INCHES LONG. | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
209 | 1985-12-19 | AL | other | BALDWIN | FLORIDA GAS TRANSMISSION CO | THIS BREAK OCCURED BETWEEN FLORIDA GAS TRANSMISSION COMPANY'S MAINLINA VALVES 11-2 AND 11-3. VALVE 11-2 IS EQUIPPED WITH AN AUTOMATIC OPERATOR WITH LINE BREAK CONTROLS. VALVE 11-2 CLOSED AUTOMATICALLY. VALVE 11-3 IS NOT EQUIPPED WITH A POWER OPERATOR AND | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
210 | 1985-12-31 | NM | technical failure | OTERO | EL PASO NATURAL GAS CO |  | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
211 | 1985-12-21 | NV | other | WASHOE | SOUTHWEST GAS CORP | A SIX-FOOT LONG SCAR AND DENT ON THE TOP AND SIDE OF THE PIPE, LEAD TO THE EVENTUAL RUPTURE. DAMAGE WAS DONE BY OUTSIDE FORCES, EITHER DURING ORIGINAL INSTALLATION IN 1963, OR DURING PARALLEL CONSTRUCTION IN 1979. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
212 | 1985-12-21 | PA | technical failure | CLINTON | CONSOLIDATED GAS TRANSMISSION CORP | PIPE RUPTURED WITH THE LENGTH OF OPENING EXTENDING APPROXIMATELY 4" ALONG THE LONGITUDINAL AXIS OF THE PIPE. CAUSE OF SEQUENCE OF EVENTS THAST LED TO THE RUPTURE AND FIRE ARE UNKNOWN AT THIS TIME. INVESTIGATION IS CONTINUING. | 465700 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
213 | 1985-12-30 | TX | other | WARD | EL PASO NATURAL GAS CO | MERRYMAN CONSTRUCTION CO UNDER CONTRACT BY EL PASO NATURAL GAS CO, HIT THE 3" PLASTIC FUEL LINE WITH A BACKHOE WHILE CHECKING THE CASING ON ONE OF EL PASO'S PIPELINES. THE PLASTIC LINE BELONGED TO THE CITY OF GRANDFALLS, TX. SERVICE WAS INTERUPTED TO GRAN | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
214 | 1986-01-27 | WY | other | CAMPBELL | PHILLIPS 66 NATURAL GAS CO | PIPELINE PRESSURE WAS BEING REDUCED BY VENTING TO THE ATMOSPHERE. SOME UNKNOWN SOURCE IGNITED THE GAS. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
215 | 1986-01-17 | IL | other | MORGAN | PANHANDLE EASTERN PIPELINE CO | THE OPERATION OF A BACKHOE IN THE VICINITY OF A 2" BRANCH CONNECTION INTRODUCEDSTRESSES IN THE PIPING WHICH CAUSED IT TO BREAK AT THE TAP CONNECTION TO A 16" PIPELINE | 60000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
216 | 1986-01-15 | LA | other | OFFSHORE | COLUMBIA GULF TRANSMISSION CO |  | 120000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
217 | 1986-02-10 | AL | technical failure | BALDWIN | FLORIDA GAS TRANSMISSION CO | CRACK ON TOP OF GIRTH WELD WAS LEAKING. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
218 | 1986-02-21 | TX | other | HARRIS | TRANSWESTERN PIPELINE CO | A BROKEN BOLT IN THE COMPRESSOR CAUSED VIBRATION WHICH CAUSED A 4.5" NIPPLE FROM A SUCTION BOTTLE TO BREAK AROUND A CIRCUMFERENTIAL FILLET WELD. | 117000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
219 | 1986-02-21 | KY | other | GARRARD | TEXAS EASTERN GAS PIPELINE CO | THE PIPELINE RUPTURED NEAR THE SOUTH END OF A ROAD CROSSING AT KENTUCKY STATE HIGHWAY #52. THE CAUSE OF THE INCIDENT IS CURRENTLY UNDER INVESTIGATION. | 1300000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
220 | 1986-02-14 | KS | other | WALLACE | KN ENERGY INC (KANSAS NEBRASKA NATURAL GAS CO INC) | LEAK REPORT COVERS A NATURAL GAS LEAK THAT OCCURED ON K N ENERGY, INC.'S (K N) 3-INCH TRANSMISSION PIPELINE IN WALLACE COUNTY, KANSAS ON FEBRUARY 14, 1986. IGNITION DID NOT OCCUR. HOWEVER, THE LEAK DID DISRUPT SERVICE TO CITY OF SHARON SPRINGS, KS, FOR A | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
221 | 1986-02-13 | WV | other | LEWIS | CONSOLIDATED GAS TRANSMISSION CORP | STATION EMPLOYEE OPENED 1" BALL VALVE ON BYPASS WHICH ALLOWED GAS AT 835 PSIG TO ENTER EMCO METER (RATED AT 100 PSIG) RESULTING IN METER CASE RUPTURING. | 600 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
222 | 1986-02-19 | NV | other |  | SOUTHWEST GAS CORP | FLOODING OF THE TRUCKEE RIVER NEAR WADSWORTH, NV CAUSED THE 12" STEEL HIGH PRESSURE CARSON LATERAL TO BE WASHED OUT WHERE IT CROSSES THE TRUCKE RIVER.SEE ATTACHED LETTER.INTENSE RAIN STORMS BEG. ON THE 13TH OF FEB. CAUSED FLOODINGOF THE TRUCKEE RIVER. THI | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
223 | 1986-02-24 | AR | technical failure | NEVADA | ARKANSAS LOUISIANA GAS CO (ARKLA GAS CO) | LINE "S", 20" O.D. PIPELINE BLEW OUT AT 75' SECTION IN THE BODY OF THE PIPE. | 147354 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
224 | 1986-02-23 | CA | other | TEHAMA | PACIFIC GAS & ELECTRIC CO | TRANSMISSION MAIN RUPTURED DUE TO STRESS CAUSED BY EXCESSIVE WATER FLOW IN SACRAMENTO RIVER DURING FLOODING. | 1350000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
225 | 1986-03-06 | CA | other | PLACER | PACIFIC GAS & ELECTRIC CO | PREVIOUS DAMAGE TO PIPELINE BY CONTRACTOR WAS DISCOVERED BY PG AND E PERSONNEL AND LEAKAGE REPAIRED. CONTRACTOR, WHILE GRADING PROPERTY, STRUCK STEEL PIPELINEWITH A CATERPILLAR TRACTOR ALLOWING GAS TO ESCAPE TO ATMOSPHERE. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
226 | 1986-03-17 | TX | technical failure | GALVESTON | CHEVRON PIPELINE CO | EQUIPMENT FAILURE INSIDE A GAS FIRED - WATER FILLED ETHYLENE HEATER. THIS HEATER HAS ETHYLENE PASSING THRU A TUBE COIL ETHYLENE HEATER. ITS TEMPERATURE FOR BETTER MEASUREMENT. IT APPEARS THAT THERE WAS A TUBE FAILURE. UNTIL DOW PIPE LINE COMPLETES THE | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
227 | 1986-03-26 | KY | other | KNOX | DELTA NATURAL GAS CO INC | AN EQUIPMENT OPERATOR MINING COAL AT 9:30P.M. GOUGED A HOLE IN THE 6" STEEL PIPELINE. THE AFFECTED SECTION OF THE LINE WAS TAKEN OUT OF SERVICE UNTIL THE NECESSARY REPAIRS WERE MADE. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
228 | 1986-03-09 | CA | other | COLUSA | PACIFIC GAS & ELECTRIC CO | IT IS SPECULATED THAT HEAVY WATER RUN-OFF CREATED UNDUE FFORCE ON THE 10" PIPELINE RESULTING IN THE LINE BREAK. | 88000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
229 | 1986-03-02 | TX | other | WALLER | TENNESSEE GAS PIPELINE CO |  | 244662 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
230 | 1986-04-03 | NJ | other | SALEM | SUNOLIN CHEMICAL CO | DUPONT ADVISED SUN OLIN THAT SOME ELECTRICAL WORK WAS GOING TO BE DONE AT THE UNION CARBIDE CONSTRUCTION SITE IN NEW JERSEY NEAR THE METERING STATION. SUN OLINNOTITIED SUN PIPELINE TO SUPPLY SOMEONE FOR THE JOB. SUN PIPELINE REPRESENTATIVE, JIMMY JACKSON | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
231 | 1986-01-23 | LA | other | ST JOHN THE BAPTIST | ST JOHN THE BAPTIST PARISH UTILITIES | THE CONTRACTOR WAS IN THE PROCESS OF CONDEMNING AN EXISTING GAS LINE WHEN LEAKING GAS IGNITED. | 15000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
232 | 1986-03-24 | LA | other | TERREBONNE | UNITED GAS PIPELINE CO | A CARGO VESSEL (THE GREEN CANYON EXPRESS) TRAVELING IN DENSE FOG, COMPLETELY OUTOF THE CHANNEL, IN THE HOUMA NAVIGATION CANAL, STRUCK THE CANAL CROSSING RISER, SEVERING THE LINE AND IGNITING THE GAS. THE GAS SUPPLY WAS CUT OFF WITHIN MINUTES BY SUPERIOR | 260000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
233 | 1986-04-01 | LA | other | AVOYELLES | UNITED GAS PIPELINE CO | OIL HOLES ON COMPRESSOR BEARING APPARENTLY WERE CLOGGED CAUSING THE BEARING ANDSHAFT TO OVERHEAT AND IGNITE THE OIL AND GAS. | 92906 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
234 | 1986-02-18 | AL | maintenance | WASHINGTON | COLLET VENTURES INC- COPELAND PLANT | ORIGINAL TESTING SHOWED POSSIBLE MATERIAL DEFECT BUT AFTER EXTENXIVE TESTING ITWAS PROVEN TO BE SULFIDE STRESS DUE TO LACK OF CONSTANT FLOW THROUGH LINE. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
235 | 1986-05-07 | WV | maintenance | LOGAN | UNION CARBIDE CORP | THE INCIDENT OCCURED IN A 10" NATURAL GAS PIPELINE APPROXIMATELY 40 FEET FROM THE FENCE LINE OF A COMPRESSOR STATION WHICH PUMPS NATURAL GAS. GENERAL EXTERNAL GALVANIC CORROSION ACCELERATED BY THE COMPRESSOR OUTLET TEMPERATURE (90 DEGREES F) IS BELIEVED T | 15800 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
236 | 1986-05-03 | MT | maintenance | POWELL | MONTANA POWER CO | THE RUPTURE ORIGINATED IN A LOCALIZED CORROSION AREA APPROXIMATELY ONE (1) FOOTIN DIAMETER. RUPTURE PROPAGATED TO THE THREE (3) FOOT LENGTH MENTIONED ABOVE. | 160000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
237 | 1986-04-08 | MT | other | PARK | MONTANA POWER CO | A SELF POWERED SCRAPPER PUSHED BY A D-7 TRACTOR TORE A VERY LARGE HOLE IN THE PIPE RESULTING IN A RAPID LOSS OF GAS TO THE ATMOSPHERE. | 30300 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
238 | 1986-04-21 | CO | other | MESA | ROCKY MOUNTAIN NATURAL GAS CO INC | CHANGING ORIFACE IN A "DANIELS ORIFACE FITTIN" GAS ESCAPED AND SOME IGNITION, POSSIBLE SPARK FROM STATIC ELECTRICITY FROM STEEL TOOLS OR CLOTHING UNABLE TO DETERMINE EXACTLY. VERY LITTLE EXPLOSION - FLASH BURN UNDER PRESSURE PROBLEM. | 6000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
239 | 1986-04-11 | KS | maintenance | STAFFORD | NORTHERN NATURAL GAS CO |  | 150000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
240 | 1986-04-24 | KS | other | PHILLIPS | KN ENERGY INC (KANSAS NEBRASKA NATURAL GAS CO INC) | 2 3/8" BURIED LINE WAS DAMAGED BY J B FIELD, HIRED MAN FOR NELSON FARMS, LONG ISLAND, KANSAS, WHILE CHISELING GROUND. NO PRIOR NOTIFICATION TO K N THAT WORK WAS GOING TO BE DONE. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
241 | 1986-04-17 | LA | technical failure | JACKSON | UNITED GAS PIPELINE CO | WILL BE FILLED IN AFTER METALURGICAL INVESTIGATION IS COMPLETE; ON SUPPLEMENTAL | 431224 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
242 | 1986-05-06 | KY | other | CHRISTIAN | WESTERN KENTUCKY GAS CO | DOZER OPERATOR HIT LINE WHILE MAKING A DRAINAGE WATERWAY ACROSS FARM LAND. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
243 | 1986-04-23 | CA | other | RIVERSIDE | SOUTHERN CALIFORNIA GAS CO | TWO FISHER MODEL 472-AC 6" RELIEF VALVES AT WHITEWATER STATION "FAILED" IN THE OPEN POSITION WHEN COMPANY PERSONNEL MISTAKENLY CLOSED A 2" CONTROL VALVE DURINGA PIGGING OPERATION. | 132260 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
244 | 1986-03-31 | OK | maintenance | BECKHAM | NATURAL GAS PIPELINE CO OF AMERICA | RUPTURE OCCURED DUE TO INTERNAL CORROSION. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
245 | 1986-05-31 | TX | technical failure |  | BLACK MARLIN PIPELINE CO |  | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
246 | 1986-05-31 | TX | maintenance | PANOLA | UNITED GAS PIPELINE CO |  | 250000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
247 | 1986-05-28 | LA | technical failure |  | ANR PIPELINE CO (AMERICAN NATURAL RESOURCE) | LEAK LOCATED AT LONGITUDINAL SEAM. SEAM LOCATED NEAR TOP OF PIPE AT THE 10:30 POSITION. | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
248 | 1986-04-30 | AZ | other | MARICOPA | EL PASO NATURAL GAS CO | BLUESTAKE REQUIRES UPDATE OF MARKINGS IF OVER 10 DAYS AND NO CONSTRUCTION ACTIVITY ON PAVED AREAS AND 5 DAYS ON DIRT SURFACES. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
249 | 1986-05-11 | CO | other | GARFIELD | NORTHWEST PIPELINE CORP |  | 47200 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
250 | 1986-05-09 | CA | other | CONTRA COSTA | STANDARD PACIFIC GAS LINE INC |  | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
251 | 1986-05-07 | IA | technical failure | HARRISON | NORTHERN NATURAL GAS CO |  | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
252 | 1986-04-08 | TX | other | POLK | UNITED TEXAS TRANSMISSION CO |  | 63687 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
253 | 1986-06-09 | GA | other | ROCKDALE | TRANSCO GAS PIPELINE CORP |  | 150000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
254 | 1986-06-17 | MO | other | PLATTE | NORTHWEST CENTRAL PIPELINE CORP |  | 30000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
255 | 1986-06-03 | NE | other | DAWSON | KN ENERGY INC (KANSAS NEBRASKA NATURAL GAS CO INC) |  | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
256 | 1986-07-04 | NE | other | MADISON | KN ENERGY INC (KANSAS NEBRASKA NATURAL GAS CO INC) |  | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
257 | 1986-07-12 | AL | other | AUTAUGA | SOUTHERN NATURAL GAS CO |  | 1300000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
258 | 1986-08-05 | LA | other | ASSUMPTION | ACADIAN GAS PIPELINE SYSTEM |  | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
259 | 1986-07-18 | MS | other | ADAMS | MID - LOUISIANA GAS CO |  | 130000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
260 | 1986-07-09 | LA | other | ASSUMPTION | ACADIAN GAS PIPELINE SYSTEM |  | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
261 | 1986-06-24 | TX | other | LIBERTY | ENSERCH GAS TRANSMISSION CO | A VACUUM TRUCK HIT OUR LINE. TRHE IMPACT BROKE THE WELD SADDLE OFF OF THE 16' LINE CAUSING THE PIPE TO RUPTURE AND THE GAS WAS IGNITED BY THE TRUCK ENGINE. THERESULTING FIRE KILLED THE DRIVER AND COMPLETELY DESTROYED ALL EGT MEASUREMENT AND ODORIZATION FA | 311590 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
262 | 1986-07-06 | OK | other | CLEVELAND | NORTHWEST CENTRAL PIPELINE CORP |  | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
263 | 1986-08-12 | AZ | technical failure | COCONINO | EL PASO NATURAL GAS CO | ON AUGUST 12, 1986, AT 8:35 AM, A CRANKCASE EXPLOSION OCCURED AT WILLIAMS COMPRESSOR STATION THAT RESULTED IN THE INJURY OF THREE (3) EPNG EMPLOYEES. SUBSEQUENT INVESTIGATION REVEALED A FRACTURE OF THE #2 BEARING CAP AND THE RESULTANT MELTING OF THE BEARI | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
264 | 1986-08-04 | WV | maintenance | PENDLETON | COLUMBIA GAS TRANSMISSION CORP | PIPE SECTION HAS BEEN SUBMITTED FOR METALLURGICAL ANALYSIS TO ASCERTAIN CAUSE. | 135000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
265 | 1986-07-16 | TX | technical failure | SAN PATRICIO | NATURAL GAS PIPELINE CO OF AMERICA | 30" MAINLINE RUPTURED AT A 6" COLD TAP. | 103226 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
266 | 1986-06-27 | AR | maintenance | MILLER | TEXAS EASTERN GAS PIPELINE CO | THE PIPELINE WAS OUT OF NORMAL OPERATING SERVICE AT THE TIME OF THE FAILURE. THE MAINLINE VALVE DOWNSTREAM OF THE POINT OF RUPTURE WAS CLOSED FOR PIPE REPLACEMENT ACTIVITIES IN PROGRESS IN THE DOWNSTREAM VALVE SECTION. THE PIPELINE SEGMENTWHICH FAILED WAS | 531000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
267 | 1986-08-20 | TX | maintenance | EAST ADDITION | ANR PIPELINE CO (AMERICAN NATURAL RESOURCE) |  | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
268 | 1986-08-05 | LA | other | CAMERON | NATURAL GAS PIPELINE CO OF AMERICA | PIPELINE WAS GOUGED AND DENTED BY THIRD PARTY EQUIPMENT WHICH CAUSED A CRACK THAT LEAKED.ON AUGUST 6, 1986 AT 0730 HOURS, BUBBLING WAS REPORTED ON THE RIGHT OF WAY OF NATURAL GAS PIPELINE COMPANY OF AMERICA'S #1-30" LOUISIANA MAINLINE. THE INCIDENTSITE IS | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
269 | 1986-08-28 | NM | other | SAN JUAN | EL PASO NATURAL GAS CO | ON AUGUST 28, 1986 AT 10:05 P.M. DURING NORMAL PIGGING OPERATIONS, AN EXPLOSIONAND FIRE OCCURRED AT THE PIGGING FACILITY ON THE CHACO-LINDRITH FIELD LINES WHICH RESULTED IN INJURY TO TWO(2) EPNG EMPLOYEES. SUBSEQUENT INVESTIGATION REVEALED THAT VAPORS WHI | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
270 | 1986-09-01 | NM | other | SAN JUAN | EL PASO NATURAL GAS CO | ON SEPTEMBER 1, 1986 AT 4:00 P.M. AN EXPLOSION OCCURRED AT THE PIGGING FACILITYON THE CHACO-LINDRITH FIELD LINE WHICH RESULTED IN INJURY TO THREE (3) EPNG EMPLOYEES; HOWEVER, ONLY ONE REQUIRED HOSPITALIZATION. THE INCIDENT OCCURRED WHILE A CREW WAS PREPAR | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
271 | 1986-09-09 | WY | other | CONVERSE | PHILLIPS PETROLEUM CO | AVAILABLE MEANS OF RELEASING PRESSURE FROM SPHERE RECEIVER NOT USED. RECEIVER UNDER PRESSURE WHEN EMPLOYEE TRIED TO REMOVE CAP. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
272 | 1986-09-10 | MI | other | KALKASKA | CONSUMERS POWER CO | LIGHTNING STRUCK A TREE 36 FEET AWAY FROM THE 12" PIPELINE AND TRAVELED TO THE PIPELINE VIA THE TREE'S ROOTS. THIS RESULTED IN A PINHOLE LEAK ON THE TOP OF THE | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
273 | 1986-10-01 | WV | other | LEWIS | CONSOLIDATED GAS TRANSMISSION CORP | BOTTOM BARRELL OF STEP LADDER DRIP (12" SECTION) SEPARATED IN SEAM. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
274 | 1986-10-28 | WA | other |  | CASCADE NATURAL GAS CORP |  | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
275 | 1986-10-06 | CA | other | SAN BERNARDINO | SOUTHERN CALIFORNIA GAS CO | REGULATOR MALFUNCTION | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
276 | 1986-10-10 | TX | technical failure | GRAY | WESTAR TRANSMISSION CO | CRACK IN SEAM OF PIPE OPENED CAUSING RUPTURE. THIS FAILURE WAS IN A DRAW APPROXIMATELY 12' DEEP AND 80' WIDE. BAD SEAM IN JOINT OF PIPE. NUMEROUS COROSION PITSUNRELATED TO PIPE FAILURE WERE NOTED. | 78000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
277 | 1986-11-02 | AR | technical failure | CLARK | ARKLA ENERGY RESOURCES | A SECTION OF 20" PIPE ON AN OVERHEAD CROSSING BLEW OUT, PIPE HAD APPARENTLY BEEN DAMAGED BY PIG IN 45 DEGREE E11. | 185988 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
278 | 1986-10-29 | TX | other | RUSK | SESCO PRODUCTION CO | CONSTRUCTION CREW (CHAPARRAL GENERAL CONSTRUCTION CO., INC.) RUPTURED PIPELINE WITH FRONT-END LOADER WHILE ESCAVATING FOR STREET CONSTRUCTION. | 500 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
279 | 1986-10-30 | IL | technical failure | LIVINGSTON | NATURAL GAS PIPELINE CO OF AMERICA | LEAK CAUSED BY INCOMPLETE FUSION OF THE LONGITUDINAL SEAM. | 62300 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
280 | 1986-10-31 | NJ | other | HUNTERDON | TEXAS EASTERN GAS PIPELINE CO | ON OCTOBER 31, 1986 AT 9:34 A.M. E.S.T. A SCHEDULED ROUTINE BLOW-DOWN OF TEXAS EASTERN'S 36" LINE NO. 27 WAS INITIATED JUST EAST OF THE DELAWARE RIVER HUNTERDON COUNTY, NEW JERSEY. THE PRESSURE ON LINE NO. 27 WAS 850 PSIG AT THE TIME THE BLOW-DOWN WAS STA | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
281 | 1986-11-13 | TX | other | HUTCHINSON | PANHANDLE EASTERN PIPELINE CO | A CONTRACTOR'S EMPLOYEE WAS STEAMING A FROZEN DRAIN LINE FROM A NATURAL GAS CONDENSATE STORAGE TANK, LIQUID WAS RELEASED THROUGH AN OPEN VALVE, AND VAPOR FROM THE LIQUID WAS IGNITED BY THE OPEN FLAME ON THE CONTRACTOR'S STEAMER TRUCK. | 750000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
282 | 1986-11-05 | KY | other | MADISON | TENNESSEE GAS PIPELINE CO | A SMALL 11/16" TAPERED DRILLED HOLE WAS PARTIALLY DRILLED INTO MAIN BODY OF PIPE AT THE 7 O'CLOCK POSITION. LEAK DID NOT START UNTIL AFTER HYDROSTATICALLY TESTED ON 9/30/86. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
283 | 1986-12-02 | OK | other | MUSKOGEE | OKLAHOMA NATURAL GAS CO | THE LINE THAT FAILED WAS INSTALLED IN JUNE 1986. THIS PROJECT WAS A RELOCATION REQUIRED DUE TO HIGHWAY CONSTRUCTION. THE PIPELINE WAS DESIGNED, INSTALLED, AND TESTED IN ACCORDANCE WITH THE ASME B31.8-1968 EDITION CODE FOR "GAS TRANSMISSIONAND DISTRIBUTION | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
284 | 1986-12-06 | MS | other | RANKIN | UNITED GAS PIPELINE CO | THERE IS NO APPARENT CAUSE FOR THE RUPTURE, BUT A METALLURGICAL INVESTIGATION IS UNDERWAY ON SAMPLES OF THE RUPTURED PIPE TO DETERMINE THE CAUSE OF RUPTURE. UNITED HAS TWO 30" LINES CROSSING PELAHATCHIE BAY. A VALVE SITE IS LOCATED ON EACHSIDE OF THE BAY | 685000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
285 | 1986-11-24 | LA | other |  | SEA ROBIN PIPELINE CO | A SHRIMP BOAT HUNG A NET IN THE LINE, DAMAGING A 2 INCH TAP VALVE. | 90000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
286 | 1986-12-06 | OK | other | BECKHAM | EL PASO NATURAL GAS CO | ON DECEMBER 12, 1986, AT 1:10 P.M. AN EXPLOSION OCCURRED ON THE 6-5/8" O.D. NONJURISDICTIONAL LINE TO APACHE CORP. - PUCKETT WELL #1-16, THAT RESULTED IN THE DEATH OF A BULLDOZER OPERATOR EMPLOYED BY APACHE CORP. THE OPERATOR WAS KILLED WHEN. WHILE MOVING | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
287 | 1986-11-26 | LA | maintenance |  | STINGRAY PIPELINE CO | NONE KNOWN AT THIS TIME. | 200000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
288 | 1986-11-10 | AR | other | CRAWFORD | ARKLA ENERGY RESOURCES |  | 75000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
289 | 1986-12-12 | NJ | other | MIDDLESEX | TEXAS EASTERN GAS PIPELINE CO | A BACKHOE WAS WORKING NEAR A REGULATOR PIT WHEN THE BACKHOE BUCKET STRUCK A BLEED OFF ASSEMBLY CAUSING A 1" THREADED PIPE NIPPLE TO BE STRIPPED FROM A THREAD-O-LET FITTING. ALL PERSONNEL WERE REMOVED FROM THE VICINITY OF THE LEAK AND THE AREA WAS SECURED | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
290 | 1986-11-12 | LA | other | WINN | UNITED GAS PIPELINE CO | WILL BE FILLED IN AFTER METALLURGICAL INVESTIGATION IS COMPLETE, ON SUPPLEMENTAL REPORT. | 221665 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
291 | 1986-10-14 | TX | technical failure |  | HOUSTON PIPELINE CO | IN OUR LETTER OF SEPTEMBER 12, 1986, WE REPORTED THAT THIS INCIDENT WAS ORIGINALLY REPORTED IN ERROR AN AUGUST 27, 1986 AS IT HAD BEEN DETERMINED THAT THE ORIGIN WAS NOT A PART OF OUR DISTRIBUTION SYSTEM. AFTER FURTHER INVESTIGATION, IT HASBEEN DETERMINED | 5000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
292 | 1986-12-30 | TX | other | ARANSAS | VALERO TRANSMISSION CO | PIPELINE WAS HIT BY MARINE VESSEL. WE DO NOT KNOW WHO WAS RESPONSIBLE FOR DAMAGE. APPEARS THAT A BARGE HIT PIPE CAUSING DAMAGE. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
293 | 1986-12-15 | ND | technical failure | BILLINGS | WILLISTON BASIN INTERSTATE PIPELINE CO | LEAK OR CRACK OCCURRED IN A FIBERGLASS WASTE LIQUED TANK OR IN PLASTIC PIPE LEADING TO TANK. EXACT LOCATION UNKNOWN. FIRE DESTROYED FACILITIES. | 350000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
294 | 1986-07-11 | PA | technical failure | ELK | NATIONAL FUEL GAS SUPPLY CORP | TWO INCH & FOUR INCH PIPE WAS TO BE LAID IN THE GATHERING SYSTEM OF BELMOUTH STORAGE FIELD, A REMOTE AREA IN ELK COUNTY, PA. WHEN TESTED, A TOTAL OF FIVE FAILURES WERE FOUND, ALL BELOW 2000 PSIG, 4 IN 4", AND 1 IN 2". FURTHER INVESTIGATIONREVEALED THAT AT | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
295 | 1986-12-10 | TX | maintenance | DALLAS | DELHI GAS PIPELINE CORP | INCIDENT OCCURRED DURING THE REPAIR OF A LEAK IN A 6" PIPELINE. THE LINE HAD BEEN BLOWDOWN & ISOLATED FOR THE REPAIR PROCEDURES. DURING THE REMOVAL OF THE LEAKING PIPELINE SEGMENT, A SUDDEN, SHORT DURATION GAS FLOW WAS EXPERIENCED. LINE WAS INTERNALLY INH | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
296 | 1987-02-13 | LA | maintenance |  | STINGRAY PIPELINE CO | LINE WAS BLOWN DOWN TO INSTALL REPAIR CLAMP ON LEAK AND WAS BEING REPRESSURED FOR SERVICE WHEN RUPTURE OCCURRED. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
297 | 1987-02-02 | LA | technical failure |  | ANR PIPELINE CO (AMERICAN NATURAL RESOURCE) |  | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
298 | 1987-02-01 | LA | maintenance |  | STINGRAY PIPELINE CO |  | 200000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
299 | 1987-02-17 | TX | other | MARTIN | WESTAR TRANSMISSION CO | FARMER WAS DEEP PLOWING & HIT AN ABONDONED TAP THAT EXTENDED 9 INCHES ABOVE PIPELINE (PIPELINE HAD 21 INCHES OF COVER) FARMER ALSO FAILED TO NOTIFY ANYONE UNTIL THE NEXT DAY. | 10000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
300 | 1987-02-11 | NV | other |  | SOUTHWEST GAS CORP | WHILE ATTEMPTING TO LOCATE A CULVERT, CONTRACTOR DUG INTO 8" HIGH PRESSURE TRANSMISSION LINE. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
301 | 1987-03-29 | IL | other | WASHINGTON | ILLINOIS POWER CO | SUBSIDENCE INA COAL MINE ABADONED IN 1948 CAUSED A LEAK IN THE I.,P.C. #2 GAS GAS STORAGE WELL IN ILLINOIS POWER'S TILDEN GAS STORAGE FIELD. AS ARESULT OF THISSUBSIDENCE, THE 5 1/2" O.D PRODUCTION CASING AND 8 5/8" O.D. MINE CASING WERE DAMAGEED AND GAS E | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
302 | 1987-01-13 | TX | maintenance |  | NATURAL GAS PIPELINE CO OF AMERICA | THERE ARE 2 LEAKS ON THE 12" PIPELINE DUE TO INTERNAL CORROSION | 150000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
303 | 1987-04-06 | TX | maintenance | JEFFERSON | AMOCO GAS CO | THE PIPE IS ON PILINGS PARRALLELING KEITH LAKE BRIDGE. CORROSION STARTED UNDERTHE COATING, CAUSING A SMALL PIT AND A RESULTING LEAK. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
304 | 1987-02-13 | KS | other | LINCOLN | NATURAL GAS PIPELINE CO OF AMERICA | CONTRACTOR OPERATOR GOUGEED 18" PIPELINE WITH 235 CAT BACKHOE BUCKET WHILE CLEANING DRAINAGE DICTH. PIPELINES WERE FLAGGED, PRODDED AND DEPTH RECORDED ON FLAGS ON 1/7/87. COMPANY INSPECTORS WERE PRESENT AND WITNESSED THE DAMAGE. | 70545 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
305 | 1986-12-01 | TX | maintenance | MIDLAND | PHILLIPS PETROLEUM CO | FOR APPROXIMATELY ONE YEAR, THE GENERAL AREA WHERE THE LEAK ACCURRED HAS BEEN UNDER WATER DUE TO EXCESSIVE AMOUNT OF RAINFALL AND IRRIGATION BY LANDOWNER. AREA REQUIRED DRAINAGE. | 90000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
306 | 1987-03-02 | TX | maintenance | JEFFERSON | UNITED TEXAS TRANSMISSION CO | LINE WAS LEAKING UNDER PAVED COUNTY ROAD (GENTRY ROAD). COMPANY PERSONAL MONITORED THE LEAK CONTINUALLY FROM TIME OF VERIFATION UNTIL THE LINE WAS SHUT DOWN. | 147232 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
307 | 1987-02-04 | TX | other | ZAVALA | VALERO TRANSMISSION CO | 4" PIPELINE WAS HIT BY TENNESSEE PIPELINE CONSTRUCTION COMPANY WHILE EXCAVATING. | 1000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
308 | 1987-03-06 | TX | maintenance | KLEBERG | VALERO TRANSMISSION CO | THIS IS A RESULT OF A CORROSION LEAK IN A TRANSMISSION LINE. THE LEAK DEVELOPED IN A RURAL AREA AND PRESENTED NO HAZARD. IT IS BEING REPORTED BECAUSE IT EXCEEDS THE PROPERTY DAMAGE LIMIT | 18000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
309 | 1987-05-13 | CA | other | ORANGE | EXXON CO USA | AT 1:40 PM ON MAY 13, 1987, THE LONG BEACH FIRE DEPT REPORTED AN OIL SPILL 500 YARDS OFFSHORE SEAL BEACH, CALIF. 10 BARRELS OF CRUDE OIL LEAKED OUT OF AN EIGHTINCH EMULSION PIPELINE CONNECTING EXXON'S BELMONT ISLAND PRODUCTION FACILITY WITH CRUDE OIL PROC | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
310 | 1987-07-10 | TN | other | SHELBY | MEMPHIS LIGHT GAS & WATER DIVISION | CONTRACTOR WAS TRENCHING ACROSS ROAD AND HIT GAS MAIN, CAUSING A FIRE THAT DAMAGED TRENCHER AND BURNED OPERATOR AN ARM AND NECK. | 16500 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
311 | 1987-06-30 | MD | other | FREDERICK | COLUMBIA GAS TRANSMISSION CORP | LIGHTNING STRUCK AN INDIRECT WATER BATH HEATER OWNED AND OPERATED BY WASHINGTONGAS LIGHT (WGL) AT BRINK STATION. A FIRE ENSUED AND SPREAD TO THEIR BUILDING. THE BUILDING WAS DESTROYED, DROPPING THE ROOF ONTO COLUMBIA'S MEASURING STATION AND OTHER WGL FACI | 45000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
312 | 1987-07-08 | TX | maintenance | SAN PATRICIO | FLORIDA GAS TRANSMISSION CO | CORROSION WAS EXTERNAL, ON THE BOTTOM OF THE PIPE. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
313 | 1987-06-30 | VA | other | FAIRFAX | WASHINGTON GAS LIGHT CO | ON THE EVENING OF JUNE 30, 1987, LIGHTING STRUCK A GATE STATION WHICH DELIVERS NATURAL GAS FROM COLUMBIA TRANSMISSION COMPANY TO WASHINGTON GAS LIGHT COMPANY. A LINE HEATER VALVE WAS THE POINT OF STRIKE, WAS BURNED THROUGH AND IGNITION OCCURRED. THE FLAME | 500000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
314 | 1987-06-10 | TX | maintenance | DALLAS | LONE STAR GAS CO | CORROSION IN A MAIN LINE DRIP ON LINE OS-8". | 5483 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
315 | 1987-06-08 | TX | maintenance | NUECES | DELHI GAS PIPELINE CORP | PIPELINE WAS PURCHASED FROM SUN OIL CO. IN 1971. PRIOR RECORDS INDICATE THAT SUN HAD CATHODIC PROTECTION ON PIPELINE PRIOR TO DELHI'S PURCHASE. THIS LINE IS SCHEDULED FOR REPLACEMENT ON 7/14/87 | 5441 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
316 | 1987-05-24 | LA | other | ST LANDRY | TRANSCO GAS PIPELINE CORP | PART B AS A RESULT OF THE GATES BEING CLOSED AT THE OLD RIVER DIVERSION STATION, THERE WAS A DROP IN THE LEVEL OF THE ATCHAFALAYA RIVER IN A SHORT PERIOD OF TIME . IT IS SURMISED THAT THIS CONDITION CONTRIBUTED TO THE SLOUGHING OF THE EAST BANK.PART 3 | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
317 | 1987-05-26 | CO | technical failure | RIO BLANCO | NORTHWEST PIPELINE CORP | PART C #4 3/4 - INCH CRACK IN LONGSEAM | 24000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
318 | 1987-05-25 | OH | other | CUYAHOGA | COLUMBIA GAS TRANSMISSION CORP | PART B #3INCIDENT RESULTED FROM A MOTORCYCLE TRAFFIC ACCIDENT; SEE ATTACHED COPY OF OHIOTRAFFIC ACCIDENT REPORT NO. 87-4172 BY STRONGSVILLE POLICE DEPT. THE MOTORCYCLEBROKE VALVE LOOSE FROM 1" PIPE, CAUSING GAS TO ESCAPE. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
319 | 1987-05-28 | OK | other | JEFFERSON | LONE STAR GAS CO |  | 350000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
320 | 1987-04-22 | TX | other | CRANE | LONE STAR GAS CO | BULLDOZER OPERATOR WORKING ON A WELL FOR ANOTHER COMPANY HIT LONE STAR'S 36" LINE. THE OPERATOR WAS NOT AWARE OF THE LINE. PIPELINE DID NOT RUPTURE BUT WAS DAMAGED. | 47500 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
321 | 1987-04-29 | TX | other | NAVARRO | LONE STAR GAS CO | EMPLOYEES ATTEMPTED TO RE-LIGHT THE TITARTOR, EXPLOSION AND FIRE DESTROYED THE BUILDING AND ALL THE EQUIPMENT. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
322 | 1987-05-12 | TX | maintenance | WEBB | VALERO TRANSMISSION CO | REASON FOR FAILURE IS UNKNOWN AT THIS TIME. METALLURGICAL INVESTIGATION IS BEINGCONDUCTED. | 200000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
323 | 1987-05-27 | TX | maintenance | NAVARRO | TEXAS UTILITIES FUEL CO | SMALL LEAK ABOUT 200 YARDS WEST OF MILES MARKER K-15 OFF OF COUNTY RD. LT-2-87 | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
324 | 1987-08-13 | MN | maintenance | ROSEAU | INTER - CITY GAS MINNESOTA PIPELINES LTD | CORROSION LEAK WAS DISCOVERED DURING LEAK SURVEY. CORRODED SECTION WAS REPLACEDWITH PRETESTED PIPE (1392 PSIG) - COMPLETED AUGUST 24, 1987 | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
325 | 1987-08-06 | KY | other | PENDLETON | COLUMBIA GAS TRANSMISSION CORP | PART 3:HOLLOWAY CONSTRUCTION WAS CROSSING PIPELINE WITH HEAVY EARTH MOVING EQUIPMENT (SCRAPER PANS AND DOZERS) WHEN A PAN STRUCK THE PIPELINE, AFTER REMOVING FIVE (5)FEET OF EARTH COVER. PART B # 3:THE PIPELINE HAD BEEN RELOCATED FOR CONSTRUCTION OF THE | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
326 | 1987-07-17 | MT | other | BEAVERHEAD | MONTANA POWER CO | PIPE CONTAINED MULTIPLE DENTS IN A SPACE OF 6 FEET. THERE WAS ALSO EVIDENCE OF BENDING UPWARD WHICH RESULTED IN A TENSION FAILURE IN A GIRTH WELD | 11900 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
327 | 1987-07-22 | TX | maintenance | CHAMBERS | UNITED TEXAS TRANSMISSION CO | COMPANY PERSONNEL MONITORED LEAK CONTINUALLY FROM TIME OF INITIAL NOTIFICATION ON 7/21/87 UNTIL THE LINE WAS SHUT DOWN FOR REPAIR ON 7/23/87. TELEPHONIC NOTIFICATION TO THE RRC WAS MADE WHEN LEAK WAS CONFIRMED TO BE ON UTTCO FACILITIES ON 7/22/87 | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
328 | 1987-09-16 | TX | other |  | VALERO TRANSMISSION CO | LOCATION MARKED WITH PIPELINE MARKERS WITH COMPANY NAME AND 24-HOUR EMERGENCY NUMBER. | 20000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
329 | 1987-09-11 | LA | other |  | TENNESSEE GAS PIPELINE CO |  | 111000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
330 | 1987-09-14 | TX | other | WARD | WESTAR TRANSMISSION CO | WESTAR SUPERVISOR REMAINED ON SITE UNTIL CONTRACTOR FINISHED EXPOSING & CROSSING PIPELINE. AFTER WESTAR SUPERVISOR LEFT CONTRACTOR BEGAN SHAVING TOP WALLS OF DITCH & HIT PIPELINE WITH BACKHOE BUCKET. CONTRACTOR FOR CHEVRON PUNCTURED WESTARLINE #4000 WITH | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
331 | 1987-09-24 | TX | other | FAYETTE | CLAJON GAS CO | THE GRADALL VEHICLE WAS WEST BOUND ON 2981 WHEN THE DRIVER MR. LUNA LOST CONTROLON A DOWN HILL SLOPE-RAN OFF THE ROAD TO THE LEFT, CROSSED THE DITCH, THE FENCEAND HIT THE PIPELINE TAP-PASSING OVER THE TAP AND CAME TO REST APPROX. 10' WESTOF THE TAP. MR. L | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
332 | 1987-07-27 | TN | other | WASHINGTON | EAST TENNESSEE NATURAL GAS CO |  | 18000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
333 | 1987-09-03 | PA | technical failure | ELK | NATIONAL FUEL GAS SUPPLY CORP | HORIZONTAL FAILURE. LINE C WAS LAID IN 1908. IN 1947 THE PIPE WAS PICKED UP, RECONDITIONED AND PUT BACK IN THE GROUND. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
334 | 1987-08-09 | TX | other | JIM WELLS | C B GAS GATHERING INC | SMALL LEAK IN STARTING GAS SYSTEM WHICH POSSIBLY IGNITED FROM ELECTRICAL SYSTEMAND BURNED 125# START GAS HOSE IN HALF TO FEED FIRE. | 33000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
335 | 1987-09-09 | TX | other | HARRIS | TEXAS SOUTHEASTERN GAS CO | PEANUT FARMER HIT OUR PIPELINE WITH HIS HARVESTING MACHINE. | 4000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
336 | 1987-08-20 | LA | maintenance |  | ANR PIPELINE CO (AMERICAN NATURAL RESOURCE) |  | 82000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
337 | 1987-08-13 | AR | maintenance | CLARK | ARKLA ENERGY RESOURCES | A SECTION OF 20" PIPE IN CREEK CROSSING RUPTURED. | 70352 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
338 | 1987-09-02 | MA | other | NORFOLK | ALGONQUIN GAS TRANSMISSION CO | LINE WITH A FRONT END LOADER, STRUCK AND PUNCTURED THE PIPELINE. THE LOCATION OF THE PIPELINE HAD BEEN ERRONEOUSLY MARKED. LOCATION OF PIPELINE HAD BEEN ERRONEOUSLY MARKED. | 38175 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
339 | 1987-08-25 | TX | other | EASTLAND | SOUTHWESTERN GAS PIPELINE INC | WELL SITE BEING CONSTRUCTED BY A PRODUCING COMPANY. DID NOT CALL TO HAVE PIPELINES LOCATED. IGNORED POSTED LINE MARKERS IN THE VICINITY INDICATING PIPELINES ARE PRESENT. | 251939 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
340 | 1987-08-21 | TX | other |  | HOUSTON PIPELINE CO | DURING THE GAS PURGE OF THE LINE, LIQUID HYDROCARBON SPRAYED FROM THE BLOWDOWN RISER. THE PURGING OPERATION WAS SHUTDOWN IMMEDIATELY BUT ABOUT 10 MINUTES LATERTHE GAS/LIQUID PHASE CAUGHT FIRE. | 10000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
341 | 1987-10-08 | TX | other |  | DELHI GAS PIPELINE CORP | DURING EXCAVATION OF DELHI'S FARM SYSTEM 12" A LEAK WAS DISCOVERED IN THE THREADS OF A 1" PIPELINE TAP. THE LEAK WAS DUE TO EXTERNAL FORCE OF MESQUITE TREE ROOTS WHICH HAD GROWN AROUND THE 1" FITTING AND VALVE. THE TAP WAS INACTIVE AND THEVALVE WAS PLUGGE | 9000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
342 | 1987-10-10 | TX | other | FAYETTE | CLAJON GAS CO | PRELIMINARY INDICATIONS POINT TO THE CARBURATION IN THE FUEL SYSTEM. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
343 | 1987-11-04 | KY | technical failure | FLOYD | KENTUCKY - WEST VIRGINIA GAS CO | PIPE BROKE IN 45DEGREE MITER WELD. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
344 | 1987-10-27 | FL | maintenance | SANTA ROSA | FLORIDA GAS TRANSMISSION CO | EXTERNAL CORROSION OVER ABOUT A 15 INCH AREA WITH PITTING AS DEEP AS 0.170" IS THE APPARENT CAUSE OF THE FAILURE. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
345 | 1987-08-28 | CA | other | SOLANO | PACIFIC GAS & ELECTRIC CO | CONTRACTOR EXCAVATING FOR NEW SUBDIVISION STRUCK LINE WITH A TRACTOR, ALLOWING GAS TO ESCAPE TO ATMOSPHERE. BUILDINGS WERE EVACUATED AND TRAFFIC REROUTED. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
346 | 1987-09-10 | LA | other |  | STINGRAY PIPELINE CO | SHRIMP BOAT WAS REPORTED IN AREA OF DAMAGE AT TIME OF LEAK. | 200000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
347 | 1987-09-15 | IL | maintenance | FRANKLIN | TRUNKLINE GAS CO | FAILURE OCCURRED IN INACTIVE CORROSIVE BLOTCH. | 60000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
348 | 1987-08-05 | TX | maintenance | HIDALGO | RIO GRANDE VALLEY GAS CO | OUR INITIAL REPORT STATED THE FAILURE OCCURRED AT 530 PSIG. HOWEVER, ATTACHED IS A COPY OF A PRESSURE CHART TAKEN FROM THE METER STATION JUST UPSTREAM OF THE RELIEF VALVE WHICH IS CALIBRATED IN PSIA. THIS CHART SHOWS THE FAILURE OCCURRED AT518 PSIA. THE D | 40000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
349 | 1987-08-24 | PA | maintenance | FOREST | NATIONAL FUEL GAS SUPPLY CORP | GENERAL CORROSION REDUCED WALL THICKNESS OF PIPE. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
350 | 1987-10-28 | MI | other |  | MICHIGAN CONSOLIDATED GAS CO (MICHCON) | OPERATOR IN PREPARING TO REMOVE PIG BALL FROM LINE ASSUMED THAT HE COMPLETELY BLEW DOWN RECEIVER. PRESSURE REMAINED IN THE RECEIVER AND THE CAP WAS REMOVED WITH PRESSURE REMAINING IN THE RECIEVER BODY. THE CAP BLEW OFF RESULTING IN INJURY OF TWO COMPANY | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
351 | 1987-10-24 | AR | maintenance |  | ARKLA ENERGY RESOURCES | A SECTION OF "8" PIPE RUPTURED. | 12150 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
352 | 1987-10-14 | NM | other | SAN JUAN | EL PASO NATURAL GAS CO | ON WEDNESDAY, OCTOBER 14, 1987, AT 7:30 P.M. THE BLANCO "C" #2 TURBINE CONTROL CAB EXPLODED, WRECKING THE CONTROL SYSTEM WIRING, THE UNIT MOTOR FROM VARIOUS SYSTEM COMPONENTS RESULTED IN AN UNCONTROLLED LEAKAGE OF GAS FROM THE COMPRESSOR CASE THROUGH THE | 500000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
353 | 1987-10-22 | TX | other | GULF OF MEXICO | TRANSCO GAS PIPELINE CORP | A LARGE TRAWLING NET AND CABLES WERE FOUND WRAPPED AROUND A 2" TAP VALVE. IT IS ASSUMED THAT THE NET WAS DRAGGED ACROSS THE PIPELINE AND DISLODGED THE 2" VALVE AND WELD-O-LET. | 66700 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
354 | 1987-11-18 | VA | other | SUFFOLK | COMMONWEALTH GAS PIPELINE CORP | FAILURE OCCURED WHILE D-6 DOZER WAS BEING OPERATED OVER THE PIPELINE. PIPE MAYHAVE BEEN HIT BY TRACK CLEAT. | 5000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
355 | 1987-10-27 | KY | other | FLOYD | COLUMBIA GAS TRANSMISSION CORP | A CONTRACTOR'S CONSTRUCTION CREW WAS REMOVING COVER FROM THE LINE. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
356 | 1987-11-02 | TX | other |  | ANR PIPELINE CO (AMERICAN NATURAL RESOURCE) |  | 500000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
357 | 1987-11-06 | WY | other | LINCOLN | NORTHWEST PIPELINE CORP | PROJECTS WERE NEARING COMPLETION TO REPLACE THE CONCRETE FOUNDATIONS AND INSTALLNEW PULSATION BOTTLES ON THE TWO REFRIGERATION COMPRESSORS, #1 CLARK AND #2 CLARK. A SCHEDULED, ONE DAY MAINTENANCE SHUT DOWN OF THE OIL PLANT BEGAN A 6:45AMON NOVEMBER 6,198 | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
358 | 1987-11-03 | TX | maintenance | NUECES | VALERO TRANSMISSION CO | AN EXTERNAL CORROSION PIT DEVELOPED IN THE CARRIER PIPE LOCATED INSIDE A CASING. LEAK WAS IN AN AREA OF DAMAGED COATING. THE PIPELINE WASA TAKEN OUT OF SERVIOCE AND A NEW SECTION OF PIPE WAS INSTALLED IN THE EXISTING CASING. | 10000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
359 | 1988-01-13 | NE | other | SHERIDAN | KN ENERGY INC (KANSAS NEBRASKA NATURAL GAS CO INC) | THE ATTACHED INCIDENT REPORT COVERS A LEAK THAT OCCURRED ON K N ENERGY, INC.'S (K N'S) 4-INCH TOP-OF-GROUND TRANMISSION PIPELINE IN SHERIDAN COUNTY, NEBRASKA ON JANUARY 13, 1988. IGNITION DID NOT OCCUR AND THERE WERE NO INJURIES OR FATALITIES AS A RESULT | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
360 | 1987-12-05 | WV | other | LEWIS | EQUITABLE GAS CO | CONTRACTOR CUT GAS SERVICE LINE WHILE TRENCHING TO INSTALL ELECTRIC CABLE. GASIGNITYED AND DESTROYED THE TRENCHING MACHINE. ( NO SECOND COPY).GE FIELD POOL LOCATED IN THE STONEWALL JACKSON LAKE PROJECT, LEWIS COUNTY, WESTVIRGINIA. THIS PROJECT IS UNDER | 128000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
361 | 1987-12-04 | OK | other |  | OKLAHOMA NATURAL GAS CO | COUNTY CUTTING NEW ROAD PUNCTURED GAS LINE. GRADER BURNED. OPERATOR WAS TREATED AND RELEASED FROM LOCAL HOSPITAL. | 25549 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
362 | 1987-12-14 | TN | other | SEVIER | EAST TENNESSEE NATURAL GAS CO | PROPERTY OWNER THOUGHT THE PIPELINE WAS DEEPER AND FAILED TO FOREWARN THE BULLDOZER OPERATOR OF THE EXISTENCE OFTHE PIPELINE. EXISTING STRUCTURE COUSING NATURAL GAS TO BLOW INTO CELLAR AREA AND EVENTURALLY WAS IGNITED AND EXPLODED. THE GAS COMPANY WAS NO | 25000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
363 | 1987-12-14 | CO | technical failure | ADAMS | PUBLIC SERVICE CO OF COLORADO | 1/2" NIPPLE USED FOR PRESSURE TAP BROKE AT PIPE THREADS BELOW VALVE. ESCAPING GAS WAS IGNITED BY AN UNKNOWN SOURCE RESULTING IN A FIRE THAT DESTROYED THE REGULATOR/METER STATION. CAUSE OF RUPTURE AND FIRE IS UNDER INVESTIGATION.PART C- 1/2" NIPPLE CRACK | 102000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
364 | 1987-12-11 | TX | maintenance | HARRIS | EXXON CO USA | INTERNAL CORROSION CAUSED BY SULFATE REDUCING BACTERIAL GROWTH.PART A- A CONTINUOUS CORROSION INHIBITOR INJECTION PROGRAM IS CURRENTLY IN PLACE. THIS PROGRAM WILL BE MIDIFIED TO INCLUDE BACTERIAL BATCH TREATMENT. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
365 | 1988-01-09 | TX | other | BURLESON | CLAJON GAS CO | VIBRATION OF TUBING CAUSED METAL FATIGUE & BREAKAGE IN SUPPLY TUBING & WAS IGNIGHTED BY FIRE IN REBOILER | 500 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
366 | 1988-01-09 | OK | other | BEAVER | COLORADO INTERSTATE GAS CO | ICE BUILD-UP ON THE OFFICE BUILDING WALL PLUGGED THE VENT ON THE REGULATOR SUPPPLYING GAS TO THE BUILDING (HEAT & HOT WATER). 26.7 PSIG GAS WENT TO THE FURNACE& HOT WATER HEATER, RESULTING IN AN EXPLOSION WHICH DESTROYED THE 33' X 58' SINGLE STORY BUILDIN | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
367 | 1987-12-30 | TX | other | WHEELER | PALO DURO PIPELINE CO | PIPELINE RUPTURED AT 100 PSIG WHILE BEING PRESSURED UP AFTER TIE-IN SHUTDOWN ATWHEELER COMPRESSOR STATION II. | 36000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
368 | 1987-12-23 | IL | other | CLINTON | NATURAL GAS PIPELINE CO OF AMERICA | PENDING METALLURGICAL ANALYSIS OF FAILED SECTION. FRACTURE OCCURRED AT A WELD CONNECTING AN 8" X 30" SADDLE TO A REINFORCING SLEEVE OF A BRANCH CONNECTION ASSEMBLY | 160000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
369 | 1987-07-24 | LA | other | ACADIA | FLORIDA GAS TRANSMISSION CO | TWO CONTRACTOR EMPLOYEES WORKING WITH A TORCH WERE BURNED WHEN THEIR TORCH IGNITED GAS VENTING FROM A SCRUBBER WASTE STORAGE TANK'S VENT LINE AT FGT'S COMPRESSOR STATION.. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
370 | 1988-01-05 | PA | maintenance | PIKE | COLUMBIA GAS TRANSMISSION CORP |  | 150000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
371 | 1988-01-27 | PA | technical failure | CAMERON | NATIONAL FUEL GAS SUPPLY CORP | NO REMARKS GIVEN. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
372 | 1988-01-09 | IL | technical failure | COOK | PEOPLES GAS LIGHT & COKE CO | FOR UNKNOWN REASONS, A SEGMENT OF H.P. STEEL PIPE EXPOSED ON A STRUCTURE OVER R.R. TRACKS, RUPTURED. THE PIPELINE SUPPLIES TWO LARGE CUSTOMERS. THE ONE SUPPLYTO THIS LINE CONTAINS AN AUTOMATIC VALVE WHICH COLSED AND SHUT OFF THE FOW OF GAS. THE GAS DID | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
373 | 1988-01-12 | TX | other | BRAZORIA | UNITED TEXAS TRANSMISSION CO | AFTER ISOLATING THE LINE, WE DUG UP THE PIPELINE LEAK AND OBSERVED A 3 FT. GOUGE AT APPROXIMATELY 11:00 ON THE DOW 20" LINE, APPARENTLY CAUSED BY A THIRD PARTYCONTRACTOR WORKING OVER OUR PIPELINE SYSTEM. A 4"X1/8" PORTION OF THE 3 FT. GOUGE ACTUALLY PENE | 75000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
374 | 1988-01-14 | LA | technical failure | CAMERON | TENNESSEE GAS PIPELINE CO |  | 130000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
375 | 1988-01-27 | TX | maintenance | CHAMBERS | AMOCO GAS CO | BOLTS CONNECTING A 2" TAP VALVE TO 16" TRANSMISSION LINE HAD DETERIORATED AND ALEAK HAD OCCURRED.MAIN LINE UNDER CATHODIC PROTECTION. TAP VALVE LINE WAS NOT ON IDLE. | 5850 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
376 | 1988-01-19 | FL | other | PINELLAS | FLORIDA GAS TRANSMISSION CO | THE ENCLOSED INCIDENT REPORT FOR FLORIDA GAS TRANSMISSION CO. DESCRIBES A DIG-IN BY AN OUTSIDE PARTY WHICH OCCURRED JANUARY 19, 1988. AT TRHE TIME OF OCCURRENCE THIS APPEARED NOT TO BE REPORTABLE NOTIFIED ONJANUARY 19, 1988 AS A COURTESY.AS COSTS OF MAKI | 250000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
377 | 1988-02-11 | LA | other | ST CHARLES | BRIDGELINE GAS DISTRIBUTION CO | THE SEGMENT THAT FAILED WAS IN A CROSSING OF THE MISSISSIPPI RIVER. THE SEGMENTWAS ISOLATED WITH APPROXIMATELY 450 PSIG PRESSURE WHEN FAILURE OCCURRED. NO INSPECTION OF THE LINE TO DETERMINE CAUSE OF FAILURE IS POSSIBLE UNTIL THE RIVER REACHES A LOWER S | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
378 | 1988-02-08 | CO | other | GARFIELD | NORTHWEST PIPELINE CORP | THE DELAY IN TELEPHONIC REPORTING WAS DUE TO ORIGINAL COST ESTIMATE BEING LESS THAN $50,000. | 87000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
379 | 1988-01-07 | OH | other | SUMMIT | EAST OHIO GAS CO |  | 90000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
380 | 1988-01-23 | PA | other | CAMBRIA | TEXAS EASTERN GAS PIPELINE CO | THE INCIDENT CONSISTED OF A LUBRICATING OIL FIRE IN A TURINE UNIT AT THE COMPRESSOR STATION. THE CAUSE OF THE INCIDENT IS UNDER INVESTIGATION. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
381 | 1988-02-21 | IL | other | WILL | ANR PIPELINE CO (AMERICAN NATURAL RESOURCE) | A RUNAWAY 18-WHEELED SEMI STRUCK AND DISLODGED TWO ABOVEDGROUND 12" FLANGED JOINTS AND IGNITED ESCAPING GAS. THE FIE CAUSED A SECONDARY PIPELINE FAILURE. A HOUSE LOCATED APPROXIMATELY 165' FROM TH FIE CENTER, CAUGHT FIRE AND WAS DESTROYED. THE DRIVER O | 750000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
382 | 1988-03-11 | TX | other | LUBBOCK | POWER TEX JOINT VENTURE | PRESSURE REGULATOR THAT IS PILOT OPERATED FAILED OPEN DUE TO THE FAILURE IN A DIAPHRAM IN THE CONTROL PILOT AND THUS CAUSE TEH DOWNSTREAM RELIEF VALVE TO GO OFF. A FIRE WAS STARTED BY STATIC ELECTRICITY OR SOME FOREIGN MATTER MOVING THROUGH THE RELIEF AND | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
383 | 1988-03-11 | WV | maintenance | KANAWHA | CONSOLIDATED GAS TRANSMISSION CORP |  | 189600 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
384 | 1988-01-17 | KS | other | SEDGWICK | WILLIAMS NATURAL GAS CO |  | 4256 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
385 | 1988-03-11 | LA | other |  | ANR PIPELINE CO (AMERICAN NATURAL RESOURCE) |  | 200000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
386 | 1988-02-15 | LA | technical failure | JEFFERSON DAVIS | TENNESSEE GAS PIPELINE CO | PINHOLE LEAK IN LONGITUDINAL SEAM DUE TO MATERIAL DEFECT. | 67000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
387 | 1988-02-08 | CO | other | LOGAN | NATURAL GAS PIPELINE CO OF AMERICA | SEISMIC CREW USING A 5" AUGER GOUGED THE 36" PIPELINE. THERE WAS NO RELEASE OFGAS TO ATMOSPHERE. OPERATOR HAS REPLACED DAMAGED SECTION.TWO YEAR OLD "ONE CALL" SYSTEM EXISTS IS COLORADO. NATURAL HAS BEEN A MEMBER FOR ONE ONE-HALF YEARS. | 85000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
388 | 1988-03-21 | TX | maintenance | GALVESTON | ANR PIPELINE CO (AMERICAN NATURAL RESOURCE) |  | 130000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
389 | 1988-03-15 | TX | other | SMITH | LONE STAR GAS CO | CONTRACTOR EXCAVATING AND HAULING FILL DIRT FOR PROPERTY OWNER STRUCK LINE SEVERAL TIMES IN A 12 FT. SEGMENT ULTIMATELY CUTTING 1 1/4 & 3 3/4 HOLE IN PIPE WITHFRONT END LOADER.LINE MARKED AT HWY. 155 APPROX. 300' S.E. OF DAMAGE AREA. CONTRACTOR WORKING F | 16000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
390 | 1988-03-11 | TX | other | LUBBOCK | CABOT GAS SUPPLY CORP | DAMAGE RESULTED FROMFIE OF THRID PARTY'S FACILITIES. | 40000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
391 | 1988-03-22 | TX | technical failure | MATAGORDA | VALERO TRANSMISSION CO | CAUSE FO RUPTURE PENDING METALLURGICAL REPORT RESULTS. | 120000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
392 | 1988-04-01 | MO | other | CASS | PANHANDLE EASTERN PIPELINE CO | MOVEMENT OF THE BANK OF A RAIN-SWOLLEN CREEK ALLOWED A JOINT OF PIPE TO PARTIALLY SLIP OUT A COUPLING. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
393 | 1988-05-16 | OK | other | CADDO | DELHI GAS PIPELINE CORP | PIPELINE WAS BEING DERPESSURED DURING PIGGING OPERATION IN A ONTROLLED AND MONITORED PROCEDURE. AN ACCUMULATION OF NATURAL GAS WAS IGNITED BY AN UNKNOWN SOURCE, RESULTING IN A FLASH FIRE AND SEBSEQUENT EXPLOSION THEREBY CAUSING BOCILY INJURY AND PROPETY | 30000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
394 | 1988-05-07 | MS | technical failure | DE SOTO | ANR PIPELINE CO (AMERICAN NATURAL RESOURCE) | FIVE FOOT LONG LAMINATION AT THE 9:00 POSITION. | 57000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
395 | 1988-04-27 | NM | other | SAN JUAN | EL PASO NATURAL GAS CO | ON APRIL 27, 1988, AT 8:50 A.M., AN EXPLOSION OCCURRED AT BLANCO "C" PLANT IN THE OIL SUMP OF THE #2 TURBINE. THIS TURBINE HAD NOT BEEN IN USE SINCE THE EXPLOSION AND FIRE THAT OCCURRED ON OCTOBER 17, 1987. SINCE THAT DATE, THE TURBINE HAD BEEN COMPLETE | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
396 | 1988-05-24 | ID | other | BANNOCK | NORTHWEST PIPELINE CORP | DIG IN BY FARMERS CONTRACTOR LANDLEVELING. | 75000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
397 | 1988-06-07 | KY | other | FLOYD | KENTUCKY - WEST VIRGINIA GAS CO |  | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
398 | 1988-06-10 | TX | maintenance |  | BLUE DOLPHIN PIPELINE CO | 250# ZINC BRACELETS ON 1/4 MILE SPACING USED DURING INITIAL CONSTRUCTION AND LINE WS BURIED FOUR FEET DEEP. RECTIFIER AND ANODE ADDED ON "A" PLATFORM IN 1969. RECTIFIER FUNCTION CHECKED OK 2-16-88. CABLES REPLACED 3/19/88.OFFSHORE OIL SHEEN REPORTED BY | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
399 | 1988-05-25 | LA | other |  | TENNESSEE GAS PIPELINE CO | PIPELINE IS LOCATED IN A KNOWN MUDSLIDE AREA. IT APPEARS THAT A MUDSLIDE CAUSED LEAK. | 60000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
400 | 1988-01-20 | NJ | other | BERGEN | TRANSCO GAS PIPELINE CORP | ON JANUARY 20, 1988 AN INCIDENT OCCURRED AT TRANSCONTINENTAL GAS PIPE LINE'S STATION 240 LNG PLANT THAT CAUSED DEFORMATION OF THE COLD BOX STRUCTURAL STEEL. AFTER THIS INCIDENT, AN INSPECTION OF THE PROCESS PIPING AND VESSELS INSIDE THE COLD BOX RESULTED | 85000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
401 | 1988-05-20 | TX | other | BROOKS | VALERO INTERSTATE TRANSMISSION CO | STRUCTURE PIPE FAILURE DUE TO POSSIBLE STRESS CORROSION, NO TEST RESULT YET. | 230000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
402 | 1988-06-16 | TX | maintenance | ECTOR | PHILLIPS PETROLEUM CO | THIS LINE WAS PURCHASE FROM EL PASO NATURAL GAS IN JANUARY, 1987. AT THAT TIME,CATHODIC PROTECTION WAS ON THE LINE AN IS PROTECTED AT THIS TIME.LOCALIZED PITTING DUE TO INTERNAL CORROSION RESULTED IN RUPTURE. H2S EMISSION FORCED EVACUATION OF 11 OCCUPANTS | 11500 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
403 | 1988-06-02 | TX | other | FRIO | VALERO TRANSMISSION CO | THIS INCIDENT WAS THE RESULT OF A ROAD GRADER HITTING THE PIPELINE AND SERVERING IT. THIS SECTION OF PIPE WAS REMOVED AND A NEW SECTION OF PIPE WAS INSTALLED.THE PIPELINE HAS BEEN RETURNED TO SERVICE. | 1500 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
404 | 1988-07-25 | TN | other | SHELBY | MEMPHIS LIGHT GAS & WATER DIVISION | CONTRACTOR DAMAGED SERVICE LINE WHILE BACKFILLING A DITCH THAT WAS CUT TO FACILITATE THE INSTALLATION OF A 66" WATER TRANSMISSION MAIN.HE BUILDING WAS OF DOUBLE BRICK WALL CONSTRUCTION WITH WOOD RAFTERS AND SHEETING, AND ASPHALT ROOF. THE BUILDING FIRE DA | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
405 | 1988-07-25 | TN | other | SHELBY | TEXAS GAS TRANSMISSION CORP | LIGHTNING STRUCK THE POWER SUPPLY AND/OR REGULATOR BUILDING OWNED BY MEMPHIS, LIGHT, GAS AND WATER (MGL&W). BUILDING WAS DOUBLE BRICK WALL WITH WOOD RAFTERS, WOOD SHEETING AND ASPHALT ROOFING. HEAT OR FALLING MATERIAL FROM ROOF STRUCTURECAUSED STEEL TUB | 500000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
406 | 1988-07-20 | TX | other | BEXAR | VALERO TRANSMISSION CO | ALAMO CEMENT COMPANY CONSTRUCTING ROAD BESIDE RIGHT-OF-WAY. D-9 DOZER HIT 6" PIPELINE CAUSING 12" RIP IN PIPE; ALSO DAMAGING OVER 20 FEET OF PIPE WITH RIPPER. | 11500 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
407 | 1988-08-03 | OK | other | LATIMER | OZARK GAS PIPELINE CORP | SOME OF THE PIPELINE MARKER FLAGS WERE PULLED UP OR DAMAGED BY LIVESTOCK IN THEAREA. INITIAL NOTIFICATION TO OZARK WAS DELAYED THREE HOURS DUE TO CONFUSION BY THE DRILLING CREW AND NOTIFICATION TO THE WRONG PIPELINE COMPANY.OZARK 20" TRANSMISSION LINE WA | 45000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
408 | 1988-09-03 | LA | other |  | ACADIAN GAS PIPELINE SYSTEM |  | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
409 | 1988-07-25 | TX | other | STARR | VALERO TRANSMISSION CO | FARM TRACTOR PLOWING FIELD HIT LINE WITH PLOW. GAS LINE WAS VERY SHALLOW AND EXPOSED DUE TO EROSION. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
410 | 1988-08-19 | LA | other | CAMERON | TEXAS GAS TRANSMISSION CORP | TEXAS GAS 6" LAKESSIDE-MALLARD BAY PIPELINE PARALLELS THE SOUTH SIDE OF THE INTRACOASTAL CANAL IN LOUISIANA AND CROSSES A CHANNEL FROM THE INTRACOASTAL CANAL TO GRAND LAKE. APPARENTLY THE PROP FROM A TUGBOAT PUSHING A HEAVY LOAD THROUGH THE CHANNEL HIT OU | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
411 | 1988-08-13 | PA | other | BERKS | TEXAS EASTERN GAS PIPELINE CO | SEVERAL MODIFICATIONS WERE BEING MADE TO UPGRADE TURBINE UNIT NO. 1 AT BERNVILLE COMPRESSOR STATION WHEN THE INCIDENT OCCURED. THE STATION WAS OUT OF SERVICE AND ALL GAS HAD BEEN VENTED FROM THE COMPRESSOR UNIT PIPING. A GAUGE PANEL WAS BEING CUT AWAY FRO | 45000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
412 | 1988-09-11 | LA | other |  | SOUTHERN NATURAL GAS CO | ON SEPTEMBER 8, 1988, THE MAIN PASS 77 STRUCTURE WAS SHUT- IN AND EVACUATED FORHURRICAN "FLORENCE". ON SEPTEMBER 11, 1988, THE PLATFORM WAS REMANNED. AN ATTEMPT TO BRING THE GAS LINE IN-SERVICE WAS ABORTED DUE TO LEAKAGE IN THE RISER. SUBSEQUENTLY, THE | 3389000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
413 | 1988-09-10 | TX | maintenance | WATERS | ANR PIPELINE CO (AMERICAN NATURAL RESOURCE) |  | 75000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
414 | 1988-09-17 | LA | other |  | TENNESSEE GAS PIPELINE CO | THE VALVE GUARD WAS PULLED OFF OF THE SIDE VALVE ASSEMBLY, POSSIBLY BY A CABLE FROM A PASSING BOAT. THE VALVE GUARD HUNG ON THE OPERATOR ON THE 12" CHECK VALVE, SHEARING OFF THE OPERATOR AND BREAKING THE 1/2" NIPPLE. | 97000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
415 | 1988-08-31 | NE | other | GAGE | NATURAL GAS PIPELINE CO OF AMERICA | TORCH IGNITED NATURAL GAS THAT HAD LEAKED INTO THE ENGINE CRANKCASE THROUGH THE COMPRESSOR PACKINGS. EMPLOYEES WERE USING A TORCH TO HEAT SPROCKET HUBS FOR REMOVAL FROM CRANKCASE. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
416 | 1988-09-02 | LA | maintenance | ST CHARLES | TEXACO INC | PINHOLE, ISOLATED LEAK DUE TO EXTERNAL CORROSION BELIEVED TO HAVE BEEN CAUSED BY STRAY CURRENT. | 12000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
417 | 1988-09-04 | TX | maintenance | REFUGIO | FLORIDA GAS TRANSMISSION CO | THE ENCLOSED INCIDENT REPORT FOR FLORIDA GAS TRANSMISSION CO. DESCRIBES A RUPTURE WHICH OCCURRED ON SEPTEMBER 4TH, 1988. AFTER CALCULATIONS HAD BEEN MADE TO DETERMINE THE AMOUNT OF NATURAL GAS RELEASED TO THE ATMOSPHERE, IT WAS DETERMINED THAT THE $50,0 | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
418 | 1988-09-01 | TX | technical failure |  | TENNESSEE GAS PIPELINE CO | 6" CRACK IN SADDLE PAD SIDE VALVE. | 200000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
419 | 1988-08-17 | OH | other | HANCOCK | COLUMBIA GAS TRANSMISSION CORP | PIPELINE PULLED-OUT OF UNDETECTED ORIGINAL COUPLING AFTER COMPLETING REPLACEMENT PIPELINE TIE-IN AND PRESSURIZING LINE. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
420 | 1988-09-01 | NM | other | SAN JUAN | GAS CO OF NEW MEXICO | FAILURE OF THE DEPARTMENT OF ENERGY (D.O.E.) MAINLINE, PRIMARILY A BARE LINE, WAS CAUSED BY EXTENSIVE CORRISIVE IN A SECTION OF WRAPPED PIPE. SEVERAL SCRATCHES WERE FOUND ON THIS SECTION WHICH HAD RESULTED IN EXTENSIVE COATING DAMAGE AND ACCELERATED CORR | 72367 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
421 | 1988-08-16 | TX | maintenance | HARRIS | AMOCO GAS CO | LEAK WAS CAUSED BY ATMOSPHERIC CORROSION AT A COATING HOLIDAY ON CARRIER PIPE IN THE CASING. | 1760 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
422 | 1988-08-24 | TX | technical failure | HARRIS | UNITED TEXAS TRANSMISSION CO | DISCOVERED LEAK HAD OCCURRED IN RUBBER OF DRESSER COUPLE ON 8-24-88, INITIALLY THOUGHT COULD BE REPAIRED WITH A BAND CLAMP. ON EVENING OF 8/24, DECIDED LINE NEEDED TO BE SHUT IN FOR REPAIR. | 5000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
423 | 1988-09-12 | TX | other | FOARD | LONE STAR GAS CO | SERVICE METER 200 FEET WEST OF WHERE LINE WAS DAMAGED PERMANENT LSG MARKER 2000FEET OF WHERE LINE WAS DAMAGED. | 8260 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
424 | 1988-09-29 | LA | other | WASHINGTON | FLORIDA GAS TRANSMISSION CO | LIGHTNING STRIKE BROKE STAINLESS STEEL TUBING GAUGE LINE AND IGNITED GAS. PIPELINE FACILITIES DAMAGED BY FIRE; ELECTRONIC FACILITIES DAMAGED BY ELECTRICAL DISCHARGE. | 51500 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
425 | 1988-08-06 | TX | other | FORT BEND | UNITED TEXAS TRANSMISSION CO | LANDOWNER WAS PLOWING FIELD AND STRUCK OUR PIPELINE CAUSING GOUGE IN PIPE. | 7500 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
426 | 1988-10-16 | TX | other | DENTON | LONE STAR GAS CO | LAND OWNER WAS CLEARING BRUSH ON PROPERTY WITH A TRACK LOADER AND PUNCTURED PIPELINE. INFLICTED 4" DIAMETER HOLE IN PIPELINE. REPAIR MADE BY TAKING LINE OUT OF SERVICE AND REPLACING DAMAGED PIPE. | 9500 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
427 | 1988-10-06 | TX | other | CANTON | LONE STAR GAS CO | 3- INCH PIPELINE HIT BY TP&L POWER DIGGER DIGGING PIER HOLES TO INSTALL H-FRAM POWER LINES CUTTING 2"X6" HOLE IN TOP QUARTER OF PIPE. | 15000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
428 | 1988-08-28 | TX | maintenance | WEBB | VALERO TRANSMISSION CO | THIS INCIDENT WAS THE RESULT OF INTERNAL CORROSION ON OUR RURAL GATHERING PIPELINE. THE LINE WAS TAKEN OUT OF SERVICE AND THIRTY (30) FEET OF PIPE WAS REPLACED. THE LINE WAS RETURNED TO SERVICE. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
429 | 1988-10-30 | TN | maintenance | PERRY | TENNESSEE GAS PIPELINE CO | EXTERNAL GENERAL CORROSION APPROXIMATELY 24" LONG X .180" - .230" DEEP. APPROXIMATELY AT THE 5:00 POSITION. | 150000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
430 | 1988-10-22 | TX | maintenance | SAN JACINTO | TENNESSEE GAS PIPELINE CO | THE INCIDENT WAS CONCLUDED TO BE CAUSED PRIMARILY BY STRESS CORROSION CRACKING (SCC). A SMALL CLUSTER OF CRACKS WHICH APPEARS TO BE SCC WAS FOUND ON A BURNED PIECE OF RUPTURED PIPE. | 120000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
431 | 1988-11-21 | TX | other | ECTOR | PHILLIPS PETROLEUM CO | 18" U GAS PIPELINE WAS BEING CLEANED BY PIGGING OPERATION. TWO RIVERS CONSTRUCTION CO., THE CONTRACTOR THE PROJECT, ALLOWED 6-INCH DRAIN LINE TO THE FRAC TANKTO COME LOOSE. SIDRO MORENO WAS HOSPITALIZED W/BROKEN FOREARM AND CUT ON FOREHEAD. ALBERT GARZ | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
432 | 1988-11-08 | IL | other | WILL | ANR PIPELINE CO (AMERICAN NATURAL RESOURCE) | LOW PRESSURE INSTRUMENT GAS VENTING FROM TRANSDUCERS IN CONTROL PANEL INSIDE THE METER BUILDING FOUND ITS WAY THROUGH ELECTRICAL CONDUIT INTO THE COMPUTER ROOM, IGNITED AND CAUSED A SMALL FIRE. | 125000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
433 | 1988-08-20 | LA | maintenance | PLATFORM | CHEVRON USA INC | THE 20" RISER WAS PROTECTED IN THE SPLASH ZONE VIA 26" CASING WITH TEH ANNULUS FILLED WITH COCRETE. THE 26" CASING TERMINATED ROUGHLY 10' ABOVE THE WATERLINE.THE CONCRETE WAS NOT ISOLATED FROM THE ENVIRONMENT AT THE 26" TERMINATION POINT. CONTINUAL WETT | 70000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
434 | 1988-10-26 | WA | other | GRANT | NORTHWEST PIPELINE CORP |  | 24000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
435 | 1988-11-09 | IL | other | COOK | NORTHERN ILLINOIS GAS CO | WHILE PURGING GAS FROM A PIPELINE PRIOR TO A TIE - IN, THE GAS WAS IGNITED BY AN UNKNOWN SOURCE ( SUSPECTED STATIC ELECTRICITY). THE HEAT MELTED OVERHEAD ELECTRIC LINES CAUSING THEY TO FAIL AND FALL TO THE GROUND. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
436 | 1988-09-23 | TX | other | JIM WELLS | VALERO INTERSTATE TRANSMISSION CO |  | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
437 | 1988-10-20 | IL | other | LAKE | NORTH SHORE GAS CO | CONTRACTOR GRADING SITE FOR ANEW PARKING AREA PIERCED 24" STEEL MAIN WITH TOOTHOF BULLDOZER. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
438 | 1988-10-22 | WV | other | RANDOLPH | COLUMBIA GAS TRANSMISSION CORP | THE DEHYDRATION PLANT EXPLOSION AND RESULTING FIRE WHICH DESTROYED TWO GLYCOL HEATER; A GAS/GLYCOL SEPARATOR; A GLYCOL ACCUMULATOR TANK; FOUR GLYCOL PUMPS; ALLASSOCIATED PIPING, VALVES, REGULATORS AND FITTINGS; AND THE EQUIPMENT ENCLOSUREMADE DETERMINING | 250000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
439 | 1988-11-12 | LA | other | STATE WATERS | TENNESSEE GAS PIPELINE CO | CONDITION OF PIPE INCIDATES A DREDGE OR DRILLING RIG HIT PIPELINE AND DAMAGED OVER 50 FEET, 37 FEET OF WHICH WAS CAUSED WHEN PIPE RUPTURED. THE RESPONSIBLE PARTY HAS NOT BEEN LOCATED. | 80000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
440 | 1988-10-24 | TX | other | DIMMIT | VALERO TRANSMISSION CO | DOZER OPERTOR DID NOT NOTIFY US BEFORE DIGGING, BUT STATED HE WAS AWARE PIPE WAS THERE BECAUSE OF SIGNS. HE ASSUMED LINE WAS BURIED DEEPER. | 1200 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
441 | 1988-11-28 | TX | other | GALVESTON | PHILLIPS PETROLEUM CO | DOZER WITH HYDRAULIC EXTENDED MOWER STRUCK NEARBY PROPANE LINE WHICH INGITED. HEAT FROM ORIGINAL RUPTURE CAUSED 10" ETHYLENE LINE TO EXPLODE AND BURN. | 70000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
442 | 1988-11-25 | AR | maintenance | OUACHITA | ARKLA ENERGY RESOURCES | TRANSMISSION LINE RUPUTURED AT CREEK CROSSING. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
443 | 1988-11-29 | LA | other | BIENVILLE | BEAR CREEK STORAGE CO |  | 54900 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
444 | 1988-12-09 | NE | other | THAYER | KN ENERGY INC (KANSAS NEBRASKA NATURAL GAS CO INC) | THE PIPELINE WS HIT BY AN OUTSIDE PARTY OPERATING A BULLDOZER. THE DAMAGED PORTION OF THE PIPELIN IS IN A CLASS I LOCATION AND WAS MARKED WITH PERMANENT LINE MARKER. A PERMANENT REPAIR WAS COMPLETED BY REPLACING FIVE (5) FEET OF THE DAMAGED PIPELINE WIT | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
445 | 1988-11-17 | TX | other |  | ANR PIPELINE CO (AMERICAN NATURAL RESOURCE) |  | 1785 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
446 | 1988-11-10 | CA | technical failure | LOS ANGELES | SOUTHERN CALIFORNIA GAS CO |  | 72000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
447 | 1988-12-06 | IN | other | OWEN | TEXAS GAS TRANSMISSION CORP | ON DECEMBER 6, 1988, AT 8:47AM., A CONTRACTOR WAS GRINDING UP TREE BRANCHES ON TEXAS GAS RIGHT-OF-WAY WITH HYDRO-AX EQUIPMENT AND HIT OUR ABOVEGROUND PIPE. THE BLADE ON THE HYDRO-AX PUT A 4 1/2" BY 1 1/2" HOLE IN THE PIPELINE. NO ONE WASHOSPITALIZED, AN | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
448 | 1988-12-07 | LA | maintenance |  | NATURAL GAS PIPELINE CO OF AMERICA | A WORK CREW FLYING BACK FROM A PLATFORM HAD OBSERVED BUBBLING, I.E. A RELEASE OF GAS. THE LINE HAS BEEN SHUT-IN, BUT INCLEMENT WEATHER IS DELAYING REPAIRES. THEREFORE, WE ARE ISSUING THIS REPORT BASED ON PRELIMENARY INFORMATION. ADDITIONAL INFORMATION | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
449 | 1988-11-28 | TX | other | GALVESTON | VALERO TRANSMISSION CO | AT APPROXIMATELY 2:00 PM. A TRACTOR MOWER STRUCK A PHILLIPS PETROLEUM PIPELINE WHICH CAUSED EXPLOSION WHICH IN TURN CAUSED OTHER PIPELINES TO RUPTURE AND EXPLODE. THIS CAUSED OUR PIPELINE TO RUPTURE. | 110000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
450 | 1988-08-26 | WY | maintenance |  | WESTERN TRANSMISSION CORP | WHEN THE PIPE WAS INITIALLY INSTALLED INTO THE DITCH, WHAT APPEARS TO HAVE OCCURRED WAS THAT THE APING MACHINE MALFUNCTIONED IN THIS AREA AND DID NOT OVERLAP THE TAPE WHICH LEFT BARE PIPE OF APPROXIMATELY 1/4/ INCH WIDE THE ENTIRE CIRCUMFERENCE OF THE PIP | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
451 | 1988-12-15 | TX | other | COLLIN | GARLAND, CITY OF | BLOW DOWN NEW PIPELINE PRIOR TO FLOWING GAS. | 1600 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
452 | 1988-04-18 | LA | maintenance | ST MARY | LOUISIANA INTRASTATE GAS CORP | PIPELINE WAS SHORTED TO ANOTHER LINE IN THE SAME RIGHT OF WAY AND WAS RECIEVINGINADEQUATE CATHODIC PROTECTION AT THAT LOCATION. | 15000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
453 | 1988-12-23 | LA | other | LA SALLE | LOUISIANA INTRASTATE GAS CORP | TIMBER CUTTING CREW WAS USING A DOZER TO PREPARE ROAD IN THE IMMEDIATE VICINITYOF THE PIPELINE. DOZER OPERATOR ALLOWED BLADE TO GOUGE PIPELINE. | 5000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
454 | 1988-12-31 | MS | other | NOXUBEE | SOUTHERN NATURAL GAS CO | CONTINUED RAIN CAUSED THE GROUND SURROUNDING THE PIPELINE TO BECOME SATURATED AND ALLOWED THE PIPE TO SHIFT, RESULTING IN THE PIPE PULLING OUT OF THE MECHANICAL COUPLING. | 220000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
455 | 1989-01-11 | TX | other | PALO PINTO | SOUTHWESTERN GAS PIPELINE INC | CONTRACTOR PLOWING IN TELEPHONE CABLE FOR SUTHWESTERN BELL TELEPHONE CO. FAILEDTO OBSERVE PIPELINE MARKING OF PAINTED CROSS FENCE AND DID NOT CALL OPERATOR FOR LINE LOCATION AND DEPTH. THREE FENCE POSTS PAINTED WITH THE COMPANIES COLORS WERE 10 FEET 6 IN | 3919 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
456 | 1989-01-20 | LA | maintenance |  | TENNESSEE GAS PIPELINE CO | LEAK WAS DISCOVERED ON 20" RISER AT +6' MEAN LOW GULF (MLG) UNDER A RISER CLAMP. RISER IS ATTACHED TO PLATFORM SUPPORT SYSTEM VIA CLAMPS. CORRODED PART OF PIPELINE WAS EXPOSED TO ATMOSHPERE AND, THEREFORE, RELIED ON COATINGS, NOT CATHODIC PROTECTION, FO | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
457 | 1989-02-01 | MI | other | CHARLEVOIX | GREAT LAKES GAS TRANSMISSION CO | ON FEBRUARY 1, 1989, A FIRE CAUSED EXTENSIVE DAMAGE IN THE INSIDE OF A COMPRESSOR BUILDING AT GREAT LAKES GAS TRANSMISSION COMPANY'S BOYNE FALLS, MICHIGAN COMPRESSOR STATION. THE EXTERNAL APPURTENANCES OF THE COMPRESSOR PACKAGE WAS DAMAGED AS WELL AS THE | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
458 | 1989-01-11 | LA | maintenance |  | CHEVRON USA INC | COATING FAILURE IN THE RISER SECTION ALLOWED SALTWATER TO COME IN CONTACT WITH THE PIPE AND CAUSED LOCALIZED PITTING. | 250000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
459 | 1989-01-27 | WY | other | WASHAKIE | WILLISTON BASIN INTERSTATE PIPELINE CO |  | 20000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
460 | 1989-01-15 | MN | other | DAKOTA | NORTHERN NATURAL GAS CO | DECEASED WAS ASPHYXIATED BY NATURAL GAS WHILE ATTEMPTING TO CLOSE VALVES IN A REGULATOR BUILDING TO ISOLATE A LEAK CAUSED BY THE FAILURE OF A REGULATOR CONTROLLINE. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
461 | 1989-01-13 | KS | other |  | KANSAS POWER & LIGHT CO | LANDOWNER WAS FARMING AT 16" TO 18" DEPTH & HIT 4" PIPELINE, PULLING ONE JOINT OF PIPE OUT OF MECHANICAL COUPLING. AVERAGE DEPTH IS 24", DEPTH WAS 17" AT LOCATION OF INCIDENT. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
462 | 1988-11-02 | CA | maintenance | LOS ANGELES | SOUTHERN CALIFORNIA GAS CO | THE REGULATOR AND METER PERSONNEL MADE AN IMMEDIATE CHECK OF THE 26,000 FEET OF 4" AND 6" STEEL HIGH PRESSURE TAPLINE AND UPSTREAM REGULATOR STATION. ALL EQUIPMENT WAS FOUND TO BE FUNCTIONING PROPERLY AND NO LINE BREAKS WERE EVIDENT. PRESSURES TAKEN AL | 160000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
463 | 1989-02-13 | TX | other | CRANE | WARREN PETROLEUM CO (NEW MEXICO GAS PIPELINE) | AFTER BEING FRACTRUED, THE CROSSHEAD WAS FORCED INTO THE COMPRESSOR CYLINDER HOUSING BY THE CONNECTING ROD WHICH HAD ENOUGH FORCE TO BREAK THE CYLINDER ANCHOR BOLTS AND DISCHARGE PIPING ALLOWING GAS TO ESCAPE. THE IGNITION SOURCE WAS A SPARK CAUSED BY TH | 200000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
464 | 1989-02-24 | TX | maintenance |  | BLUE DOLPHIN PIPELINE CO | COAST GUARD NOTIFIED US OF SPILL REPORTED IN GA 286 ABOUT 1420 HRS ON 02-24-89 BOUY DROPPED HELICOPTER 1630 HRS; LINE SHUT IN 1725 HRS; ZERO LINE PRESSURE 2400HRS; INSTALLED 1500 WP 20" BOLT-ON, SPLIT SLEEVE PLIDCO CLAMP 1432 HRS ON 02-27-89; TESTED 450 P | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
465 | 1989-02-06 | NJ | other | BERGEN | TRANSCO GAS PIPELINE CORP | A SMALL CRACK WAS FOUND IN A TUBE IN THE COIL OF THE H-4B VAPORIZER AT THE LNG FACILITY. METALLURGISTS NOW HAVE THE TUBE SECTION CONTAINING THE CRACK AND ARE IN THE PROCESS OF INVESTIGATING REPORT, A SUPPLEMENTAL REPORT WILL BE SENT TO DOT ALONG WITH A C | 300000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
466 | 1989-01-27 | MS | technical failure | MARSHALL | TENNESSEE GAS PIPELINE CO | THE CAUSE OF THE LEAK WAS DETERMINED TO BE DUE TO A MANUFACTUING DEFECT IN THE LONGITUDINAL WELD. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
467 | 1989-02-02 | MA | other | ESSEX | TENNESSEE GAS PIPELINE CO | A SUPPLEMENTAL REPORT WILL FOLLOW ONCE THE INDEPENDENT LAB REPORT DETERMINES THE CAUSE OF THE PIPE FAILURE. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
468 | 1989-02-16 | AL | other | RUSSELL | SOUTHEAST ALABAMA GAS DISTRICT | CONTRACTOR HAD FOUND UNACCEPTED SOIL ON STATE OF ALABAMA HIGHWAY PROJECT NO. 1246-6 AND FAILED TO NOTIFY GAS COMPANY THAT HE HAD RUN INTO THIS CONDITION. COROSS SECTION OF THIS AREA DID NOT SHOW ANY CUTTING OF EXISTING GRADE NECESSARY AT STATION 100 + 00 | 7894 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
469 | 1989-02-03 | NV | technical failure | STOREY | SOUTHWEST GAS CORP | A TRANSMISSON CREW WAS DISPATCHED FROM CARSON CITY. THE PRESSURE WAS LOWERED IN THE LINE. AFTER THE LINE WAS UNCOVERED, IT WAS DETERMINED THAT A 16" T.D. WILLIAMSON STOPPLE FITTING HAD A 9"-10"-LONG CRACK ON A FILET WELD. THE WELD WAS REPARIED AND THE | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
470 | 1989-02-20 | TX | maintenance | JEFFERSON | UNITED TEXAS TRANSMISSION CO |  | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
471 | 1989-03-08 | TX | other | LAMB | CABOT GAS SUPPLY CORP | AT APPROXIMATELY 11:45PM ON TUESDAY, MARCH 7, 1989 LIQUID FLOWED FROM THE MAPLE PLANT X PIPELINE INTO THE CABOT GAS SUPPLY, LUBBOCK TO FARWELL 8" +MAINLINE AT THE CABOT/MAPLE INTERCONNECT, LOCATED THREE MILES WEST OF AMHERST. APPROXIMATELY TWO WEEKS AGO, | 45000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
472 | 1989-02-28 | LA | other |  | SOUTHERN NATURAL GAS CO | ANCHOR CABLE FROM A CONSTRUCTION BARGE BECAME TANGLED IN AN UNDERWATER BYPASS VALVE ASSEMBLY. VALVE ASSEMBLY WAS BROKEN OFF OF PIPELINE. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
473 | 1989-03-05 | LA | other | TERREBONNE | TEXAS EASTERN GAS PIPELINE CO | PREPARATIONS WERE BEING MADE FOR THE INSTALLATION OD A VARIABLE SPEED MOTOR CONTROLLER FOR AN ELECTRIC MOTOR DRIVEN GAS COMPRESSOR AT THE POINTE AU CHEINFACILITY. THE LOAD BREAKER SUPPLYING ELECTRICAL POWER TO THE ELECTRIC MOTOR DRIVEN GAS COMPRESSOR HAD | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
474 | 1989-04-20 | OK | other | MAJOR | RINGWOOD GATHERING CO | A DIFFERENTIAL PRESSURE CONTROLLER ESCAPED THE LOCATED CLOSED POSITION AND PERMITTED A PNEUMATIC VALVE OPERATOR OPEN WHILE THE INJURED MEN WERE OPENING THE ORIFICE METER FLANGES PREPARATORY TO MAKING A ROUTINE INSPECTION OF THE ORIFICE PLATE. THE RESULTI | 40000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
475 | 1989-03-31 | IL | technical failure | CHAMPAIGN | ILLINOIS POWER CO | ON 3/31/89 AT APPROXIMATELY 2:00 P.M., A 12" TRANSMISSION MAIN UNDER 300 PSI OFPRESSURE SEPARATED WHERE A PLIDCO SPLIT AND SLEEVE FITING HAD BEEN INSTALLED. THE FITTING JOINTED THE ENDS OF A REPLACED SECTION OF THE MAIN AND THE EXISTING PORTION OF THE PIP | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
476 | 1989-03-19 | LA | other |  | SOUTHERN NATURAL GAS CO | ON THE MORNING OF SUNDAY, MARCH 19, 1989, PIPELINES UNLIMITED SERVICES (PLUS),SOUTHERN'S INDEPENDENT CONTRACTOR, ARRIVED AT ARCO'S SOUTH PASS BLOCK 60 "B"PLATFORM. AT APPROXIMATELY 7:00 PM, A SUBCONTRACTOR SELECTED BY PLUS INITIATEDCOLD CUTTING OF THE 18" | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
477 | 1989-02-03 | TX | technical failure | COTTLE | LONE STAR GAS CO | THERE IS NO RECORDED TEST PRESSURE ON THIS SEGMENT OF PIPE. LINE 71-5-2-1 WAS PURCHASED FROM UNITED GAS COMPANY IN 1967 AN MAXIMUM ALLOWABLE OPERATING PRESSURE WAS EXTABLISHED IN ACCORDANCE WITH 49 CFR 192.619(A)(3). | 20654 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
478 | 1989-03-02 | TX | maintenance | VICTORIA | DELHI GAS PIPELINE CORP |  | 24000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
479 | 1989-03-08 | TX | maintenance | MCLENNAN | TEXAS UTILITIES FUEL CO | SHORTED CASING, LOCALIZED EXTERNAL PITTING. SMALL LEAK. | 3000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
480 | 1989-02-23 | MI | other | GRATIOT | MICHIGAN CONSOLIDATED GAS CO (MICHCON) | CONTRACTOR PLOWING INFIELD TILE ON JULY 15, 1988,STRICK AND DAMAGED LINE, DID NOT REPORT DAMAGE. | 300000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
481 | 1989-04-11 | CT | other | LITCHFIELD | TENNESSEE GAS PIPELINE CO | OUTSIDE PARTY/THIRD PARTY CONTRACOTR'S BACKHOE SEVERED LINE. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
482 | 1989-04-02 | LA | other | CADDO | GULF STATES PIPELINE CORP | THE CAUSE IS UNKNOWN AS IT OCCURRED UNDER HIGH WATERS AND IS STILL INACCESSIBLE. ACCORDING TO THE RECORD, 1988 AND 1989 HAVE SEEN THE HIGHEST BAYOU FLOOD LEVELS SINCE THE LINE WAS COMPLETED, MAY 9, 1974. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
483 | 1989-03-02 | CO | maintenance | LA PLATA | EL PASO NATURAL GAS CO | A RUPTURE OCCURRED ON THE INTERCONNECTING LINE TO A DRIP ASSEMBLY ON LATERAL 4A-41. THE 90 DEGREE "L" OF THE DRIP SHOWED SEVERE INTERNAL CORROSION DUE TO ACCUMULATION OF WATER IN THE DRIP ASSSEMBLY. THE SOURCE OF IGNITION HAS NOT BEEN DETERMINED. | 334149 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
484 | 1989-03-08 | TX | technical failure |  | ANR PIPELINE CO (AMERICAN NATURAL RESOURCE) |  | 130000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
485 | 1989-03-21 | SD | other | MCCOOK | NORTHERN NATURAL GAS CO | MEASUREMENT TECHNICIAN CONNECTED A 125 PSIG RATED DIFFERENTIAL PRESSURE TEST APPARATUS TO PIPING OPERATING AT 700 PSIG. THE TEST APPARATUS FAILED AND A RELEASE OF GAS OCCURRED FOR A FEW SECONDS. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
486 | 1989-06-02 | MD | other | BALTIMORE | BALTIMORE GAS & ELECTRIC CO | AT APPROXIMATELY 1450 HOURS ON JUNE 2, 1989, THE PRINCIPAL GAS SYSTEM OPERATOR AT THE SPRING GARDENS GAS CONTROL CENTER NOTED AN INSTANTANEOUS INCREASE IN GAS FLOW AT THE OWINGS MILLS GATE STATION ON TYHE INSTRUMENTATION ON THE CONTROL PANEL. A CORRESPON | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
487 | 1989-05-03 | MS | maintenance | ITAWAMBA | ITAWAMBA INDUSTRIAL GAS CO | THE LEAK WAS A VERY SMALL PIN HOLE ON THE BOTTOM OF THE PIPE AND APPEARED TO BESOMETHING THAT WOULD RESULT FROM ELECTROYSIS CAUSED BY DAMAGE TO A SMALL AREA OF THE COATING. THE REPAIR WAS ACCOMPLISHED USING A SPLIT SADDLE MADE FROM A PIECE OF FOUR INCH .2 | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
488 | 1989-03-20 | TX | maintenance | MCLENNAN | TEXAS UTILITIES FUEL CO | LOCALIZED EXTERNAL PITTING. SMALL LEAK. | 20000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
489 | 1989-03-17 | TX | technical failure | VICTORIA | HOUSTON PIPELINE CO | DURING ORIGINAL CONSTRUCTION A 4" TAP WAS MADE ON THE 18" MAINLINE USING A WELD-O-LET. A THROUGH-WALL CRACK DEVELOPED IN THE 18" LINE UNDER THE TOE OF THE FILLET WELD. | 25000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
490 | 1989-04-28 | TX | other | DAWSON | RED RIVER PIPELINE CORP | THE LEAK WAS A 9" X 1.25" CRESCENT SHAPE CRACK ON THE 10" DISCHARGE PIPING OF COMPRESSOR UNIT #30006 ALONG AND NEAR THE AREA OF A 3" WELD-O-LET SERVING AS THE INLET TO A RELIEF VALVE. THE CRACK WAS CAUSED BY EXTERNAL FORCE ON THE 10" PIPING WHEN THE 3" X | 13000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
491 | 1989-04-29 | KS | other | SHAWNEE | WILLIAMS NATURAL GAS CO |  | 10000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
492 | 1989-06-05 | LA | maintenance | CADDO | J - W OPERATING CO |  | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
493 | 1989-03-21 | TX | other | DONLEY | LONE STAR GAS CO |  | 35000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
494 | 1989-04-21 | TX | maintenance |  | HOUSTON PIPELINE CO |  | 43000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
495 | 1989-04-16 | TX | maintenance | FORT BEND | MOBIL VANDERBILT-BEAUMONT PIPELINE CO |  | 42000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
496 | 1989-04-14 | TX | maintenance | NUECES | DELHI GAS PIPELINE CORP | EXTERNAL CORROSION. | 9909 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
497 | 1989-04-30 | TX | maintenance | FORT BEND | MOBIL VANDERBILT-BEAUMONT PIPELINE CO | ON APRIL 30, 1989, A LEAK WAS REPORTED AT MP 68 ON THE VANDERBILT TO BEAUMONT NATURAL GAS PIPELINE. THE PIPELINE WAS SHUT DOWN FROM THR ORIGIN STATION AT VANDERBILT TO MP 71 AND THE PRESSURE REDUCED. A FLAME IONIZATION INSPECTION WAS CONDUCTED OVER THIS | 75000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
498 | 1989-07-29 | LA | maintenance | ST HELENA | TRANSCO GAS PIPELINE CORP |  | 60000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
499 | 1989-06-09 | OH | other | HANCOCK | COLUMBIA GAS TRANSMISSION CORP | CONTRACTOR OPERATING FIELD TILING/TRENCHING MACHINE PUNCTURED LINE RESULTINGIN AN APPROXIMATE 2" DIA. HOLE. | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
500 | 1989-06-22 | NE | other | LINCOLN | K N ENERGY INC(KANSAS NEBRASKA GAS CO) | OPERATOR ACCIDENTALLY OPENED DISCHARGE ESD VALVE, ALLOWING GAS TO ESCAPE FROM OPEN DISCHARGE HEADER. | 300000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
501 | 1989-06-18 | LA | maintenance | NATCHITOCHES | LOUISIANA INTRASTATE GAS CORP |  | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
502 | 1989-05-16 | TX | maintenance | BEXAR | VALERO TRANSMISSION CO | TWO SMALL LEAKS IN SADF WEST, MEDINA RIVER SECONDARY CROSSING. BOTH LEAKS UNDERWATER REPAIRED BY CUTTING AND CAPPING SECONDARY CROSSING. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
503 | 1989-07-26 | TX | maintenance |  | BLUE DOLPHIN PIPELINE CO | MMS NOTIFIED US OF OIL SLICK 0930 HOURS ON 7-26. WE DROPPED BUOY 1330 HOURS AND STARTED SHUTDOWN. LIFT BOAT ON LOCATION 2030 HOURS 7-27. DIVER FOUND LEAK 1830 HOURS 7-28. SET CLAMP 2045 HOURS 7-29. TEST 450 PSIG OK. RESUMED GAS SALES 0700 HOURS 7-30. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
504 | 1989-06-25 | TX | other | ANGELINA | NATURAL GAS PIPELINE CO OF AMERICA | A FIRE WAS APPARENTLY CAUSED BY LUBE OIL ESCAPING FROM THE CHIP DETECTOR PIPING OF THE #10 UNIT. THE OIL WAS IGNITED BY AN UNKNOWN SOURCE. HYDRAULIC OIL AND AMBITROL SUBSEQUENTLY FUELED THE FIRE AS VALVES IN THOSE SYSTEMS MELTED. NATURAL GAS WAS NOT A | 4000000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
505 | 1989-07-04 | IA | other | MUSCATINE | NATURAL GAS PIPELINE CO OF AMERICA | A SALES METER WAS DAMAGED BY A FIRE FUELED BY NATURAL GAS. THE CAUSE OF THEINCIDENT IS UNDER INVESTIGATION. | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
506 | 1989-06-29 | TX | other | GALVESTON | CHEVRON PIPELINE CO | RELEASE WAS FROM A CRACK WHICH RESULTED FROM A DENT IN THE PIPELINE FROM AN UNKNOWN SOURCE AT AN UNDETERMINED TIME. LEAK WAS FOUND BY A SMALL AMOUNT OF PRODUCT BUBBLING UP THROUGH STANDING WATER. LINE WAS SHUT DOWN, PRUGED AND REPAIRES MADE. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
507 | 1989-07-09 | TX | technical failure | HARRIS | MOBIL VANDERBILT-BEAUMONT PIPELINE CO | FRACTURE FAILURE OF WELD NECK FLANGE DUE TO A MANUFACTURING DEFECT. HYSTOSTATIC TEST PRESSURE COULD HAVE FURTHER INDUCED WEAKENING IN THE AREA OF THE DEFECT PRIOR TO THE FAILURE. | 6200 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
508 | 1989-07-27 | LA | technical failure |  | TRANSCO GAS PIPELINE CORP | DURING A ROUTINE UNDERWATER INSPECTION USING A REMOTE OPERATED VEHICLE, BUBBLES WERE OBSERVED NEAR THE BOTTOM OF THE RISER ON THE A-4 LEG OF BLOCK 20-A PLATFORM. A VIDEO TAPE OF THE FACILITIES IN THIS AREA INDICATED THAT A LEAK WAS LOCATED APPROXIMATELY | 375000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
509 | 1989-08-02 | NE | other | HAMILTON | K N ENERGY INC(KANSAS NEBRASKA GAS CO) | THE PIPELINE WAS HIT BY AN OUTSIDE PARTY OPERATING A WEED CUTTER. THE DAMAGED PORTION OF THE PIPELINE IS IN A CLASS I LOCATION AND WAS MARKED WITH PERMANENT LINE MARKERS. A PERMANENT REPAIR WAS COMPLETED BY REPLACING TWELVE (12) FEET OF THE DAMAGED PIPEL | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
510 | 1989-07-28 | TX | maintenance |  | ANR PIPELINE CO (AMERICAN NATURAL RESOURCE) |  | 65000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
511 | 1989-05-16 | TX | other | SOMERVELL | LONE STAR GAS CO | WATER WASHED DAM OUT. PIPELINE CROSS CREEK IN DAM. | 26595 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
512 | 1989-08-02 | TX | other | WISE | LONE STAR GAS CO |  | 5000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
513 | 1989-07-26 | TX | other | CAMERON | RIO PIPELINE LP | FOREMOST PAVING HIT OUR LINE AT FM 803 AND SH 100 AT APPROXIMATELY 11:15 AM.WE BLEW THE LINE DOWN TO ATMOSPHERE AT 12:15 PM. THE LINE WAS REPAIRED AND PUT BACK IN SERVICE BY 4:30 PM. | 5000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
514 | 1989-08-14 | WV | other | HARDY | COLUMBIA GAS TRANSMISSION CORP | BACKHOE OPERATOR LOST CONTROL OF BACKHOE WHICH RAN INTO AND DESTROYED A MEASUREMENT & REGULATION STATION. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
515 | 1989-09-04 | LA | other |  | CHEVRON USA INC | BREAK APPARENTLY CAUSED BY ANCHOR RECOVERY OPERATIONS FROM A YET UNKNOWN COMPANY. THE PIPE WAS COMPLETELY SEPARATED WITH SIGNIFICANT MARKINGS CAUSED BY ANCHOR SCRAPINGS. | 500000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
516 | 1989-07-25 | NC | other | WAYNE | NORTH CAROLINA NATURAL GAS CORP | A LOCATION REQUEST TICKET WAS RECIEVED FROM U.L.O.C.O. ON 7/18/89. THE LOCATION ON THE TICKET WAS GIVEN AS THE INTERSECTION OF S.R. 1107 & MUSGRAVE ROAD. THE ACTUAL LOCATION WAS S.R. 1007 & MUSGRAVE RD. N.C.N.C. DOES NOT HAVE ANY FACILITIES ON OR NEAR S | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
517 | 1989-08-10 | TX | maintenance | JACKSON | HOUSTON PIPELINE CO | THE BREAK OCCURRED IN A SUBMERGED CROSSING OF A WATER FILLED DITCH. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
518 | 1989-08-28 | LA | other | BIENVILLE/QUACHITA PARISH | SOUTHERN NATURAL GAS CO | ON AUGUST 28, 1989, EXPLOSIVE DEVICES WERE DETECTED AT THREE LOCATIONS ON SOUTHERN'S HIGH PRESSURE INTERSTATE NATURAL GAS TRANSMISSION PIPELINE SYSTEM INBIENVILLE AND QUACHITA PARISHES, LOUISIANA. TWO DEVICES COMPOSED OF TWO FOUR-POUND STICKS OF FUSED DY | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
519 | 1989-09-15 | LA | other | WINN | LOUISIANA INTRASTATE GAS CORP | COMPANY MAINTENANCE CREW DAMAGED SIDE TAP VALVE WHILE PERFORMING ROUTINE MAINTENANCE ON PIPELINE. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
520 | 1989-09-09 | LA | other | PLAQUEMINES | SOUTHERN NATURAL GAS CO | THIRD PARTY WAS USING BARGE AND DRAGLINE TO DIG OUT ALONG RIVER BANK FOR FUTURE BARGE ACCESS. THE BUCKET HIT THE UNDERWATER RIVER LINE. SUBSEQUENT DIVER INSPECTION INDICATED VERY MINOR DAMAGE TO THE PIPE. APPROXIMATELY SIX DAYSLATER THE PIPELINE RUPTUR | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
521 | 1989-08-21 | TX | maintenance | HIDALGO | VAL GAS CO | THIS FAILURE WAS LOCATED IN A WET AREA NEAR A SEWER POND DRAINAGE. EXTERNALCORROSION OCCURRED DUE TO COATING DISBONDMENT. VOLUME LOST BASED ON VALLEY COMPLEX SYSTEM LINE PACK LOST, PRODUCTION FLOWING FOR ONE HOUR AND 3.2 MILES OF 8" PIPE BLOWN TO "0" ON | 14000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
522 | 1989-08-29 | TX | technical failure | FREESTONE | TEXAS UTILITIES FUEL CO | LEAK OCCURRED AT HEAT AFFECTED ZONE ADJACENT TO A GIRTH WELD. | 20500 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
523 | 1989-09-13 | LA | other | ST LANDRY | TRANSCO GAS PIPELINE CORP | A CONTRACTOR WAS WORKING FOR TRANSCO ON WELL#44 AT PAD 18 REMOVING SAND FROMTHE PERFORATED ZONE OF THE WELL AND HAD INSTALLED A COIL TUBING UNIT AND ANINJECTOR ASSEMBLY ON THE WELL. DURING THE DESANDING OPERATION, THE CONTRACTOR'S TUBING UNIT (#2148) DEV | 568920 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
524 | 1989-09-28 | VA | other | LOUDOUN | COLUMBIA GAS TRANSMISSION CORP | DURING LAND CLEARING OPERATION, A BACKHOE DIGGING HOLES TO BURY STUMPS PUNCTRUED PIPELINE, PRODUCING A 2-INCH BY 3-INCH HOLE. | 112000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
525 | 1989-10-05 | TX | maintenance |  | ANR PIPELINE CO (AMERICAN NATURAL RESOURCE) |  | 152000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
526 | 1989-10-02 | NM | other | LEA | LLANO INC | INSPECTION OF THE CRYOGENIC PLANT COMPRESSION FACILITIES INVOLVED IN THE INCIDENT REVEALED THE ABSENCE OF A 1 5/8" "JACK BOLT" FROM AN INBOARD, DISCHARGEVALVE CAP ON A COMPRESSOR CYLINDER. DURING DISMANTLING OF THAT COMPRESSION CYLINDER, PARTICULARLY THA | 600000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
527 | 1989-09-24 | TX | maintenance |  | ANR PIPELINE CO (AMERICAN NATURAL RESOURCE) |  | 400000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
528 | 1989-09-18 | TX | other | ANDERSON | LONE STAR GAS CO | ROAD GRADER GRADING LOGGING ROAD STRUCK PIPELINE CAUSING 3 1/4" TRIANGULAR HOL | 10142 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
529 | 1989-10-05 | TX | other | WARD | CABOT GAS SUPPLY CORP | INDEPENDENT CONTRACTOR HIT PIPELINE WITH A BACK HOE WHILE DITCHING TO LAY A WATER LINE. | 42000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
530 | 1989-09-22 | TX | maintenance | ZAVALA | VALERO TRANSMISSION CO | THIS INCIDENT WAS CAUSED BY AN EXTERNAL CORROSION LEAK ABOUT FOUR (4) MILES NORTH OF CRYSTAL CITY. THREE (3) CUSTOMERS AND ONE (1) PRODUCER WERE WITHOUTSERVICE FOR THREE (3) HOURS WHILE THE LINE WAS BLOCKED IN FOR REPAIR. | 3500 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
531 | 1989-10-24 | CO | other | ARCHULETA | WESTERN GAS SUPPLY CO | THE MICRO LOCK BRAKES FAILED ON A TOW TRUCK PARKED ON THE ROAD BEHIND THE METER STATION. THE TRUCK ROLLED DOWN THE HILL THROUGH THE STATION FENCE, STRIKING THE ABOVE GROUND PIPING. A 3" ANSI 150 PLUG VALVE RUPTURED. THE STATION PIPING ABOVE AND BELOW G | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
532 | 1989-10-23 | NJ | maintenance | GLOUCESTER | SUN REFINING & MARKETING CO | THE SIX INCH LINE UNDER RACCOON CREEK AT BRIDGEPORT, NEW JERSEY, DEVELOPED ALEAK FROM INTERNAL LOW POINT ACQUIOUS CORROSION. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
533 | 1989-10-03 | TX | other |  | NATURAL GAS PIPELINE CO OF AMERICA | FISHING BOAT STRUCK PIPELINE APPROXIMATELY 1/2 MILE OFFSHORE. | 750000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
534 | 1989-10-18 | AZ | other | MARICOPA | EL PASO NATURAL GAS CO | LAND OWNER HAD BEEN TOLD NOT TO MAKE CUTS OR REMOVE COVER FROM OUR PIPELINE.A CONTRACTOR HIRED BY LAND OWNER WAS GRADING WITH A BULLDOZER AND HIT AND RUPTURED OUR 16" LINE #2039. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
535 | 1989-10-21 | WV | other | KANAWHA | COLUMBIA GAS TRANSMISSION CORP | A DOZER CONSTRUCTING AN ACCESS ROAD HIT AND SEPARATED THE PIPELINE RESULTING IN AN EXPLOSION AND FIRE. | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
536 | 1989-11-01 | LA | maintenance |  | NATURAL GAS PIPELINE CO OF AMERICA | LEAK WAS CAUSED BY INTERNAL CORROSION.REPAIRED BY INSTALLING A PLIDCO LEAK CLAMP. | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
537 | 1989-11-30 | KY | other | ROWAN | TENNESSEE GAS PIPELINE CO | UNIT HAS BEEN DOWN SINCE 1983. RECENT OVERHAUL AND NEW CONTROLS WERE BEING VERIFIED AND ACCEPTED. POWER TURBINE FAILED. CAUSED OIL LEAK WHICH RESULTEDIN FIRE. THE FIRE DESTROYED THE UNIT WALL, ASSOCIATED WALLS, FLOOR, AND CEILING. | 3000000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
538 | 1989-11-14 | TX | other | PANOLA | TEJAS GAS CO | CONTRACTOR USING A D-7 DOZER STRUCK PIPELINE WHILE CONSTRUCING A RESERVE PITFOR A NEW PENZOIL WELL LOCATION. | 5000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
539 | 1989-11-13 | OH | maintenance | HOCKING | COLUMBIA GAS TRANSMISSION CORP | NO KNOWN OUTSIDE FACTORS. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
540 | 1989-11-10 | LA | technical failure | CAMERON | NATURAL GAS PIPELINE CO OF AMERICA | LEAK DUE TO LAMINATION IN PIPE WALL. | 130000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
541 | 1989-12-16 | LA | other | CADDO | J - W OPERATING CO |  | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
542 | 1989-12-02 | LA | other |  | COLUMBIA GULF TRANSMISSION CO | THE EXISTING 12" PIPELINE FROM PENNZOIL PLATFORM "A" IN SOUTH PASS BLK. 57 TO A CONNECTION IN TENNESSEE GAS' 26" PIPELINE IN SOUTH PASS BLK. 77, A DISTANCE OF APPROXIMATELY 3.85 MILES, WAS PULLED OUT OF ITS ORIGINAL POSITION APPROXIMATELY 1800 TO 2400 FEE | 4702000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
543 | 1989-11-29 | MN | other | DAKOTA | NORTHERN NATURAL GAS CO | A 1/2" NPS NIPPLE ON THE #4 COMPRESSOR RELIEF VALVE SENSING LINE FAILED RESULTING IN THE COMPRESSOR PLANT (FIVE COMPRESSORS) EMERGENCY SHUT DOWN SYSTEM ACTIVATING.SUPPLEMENTAL : AN UNNECCESSARY, UNPLANNED ACTIVATION OF THE COMPRESSOR PLANT (5UNITS) EMERGE | 91700 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
544 | 1989-11-25 | MS | other |  | ANR PIPELINE CO (AMERICAN NATURAL RESOURCE) | PRELIMINARY CONCLUSION: ELECTRICAL MALFUNCTION OF TURBINE CONTROL SYSTEMS COUPLED WITH LUBE OIL AND GAS LEAK APEAR TO HAVE CAUSED THE FIRE. INVESTIGATION IS STILL IN PROGRESS. | 1000000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
545 | 1989-12-27 | TX | maintenance |  | BLUE DOLPHIN PIPELINE CO | HELICOPTER LINE SURVEY FOLLOWING CLAMP #5 AND GAS TEST PRESSURE APPLIED TO PIPELINE LOCATED BUBBLES IN BLOCK GA 286; SO DIVER BOAT WAS MOVED THERE AND CLAMP WAS SET BY 1502 HOURS ON 12/29/89 AND 400 PSI GAS PRESSURE TEST WAS SUCCESSFUL. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
546 | 1989-12-21 | TX | maintenance |  | BLUE DOLPHIN PIPELINE CO | SLICK OBSERVED BY ARMS PERSONNEL IN HELICOPTER WAS REPORTED BY RADIO/TELEPHONE; SO A MARKER BOUY WAS DROPPED. PRODUCERS SHUT DOWN GAS DELIVERY WITHIN TWO HURS BUT REPAIR WAS WAS DELAYED BY HIGH SEAS AND RECORD COLD. SET PLIDCO, SPLIT SLEEVE, BOLT-ON, 15 | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
547 | 1989-11-21 | TX | other | PECOS | VALERO TRANSMISSION CO | WHILE PERFORMING SCHEDULED MAINTENANCE WORK, TWO WORKERS WERE BURNED WHEN AFLASH FIRE ERUPTED. THE WORKERS WERE ATTEMPTING TO WELD A 24" END CAP TO A 24" PIPE IN THE WAHA COMPRESSOR YARD PIPING. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
548 | 1989-12-23 | AR | technical failure | GRANT | ARKANSAS LOUISIANA GAS CO (ARKLA GAS CO) | A CRACK DEVELOPED IN A WRINKLE BEND. CRACK FOLLOWED WRINKLE AND PIPE SPLIT, 22" LONG, WIDEST OPENING 1/4". | 176000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
549 | 1989-12-19 | PA | maintenance | WASHINGTON | COLUMBIA GAS TRANSMISSION CORP | NO OUTSIDE CONTRIBUTING FACTORS. | 101000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
550 | 1989-12-29 | NY | other | BRONX | CONSOLIDATED EDISON CO OF NEW YORK | FIRE AT RUPTURED 30" HIGH PRESSURE STEEL GAS MAIN. INVESTIGATION IS CONTINUING; SUPPLEMENTAL REPORT TO FOLLOW.SUPPLEMENT - AN EXPLOSION OCCURED IN TWO ELECTRIC MANHOLES, CAUSED BY THE IGNITION OF A GAS OF UNDETERMINED ORIGIN. THE EXPLSION IN THE MANHOLES | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
551 | 1989-12-28 | LA | other |  | UNITED GAS PIPELINE CO | CAUSE OF DAMAGE IS NOT CONFIRMED, BUT PRELIMINARY EVIDENCE INDICATES THAT THE DAMAGE WAS CAUSED BY A SHELL DREDGE. | 120000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
552 | 1989-12-22 | TX | other | MONTGOMERY | MORGAS CO | EMPLOYEES WERE ATTEMPTING TO OPEN CITY GATE BY-PASS. EXCESSIVE PRESSURE REACHED POSITIVE DISPLACEMENT. METER EXPLODED. | 7500 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
553 | 1990-01-21 | TX | maintenance | BRAZORIA | BLUE DOLPHIN PIPELINE CO | HELICOPTER INVESTIGATION OF REPORTED OIL SLICK VERIFIED 100' WIDE X 5 MILES LONG COMING FROM BUBBLES IN GA-275; DROPPED BOUY 1000 HR ON 1/21; COMMENCED TELEPHONE REPORTS, FIELD SHUT IN, MOBILIZATION OF DIVERS, FABRICATION OF CLAMP BY TEAM IN ALVIN; DELIVE | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
554 | 1990-01-20 | MS | other | YAZOO | MUSTANG FUEL CORP OF MISSISSIPPI | GROUND SHIFTING | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
555 | 1990-01-03 | NM | other | EDDY | GAS CO OF NEW MEXICO | A JETCO 7332 TRENCHER OWNED BY B & H CONSTRUCTION, P.O. BOX 977, EUNICE, NM 88231 AND OPERATED BY B.J. PILKENTON HIT AND SEVERED AN 8" GAS TRANSMISSION LINE. CONTRACTOR REQUESTED LINE LOCATE AND THEN BEGAN EXCAVATION BEFORE LINE WAS LOCATED BY OPERATOR. | 150000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
556 | 1990-01-11 | TN | technical failure | MCNAIRY | TENNESSEE GAS PIPELINE CO | RUPTURE OCCURRED IN WRINKLE (SAG) BEND. THERE WAS NO FIRE AND THE ONLY DAMAGE WAS TO THE PIPE INCLUDING GAS LOST. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
557 | 1989-12-23 | TX | other | AZLE | LONE STAR GAS CO |  | 32200 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
558 | 1989-11-12 | TX | other | JEFFERSON | UNITED TEXAS TRANSMISSION CO | BACK HOE HIT 2" DUMP LINE ON TRANSMISSION MAIN WHILE EXCAVATING FOR A VALVE REPLACEMENT. | 26761 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
559 | 1990-01-19 | NE | technical failure | NUCKOLLS | K N ENERGY INC(KANSAS NEBRASKA GAS CO) | TOWN METERING CHART (1.5 MILES AWAY FROM LEAK ARE) INDICATED A DROP IN SUPPLY PRESSURE OCCURRED ABOUT 5 A.M. ON 1/19/90. LEAKAGE INCREASED OVER THE NEXTFEW DAYS UNTIL A FEW CUSTOMER SERVICES WERE LOST IN TOWN. LEAKAGE INVESTIGATION CREW LOCATED DEFECTIV | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
560 | 1990-01-12 | OK | other | PAYNE | ONG TRANSMISSION CO | CONTRACTOR CONSTRUCTING WELL LOCATION PUNCTURED PIPELINE WITH DOZER. LOST TOWNS OF PAWNEE AND INGALLS, OKLAHOMA; APPROXIMATELY 1350 CUSTOMERS. | 52200 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
561 | 1989-12-01 | TX | maintenance |  | COASTAL STATES GAS TRANSMISSION CO |  | 10000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
562 | 1990-01-13 | TX | maintenance | LEON | TEXAS UTILITIES FUEL CO | PINHOLE LEAK IN 8 INCH PIPELINE BETWEEN MILE MARKER BVA65 AND BVA68 IN LEON CO.ON THE GRAPELAND - OLETHA PIPELINE. PINHOLE LEAK DUE TO CORROSION. | 28000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
563 | 1989-01-18 | TX | other |  | LONE STAR GAS CO | RUPTURED PIPE TO BE TESTED BY A METALLURGIST AT A LATER DATE FOR FURTHER INFORMATION ON CAUSE OF RUPTURE. PIPE TO SOIL READINGS AT THE SIGHT WERE NO. END:.87 SO. END:.91 WITH A SOIL POTENTIAL OF NEUTRAL. | 15000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
564 | 1990-02-05 | OH | technical failure | ATHENS | TEXAS EASTERN GAS PIPELINE CO | IMPELLER WHEEL IS A PART OF THE AERO ASSEMBLY WHICH IS THE INTERNAL MAKE-UP OF THE CENTRIFUGAL COMPRESSOR.PART 3 - THE FAILURE OF THE COMPRESSOR UNIT WAS CAUSED BY THE DISINTEGRATION OFTHE RIVETED IMPELLER IN THE CLARK COMPRESSOR, RESULTING IN A VIBRATION | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
565 | 1990-02-22 | TX | maintenance | BRAZORIA | BLUE DOLPHIN PIPELINE CO | 0745 HRS SHEEN REPORTED BY COASTAL HELICOPTED MARKED BY OUR BUOY 1150 HRS. DIVE BOAT ARRIVED 2/24/90, 0600 HRS; LEAK LOCATED 1716 HRS; CLAMP SET 2131 HRS; TESTED OK 400 PSI GAS, 2/25/90 0001 HRS; CHECKED BLACK LIGHT = OK, 0702 HRS 2/25/90, STARED GAS SAL | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
566 | 1990-02-07 | TX | other |  | LONE STAR GAS CO | WHILE DIGGING OUT CONCRETE DRAIN PIPE, TRACK MOUNTED LOADER OPERATOR STRUCK AND PUNCTURED 6" STEEL PIPELINE. | 9700 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
567 | 1990-02-26 | TX | other | CASTRO | WESTAR TRANSMISSION CO | FARMER HIT WHILE DEEP PLOWING. THIS PORTION OF LINE RUNS DOWNHILL INTO AN OLD LAKE BED. SOIL EROSION TOOK COVER FROM PIPELINE. | 5500 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
568 | 1990-02-23 | LA | technical failure |  | UNITED GAS PIPELINE CO | LEAK OCCURRED DUE TO THE FAILURE OF AN 0-RING SURROUNDING A DUST COVER ON THE EXTENDED ARM ( SEE ATTACHED SKETCH). THE 0-RING IS MADE OUT OF VITON "A" MATERIAL.SUPPLEMENT: AT 1610 HOURS ON 4/20/90 A PLIDCO CLAMP WAS INSTALLED TO FINALIZETHE REPAIRS. | 98249 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
569 | 1990-02-10 | LA | other | PLAQUEMINES | UNITED GAS PIPELINE CO | LARGE SHIP, ATTEMPTING TO ANCHOR IN THE MISSISSIPPI RIVER, CAUGHT ANCHOR ON PIPELINE. IN ATTEMPTING TO FREE HIMSELF, PIPELINE WAS RUPTURED. PIPELINE CROSSING ALSO LISTED ON NOAA NAVIGATIONAL CHARTS OF MISSISSIPPI RIVER DELTA NO.11361. | 500000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
570 | 1990-02-14 | LA | other |  | TENNESSEE GAS PIPELINE CO | LOCATION OF INVOLVED FACILITIES LIMITS MARKING OF PIPELINE; HOWEVER, DETAILED CONSTRUCTION DRAWINGS EXIST FOR EXACT FACILITY COORDINATES.CONSTRUCTION BARGE WORKING IN THE EUGENE ISLAND BLOCK 338 AREA DRUG AN ACHOR ACROSS EXISTING VALVE ASSEMBLY SHEARING A | 200000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
571 | 1990-02-16 | CT | technical failure | LITCHFIELD | TENNESSEE GAS PIPELINE CO | TGP'S 4" TORRINGTON LATERAL RUPTURED NEAR YAKMOSHUK ROAD IN BARKHAMSTED, CONNECTICUT. THERE WAS NO LOSS OF SERVICE TO CUSTOMERS. ORIGINATED AT A DENT AND 5" GOUGE. | 5000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
572 | 1990-03-11 | AR | technical failure | HOT SPRING | ARKLA ENERGY RESOURCES | SEAM FAILURE, PIPE TO BE ANALYZED BY BATTELLE. MOP REDUCED TO 332 PSIG UNTIL BATTELLE RECOMMENDATINS ARE RECEIVED. | 51000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
573 | 1990-03-12 | LA | maintenance | FEDERAL WATERS | ANR PIPELINE CO (AMERICAN NATURAL RESOURCE) |  | 63000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
574 | 1990-03-01 | KS | other | LABETTE | WILLIAMS NATURAL GAS CO |  | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
575 | 1990-03-12 | TX | maintenance | BRAZORIA | BLUE DOLPHIN PIPELINE CO | OIL SLICK OBSERVED BY COASTAL HELICOPTER REPORTED TO US. WE DROPPED BUOY MARKER AND ORDERED OUT LOCAL DIVERS ON BOAT FROM LOUISIANA WHICH ARRIVED 1400 HRS. 13 MAR., BUT WAS FORCED OFF LOCATION BY WEATHER 14 MAR. AND RETURNED 15 MAR. TO INSTALL A CLAMP, T | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
576 | 1990-02-25 | LA | maintenance | ST HELENA | TRANSCO GAS PIPELINE CORP | THE RUPTURE BLEW OUT APPROXIMATELY 27 FEET OF THE PIPELINE. MEASUREMENTS MADE ALONG TEH SEAM WELD OF THE RECOVERED PIECES SHOWED THAT ALL THE MISSING PIPE FROM THE LINE HAD BEEN FOUND. THE RESULTS OF THE FIELD AND LABORATORY EXAMINATIONS SHOWED THAT THE | 150000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
577 | 1990-03-14 | LA | maintenance |  | NATURAL GAS PIPELINE CO OF AMERICA | THE PIPELINE HAD BEEN SHUT-IN FOR TWO YEARS PRIOR TO LEAK. THE PIPELINE HASNOW BEEN FILLED WITH WATER IN PREPARATION FOR ABANDONMENT. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
578 | 1990-03-22 | TX | other | JACKSON | LONE STAR GAS CO | ONE MARKER 110 FEET AND THE OTHER MARKER IS 1957' FROM DAMAGE AREA. | 17485 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
579 | 1990-03-20 | FL | other | ESCAMBIA | UNITED GAS PIPELINE CO | ESCAMBIA COUNTY MAINTENANCE DEPARTMENT ROAD GRADER HIT LINE WHILE GRADING ROAD DITCH. | 10700 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
580 | 1990-03-19 | KY | technical failure | ROWAN | TENNESSEE GAS PIPELINE CO | A FLEXIBLE (STEEL BRAIDED) FUEL GAS LINE TO THE #3 ENGINE BROKE AND IGNITED. THE FIRE BURNED THROUGH A RUBBER OIL DRAIN BOOT CAUSING OIL TO IGNITE AND SPREAD THE FIRE ON ONE SIDE OF THE #3 UNIT AND IMMEDIATELY UNDER THE UNIT AT BASEMENT LEVEL. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
581 | 1990-03-23 | TX | other |  | CHANNEL INDUSTRIES GAS CO | COMPANY'S CONTRACTOR WAS WORKING IN WET SOIL CONDITIONS WHICH CAUSED BACKHOETO PUSH SOIL AGAINST NIPPLE AND SIDE VALVE, CAUSING NIPPLE TO BREAK. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
582 | 1990-04-02 | LA | other |  | TENNESSEE GAS PIPELINE CO | RUPTURE OCCURRED IN APPROXIMATELY THE MIDDLE OF THE RED RIVER CROSSING. EXISTING HEAVY FLOODING CONDITIONS AND RESULTING STRONG CURRENTS AND RIVERBED WASHING WAS THE CAUSE OF THE INCIDENT. | 1000000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
583 | 1990-04-03 | LA | other | PLAQUEMINES | TENNESSEE GAS PIPELINE CO | MISSISSIPPI RIVERBED WASHIING FROM FLOODING AND STRONG CURRENTS PROBABLY CAUSED PIPELINE FAILURE. ACCESSIBILITY IS LIMITED UNTIL CURRENT FLOODING CONDITIONS SUBSIDE. THE LINE HAS BEEN TAKEN OUT OF SERVICE. | 800000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
584 | 1990-04-06 | IL | technical failure | MERCER | ANR PIPELINE CO (AMERICAN NATURAL RESOURCE) | THIS INCIDENT OCCURRED WHILE THE PIPELINE SEGMENT WAS BEING INSPECTED WITH ALINALOG DEVICE. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
585 | 1990-04-25 | TX | other | GAINES | NORTHERN NATURAL GAS CO (ENRON) | LOSS OF AC POWER DUE TO LIGHTNING ACTIVATED STATION EMERGENCY SHUTDOWN SYSTEM. SUCTION SIDE VALVE FAILED TO OPERATE WHICH ALLOWED GAS TO VENT THROUGH STATION BLOWDOWNS UNTIL MANUALLY CLOSED (75 MIN.). | 210000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
586 | 1990-04-22 | TX | maintenance | BOWIE | NATURAL GAS PIPELINE CO OF AMERICA | THE COVER BOLTS ON A 2" CHECK VALVE IN SOUR GAS SERVICE FAILED. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
587 | 1990-04-13 | AR | other | LONOKE | MISSISSIPPI RIVER TRANSMISSION CORP |  | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
588 | 1990-05-09 | OR | technical failure | KLAMATH | NORTHWEST PIPELINE CORP | THERE WERE SEVERAL PINHOLE LEAKS IN THE LONG SEAM. THE LEAK WAS DISCOVERED DURING THE ANNUAL LEAK SURVEY. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
589 | 1990-05-06 | AR | technical failure | LAWRENCE | MISSISSIPPI RIVER TRANSMISSION CORP | THE INITIAL REPORT FROM AN INDEPENDENT LABORATORY SUGGESTS THAT A GOUGE IN THE PIPE WAS THE ORIGIN OF FAILURE. | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
590 | 1990-06-01 | TX | maintenance |  | ANR PIPELINE CO (AMERICAN NATURAL RESOURCE) |  | 170000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
591 | 1990-06-06 | LA | other | CADDO | TEXAS GAS TRANSMISSION CORP | NO REMARKS SHOWNED. | 1586450 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
592 | 1990-06-10 | TX | other | LAMAR | NATURAL GAS PIPELINE CO OF AMERICA | THE RUPTURE INITIATED AT A 12" LONG GOUGE THAT WAS POSITIONED BETWEEN 3 O'CLOCK AND 6 O'CLOCK. PIPE WAS GOUGED A PERIOD OF TIME BEFORE THE INCIDENT OCCURRED. | 600000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
593 | 1990-06-25 | MN | other | KANDIYOHI | NORTHERN NATURAL GAS CO (ENRON) | MINNESOTA BRANCHLINE MNB 75601 WAS SEVERED BY A SCRAPER DOING EXCAVATION WORK FOR RECONSTRUCTION OF A COUNTY ROAD. | 61000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
594 | 1990-06-25 | LA | other |  | SEA ROBIN PIPELINE CO | A CREW OF THREE (3) MEN WERE ATTEMPTING TO REMOVE A SPHERE FROM A PIG RECEIVER. AFTER BELIEVING THE PIGTRAP WAS "BLOWNDOWN" THEY ATTEMPTED TO OPEN THE PITTRAP DOOR. TRAPPED PRESSURE EJECTED BOTH THE PIG AND CLOSURE. THREE (3) MEN WERE INJURED, WITH TWO | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
595 | 1990-07-03 | OH | other | MUSKINGUM | TEXAS EASTERN GAS PIPELINE CO | MOVEMENT OF A LANDSLIDE CAUSED TEXAS EASTERN TRANSMISSION'S 24" PIPELINE TO FAIL. THIS PIPELINE IS LOCATED IN A MAJOR LANDSLIDE AREA THAT ENCOMPASSES MOST OF THE PIPELINE RIGHT-OF-WAY. THIS LANDSLIDE IS TYPICAL OF MANY IN THIS REGION OF OHIO, BEING CHAR | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
596 | 1990-06-27 | LA | maintenance |  | NATURAL GAS PIPELINE CO OF AMERICA | THE ATTACHED REPORT CONCERNS AND INCIDENT THAT OCCURRED OFFSHORE OF LOUISIANA. ON JUNE 30,1990, A LEAK WAS CONFIRMED ON THE WC-551 LATERAL IN WEST CAMERON BLOCK 552. THE LEAK WAS REPAIRED THE SAME DAY BY INSTALLING A CLAMP ON THE PIPE. NATURAL GAS PIPE | 90000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
597 | 1990-07-03 | TX | technical failure | SCHLEICHER | HANOVER ENERGY INC | SYSTEM PURCHASED FROM BP AMERICAN OCTOBER 1, 1988. OUR KNOWLEDGE IS LIMITEDDUE TO THE INFORMATION RECEIVED BY BP AMERICA. DURING CONSTRUCTION A JOINT OF .125 WALL X-42 WAS USED INADVERTENTLY. | 350000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
598 | 1990-07-18 | NY | other | WYOMING | CNG TRANSMISSION CORP | LANDSLIDE PARALLEL TO PIPELINE CAUSED PIPE TO BUCKLE AND EVENTUALLY CRACK LONGITUDINALLY ALONG THE BUCKLE. FAILURE OCURRED UNDER TONAWANDA CREEK. | 217000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
599 | 1990-07-10 | LA | maintenance |  | TENNESSEE GAS PIPELINE CO |  | 221000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
600 | 1990-08-17 | IL | other | LA SALLE | ILLINOIS POWER CO | ON AUGUST 17, 1990, AT APPROXIMATELY 7:50AM, A FIRE WAS REPORTED AT THE LASALLE #2 DELIVERY STATION WHICH RECEIVES NATURAL GAS FROM NGPL. THE FIRE WAS REPORTED BY A NEIHBOR WHO NOTED A LIGHTENING STRIKE IN THE IMMEDIATE VICINITY & NOTED TWO DISTINCT FIRES | 70000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
601 | 1990-08-12 | IL | other | CHAMPAIGN | PEOPLES GAS LIGHT & COKE CO | A FRACTURE OCCURED IN A COMPRESSOR ROD AT THE POINT WHERE THE ROD ATTACHES TO THE COMPRESSOR PISTON. THIS FAILURE IN TURN CAUSED THE CYLINDER HEAD TO FAILAND THE COMPRESSOR FLANGE, HEAD AND PISTON WERE BLOWN OFF AND OUT OF THE COMPRESSOR. AUTOMATIC EQUIP | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
602 | 1990-07-30 | WV | technical failure | RANDOLPH | COLUMBIA GAS TRANSMISSION CORP | A PRELIMINARY INVESTIGATION INDICATED THAT THE RUPTURE INITIATED IN A 26 X 24 INCH OD, SADDLE REINFORCED BRANCH CONNECTION INSTALLED IN '51. THE PIPE MATERIALS USED HAVE BEEN DESCRIBED IN THE REPORT FORM. AT THE TIME OF THE RUPTURE THERE WAS CONTRUCTIONIN | 150000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
603 | 1990-07-24 | TX | other | BRAZORIA | HOUSTON PIPELINE CO | PIPE ON COMPRESSOR DISCHARGE HEADER FAILED, RESULTING IN A FIRE. | 300000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
604 | 1990-07-19 | OK | other | CADDO | FORT COBB FUEL IRRIGATION AUTH | THE INCIDENT WAS A FIRE SUPPORTED BY ESCAPING NATURAL GAS DURING ROUTINE LINE MAINTENANCE. THE SPECIFIC TASK BEING PERFORMED WAS THE REPLACEMENT OF AN APPROXIMATE 390 FOOT SEGMENT OF 2" PVC DISTRIBUTION LINE TO PERMIT LOWERING OF THIS SEGMENT. THE SEGMENT | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
605 | 1990-08-09 | NM | other | MCKINLEY | EL PASO NATURAL GAS CO | A CONTRACTOR, WHILE REMOVING A CONCRETE VAULT FROM AROUND A DRIP THAT WAS BEING REMOVED FROM AROUND A DRIP THAT WAS BEING REMOVED FROM OUR 30-INCH PERMIAN - SAN JUAN LINE NO. 1300, ACCIDENTLY KNOCKED OFF A 1-INCH NIPPLE DIRECTLY CONNECTED TO THE LINE, CAU | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
606 | 1990-08-28 | NM | other | LEA COUNTY | LLANO INC | LLANO EMPLOYEES HAD INSTALLEDNEW PRESURE PACKING ON A FIRST STAGE COMPRESSORCYLINDER. THE DISTANCE PIECE INSPECTION DOOR HAD BEEN REPLACED AND RE-PRESSURING OF THE COMPRESSOR CYLINDER INITIATED. GAS LEAKING BY THE NEW PRESSURE PACKING EXCEEDED THE CAPAC | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
607 | 1990-08-03 | OK | technical failure | BECKHAM | CAPROCK PIPELINE CO | A VENT ON A POSITIONER VALVE WAS CLOGGED. NATURAL GAS SEEPAGE THROUGH THE CONDUIT, ENTERED THE INSTRUMENTATION BUILDING. THE GAS IGNITED AND A FLASH FIRE ENSUED. | 8500 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
608 | 1990-08-31 | LA | technical failure |  | SOUTHERN NATURAL GAS CO | THE BOLTED BONNET COVER UTLITZES A RUBBER O-RING TYPE GASKET SEAL. APPARENTLY THE RUBBER GASKET HAS CRACKED OR DETERIORATED IN SEVERAL PLACES.PART 3 - DIVERS WERE INSPECTING A 12" RUTURE TAP AND DISCOVERED SLOW RELEASE OFBUBBLES FROM EXISTING CRACKS IN C | 200000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
609 | 1990-08-30 | PA | other | ALLEGHENY | PEOPLES NATURAL GAS CO | CONTRACTOR HIT TP-7575 WITH BULLDOZER. LINE HAD BEEN LOCATED AND MARKED BY THE PEOPLES NATURAL GAS COMPANY. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
610 | 1990-08-04 | CA | other | LOS ANGELES | SOUTHERN CALIFORNIA GAS CO | USA TICKET INDICATED WORK TO BE DONE ON 8/3/90. SURVEILLANCE PERSON WENT TOJOB SITE, MARKED PIPELINE IN INTERSECTION, NO ONE WAS AT JOB SITE.ADDITIONAL - ON AUGUST 4, 1990, AT APPROXIMATELY 1:55PM THE LOS ANGELES FIRE DEPT. NOTIFIED OUR COMPANY OF BLOWIN | 68000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
611 | 1990-09-08 | KS | technical failure | JOHNSON | WILLIAMS NATURAL GAS CO | VALVE SEPARATION - MAIN BODY SEPARATED FROM FLANGE ALLOWING GAS ESCAPE. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
612 | 1989-12-16 | LA | other | ACADIA | TRANSCO GAS PIPELINE CORP | ON DECEMBER 16, 1989 AT 1:30 A.M. TRANSCO FIELD PERSONNEL NOTICED A LOSS OF PRESSURE IN LINE A OF THE CENTRAL LOUISIANA LATERAL WHICH HAD BEEN OPERATING AT A PRESSURE OF 840 PSI. AS TRANSCO BEGAN SHUTTING IN THE AFFECTED PIPELINE SECTION, AT 1:40 A.M., HO | 140000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
613 | 1990-08-23 | CA | other | SAN BERNARDINO | SOUTHERN CALIFORNIA GAS CO |  | 21200 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
614 | 1990-09-20 | KS | other | JOHNSON | WILLIAMS NATURAL GAS CO | ACCIDENTLY STRUCK 1" TAP WHILE PERFORMING MAINTENANCE ACTIVITY | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
615 | 1990-10-03 | TX | other | HARDIN | HOUSTON PIPELINE CO | LIQUIDS WERE BEING REMOVED FROM A PIPELINE (16", ACCT. 1136) BY PIGGING. REMOVED LIQUIDS AND VENTING GAS WERE BEING DISCHARGED INTO A 500 BBL. TANK OPENTO THE ATMOSPHERE. IT IS SURMISED THAT HEAVY HYDROCARBON VAPORS VENTING FROM THE TANK, COLLECTED NEAR | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
616 | 1990-09-21 | OK | technical failure | CARTER | ONG TRANSMISSION CO |  | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
617 | 1990-09-23 | TX | maintenance | SOUTH ADDITION | ANR PIPELINE CO (AMERICAN NATURAL RESOURCE) |  | 202500 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
618 | 1990-09-19 | PA | other | TIOGA | CNG TRANSMISSION CORP | A 1" REGULATOR ON THE PILOT LINE TO THE 6" STATION BLOWOFFS FAILED CAUSING THE PILOT LINE TO DRAIN AND OPENING THREE BLOWOFF VALVES AT SABINSVILLE COMPRESSOR STATION | 143000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
619 | 1990-09-20 | NM | other | GRANT | EL PASO NATURAL GAS CO | EPNG'S 6 5/8" LINE NO. 2010 WAS HIT BY A GRADER OWNED BY PHELPS DODGE, CAUSING AN 18 INCH TEAR.NEW MEXICO ONE-CALL SYSTEM IS PRESENTLY BEING IMPLEMENTED | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
620 | 1990-10-02 | NM | other | SAN JUAN | EL PASO NATURAL GAS CO | A MAINTAINER BEING OPERATED BY BROKEN HILLS PROPRIETARY COMPANY WAS GRADING ADITCH PARALLELING OUR 24-INCH PIPELINE WHEN IT HIT AND RUPTURED THE PIPELINE. THERE WAS NO FIRE OR EXPLOSION BUT THE FORCE | 209210 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
621 | 1990-09-30 | NM | other | BLANCO | EL PASO NATURAL GAS CO | A FIRE INVOLVING TWO MERIDIAN OIL COMPANY TRUCKS WHICH WERE UNLOADING LIQUIDDRIP, OCCURRED AT THE BLANCO STORAGE TANKS LOCATED BETWEEN THE BLANCO AND CONOCO PLANTS. THE FIRE STARTED WHEN VAPORS FROM THE DOME HATCH OF THE TRUCK MIGRATED TO THE AIR INTAKE | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
622 | 1990-09-25 | TX | other | MOORE | NATURAL GAS PIPELINE CO OF AMERICA | WHILE PERFORMING MAINTENANCE INSIDE AN ABSORBER TOWER, 4 EMPLOYEES WERE BURNED BY A FLASH FIRE. TWO EMPLOYEES WERE HOSPITALIZED, AND 2 WERE TREATED AND RELEASED. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
623 | 1990-10-02 | CO | technical failure | ARAPAHOE | COLORADO INTERSTATE GAS CO | FACTORS CONTRIBUTING TO THIS INCIDENT INCLUDE THE EXTREMELY LOW GAS FLOWS ANDA LOSS OF SENSITIVITY IN THE CONTROL SYSTEM, RESULTING IN INACCURATE READINGSBEING SUPPLIED TO PERSONNEL CONTROLLING THE GAS/AIR BLENDING SYSTEM. THE VOLUME DEMAND THROUGH THE G | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
624 | 1990-09-13 | TX | other | BURLESON | CLAJON GAS CO | D THE BELLHOLE. WHEN WELDERS STARTED WELDING, THE VAPORS IGNITED IN FLASH FI | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
625 | 1990-10-16 | LA | maintenance | UNKNOWN | NATURAL GAS PIPELINE CO OF AMERICA | AT 6:15 PM ON OCTOBER 16, 1990, BUBBLING WATER WAS OBSERVED ABOUT 0.5 MILES FORM THE ARCO 212C PLATFORM. THE LEAK WAS CONFIRMED AT 9:17 AM ON OCTOBER 17AND REPAIRED WITH A LEAK CLAMP ON OCTOBER 20. NATURAL GAS PIPELINE COMPANY OF AMERICA OPERATES AND SH | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
626 | 1990-10-22 | CA | other | KERN | SOUTHERN CALIFORNIA GAS CO | THE PIPELINE WAS HIT BY A RIPPER THAT WAS SUBSOILING TO REPLANT A FIELD. | 55000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
627 | 1990-10-17 | LA | other | BOSSIER | TEXAS EASTERN GAS PIPELINE CO | TRACTOR WAS DISKING THE FIELD WHEN PRODUCERS PIPING WAS HIT BY A DISK. THE 2" WELDOLET WAS TORN FROM THE PIPELINE AND APPROXIMATELY 30 FEET OF PIPE SPLIT OPEN. | 90000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
628 | 1990-10-16 | LA | other | BIENVILLE | UNITED GAS PIPELINE CO | AN EXPLOSIVE ATMOSPHERE DEVELOPED OVER AN OPEN OIL AND WATER PIT AT BISHTINEAU COMPRESSOR SATION. THE EXPLOSIVE ATMOSPHERE IGNITED DUE TO CONSTRUCTION AT THE PIT. THE RESULTING "FLASH" CAUSED 2 MEN TO SUSTAIN BURN INJURIES REQUIRING HOSPITALIZATION. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
629 | 1990-11-07 | CA | other | RIVERSIDE | SOUTHERN CALIFORNIA GAS CO | THE SOCALGAS OPERATES AND MAINTAINS AN UNDERGROUND 30-INCH NATURAL GASTRANSMISSION PIPELINE (LINE 2000) PARALLEL TO THE AT&SF TRACK IN THE GENERALAREA OF THE COLLISION SITE. THE DISTANCE FROM OUR PIPELINE TO THE RAILROADTRACKS VARIES FROM 60 TO 70 FEET, | 210000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
630 | 1990-11-01 | LA | other | ST MARY | TENNESSEE GAS PIPELINE CO | SUSPECT MARIN VESSEL CAUSED DAMAGE AND SUBSEQUENT RUPTURE. | 500000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
631 | 1990-11-10 | AZ | maintenance | LA PAZ | EL PASO NATURAL GAS CO | GENERAL PIPE CORROSION IN THE IMMEDIATE AREA CAUSED THE PIPELINE TO RUPTURE AND THE FRICTION OF THE PIPELINE RIPPING IGNITED THE GAS. | 300000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
632 | 1990-11-24 | TX | maintenance | REFUGIO | FLORIDA GAS TRANSMISSION CO |  | 150000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
633 | 1990-11-27 | KY | other | JESSAMINE | DELTA NATURAL GAS CO INC | AT APPROXIMATELY 8:55 A.M. NOVEMBER 27, 1990, DELTA'S NICHOLASVILLE OFFICE RECEIVED A TELEPHONE CALL REPORTING A LINE BREAK ON THE NICHOLASVILLE BY-PASS NEAR KIMBERLY HEIGHTS SUBDIVISION. BILL GARDNER, DELTA'S NICHOLASVILLE/WILMORE DISTRIBUTION SUPERVISO | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
634 | 1990-11-20 | LA | technical failure |  | SOUTHERN NATURAL GAS CO | THE BOLTED BONNETT COVER UTILIZES A RUBBER O-RING GASKET SEAL. APPARENTLY THE RUBBER GASKET HAS CRACKED OR DETERIORATED IN SEVERAL PLACES.PART 3 - DIVERS WERE INSPECTING AN UNUSED UNDERWATER 12" TAP AND DISCOVERED A SLOW RELEASE OF BUBBLES FROM EXISTING | 160000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
635 | 1990-11-26 | TX | other | WEBB | VALERO TRANSMISSION CO | REASON FOR FAILURE IS UNKNOWN AT THIS TIME. METALLUGICAL INVESTIGATION IS BEING CONDUCTED. | 105630 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
636 | 1990-11-24 | NY | other | RICHMOND | TEXAS EASTERN GAS PIPELINE CO | BARGE OR TUG BOAT APPARENTLY HIT THE PIPELINE UNDER THE AUTHUR KILL RIVER, CAUSING A PUNCTURE THAT ALLOWED GAS TO BLOW TO ATMOSPHERE. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
637 | 1990-12-07 | NM | technical failure | TORRANCE | EL PASO NATURAL GAS CO | BELEN COMPRESSOR STATION EXPERIENCED A LOW SUCTION PRESSURE ALARM AT 9:10 PMON DECEMBER6, AND AN ESD AT 9:15 PM. LINCLON COMPRESSOR STATION REPORTED LOWREADINGS AND AT 9:30 PM PERSONNEL WERE DISPATCHED TO PATROL THE PIPELINE TO DETERMINE IF THERE HAD BEEN | 370299 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
638 | 1990-12-04 | WV | maintenance | BOONE | CNG TRANSMISSION CORP | RUPTURE OCCURRED IN STREAM CROSSING. ESCAPING GAS IGNITED RESULTING IIN DAMAGE TO DWELLINGS NEAR PIPELINE. | 150000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
639 | 1990-12-16 | MS | other | PANOLA | TENNESSEE GAS PIPELINE CO | COMPRESSOR OPERATOR SUFFERED BURNS WHEN GAS LEAKING FROM COMPRESSOR PACKINGIGNITED FROM UNKNOWN SOURCE. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
640 | 1990-12-10 | LA | technical failure | IBERVILLE | SOUTHERN NATURAL GAS CO | EMPLOYEES WERE REMOVING MOTOR AND GEARBOX ASSEMBLY FROM COMPRESSOR STATION #3 SCRUBBER. AS THE GEARBOX ASSEMBLY WAS REMOVED, THE SHAFT WAS BLOWN OUT OF THE SCRUBBER INJURING ONE EMPLOYEE. THE APPARENT CAUSE WAS AN INTERNAL BEARING FAILURE WHICH RESULTED | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
641 | 1990-12-06 | LA | other | UNKNOWN | TRUNKLINE GAS CO | UNION RIG KEYS #303 DRUG LEGS ACROSS PIPELINE WHILE PREPARING TO SET UP ON UNOCAL SS 253 PLATFORM. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
642 | 1990-12-10 | MS | technical failure | COVINGTON | TRANSCO GAS PIPELINE CORP | MECHANICAL WEAR IN BRONZE COMPRESSOR ROD PACKING CAUSED GAS TO ESCAPE AND PASS BY IGNITION TRANSFORMERS. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
643 | 1990-11-17 | NY | other | NEW YORK | CONSOLIDATED EDISON CO OF NEW YORK | PRESSURE REGULATORS AT A TRANSMISSION METER STATION LOST CONTROL, ALLOWING DELIVERY PRESSURE TO INCREASE. FURTHER INVESTIGATION DISCLOSED THAT OVERRIDE SYSTEM OPERATED PROPERLY AND MAOP WAS NOT EXCEEDED. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
644 | 1990-12-29 | NE | other | FURNAS | K N ENERGY INC(KANSAS NEBRASKA GAS CO) | OVERHEAD CREEK CROSSING WAS HIT BY VEHICLE WHICH RAN OFF A GRAVEL ROAD. | 6000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
645 | 1990-12-18 | NM | technical failure | SAN JUAN | EL PASO NATURAL GAS CO | A 1/2" DIAMETER GLYCOL HOSE (FUEL LINE) TO THE DEHYDRATOR ON THE STANOLIND GAS COM. #1A GAS WELL BROKE AND IGNITED, SETTING FIRE TO THE DEHYDRATOR. THEGAS WELL WAS SHUT-IN AND THE FIRE WAS DYING OUT WHEN THE NAVAJO DAM VOLUNTEER FIRE DEPARTMENT ARRIVED | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
646 | 1991-01-04 | AR | other | CHICOT | TEXAS GAS TRANSMISSION CORP | SINCE 1950, TEXAS GAS HAS OPERATED TWO 20" UNDERGROUND, NATURAL GAS PIPELINES CROSSING THE MISSISSIPPI RIVER AT THE LOCATION DESCRIBED ON THE ATTACHED FORM RSPA F7100.2. THESE LINES HAVE THE TEXAS GAS DESIGNATED NUMBERS OF 20" LINES 5 AND 6. ON JANUARY | 235000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
647 | 1991-01-18 | LA | other | WEST FELICIANA | TRANSCO GAS PIPELINE CORP | INCIDENT HAS BEEN VERIFIED TO BE THE 18" UNDERWATER PIPELINE CROSSING THE MISSISSIPPI RIVER. THE AFFECTED RIVER CROSSING WAS ISOLATED BY AUTOMATIC VALVEOPERATORS AT THE TIME OF THE INCIDENT. THE RIVER CROSSING IS ISOLATED & AUTOMATIC VALVE OPERATORS DE | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
648 | 1991-01-06 | LA | other |  | ANR PIPELINE CO | 2" X 6" CONNECTION LOCATED IN 120' OF WATER IN GULF OF MEXICO. | 125000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
649 | 1991-01-26 | LA | other | ASSUMPTION | ACADIAN GAS PIPELINE SYSTEM |  | 105000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
650 | 1991-01-17 | TN | other | HAWKINS | EAST TENNESSEE NATURAL GAS CO | PIPELINE STRUCK BY OUTSIDE PARTY EXCAVATING SOIL FROM PIPELINE RIGHT-OF-WAY. NO PRIOR NOTIFICATION OF EXCAVATION WAS GIVEN BY OUTSIDE PARTY. PIPELINE IS MARKED WITH PERMANENT PIPELINE MARKERS IN AREA OF EXCAVATION. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
651 | 1991-01-18 | LA | other | TERREBONNE | UNITED GAS PIPELINE CO | TUG KAREN ELIZABETH, WITH FOUR EMPTY ARGES IN TOW, SRUCK AND RUPTURED 12" LINE CROSSING INTRACOASTAL CANAL IN TERREBONNE PARISH. | 500000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
652 | 1991-02-25 | OK | maintenance | CANADIAN | CONOCO INC |  | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
653 | 1991-02-10 | LA | maintenance |  | NATURAL GAS PIPELINE CO OF AMERICA |  | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
654 | 1991-02-05 | IA | technical failure | MARION | NATURAL GAS PIPELINE CO OF AMERICA |  | 53800 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
655 | 1991-01-22 | AR | technical failure | HOT SPRING | NATURAL GAS PIPELINE CO OF AMERICA |  | 71700 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
656 | 1991-02-15 | TX | other | BROOKS | VALERO INTERSTATE TRANSMISSION CO |  | 143000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
657 | 1991-02-17 | CA | maintenance | LOS ANGELES | SOUTHERN CALIFORNIA GAS CO | ON FEBRUARY 17, 1991, AT APPROXIMTELY 1:10 AM., WE DISCOVERED LEAK WHICH WASLATER DETERMINED TO BE CAUSED BY INTERNAL CORROSION. THE PIPELINE WAS SHUT-IN AT 1:25 AM. REPAIRS WERE MADE BY INSTALLING A 4" LEAK CLAMP. THE PIPELINE HAS NOT BEEN RETURNED TO | 60000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
658 | 1991-02-15 | PA | technical failure | LYCOMING | TRANSCO GAS PIPELINE CORP | AT APPROXIMATELY 8:50 PM. EST ON FEBRUARY 15, 1991, TRANSCONTINENTAL GAS PIPELINE CORPORATIONS'S 12,600 HP SOLAR MARS TRUBINE EXPERIENCED A SLIGHT EXPLOSION, CAUGHT FIRE, AND BURNED. THE APPARENT CAUSE OF THE INCIDENT IS UNKNOWNAT THIS TIME. A TASK GROU | 6000000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
659 | 1991-03-31 | TX | maintenance | SMITH | LONE STAR GAS CO | LINE BLEW OUT CREEK BOTTOM. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
660 | 1991-03-23 | IA | other | WRIGHT | NORTHERN NATURAL GAS CO (ENRON) | FROST HEAVE AND/OR FLOTATION CAUSED PIPE TO RAISE UP, RESULTING IN A LEAK ATA DRESSER COUPLED JOINT. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
661 | 1991-04-01 | OR | other | UNION | NORTHWEST PIPELINE CORP | A CABLE PLOWING TRACTOR, LAYING TELEPHONE CABLE STRUCK THE PIPELINE; 3" X 4"PUNCTURE. | 87600 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
662 | 1991-03-12 | MO | other | BUCHANAN | WILLIAMS NATURAL GAS CO | FARMER BURNING BRUSH AND GRASS NEAR VALVE CAUSED PACKING TO FAIL. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
663 | 1991-04-13 | KY | other | MARTIN | COLUMBIA GAS TRANSMISSION CORP | PASSENGER VEHICLE BROKE THROUGH BARRICADE AND HIT DRIP LINE RESULTING IN BELOW GROUND BREAK AT SHUT-OFF VALVE. 1/2" DRIP LINE BROKEN OFF BY PASSENGER VEHICLE ACCIDENT RESULTING IN IGNITION AND DESTRUCTION OF TWO MOTOR VEHICLES AND HOSPITALIZATION OF DRIV | 18400 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
664 | 1991-04-16 | OK | other | GRANT | WILLIAMS NATURAL GAS CO | A NATURAL GAS LEAK OCCURRED INSIDE A COMPRESSOR STATION BUILDING. THE GAS WAS IGNITED APPARENTLY BY AN ELECTRICAL SOURCE IN AN ADJACENT PART OF THE STRUCTURE. A COMPRESSOR VALVE CAP IS BELIEVED TO BE THE ORIGIN OF THE LEAK. | 400000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
665 | 1991-05-01 | TX | maintenance | UNKNOWN | BLUE DOLPHIN PIPELINE CO | WAS IN THE PROCESS OF PRESSURE TESTING THE PIPELINE WITH NATURAL GAS TO ESTABLISH AN NEW MAOP. LEAK OCCURRED AT APPROXIMATELY 500 PSI. PRESSURE WAS BLED TO 300 PSI AT WHICH TIME DIVERS INSTALLED A 1500 PSI WP BOLTED CLAMP. THE PIPELINE AND CLAMP WERE T | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
666 | 1991-05-14 | NE | other | SCOTTS BLUFF | K N ENERGY INC(KANSAS NEBRASKA GAS CO) | THIS REPORT COVERS A LINE HIT THAT OCCURRED ON KN ENERGY, INC.'S (K N'S) 16-INCH STEEL, BURIED TRANSMISSION PIPELINE IN SCOTTS BLUFF COUNTY, NEBRASKA ON MAY 14, 1991. IGNITION DID NOT OCCUR AND THERE WERE NO INJURIES FATALITIES AS A RESULT OF THE LINE BEI | 25000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
667 | 1991-05-07 | MI | other | OAKLAND | CONSUMERS POWER CO | EXPLOSION RESULTED WHEN GAS WAS VENTED FROM PIPING LOCATED AT THE CITY GATESTATION. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
668 | 1991-05-14 | AR | maintenance | MILLER | NATURAL GAS PIPELINE CO OF AMERICA | INTERNAL CORROSION SUSPECTED | 97000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
669 | 1991-06-09 | TX | maintenance | CRANE | VALERO TRANSMISSION CO | THE PIPELINE RUPTURED AT APPROXIMATELY 5 AM. ON JUNE 9, 1991. PROBABLE CAUSE IS EXTERNAL CORROSION PENDING VERIFICATION BY METALLURGICAL ANALYSIS. NO FIRE AND NO INJURIES. PIPELINE REPAIRED BY REPLACING WITH NEW PIPE. LINE BACKIN SERVICE ON JUNE 12,199 | 325000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
670 | 1991-06-01 | AR | other | PULASKI | TEXAS EASTERN GAS PIPELINE CO | BULLDOZER MOVING FILL DIRT ON LEVEE, GOUGED A 5.5" X 1.5" X 5.75" PUNCTUREOF THE PIPELINE. NO FIRE OR FATALITIES OCCURRED. | 90000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
671 | 1991-06-11 | PA | other | WASHINGTON | PEOPLES NATURAL GAS CO |  | 51000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
672 | 1991-06-19 | KS | other | GRAHAM | K N ENERGY INC(KANSAS NEBRASKA GAS CO) |  | 3300 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
673 | 1991-07-17 | PA | maintenance | CLARION | CNG TRANSMISSION CORP |  | 60250 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
674 | 1991-04-10 | KS | other | SEDGWICK | KANSAS NATURAL INC | ELY 4:45 AM., THE LIQUIDS IN FRONT OF THE TPIG BEGAN TO ARRIVE AT THE FACILITY. THE LIQUIDS WERE SEPARATED FROM THE GAS IN A SEPARATOR AND THEN LEVEL CONTROLLED INTO TWO FRAC TANKS. DUE TO THE VOLATILITY OF THE LIQUIDS, HYDROCARBON VAPOR WAS GENERATED O | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
675 | 1991-08-06 | LA | maintenance | RED RIVER | UNITED GAS PIPELINE CO | INVESTIGATION INDICATES INNER DIAMETER FAILURE OF A LONGITUDINAL WELD SEAM ATTRIBUTED TO INTERNAL CORROSION. | 344174 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
676 | 1991-08-03 | LA | maintenance |  | ANR PIPELINE CO | SUSPECTED INTERNAL CORROSION; NOT VERIFIED SINCE GRIPPER CLAMP WAS INSTALLED. | 101800 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
677 | 1991-08-19 | OK | other | TULSA | TRANSOK INC | A BULLDOZER OPERATED BY BENNY CRAIG, SHERWWOD CONT\STRUCTION 4716 N. 193 E. AVE. TULSA, OKALHOMA 918-266-6861, WAS BUILDING A TEMPORARY BYPASS ROAD ALONGMINGO ROAD FOR THE OKLAHOMA DEPARTMENT OF TRANSPORTATION. THE BULLDOZER HITTHE PIPELINE RESULTING IN | 16700 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
678 | 1991-08-02 | IN | other | PORTER | NORTHERN INDIANA PUBLIC SERVICE CO | CONTRACTOR WAS CLEARING THE AREA OF TREES AND BRUSH, USING A BULLDOZER, WHENHE PUNCTURED THE LINE THAT WAS CLEARLY MARKED. THE LEAKING GAS SOMEHOW IGNITED, CAUSING BURNES TO UPPER HALF OF THE BODY OF THE OPERATOR AND DESTROYING THE EQUIPMENT. | 400000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
679 | 1991-07-23 | MS | other | LOWNDES | TENNESSEE GAS PIPELINE CO | GAS ESCAPING FROM TWO IMPROPERLY SEATED VALVE CAP GASKETS IGNITED CAUSING BURNES TO FOUR WORKMEN IN THE VICINITY. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
680 | 1991-07-23 | KY | other |  | TENNESSEE GAS PIPELINE CO | AN EQUIPMENT OPERATOR DIGGING NEAR OUR LINE, GOUGED THE PIPELINE, CAUSING A LEAK AND SUBSEQUENT RUPTURE. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
681 | 1991-08-03 | PA | other | MONTGOMERY | TEXAS EASTERN GAS PIPELINE CO | WIND FROM STORM BLEW PART OF ROOF FROM A NEARBY WAREHOUSE INTO THE CONTROL LINE FOR A PRESSURE REGULATOR AT MEASURING STATION 517. THE PRESSURE REGULATOROPENED FULLY AND THE RELIEF VALVE WAS ACTIVATED AT 220 PSI AS DESIGNED. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
682 | 1991-05-10 | MT | other | FLATHEAD | MONTANA POWER CO | A LARGE LOG LOADER WAS PICKING UP LOGS STACKED IN THE AREA TRAVERSEE BY THE PIPELINE. IN AN EFFORT TO GET UNDER THE BOTTOM OF THE STACK, A LARGE BOTTOM TINE ON THE LOADER WAS DRIVEN BELOW THE SURFACE OF THE GROUND COVERING THE PIPELINE, PENATRATING THE P | 145757 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
683 | 1991-08-29 | OH | maintenance | RICHLAND | COLUMBIA GAS TRANSMISSION CORP | RUPTURE OF UNDERSLUNG PIPELINE DRIP LIFTED APPROXIMATELY 165' OF 20" PIPELINE OUT OF GROUND. INTERNAL CORROSION RESULTED IN A BRITTLE FRACTURE TYPE FAILURE. | 280000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
684 | 1991-09-21 | NC | other | WILSON | NORTH CAROLINA NATURAL GAS CORP | CONTRACTOR LAYING PARALLEL PIPELINE HIT EXISTING LINE TRACK HOE BUCKET. | 80000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
685 | 1991-09-24 | CA | other | LOS ANGELES | SOUTHERN CALIFORNIA GAS CO | FIRE. ON SEPTEMBER 24, 1991, AT APPROXIMATELY 6:30 PM, A FIRE OF UNKKNOWNORIGIN DESTROYED THE CONTENTS OF THE INSTRUMENTATION BUILDING AT THISFACILITY. GAS WAS CONTROLLED BY CLOSING THE VALVES ON PIPING LEADING INTO THEBUILDING. INVESTIGATION INTO THE C | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
686 | 1991-09-17 | LA | other | GULF OF MEXICO | CHEVRON USA INC | THE EXACT TIME OF INCIDENT IS UNKNOWN BECAUSE THE PIPELINE WAS NOT PRESSUREDUP DUE TO CONSTRUCTION ACTIVITIES AT MP 299 "B". | 300000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
687 | 1991-09-28 | LA | other | ASCENSION | MONTEREY PIPELINE CO | LINE WAS HIT BY A BACKHOE DIGGING IN THE AREA. | 75000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
688 | 1991-04-05 | TX | other | BASTROP | VALERO TRANSMISSION CO | VALVE (6") CASTING CRACKED FOR UNKNOWN REASON. THIS 6" VALVE WAS REMOVED AND THE 6" LINE WAS TIED INTO THE 12" LINE. | 7500 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
689 | 1991-03-27 | TX | other | NAVARRO | LONE STAR GAS CO | LINE WAS CUT INTO BY LAND OWNER USING BULL DOZER | 20000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
690 | 1991-02-26 | TX | technical failure | FORT BEND | UNITED TEXAS TRANSMISSION CO | UNITED TEXAS PERSONNEL FOUND DURING LEAK ANNUAL VALVE INSPECTION AND DISCOVERED A CRACK IN THE VALVE FLANGE. FOUND CRACK ON BOTTOM OF 8" FLANGE. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
691 | 1991-02-09 | TX | other | FANNIN | LONE STAR GAS CO | LINE WAS STRUCK AND PUNCTURED BY A DOZER BEING USED TO FILL IN AN OLD POND. | 5000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
692 | 1991-10-08 | CA | other | SANTA CLARA | PACIFIC GAS & ELECTRIC CO | CONTRACTOR STRUCK TRANSMISSION LINE WITH BULLDOZER CASUING SEVERAL DENTS ANDGOUGES; PRESSURE REDUED IN LINE TO SAFE PRESSURE. SECTION REPLACED | 60000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
693 | 1991-09-22 | TX | other |  | VALERO TRANSMISSION CO | THE PILELINE RUPTURED SEPTEMBER 22, 1991 FROM UNDETERMINED CAUSES AND WAS TAKEN OUT OF SERVICE IMMEDIATELY. THE RUPTURED SECTION WAS REPLACED AND PIPELINE WAS PLACED IN SERVICE ON OCTOBER 17, 1991. A METALLURGICAL ANALYSIS OF THE FAILED PIPE IS BEING CO | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
694 | 1991-09-27 | LA | maintenance |  | ANR PIPELINE CO | LOCALIZED INTERNAL CORROSION, | 323000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
695 | 1991-10-18 | LA | maintenance |  | SOUTHERN NATURAL GAS CO |  | 120000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
696 | 1991-05-14 | TX | other | HENDERSON | TEXAS UTILITIES FUEL CO | TUFCO'S 16" PIPELINE WAS STRUCK AND PUNCTURED BY EQUIPMENT USED BY A THIRD PARTY CONTRACTOR INSTALLING A FIBER-OPTIC TELEPHONE CABLE. | 55000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
697 | 1991-06-07 | TX | other | HOPKINS | TEXAS UTILITIES FUEL CO | LIGHTNING STRIKE TO STEEL DUMP LINE ATTACHMENT TO 210 BBL. FIBERGLASS NATURAL GAS CONDENSATE STORAGE TANK. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
698 | 1991-06-12 | TX | maintenance | JEFFERSON | UNITED TEXAS TRANSMISSION CO | DUPONT EMPLOYEE DISCOVERED BUBBLES AROUND PIPELINE CASING VENT. UTTCO CREW EXCAVATED AND DISCOVERED LEAK COMING FROM INSIDE FILLED CASING. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
699 | 1991-07-09 | TX | other | BAYLOR | LONE STAR GAS CO | PIPE WAS HIT BY PLOW, KNOCKING A SMALL HOLE 1/2" DEEP. | 7000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
700 | 1991-08-19 | TX | other | KNOX | LONE STAR GAS CO | MR. BROWN'S EMPLOYEE WAS DEEP PLOWING WITH A MOLD BOARD BREAKING PLOW WHEN THE PLOW STRUCK THE LINE CAUSING A HOLE AND LOSS OF GAS. | 6800 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
701 | 1991-08-20 | TX | other | DONLEY | LONE STAR GAS CO | LINE WAS HIT BY PLOW. | 7600 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
702 | 1991-08-22 | TX | other | LEON | TEXAS UTILITIES FUEL CO | THIRD PARTY RIGHT-OF-WAY CLEARING CREW WERE WORKING ON TUFCO R.O.W. CONTRACTOR'S EQUIPMENT SHEARED A 2 INCH VALVE FROM A TWO INCH RISER THAT WAS CONNECTED TO THE 8" PIPELINE. | 5296 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
703 | 1991-09-16 | TX | other | PALO PINTO | LONE STAR GAS CO | DOZER WAS DIGGING A DRILLING SITE AND HIT THE LINE CAUSING HOLE IN THE PIPE. PIPELINE ROAD MARKINGS WERE 2998' FROM THE INCIDENT. | 22634 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
704 | 1991-04-05 | OK | other | GARVIN | LONE STAR GAS CO | LINE WAS HIT BY FRONT END LOADER. | 6827 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
705 | 1991-10-30 | OK | other | COMANCHE | TRANSOK INC | BULLDOZER OPERATOR RICKY NUNN CALLED IN TEAR AT 16:10 DURING CONVERSTATION HE STATED NO NOTIFICATION HAD BEEN GIVEN TO ANYU ONE-CALL SYSTEM. A BULLDOZEROPERATED BY RICKY NUNN'S DOZER SERVICE WAS BURYING TRASH FOR LAND OWNER (DALE COOBY). WHILE DIGGING T | 12500 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
706 | 1991-10-24 | LA | other | ST JOHN THE BAPTIST | UNITED GAS PIPELINE CO | CONTRACTOR INSTALLING A NEW LINE, TO REPLACE INCIDENT INVOLVED FACILITY, CAUSED EARTH MOVEMENT WHICH RESULTED IN SEPARATION AT A COUPLING. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
707 | 1991-10-25 | KS | other | OSBORNE | WILLIAMS NATURAL GAS CO | FARMER TORE HOLE IN PIPELINE WITH DEEP GROUND RIPPER. | 5000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
708 | 1991-11-01 | CA | other | KERN | ARCO OIL & GAS CO - DIV OF ATLANTIC RICHFIELD | ON 11/1/91 AT APPROXIMATELY 10:15 A.M. A 1986 TOYOTA COROLLA WAS TRAVELLING EASTBOUND ON HIGHWAY 119 APPROXIMATELY 1.3 MILES EAST OF THE INTERSEDTION OF UTUPMAN ROAD AND HIGHWAY 119. THE VEHICLE VEERED OFF THE SOUTH SIDE OF THE HUGHWAY TRAVELLING APPROXI | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
709 | 1991-11-05 | WV | maintenance | RANDOLPH | COLUMBIA GAS TRANSMISSION CORP | RELATED CORROSION ACROSS ADJACENT FULL ENCIRCLEMENT FITTING AND OTHER PIPE TOTALED APPROXIMATELY 32" IN LENGTH X MAXIMUM 9" WIDTH. REMAINING PIPE IN EXCELLENT CONDITION. | 34000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
710 | 1991-10-17 | AR | other | LAFAYETTE | LOUISIANA - NEVADA TRANSIT | ARKANSAS ACT 762 OF 1991 SPECIFIES THAT ANYONE DIGGING IN THE VICINITY OF GAS OR HAZARDOUS CHEMICALS IS REQUIRED TO GIVE NOTICE TO THE ARKANSAS ONE-CALL CENTER. NO NOTICE RECEIVED. I ATTEMPTED TO NOTIFY D.O.T. BEGINNING AT 4:45 P.M. ON THAT DATE AT 1-80 | 66400 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
711 | 1991-11-12 | KS | other | KEARNY | COLORADO INTERSTATE GAS CO | COMBUSTION GASES FROM THE CYLINDER OF A GAS COMPRESSOR ENGINE ESCAPED THRU THE STARTING AIR INTAKE VALVE INTO THE STARTING AIR SYSTEM. AN EXPLOSION OCCURRED IN THE AIR PIPING IN THE COMPRESSOR & AUXILIARY BUILDINGS WHEN ACCUMULATED OIL FROM THE AIR IN TH | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
712 | 1991-11-05 | LA | maintenance | CAMERON | TENNESSEE GAS PIPELINE CO | PIPELINE RUPTURED, CAUSING A FIRE AT CANAL CROSSING IN A RICE FIELD. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
713 | 1991-11-25 | NM | other | LEA | MAPLE GAS CORP | PIPELINE WAS ACQUIRED FROM TUCO, INC IN 1979 AND NO TEST RECORDS WERE TRANSFERRED AT THE TIME OF ACQUISITION.THIS IS THE PIPELINE WE BELIEVE SHOULD BE CLASSIFIED AS A GATHERING LINE. UNTIL A FINAL DETERMINATION IS MADE ON THE PROPER CLASSIFICATION OF THI | 300000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
714 | 1992-01-03 | PA | other | GREENE | COLUMBIA GAS TRANSMISSION CORP | SUBSTRATE COAL SEAM UNDER EFFECTED AREA WAS NOT MINED. SUBSIDENCE WAS NOT EXPECTED. ACTIVE MINING 1000 FEET AWAY. PIPELINE BROKE IN SCREW COUPLING DUETO LONGWALL MINING SUBSIDENCE. GAS MIGRATED 26 FEET TO HOUSE. EXPLOSION OCCURRED; HOUSE AND VEHICLE | 105000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
715 | 1991-12-14 | OK | other | MCCLAIN | ONEOK EXPLORATION CO | LINE LOCATED AND GLAGGED IN 5 AREAS WHERE THE LINE WAS TO BE CROSSED. A PERMANENT CROSSING MARKER WAS WITHIN 60' OF THE POINT WHERE THE LINE WAS HIT. DOZER OPERATOR DEVIATED FROM PREDETERMINED ROUTE, WHICH WAS AGREED UPON BY CONTRACTOR AND ONEOK SERVICE | 42200 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
716 | 1991-12-31 | VA | other | LOUDOUN | COLUMBIA GAS TRANSMISSION CORP | CONTRACTOR EMPLOYEE WAS HAMMERING HARD ON ROOF GAS VENT PIPE AND CAUSED A RELIEF DEVICE TO ACTIVATE. THE THRUST, FROM THE UNINTENDED RELEASE OF GAS, THREW THE EMPLOYEE OFF THE ROOF CAUSING INJURY. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
717 | 1992-01-19 | TX | other | RAINS | LONE STAR GAS CO | GAS CONTAINING HYDROGEN SULFIDE WAS ALLOWED TO ENTER TRANSMISSION SYSTEM. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
718 | 1992-01-20 | FL | technical failure | BRADFORD | FLORIDA GAS TRANSMISSION CO | THE FLANGE GASKET WHICH DEVELOPED THE LEAK WAS INSTALLED USING A FIBER GASKET AND A SEALER. THE SEALANT MATERIAL DAMAGED THE FIBER GASKET INSTALLATION RESULTING IN A LEAK. | 400000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
719 | 1991-12-07 | KS | other | SEWARD | CENTANA ENERGY CORP | ON DECEMBER 02/1991 JIM WHISENNAND, THE OWNER OF J&J OILFIELD SERVICE, PLACEDA ONE-CALL OPERATOR INFORMED MR. WHISENNAND THAT CENTANA ENERGY HAD FACILITIES IN THE AREA WHERE THE LINE RUPTURE OCCURRED ALONG WITH PANHANDLE EASTERN PIPELINE COMPANY (PEPL) AN | 230000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
720 | 1992-01-09 | LA | other | VERMILION | NERCO OIL & GAS INC | TUG WAS PULLING ANCHORS TO DERRICK BARGE WHEN ANCHOR CABLE RUBBED HOLE IN PIPELINE. DRY GAS ESCAPED. NO POLLUTION. PLATFORM SUPPLYING GAS TO PIPELINE SHUTIN ON PSL. PIPELINE BLEW DOWN IN APPROXIMATELY 45 MINUTES. LINE INSTALLED IN 1971. NOT BURIED. | 65000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
721 | 1992-01-18 | LA | other | ST CHARLES | BRIDGELINE GAS DISTRIBUTION CO | A TEXACO 4" GAS PIPELINE RUPTURED IN A PIPE RACK AREA OF TEXACO'S PARADIS PLANT AROUND 5:00 O'CLOCK P.M. ON 1/18/92. BRIDGELINE'S LULING SYSTEM SUPPLY REGULATOR STATION IN LOCATED ADJACENT TO WHERE THIS TEXACO 4" PIPELINE RUPTURED. UPON RUPTURING, THE T | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
722 | 1992-02-10 | HI | other | HONOLULU | GASCO INC | CONRACTOR EXCAVATING FOR NEARBY OIL LINE, PUNCTURED GAS LINE WITH TOOTH OF BACKHOE FRONT BUCKET. CONTRACTOR WAS TOLD GASCO WOULD COME OUT THE NEXT DAY. | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
723 | 1992-02-07 | TX | other | AUSTIN | UNITED TEXAS TRANSMISSION CO | ON FEBRUARY 4, 1992, ENTEX REPORTED A SERVICE INTERRUPTION ON UNITED TEXAS' SEALY 4" (INDEX 90-17). UNITED TEXAS PERSONNEL PATROLLED THE LINE BY AERIAL PATROL AND DETECTED A GAS LEAK IN THE BRAZOS RIVER. EXTENSIVE FLOODING OF THEBRAZOS RIVER WAS THE APP | 30700 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
724 | 1992-01-22 | TX | other | MCLENNAN | LONE STAR GAS CO | IT IS BELIEVED THAT COOL WEATHER AND EXCESSIVE RAIN CAUSED PIPE TO BREAK. | 68117 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
725 | 1992-03-15 | TN | technical failure | DICKSON | TENNESSEE GAS PIPELINE CO | PIPELINE RUPTURED AT CROSSOVER PIPING, CAUSING A FIRE NEAR ROAD CROSSING ANDRUPTURING UPSTREAM AND DOWNSTREAM BLOW OFFS AND CROSSOVERS. | 4000000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
726 | 1992-03-10 | LA | other | MADISON | UNITED GAS PIPELINE CO | PIPELINE CREW INSTALLING WELDOVER SLEEVE OVER MECHANICAL COUPLING AT THE TIME OF THE INCIDENT. CONTRIBUTING FACTORS UNKNOWN AT THIS TIME. | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
727 | 1992-04-05 | TX | other | GALVESTON | UNION CARBIDE CORP | INCIDENT AND FIRE AT ADJACENT METER DAMAGED GASKETS AND GAUGE AT ABOVE GROUND VALVE RESULTING IN PRODUCT LEAKAGE. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
728 | 1992-04-10 | TX | other | COLORADO | INTRATEX GAS CO | MINOR GAS LEAKAGE AT TWO LOCATIONS ON 8" BLOWDOWN VALVES - STEM SEAL AND FLANGE SURFACE BETWEEN BONNET AND MAIN VALVE BODY. | 140500 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
729 | 1992-03-18 | NE | maintenance | OTOE | NATURAL GAS PIPELINE CO OF AMERICA | THE LEAKING SEGMENT OF PIPE WAS REMOVED AND REPLACED WIHT PRETESTED PIPE ANDRETURNED TO SERVICE ON APRIL 15. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
730 | 1992-04-20 | TX | other | HARRISON | CROSSTEX PIPELINE CO | AN ENGINE ON ONE OF THE BOOSTER COMPRESSORS CAUGHT FIRE. THE HEAT OF THE FIRE MELTED THE FUEL GAS REGULATORS CAUSING FUEL GAS TO FURTHER FUEL THE FIRE. DAMAGE WAS TOO EXTENSIVE TO DRAW ACCURATE CONCLUSIONS. | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
731 | 1992-04-05 | TX | other | GALVESTON | HOUSTON PIPELINE CO | THE COMBUSTION OF A LIQUID MATERIAL LOCATED IN A ROAD DITCH ADJACENT TO THE M | 102000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
732 | 1992-04-16 | LA | maintenance |  | STINGRAY PIPELINE CO |  | 53100 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
733 | 1992-04-23 | CO | other | LOGAN | K N ENERGY INC(KANSAS NEBRASKA GAS CO) | PRODUCER DISCONNECTED WELL LINE FROM METER RUN SO IT COULD RUN PIG AND ALCOHOL THROUGH LINE TO LOWER DEWPOINTS. PRODUCSER'S LINE WAS OPEN TO ATMOSPHERE AND POINTING TOWARD K N METER RUN. WHEN PIG EXITED LINE, IT SOME HOW IGNITEDGAS. THE RESULTING FIRE | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
734 | 1992-04-05 | TX | other | GALVESTON | BLACK MARLIN PIPELINE CO | THE COMBUSTION OF A LIQUID MATERIAL LOCATED ON A ROAD DITCH ADJACENT TO THE METER STATION APPEARS TO HAVE ALLOWED NATURAL GAS LEAKAGE AT THE FLANGED JOINTS DUE TO EXCESSIVE HEATING. | 216000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
735 | 1992-04-14 | WV | maintenance | GILMER | COLUMBIA GAS TRANSMISSION CORP | INVESTIGATION REVEALED THAT A 62' SEGMENT OF OPERATOR'S LINE TM-7 WAS DAMAGED RESULTING FROM 1 43' RUPTURE ATTRIBUTED TO SELECTIVE SEAM CORROSION. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
736 | 1992-04-21 | LA | technical failure |  | TENNESSEE GAS PIPELINE CO | LEAK OCCURRED IN TEE FITTING | 125000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
737 | 1992-04-21 | MS | other | PANOLA | TENNESSEE GAS PIPELINE CO | CAUSE UNKNOWN UNDER INVESTIGATION. RUPTURE WITH NO FIRE ON 100-2 LINE IN WRINKLE BEND UPSTREAM OF HWY. 315 CASED CROSSING. | 98000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
738 | 1992-06-01 | KY | other | HANCOCK | WESTERN KENTUCKY GAS CO | UNDERGROUND GAS STORAGE WELLHEAD 3/4" LINE STRUCK BY A TRACTOR CAUSING A NIPPLE TO BREAK AND RELEASE GAS. THE GAS IGNITED CAUSING DRIVER TO SUSTAIN BURNS | 2000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
739 | 1992-06-24 | AL | other | LAWRENCE | DECATUR UTILITIES - DECATUR GAS DEPARTMENT | CONSTOCK COMMUNICATIONS, INC. A CONTRACTOR INSTALLING FIBER OPTICS CABLE FOR SOUTHCENTRAL BELL, HIT AND RUPTURED DECATUR UTILITIES' 10 INCH GAS MAIN AT APPROXIMATELY 17:55 JUNE 24, 1992. THE RUPTURE OCCURRED AT A STREAM CROSSING(FOXES CREEK ALONG U.S. H | 200000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
740 | 1992-06-16 | LA | other |  | TENNESSEE GAS PIPELINE CO | LEAK AT INTERSECTION OF SIDE VALVE ASSEMBLY 525C-101.2. LEAK WAS NOT CONDSIDERED A HAZARD | 250000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
741 | 1992-06-17 | CA | other | LOS ANGELES | SOUTHERN CALIFORNIA GAS CO | CREW MEMBERS OVERPRESSURED A TWO-INCH RUBBER HOSE ASSEMBLY, CAUSING IT TO SEPARATE AND STRIKE THREE PEOPLE. HOSE RATING AND MAOP UNKNOWN. ONN JUNE 17,1992 AT APPROXIMATELY 6:30 A.M., GAS COMPANY EMPOYEES BEGAN BLOWING DOWN A SIX-FOOT SECTION OF LINE 76 | 300 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
742 | 1992-06-15 | NM | maintenance |  | EL PASO NATURAL GAS CO | WELD SEAM CORROSION AND THE DEVELOPMENT OF A NARROW OR CRACK-LIKE CORROSION PENETRATION IN THE EFW SEAM CAUSED THE PIPELINE TO RUPTURE. | 135708 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
743 | 1992-07-09 | LA | maintenance | (OFFSHORE) | ANR PIPELINE CO |  | 921400 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
744 | 1992-07-05 | IA | other | WARREN | NATURAL GAS PIPELINE CO OF AMERICA | FOLLOWING A PROCEDURE TO RESTORE SERVICE AT HIS BLOWNDOWN STATION, AN OPERATOR ACTIVATED THE VALVE CONTROL PANEL WHILE THE BLOWDOWN VALVES WERE BEING RESET. GAS VENTED THROUGH 4 OF THE 6 BLOWDOWN VALVES. | 90000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
745 | 1992-07-02 | LA | technical failure |  | TRANSCO GAS PIPELINE CORP | BUBBLES WERE OBSERVED BY TRANSCO PERSONNEL IN THE VICINITY OF TRANSCONTINENTAL GAS PIPE LINE CORPORATION'S PIPELINE WHILE FLYING OFFSHORE. DIVERS WERE DISPATCHED AND CONFIRMED THAT THE LEAK WAS A PINHOLE (3/16") IN THE 6 O'CLOCK POSITION IN A GIRTH WELD | 53500 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
746 | 1992-07-13 | KS | maintenance | PAWNEE | NORTHERN NATURAL GAS CO (ENRON) |  | 107000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
747 | 1992-08-03 | WY | other | CAMPBELL | M I G C INC | STRESS ON LINE AT END OF CASING CAUSED RUPTURE. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
748 | 1990-12-23 | MS | other | MONROE | MISSISSIPPI VALLEY GAS | ONE LINE IN A DUAL 8" RIVER CROSSING BROKE IN A WELD AFTER BEING UNDERMINED BY FLOOD WATERS AND SUBJECTED TO FORCE OF RUSHING WATER, COLLECTED DEBRIS ANDWEIGHT OF PIPE IN THE RESULTING UNSUPPORTED SPAN. GAS SERVICES WAS LOST TO ABOUT 12,000 CUSTOMERS DOW | 536693 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
749 | 1992-08-02 | TX | technical failure | BRAZOS | FERGUSON-BURLESON COUNTY GAS GATHERING SYSTEM | JGM ARIEL THREE (3) STAGE NATURAL GAS COMPRESSOR PART OF A RURAL NATURAL GASGATHERING SYSTEM HAD A FAILURE RELEASING NATURAL GAS TO THE ATMOSPHERE AND INGNITED CAUSING THE COMPRESSOR TO BURN. THIS UNIT WAS STARTED ON 4-16-92. THE RESULTS OF THE METALURG | 500000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
750 | 1992-07-21 | TX | other | WHEELER | PALO DURO PIPELINE CO | THE INCIDENT OCCURRED ON JULY 21 DURING SCHEDULED ROUTINE MAINTENANCE. A TWO(2) INCH VALVE ASSEMBLY USED TO BLOWDOWN A VERTICAL SEPARATOR BECAME DISCONNEDTED FROM THE THREADED NOZZLE OM THE SEPARATOR. THE FORCE OF THE BLOWDOEN GAS ROTATED THE VALVE ASSE | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
751 | 1992-07-28 | TX | other | BRAZOS | LONE STAR GAS CO OF TEXAS, INC |  | 5000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
752 | 1992-08-03 | LA | maintenance |  | NATURAL GAS PIPELINE CO OF AMERICA | INTERNAL CORROSION CAUSED LEAKS FROM TWO ISOLATED PITS 26 INCHES APART. THEPIPELINE HAD BEEN SHUT-IN. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
753 | 1992-08-19 | OH | other | FAIRFIELD | TEXAS EASTERN GAS PIPELINE CO | A FIBER OPTIC CABLE CONTRACTOR STRUCK TEXAS EASTERN'S 26" LINE 3. A FIRE BEGAN AND TWO CONTRACT CABLE EMPLOYEES DIED. THE FIRE LASTED 2 HOURS 35 MIUNTES. | 154000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
754 | 1992-08-27 | LA | other |  | TENNESSEE GAS PIPELINE CO | PLATFORM DESTROYED BY HURRICANE ANDREW | 1600000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
755 | 1992-08-24 | LA | technical failure |  | SOUTHERN NATURAL GAS CO | SEVERAL YEARS PRIOR TO THE INCIDENT UNDER CONSIDERATION, THE 12" EUGENEISLAND 261 SEA ROBIN PIPELINE WHICH TIES INTO THE 24" EUGENE ISLAND 330-206PIPELINE HAD A LEAK IN S SET OF FLANGES AT THE EUGENE ISLAND BLOCK 273 TIE-INLOCATION. SEA ROBIN INSTALLED A | 120000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
756 | 1992-08-30 | TX | technical failure | ANDERSON | LONE STAR GAS CO | GIRTH WELD CRACKED WHERE A 30 DEGREE MITER CUT WAS MADE ON PIPE. | 5000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
757 | 1992-08-26 | LA | other | OFFSHORE | SOUTHERN NATURAL GAS CO | SHEAR JOINT (INSTALLED ON PIPELINE IN 1985) SEPARATION CAUSED BY A MUDSLIDE DURING HURRICANE ANDREW. | 1500000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
758 | 1992-08-25 | LA | other | OFFSHORE | TRUNKLINE GAS CO | DURING HURRICANE PLATFORM WAS SUBMERGED. UNKNOWN CONDITION. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
759 | 1992-08-27 | MS | other | ADAMS | MID - LOUISIANA GAS CO | HEAVY RAINFALL FROM HURRICANE ANDREW CAUSED RIVER TO RISE TO WITHIN 3' OF TOP BANK, EROSION OF BANK IN RIVERBEND ALLOWED TREES FLOATING DOWN RIVER TO STRIKE LINE, BREAKING 45 DEGREE ELBOW. | 31000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
760 | 1992-09-01 | TX | other | COLLIN | TEXAS UTILITIES FUEL CO | THIRD PARTY CONTRACTOR WAS TRENCHING FOR A NEW PIPELINE. CONTRACTOR WAS AWARE OF TUFCO'S PIPELINE AND HAD CEASED TRENCHING TO MOVE TO OPPOSITE SIDE OF TUFCO'S RIGHT-OF-WAY. IN ERROR, CONTRACTOR RESUMED DIGGING AT TURCO'S PIPELINE | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
761 | 1992-08-27 | LA | other |  | TRANSCO GAS PIPELINE CORP | AT APPROXIMATELY 9:35 A.M. ON AUGUST 27, 1992, HURRICANE ANDREW DESTROYED THE BLOCK 118E SHIP SHOAL PLATFORM OWNED BY ODECO. THE PLATFORM AND RISER WERECOMPLETELY OVERTURNED AND DESTROYED. TRANSCO HAD ONE 10" RISER ON THE PLATFORM. NO GAS WAS ONSERVED | 750000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
762 | 1992-08-27 | LA | other |  | TRANSCO GAS PIPELINE CORP | ON AUGUST 27, 1992 THE EFM EQUIPMENT DATA INDICATED THE BLOCK 72A SHIP SHOALPLATFORM OWNED BY MOBIL GAVE WAY DUE TO HURRICANE ANDREW AT 9:35 A.M. TRANSCO HAD TWO 12" RISERS (ONE BELONGING TO NORTHERN NATURAL AND OPERATED BY TRANSCO), ONE 6" RISER, THREE | 4000000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
763 | 1992-09-05 | CA | maintenance | LOS ANGELES | STOCKER RESOURCES INC | STOCKER RESOURCES, INC. (STOCKER) WAS INFORMED IN SATURDAY, SEPTEMBER 5, 1992, BY CHEVRON PIPELINE CO. THAT A POSSIBLE LEAK EXISTED IN THE GRASSY MEDIAN DSTRIP OF SAN VICENTE BLVD. AT FOREST DRIVE. IT IS UNCLEAR WHETHER CHEVRON DISCOVERED THE LEAK DURING | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
764 | 1992-09-19 | IA | other | ADAMS | CORNING MUNICIPAL UTILITIES | FLOOD WATER WASHED OUT THE PIPELINE RIVER CROSSING AND TRESS CAME DOWN THE RIVER AND HIT THE PIPE IN THE RIVER. THIS CAUSED TO BREAK IN AN ELBOW IN THE REVIER BANK. LINE WAS SHUT DOWN AND BREAK WAS CUT OUT AND A NEW 10 FT. SECTION WAS WELED IN. | 15000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
765 | 1992-09-23 | LA | other | CAMERON | TENNESSEE GAS PIPELINE CO | PLATFORM LEGS AND PIPELINES. ABOVE WATER PIPELINE RISERS ON CENTRAL GATHERING PLATFORM WERE VISIBLE ON A CLEAR DAY. | 3000000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
766 | 1992-10-01 | MO | other | CASS | WILLIAMS NATURAL GAS CO | CONTRACTOR WAS CLEANING CREEK BOTTOM WITH A HIGH LOADER. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
767 | 1992-10-14 | TX | other | WHARTON | GULF COAST NATURAL GAS CO | A HEAVY EQUIPMENT OPERATOR USING A 12-G MAINTAINER TO EXCAVATE AN EXITING DRAINAGE DITCH, STRUCK THE PIPELINE CUTTING A 3 X 2.5 INCH HOLE INTO THE PIPE. | 70000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
768 | 1992-10-05 | AL | other | DALLAS | TRANSCO GAS PIPELINE CORP | ON THE MORNING OF OCTOBER 5, 1992 AT 2:45 A.M., A PIPELINE RUPTURE AND FIRE OCCURRED ON MAIN LINE "A" AT MILE POST 867.56 IN DALLAS COUNTY, ALABAMA. THELINE SEGMENT WAS ISOLATED BY 4:14 A.M. AND ALLOWED TO BURN ITSELF OUT BY 7:45 A.M. THERE WERE NO REPO | 1860900 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
769 | 1992-10-20 | TX | other |  | TRANSCO GAS PIPELINE CORP | VEHICLE STRUCK BUILDING AND METER SET. THE IMPACT CRACKED THE STRAINER WHICHPRODUCER HAD ABANDONED PRODUCTION FROM HIGH ISLAND 206 AND MADE NEW CONNECTIO IGNITED.N TO SAME TRANSCO UWTV ASSEMBLY FROM HIGH ISLAND 207. PRODUCER HAD COMPLETED DISASSEMBLING | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
770 | 1992-10-20 | TX | other |  | DELMAR OPERATING, INC | THE 10-INCH GEAR OPERATED BALL VALVE INSTALLED ON DELMAR'S TIE-IN ASSEMBLY WAS BURIED TO THE PROPER DEPTH AND WAS COVERED WITH LOOSE SAND WHICH HAD NATURALLY BACK FILLED INTO THE HOLE MADE DURING THE INSTALLATION OF THE ASSEMBLY.AS THE "CAPTAIN JIMMY" WAS | 302600 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
771 | 1992-10-20 | TX | technical failure |  | DELMAR OPERATING, INC |  | 202600 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
772 | 1992-10-07 | OK | maintenance | TEXAS | PANHANDLE EASTERN PIPELINE CO | STILL UNDER INVESTIGATION.THE TGPL SUBSEA TIE-IN VALVE ASSEMBLY AND THE DELMAR PIPELINE WERE REPAIRED AND ON NOVEMBER 6, 1992, THE PIPELINE FROM HIGH ISLAND 207 PLATFORM WAS IN THE PROCESS OF BEING PRESSURED UP BY BACK FLOWING FROM THE SUBSEA TIE-IN ASSEM | 130000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
773 | 1992-10-12 | MO | other | CALLAWAY | FULTON BOARD OF PUBLIC WORKS | LINE WAS MARKED AND LOCATOR HAD GONE TO OFFICE TO CHECK RECORDS FOR DEPTH.CONTRACTOR EXCAVATING FOR NEW STATE HIGHWAY HIT LINE. LINE WAS LOCATED AND MARKED. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
774 | 1992-11-10 | TX | other | WHARTON | TRANSCO GAS PIPELINE CORP | ON NOVEMBER 10, 1992 AN OUTSIDE COMPANY WAS PERFORMING SEISMIC WORK IN THE VICINITY OF TGPL'S 243" MCMULLEN LATERAL. IT APPEARED THAT WHILE PERFOMING THEIR WORK, THE SEISMOGRAP CREW HAD DRILLED A SHOT HOLE DIRECTLY OVER THE TGPL PIPELINE AND PLACED A 1/3 | 75000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
775 | 1992-11-17 | TX | other |  | TRANSCO GAS PIPELINE CORP | AS A RESULT OF THE LEAK INCIDENT, REPORTED BY TGPL, ON OCTOBER 20, 1992, (DOT CASE NO. 141753) PRODUCER INSTALLED A MECHANICAL CONNECTOR TO ONE END OF THEIR 1O" PIPELINE. ON NOVEMBER 6, 1992 PRODUCER'S MECHANICAL CONNECTOR FAILEDDURING REPRESSURING OF FA | 60000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
776 | 1992-11-03 | IL | other | DU PAGE | NATURAL GAS PIPELINE CO OF AMERICA | VISUAL INSPECTION OF THE CARRIER PIPE FOUND THE EXTERNAL COATING TO BE IN GOOD CONDITION AND NO INTERNAL CORROSION. THE LEAK WAS NOT FOUND. NEW PIPE WAS INSTALLED. | 300000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
777 | 1992-11-03 | TX | other | SHIP SHOAL BLOCK 90 | TRUNKLINE GAS CO | FAILURE INITIATED IN DENT AT (PIPE POSITION) 12:00. BUT NOT ALL PIPE CAN BE ACCOUNTED FOR. | 1000000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
778 | 1992-11-10 | TX | other |  | LONE STAR GAS CO | PIPELINE HAD BEEN REMOVED FROM SERVICE TO INSTALL A REPLACEMENT SECTION. AFTER JOB COMPLETION, PIPELINE SEGMENT WAS PURGED, REPRESSURED AND RETURNED TO NORMAL SERVICE. APPROX. 20 MINUTES LATER A JOINT OF EXISTING PIPE SLIPPED FROM A DRESSER COUPLING AND | 2350 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
779 | 1992-11-20 | TX | other | WEBB | VALERO TRANSMISSION CO | A METALLURIGICAL ANALYSIS IS BEING CONDUCTED TO DETERMINE THE CAUSE OF THIS FAILURE. | 47000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
780 | 1992-11-16 | TX | other | NUECES | VALERO TRANSMISSION CO | A FAILURE ANALYSIS IS BEING CONDUCTED TO VERIFY THE CAUSE OF THE RUPTURE. | 232000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
781 | 1992-11-24 | KS | other | SEDGWICK | WILLIAMS NATURAL GAS CO | PIPELINE WAS MARKED; HOWEVER, DUE TO HEAVY EXCAVATION FROM NEW PIPELINE CONSTRUCTION, OPERATOR ACCIDENTALLY HIT EXISTING LINE WHILE SHORING FOR NEW TRENCH | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
782 | 1992-11-22 | VA | other | LOUDOUN | CNG TRANSMISSION CORP | DURING COMMISSIONING OF COMPRESSOR STATION, THE ESD SYSTEM LOST PRESSURE. THE OPERATING SOFTWARE DID NOT ALLOW THE PRESSURE TO BE MADE UP AND THEREFORE A FULL ESD OCCURRED. ABLOCK VALVE DID NOT CLOSE AND HAD TO BE CLOSED MANUALLY. ALL CONDITIONS WERE C | 54390 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
783 | 1992-10-08 | KS | maintenance | ELLSWORTH | NORTHERN NATURAL GAS CO (ENRON) |  | 183000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
784 | 1992-12-11 | TX | other | MCMULLEN | TRANSCO GAS PIPELINE CORP | WHILE PERFORMING PIGGING OPERATIONS ON DECEMBER 11, 1992, ON THE TGPL 20" SOUTH MCMULLEN LATERAL. LIQUIDS WERE BEING STORED IN FIVE FRAC TANKS SET UP ON TGPL PROPERTY AT STATION 04. ALL OF THE FRAC TANKS WERE FULL AND OVER NIGHT THE ATMOSPHERIC CONDITION | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
785 | 1992-11-20 | NY | other | NEW YORK | CONSOLIDATED EDISON CO OF NEW YORK | A CON EDISON CREW WAS PERFORMING A SCHEDULED REINFORCEMENT OF AN INSULATING CDURING SCHEDULED REINFORCEMENT OF TRANSMISSION MAIN, THE WELDER BURNED HOLE IOUPLING ON A 30-INCH TRANSMISSION MAIN WHEN THE WELDER UNINTENTIONALLY BURNEDN PIPE WALL CAUSING A LE | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
786 | 1992-12-05 | LA | other |  | UNITED GAS PIPELINE CO |  | 98000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
787 | 1992-12-11 | WY | other | PARK | WILLISTON BASIN INTERSTATE PIPELINE CO | EXPLOSION AND FIRE RESULTED FROM FAILURE OF HEAT EXCHANGE COIL WITHIN FIRED HEATER FOR THE DRY BED DEHYDRATION SYSTEM.7 | 150000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
788 | 1993-01-06 | ID | other | OWYHEE | NORTHWEST PIPELINE CORP | CONTRACT BACKHOE RUPTURED PIPE DURING BACKFILL OPERATION OF NEW LOOP IN SPITE OF PIPE DEPTHS MARKED ON THE IN-SERVICE 16 INCH LINE EVERY 100 FEET. COMPANY INSPECTOR WAS AT PADDING OPERATION ONE-HALF MILE AWAY. | 170000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
789 | 1992-12-29 | PA | maintenance | FAYETTE | COLUMBIA GAS TRANSMISSION CORP | RELATED CORROSION AREA TOTALED 16 SQUARE INCHES. REMAINING PIPE IN EXCELLENT CONDITION. INVESTIGATION REVEALED THAT A 57.5' SEGMENT OF OPERATOR'S LINE 1804 WAS DAMAGED RESULTING FROM A 41' RUPTURE ATTRIBUTED TO AN ISOLATED CORROSION DEFECT WHICH REDUCED | 165000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
790 | 1993-01-14 | AZ | other | PINAL | EL PASO NATURAL GAS CO | NUMBER OF OUR PIPELINES IN THAT STATE. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
791 | 1993-01-13 | AZ | other |  | EL PASO NATURAL GAS CO | THIS PIPELINE SEGMENT HAD BEEN BLOWNDOWN ON 1/10/93 AS A PRECAUTION. RECENTOF OUR PIPELINES IN THAT STATE. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
792 | 1993-01-08 | AZ | other |  | EL PASO NATURAL GAS CO | RECENT RAINS IN THE STATE OF ARIZONA HAVE FLOODED RIVERS, CAUSING DAMAGE TO A NUMBER OF OUR PIPELINES IN THAT STATE. FLOOD WATERS FROM THE SAN PEDRO RIVER WASHED AWAY SOME PEERS FOR A PIPELINE BRIDGE SUPPORTING OUR 6 5/8" LINE2071. THIS CAUSED THE PI | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
793 | 1992-12-15 | MI | other | OSCEOLA | MICHIGAN CONSOLIDATED GAS CO (MICHCON) | MICHCON CONTRACTOR'S BACKHOE STRUCK 3" DIS. 3' UNKNOWN STUB ON SIDE OF PIPELINE THAT WAS NOT RECORDED BY PREVIOUS OWNER OF PIPELINE. STAKING LOCATION OFTHE PIPELINE WAS INACURATE | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
794 | 1992-11-20 | TX | technical failure | WARD | AMERICAN CENTRAL GAS CO INC | TESTS REVEAL THAT TGE 8" LINE PIPE INVOLVED FAILED DUE TO INTERNAL OVER-PRESSURIZATION. THE WALL THINNING IN THE ERW WELD SEAM FUSION LINE AT THE ORIGINOF THE BURST WAS THE RESULT OF SULFUR COMPOUNDS CORROSION. THE CORROSION HAD OCCURRED FROM THE I.D. P | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
795 | 1993-01-21 | AZ | technical failure |  | EL PASO NATURAL GAS CO | OUR 30" CALIFORNIA LOOP LINE 1103 RUPTURED DUE TO A SEAM FAILURE. THERE WASA FIRE AND A 600' SEGMENT OF PIPE LINE WAS BLOWN OUT. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
796 | 1993-01-19 | AZ | other |  | EL PASO NATURAL GAS CO | OF OUR PIPELINES IN THAT STATE. FLOOD WATERS FROM THE GILA RIVER CAUSED OUR 26" CALIFORNIA LINE 1100 AND OUR 30" CALIFORNIA 1ST LOOP LINE 1103 TO RUPTURE. RELEASED GAS, EXPLODED AND IGNITED. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
797 | 1993-01-19 | AZ | other |  | EL PASO NATURAL GAS CO | OF OUR PIPELINES IN THAT STATE. FLOODS WATERS FROM THE GILA RIVER CAUSED OUR 8 5/8" MORENCI LINE 2006 TO RUPTURE. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
798 | 1993-01-19 | AZ | other |  | EL PASO NATURAL GAS CO | RAINS IN THE STATE OF ARIZONA HAVE FLOODED RIVERS, CAUSING DAMAGE TO A NUMBER OF OUR PIPELINES IN THAT STATE. FLOOD WATERS FROM THE GILA RIVER CAUSED OUR 6 5/8" MORENCI LOOP LINE 2007 TO RUPTURE. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
799 | 1993-01-07 | ID | other | BOUNDARY | PACIFIC GAS TRANSMISSION CO | MAINLINE RELIEF VALVE WITH A SET PRESSURE OF 930 PSIG OPENED PREMATURELY AT A LINE PRESSURE OF 781 PSIG. FATIGUE FAILURE OF A 1/4-INCH VALVE PREVENTED AUTOMATIC CLOSING OF THE RELIEF VALVE. DAMAGE TO FACILITIES WAS LESS THAN $1,000 AND CONSISTED ONLY O | 85000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
800 | 1993-01-21 | VA | technical failure | CAMPBELL | TRANSCO GAS PIPELINE CORP |  | 54000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
801 | 1993-01-10 | OK | other | GARFIELD | ENOGEX INC (EX. MUSTANG FUEL CORP) | ON JANUARY 10, 1993, AT APPROXIMATELY 6:30 A.M., A LOW PRESSURE STORAGE TANKAT THE ENID POWER PLANT STATION FAILED. THE PRESSURE AT WHICH THE FAILURE OCCURRED IS STILL UNKNOWN. THERE WERE NO DEATHS OR INJURIES INVOLVED AND FIREDID NOT OCCUR AS A RESULT | 80000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
802 | 1993-01-15 | WY | other | CAMPBELL | M I G C INC | ON JANUARY 15, 1993 A FIRE OCCURRED IN A MIGC, INC. COMPRESSOR STATION. DAMAGES OCCURRED TO THE WHITE ENGINE WHICH DRIVES ONE COMPRESSOR. TELEPHONIC MOTICE TO 1-800-424-8802 WAS MADE ON JANUARY 1118, 1993. TELEPHONIC NOTICE TO1-777-7427, STATE OF WYOM | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
803 | 1993-01-20 | KY | maintenance | PIKE | ASHLAND EXPLORATION CO | INVESTIGATORS OF THE SURROUNDING AREA DISCOVERED A LEAK ON AN UNKNOWN SECTION OF ABANDONED PIPELINE OWNED BY AEI. THIS LEAK WAS A POSSIBLE SOURCE OF THEEXPLOSION ALTHOUGH THE ACTUAL SOURCE WAS NEVER CONCLUSIVELY CONFIRMED. INJURED PARTY RELEASED FROM HO | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
804 | 1993-01-23 | TX | maintenance |  | UNOCAL NORTH AMERICAN OIL & GAS DIV | LEAK WAS FOUND IN 6 -5/8" RISER ABOVE THE WATER LEVEL. THE SPLASHTRON COATING WORE OFF IN THE AREA OF THE LEAK ALLOWING CORROSION TO OCCUR. THE SUBJECTPIPE WAS REPLACED AND THE SYSTEM WAS PRESSURE TESTED AND PLACED BACK ON PRODUCTION 1/29/93.7 | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
805 | 1993-01-13 | LA | other |  | UNITED GAS PIPELINE CO | METULURGICAL REPORT & FURTHER INVESTIGATION IN PROGRESS. | 52000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
806 | 1993-01-24 | MA | other | ESSEX | TENNESSEE GAS PIPELINE CO | PIPELINE BEGAN TO LEAK WHEN THE SOIL OVERBURDEN CAUSED EXCESSIVE PRESSURE ONTHE PIPELINE IN AN AREA OF SOFT, UNSTABLE SOIL. (LARGE VOLUMES OF FILL WEREPLACED ON TOP OF PIPE IN A WET/BOGGY AREA). | 58000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
807 | 1993-01-12 | TX | maintenance | ORANGE | TRISTAR GAS COMPANY | ON JANUARY 12, 1993 AT APPROXIMATELY 10:00P.M., THE REGULATOR AT THE GAS SUPPLY SOURCE ON TRISTAR GAS COMPANY'S PIPELINE MALFUNCTION. THIS ALLOWED THE PRESSURE ON TRISTAR'S LINE TO REACH 310 PSIG. THE REGULATOR AT THE DELIVERY POINT TO TRINITY INDUSTRIE | 5000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
808 | 1992-12-28 | LA | maintenance |  | ANR PIPELINE CO |  | 52000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
809 | 1993-02-10 | TX | technical failure | REFUGIO | UNITED GAS PIPELINE CO | THE MATERIAL DEFECT WAS A "HARDSPOT" ON THE PIPE DUE TO THE MANUFACTURE'S PROCESS. THE "HARDSPOT" WAS PREVIOUSLY INDENTIFIED AND REINFORCED WITH A SLEEVE. THE REINFORCING SLEEVE CONTAINED THE DEFECT. | 55000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
810 | 1993-02-27 | CA | other | SAN BERNARDINO | SOUTHERN CALIFORNIA GAS CO | ON FEBRUARY 27, 1993, AT 8:20 A.M., WE REALIZED A DROP IN PRESSURE ON LINE 2000. OUR INVESTIGATION REVEALED THAT A LANDSLIDE, ATTRIBUTE TO RECENT RAINS,STRESSED THE LINE TO THE POINT OF FAILURE. PERMANENT REPAIRS WERE COMPLETEDBY RELOCATING 2033' AROUND | 500000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
811 | 1993-03-04 | KS | other | RUSH | K N ENERGY INC(KANSAS NEBRASKA GAS CO) | FOR EXAMINATION UNTIL WINTER SNOW MELT DECREASES. A TEMPORARY BYPASS LINE HAS BEEN INSTALLED ON AN EXISTING COUNTY ROAD BRIDGE NEARBY. THE PIPELINE SECTION CANNOT BE REMOVED UNTIL THE HEAVY STREAM FLOW RECEDES. THIS AREA HAS RECEIVED CONSIDERABLE AMOUNT | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
812 | 1993-03-01 | OH | other | HOLMES | COLUMBIA GAS TRANSMISSION CORP | PRIVATE PROPERTY OWNER'S BULLDOZER BROKE MAINLINE FEED TO TOWN OF MILLERSBURG, OHIO. GAS SERVICE WAS INTERRUPTED TO APPROXIMATELY 1,330 COLUMBIA GAS OF OHIO DISTRIBUTION CUSTOMERS FOR 24-HOUR PERIOD. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
813 | 1993-03-07 | NE | other | FRANKLIN | K N ENERGY INC(KANSAS NEBRASKA GAS CO) | PIPELINE RUPTURED UNDER FLOWING STREAM. RUPTURED PORTION CAN NOT BE REMOVEDFOR EXAMINATION UNTIL WINTER SNOW MELT DECREASES. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
814 | 1993-02-24 | CA | other | LOS ANGELES | SOUTHERN CALIFORNIA GAS CO | ON FEBRUARY 24, 1993, AT 9:00 A.M., WE RECEIVED A REPORT THAT LINE 85 HAD RUPTURED AND WAS ON FIRE. OUR INVESTIGATION REVEALED THAT A LANDSLIDE, ATTRIBUTED TO RECENT RAINS, STRESS THE LINE TO THE POINT OF FAILURE AND THE ESCAPINGGAS WAS THEN IGNITED BY O | 552628 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
815 | 1993-02-20 | TX | technical failure |  | TRANSCO GAS PIPELINE CORP | AT APPROXIMATELY 10:00 A.M. ON FEBRUARY 20, 1993 ENRON PERSONNEL REPORTED TOTGPL'S GAS CONTROL THAT BUBBLES WERE SIGHTED IN THE VICINITY OF TGPL'S PIPELINE IN MATAGORDA ISLAND BLOCK 681. LATE AFTERNOON IN FEBRUARY 20, 1993, TRANSCO PERSONNEL WERE ABLE TO | 56000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
816 | 1993-03-18 | TX | technical failure | BRAZOS | BRAZOS PIPELINE SYSTEM | AAA 1/2 INCH HEAVY DUTY PIPE NIPPLE RATED AT 6,125 PSI CRACKED IN THE THREADS CAUSING THE RELEASE OF GAS WHICH IGNITED CAUSING THE RELEASE OF GAS WHICH IGNITED CAUSING THE 1969 WAUKESHA GAS COMPRESSOR TO CATCH ON FIRE. THIS IS A MANUFACTURED COMPONENT. | 300000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
817 | 1993-03-23 | NY | other | NEW YORK | CONSOLIDATED EDISON CO OF NEW YORK | A CRACK DEVELOPED ON A SEGMENT OF THE NEW YORK FACILITIES. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
818 | 1993-05-02 | CO | technical failure | MONTEZUMA | NORTHWEST PIPELINE CORP | PIPE WAS SUBJECTED TO LINEALOG SURVEY IN 1972 AND NO CORROSION WAS IDENTIFIED IN THIS AREA AT THAT TIME. VISUAL EXAMINATION OF THE DAMAGED PIPE FOUND THE INTERNAL AND EXTERNAL CONDITION TO BE GOOD. THEE CAUSE OF THE FAILURE IS STILL BEING INVESTIGATED. | 365500 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
819 | 1993-04-27 | NE | other | ANTELOPE | K N ENERGY INC(KANSAS NEBRASKA GAS CO) | A 2-INCH STEEL, BURIED TRANSMISSION PIPELINE WAS HIT BY A THIRD PARTY CONTRACEXPLOSION DEMOLISHED STRUCTURE. (SUSPECTED OF BEING FUELED BY NATURAL GAS) LETOR IN ANTELOPE COUNTY, NEBRASKA ON APRIL 27, 1993. IGNITION DID NOT OCCUR AAK WAS DETECTED ON SERVI | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
820 | 1993-05-10 | OK | other | HUGHES | TRANSOK INC | ON MAY 10, 1993 AT 15:30 AN OPERATOR AT TRANSOK'S GREASY CREEK PROCESSING PLANT NOTIFIED THE GAS CONTROL CENTER THAT ALL COMPRESSORS HAD SHUTDOWN DUE TO LOW SUCTION PRESSURE. AT THIS SAME TIME GAS CONTROL WAS NOTICING A PRESSURE LOSS ON THE LINE FEEDING | 600000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
821 | 1993-04-16 | TX | maintenance | LIMESTONE | TEXAS UTILITIES FUEL CO | TOP COATING AT LEAK SITE WAS DISBONDED. | 78876 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
822 | 1993-05-06 | TX | technical failure | GAINES | AMAERICAN GAS STORAGE CORP |  | 3000000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
823 | 1993-05-28 | AK | other | SUSITNA BOROUGH | ENSTAR NATURAL GAS CO |  | 3500000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
824 | 1993-05-12 | KS | other | SEDGWICK | WILLIAMS NATURAL GAS CO | TURBULENT FLOODWATERS IN THE ARKANSAS RIVER CAUSED THE 16" LINE TO SEPARATE. THE LINE WAS CAPPED ON EACH SIDE OF THE RIVER. THE REPAIRS TO THE LINE WILL BE MADE AFTER THE WATER RECEDES. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
825 | 1993-05-12 | LA | other |  | SEA ROBIN PIPELINE CO | TWO SMALL PINHOLE LEAKS WERE DISCOVERED AT THE 6 O'CLOCK POSITION ON THE PIPE. INSPECTION BY DIVERS REVEALED NO EVIDENCE OF COATING DAMAGE OR EXTERNAL DETERIORATION OF THE PIPE. AN ULTRASONIC THICKNESS GAUGE WAS EMPLOYED TO CHECK THE PIPE WALL THICKNESS | 206000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
826 | 1993-05-12 | NC | other | BURKE | PIEDMONT NATURAL GAS CO INC | CONTRACTOR INSTALLING NEW PIPELINE PARALLEL TO EXISTING LINE FOR PIEDMONT DAMAGED EXISTING LINE DURING EXCAVATION. CONTRACTOR WAS OBLIGATED TO LOCATE EXISTING LINE BY EXPOSING IT WAS NEEDED. THE INTERVAL IN THE AREA OF DAMAGE WAS TOO LARGE. AS A RESULT | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
827 | 1993-05-19 | LA | maintenance |  | COLUMBIA GULF TRANSMISSION CO | SCENARIO: LEAK DISCOVERED BY SEA ROBIN HELICOPTER PILOT 5/19/93. DIVING CONTRACTOR MOBILZED MIDNIGHT 5/20/93. LEAK CONFIRMED TO BE COLUMIA PIPELINE 9:00 PM 5/22/93. PINHOLE LEAK REPAIR COMPLETED WITH HYDROTECH SUB-SEA REPAIR CLAMP 7:00 PM 5/25/93.ISOLA | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
828 | 1993-05-01 | NY | other | ALBANY | SELKIRK COGEN PARTNERS | BECHTEL CORPORATION OF NEVADA EXPOSED AND DAMAGED A 3 FOOT LONG SECTION OF THE PIPELINE DURING EXCAVATION ACTIVITIES ON THE PHASE II SITE. DATE OF NOTIFICATION : 05/03/93. TIME OF NOTIFICATION : 8:00 AM. RESPONSE: UPON NOTIFICATION THAT DAMAGE TO THE | 40000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
829 | 1993-04-28 | KS | other | JOHNSON | WILLIAMS NATURAL GAS CO | UNAUTHORIZED ENTRY OF WNG FACILITIES IN WHICH THE CONTROLLERS ON REGULATORS WERE ADJUSTED RESULTING IN AN OVERPRESSURE SITUATION. THE MAOP OF THE TWO PIPELINES WERE EXCEEDED. THE FBI WAS BROUGHT IN TO INVESTIGATE. TWO 26" PIPELINES WERE OVERPRESSURED F | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
830 | 1993-06-07 | LA | other | CONCORDIA | MID - LOUISIANA GAS CO | PART 3 - STRONG RIVER CURRENT SCOURED CHANNEL BELOW THE PIPE NEAR THE EDGE OF ALEAK OCCURRED IN MISS. RIVER. STRONG CURRENT HAS PREVENTED COMPLETION OF INVOF A SANDBAR CAUSING PIPE TO BECOME SUSPENDED OVER THE BOTTOM. THE FORCE OF THEESTIGATION AND REPA | 150000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
831 | 1993-06-15 | MI | other | ST CLAIR | MICHIGAN CONSOLIDATED GAS CO (MICHCON) | INGNITION OF GAS VENTING FROM WELL RIG LUBRICATOR BOTTLE DURING ROUTINE WELLWORK TO RETRIEVE A PACKER. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
832 | 1993-06-06 | LA | other |  | NATURAL GAS PIPELINE CO OF AMERICA | THE PIPELINE WAS APPARENTLY STRUCK BY A JACK-UP RIG BEING TOWED TO A DRILLING SITE. REPAIRS ARE IN PROGRESS. | 500000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
833 | 1993-05-31 | TX | other | GAINES | AMAERICAN GAS STORAGE CORP | 1/2" XH PIPE NIPPLE (SCH 40) BROKE OFF AT THREADS. IF METALURGICAL REPORT DIFFERS FROM INITIAL FINDINGS, A SUPPLEMENTAL REPORT WILL BE SUBMITTED. | 400000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
834 | 1993-06-03 | AL | technical failure | CHILTON | TRANSCO GAS PIPELINE CORP | AT APPROXIMATELY 10:30 PM CST ON JUNE 3, 1993, A FIRE OCCURRED AT COMPRESSORSTATION 100 LOCATED NEAR BILLINGSLEY, ALABAMA. THE FIRE OCCURRED ON STEAM TURBINE UNIT #2. TWO EMPLOYEES SUFFERED MINOR INJURIES AND WERE TAKEN TO A LOCAL HOSPITAL. ONE EMPLOYE | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
835 | 1993-06-19 | CA | other | RIVERSIDE | SOUTHERN CALIFORNIA GAS CO | ON JUNE 19,1993 , AT APPROXIMATELY 11:34 AM, CASH EQUIPMENT RENTALS DAMAGED LINE 2000 WITH A TOOTH ON THE FRONT BUCKET OF A CATIPILAR MODEL 988 LOADER WHILE EXCAVATING. A 6"X3" HOLE WAS GOUGED IN THE LINE AT ABOUT THE ONE O'CLOCK POSITION. ALL OFF - LINE | 62500 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
836 | 1993-06-15 | TX | other | BRAZOS | TEXAS UTILITIES FUEL CO | OPERATOR WAS LOADING FILL DIRT WITH A JOHN DEERE 544E FRONT END LOADER ON TUFCO R.O.W. KNOCKED HOLE IN 24" LINE NORTH OF BVO 113 ABOUT 200 YDS.PIPELINE COLORS & TUFCO SINGS. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
837 | 1993-06-24 | LA | maintenance | OUACHITA | TENNESSEE GAS PIPELINE CO | LINE 100-2, DOWNSTREAM OF COMPRESSOR STATION RUPTURED, CAUSING A FIRE. | 300000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
838 | 1993-07-30 | LA | technical failure |  | TRANSCO GAS PIPELINE CORP | THE CHECK VALVE DID NOT CLOSE COMPLETELY WHEN MECHANICAL SLIP JOINT DISENGAGED, ALLOWING THE RELEASE OF GAS PRESSURE. | 350000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
839 | 1993-07-15 | WA | other | SPOKANE | PACIFIC GAS TRANSMISSION CO | WHILE REPAIRING A TIE-IN WELD ON NEW 34-INCH STATION PIPING, AN EXPLOSIVEMIXTURE OF GAS BUILT UP INSIDE THE PIPE FROM A LEAKING VALVE RESULTING IN AFLASH FIRE. THE WELDER REPAIRING THE WELD WAS BURNED OVER THE LOWER HALF OFHIS BODY AS THE HOT GASES CAME | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
840 | 1993-07-13 | TX | other | MATAGORDA | TRANSCO GAS PIPELINE CORP | AT APPROXIMATELY 8:40 PM CST ON JULY 13,1993 A SMALL EXPLOSION AND FLASH FIRE OCCURRED ON THE NUMBER 1 SLUG CATCHER AT COMPRESSOR STATION 24 LOCATED IN MARKHAM, TEXAS. TWO EMPLOYEES SUFFERED INJURIES. ONE EMPLOYEE WAS TREATED AND RELEASED WITH MINOR BRUIS | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
841 | 1993-07-15 | LA | other | LAFOURCHE | TENNESSEE GAS PIPELINE CO |  | 55000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
842 | 1993-07-24 | NM | maintenance | HIDALGO | EL PASO NATURAL GAS CO | PART 3. ON 7/24 AT 7:30 PM (MDT) A LEAK WAS REPORTED ON OUR PIPLINE. AN 18" RUPTURE WAS DISCOVERED AND THE PIPELINE SEGMENT WAS ISOLATED BY 10:40 PM. THEPIPELINE WAS REPAIRED AND ETURNED TO SERVICE BY 3:38PM ON 7/25. AT THE TIME OF THE RUPTURE THIS INCIDE | 108000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
843 | 1993-07-30 | MO | other | HOWARD | PANHANDLE EASTERN PIPELINE CO | FLOODING ON THE MISSOURI RIVER CAUSED A LEVEE TO BREAK ON THE EAST SIDE OF THE RIVER NEAR PEPL'S FOUR PIPELINES. THE WATER VELOCITY WASHED COVER OFF THE PIPELINE RESULTING IN LINES FLOATING TO THE WATER SURFACE AS WELL AS UNDERMINING VALVE AND PIPING SUPP | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
844 | 1993-08-01 | NM | other | RIO ARRIBA | GAS CO OF NEW MEXICO | LINE BREAK AT RIVER CROSSINGLINE BREAK AT RIVER CROSSING. THEORIZED THAT RIVER BOTTOM LOWERED. THE EROSION OF TH BOTTOM EXPOSED PIPELINE THAT BROKE DUE TO WATER AND MATERIAL FORCES. | 225000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
845 | 1993-08-04 | TX | technical failure | GUADALUPE | INTRATEX GAS CO | PROBABLE CAUSE OF FAILURE WAS A HARD SPOT ON THE BODY OF THE PIPE 29" FROM THE DSAW SEAM AT THE 7:00 O'CLOCK POSITION. | 614334 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
846 | 1993-08-14 | NY | maintenance | BROOME | COLUMBIA GAS TRANSMISSION CORP | A CORROSION INDUCED DUCTILE PIPELINE RUPTURE OCCURRED DUE TO AN APPARENT SHIELDING OF CATHODIC PROTECTION CURRENT. GAS IGNITED AND THE SUBSEQUENT FIRE DESTROYED A NEARBY DWELLING. | 277000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
847 | 1993-08-24 | LA | other | EAST CARROLL | COLUMBIA GULF TRANSMISSION CO | ON AUGUST 24, 1993, BETWEEN 10:30 AND 10:45 AM, COLUMBIA GULF PIPELINE 200 RUPTURED IN A CROSSING OF THE MISSISSIPPI RIVER NEAR LAKE PROVIDENCE, LOUISIANA. GAS ESCAPING FROM THE RUPTURE IGNITED NEAR THE WEST BANK OF THE RIVER. VALVES UPSTREAM AND DOWNSTRE | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
848 | 1993-08-21 | TX | maintenance | MCLENNAN | TEXAS UTILITIES FUEL CO | PART 3 NARRATIVE - THE RUPTURE WAS WEST OF TRADINGHOUSE POWER PLANT; AND ABOUT TWO HUNDRED YARDS OUT IN LAKE TRADINGHOUSE. | 952000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
849 | 1993-07-27 | TX | other | GALVESTON | AMOCO GAS CO | PLEASE REFERNCE INVESTIGATION CONDUCTED BY DAVID BORN OF YOUR HOUSTON OFFICE. ON THE MORINGING OF JULY 27, 1993 AMOCO GAS COMPANY REMOVED THE CHOCLATE BAYOU TRANSMISSION LINE FROM SERVICE. LATER THAT MORNING, WE REMOVED FROM SERVICE A LOOP LINE BY COLD CU | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
850 | 1993-08-01 | TX | other | GREGG | UNITED GAS PIPELINE CO | PART 3 NARRATIVE - THE CAUSE OF THE FAILURE IS UNDER METALLURGICAL INVESTIGATION. A SUPPLEMENTAL REPORT WILL BE SUBMITTED AS SOON AS POSSIBLE. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
851 | 1993-09-09 | LA | technical failure | JEFFERSON DAVIS | TENNESSEE GAS PIPELINE CO | PART 3 NARRATIVE - DURING REMOVAL OF WALKER RICE FARM SALES METER, 2 INCH SIDE VALVE 507F - 131 FAILED, CAUSING GAS TO LEAK. IN PULLING VALVE STEM, INCORRECT BOLTS WERE REMOVED CAUSING VALVE TO DISASSEMBLE. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
852 | 1993-09-12 | KS | technical failure | OTTAWA | NORTHERN NATURAL GAS CO (ENRON) | HARD SPOT IN PIPE WALL | 260000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
853 | 1993-09-18 | WV | maintenance | POCAHONTAS | COLUMBIA GAS TRANSMISSION CORP | AN INTERNAL CORROSION INHIBITOR PROGRAM IS SCHEDULED TO BEGIN AT THE BEGINNING OF THE 1993 STORAGE WITHDRAWAL SEASON.INTERNAL CORROSION CAUSED RUPTURE OF STORAGE LINE DRIP, RESULTING IN IGNITION AND THE BURNING OF APPROXIMATELY 5 ACRES OF TREES. | 105000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
854 | 1993-09-18 | WV | maintenance | COCO KANAWHA | COLUMBIA GAS TRANSMISSION CORP | PART 3 NARRATIVE - BARE PIPE IS LOCATED ON A 65% GRADE ROCK HILLSIDE WITH 1 FOOT OF UNCONSOLIDATED ROCK COVER. THIS RESULTED IN INEFECTIVE CATHODIC PROTECTION AT THE POINT OF FAILURE. | 91000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
855 | 1993-09-23 | AZ | other | MARICOPA | BLACK MOUNTAIN GAS CO | BLUE STAKE WAS NOT COMPLETE. CONTRACTOR DUG AFTER DIGGING POTHOLE CONTRACTORASSUMED BLUE STAKE WAS WRONG. BACKHOE HIT LINE. | 5000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
856 | 1993-08-09 | TX | other | GALVESTON | VALERO TRANSMISSION CO | THE PIPELINE RUPTURED AT THIS LOCATION. AT THIS TIME, THE CAUSE OF THE RUPTURE IS NOT KNOWN THE RUPTURED PIPE IS BEING ANALYZED BY A METALLURGIST. WHEN THE RESULTS ARE AVAILABLE A COPY WILL BE SENT TO THE TRRC. | 48000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
857 | 1993-08-25 | TX | other | KLEBERG | VALERO TRANSMISSION CO | OUR PIPELINE WAS HIT AND PUNCTURED BY A MESQUITE EARTH MOVER WHILE KING RANCH PERSONNEL WERE DIGGING A DRAINAGE DITCH ACROSS THE ROW. VALERO PERSONNEL HAD LOCATED, FLAGGED AND STAKED THE LINE AND HAD MADE DAILY CHECKS UNTIL THE PIPELINE WAS EXPOSED. THE L | 45000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
858 | 1993-09-04 | CT | other |  | IROQUOIS GAS TRANSMISSION SYSTEM | ON SEPTEMBER 4, 1993, AT APPROXIMATELY 17:30 HOURS A SURVEY CREW UNDER CONTRACT TO IROQUOIS TO PERFORM A MARINE HYDROGRAPHIC AND GEOPHYSICAL SURVEY OF OUR OFFSHORE PIPELINE DISCOVERED AN ACOUSTIC DISTURBANCE IN THE WATER COLUMN. UPON FURTHER INVESTIGATION | 91000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
859 | 1993-10-04 | LA | maintenance |  | COLUMBIA GULF TRANSMISSION CO |  | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
860 | 1993-09-27 | LA | other |  | COLUMBIA GULF TRANSMISSION CO |  | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
861 | 1993-10-22 | TN | other | PUTNAM | TENNESSEE GAS PIPELINE CO | CONSTRUCTION CREW PERFORMING CONSTRUCTION OF 10' OFFSET LINE STRUCK 4 INCH LATERAL LINE WITH BACKHOE. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
862 | 1993-10-07 | WV | maintenance | DODDRIDGE | COLUMBIA GAS TRANSMISSION CORP | A 62 FT. SECTION OF PIPELINE SUSTAINED A RUPTURE AS THE RESULT OF SELECTIVE SEAM CORROSION. | 91000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
863 | 1993-10-15 | LA | other | CAMERON | COLUMBIA GULF TRANSMISSION CO | PIPE APPEARS TO HAVE BEEN SNAGGED BY OUTSIDE FORCE, EITHER A BARGE OR A TUG, AND PULLED OFF DITCH LINE APPROXIMATELY 12' CAUSING A BUCKLE AND CRACK IN THE PIPE ALONG A FIELD GIRTH WELD RESULTING IN A LEAK. | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
864 | 1993-10-12 | KS | other | MEADE | NATURAL GAS PIPELINE CO OF AMERICA | PART 3 NARRATIVE - VENTED 24" NIGHT CAP EXITTED PIPE DUE TO A PRESSURE DIFFERENTIAL OF UNKNOWN SIZE. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
865 | 1993-10-12 | MO | other | BUTLER | MISSISSIPPI RIVER TRANSMISSION CORP | DRESSER COUPLING FAILED WHILE REPAIRING A LEAK. PIPE PULLED FROM THE COUPLING. UNEVEN TERRAIN PLUS NORMAL AND AXIAL FORCES CONTRIBUTED TO THE FAILURE.PART 2 OTHER- DRESSER COUPLING. | 192000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
866 | 1993-08-05 | CO | other |  | ROCKY MOUNTAIN NATURAL GAS CO INC |  | 930000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
867 | 1993-10-02 | LA | technical failure |  | NATURAL GAS PIPELINE CO OF AMERICA | LEAKING FLANGE CONNECTION ON 24" BALLFLANGE CONNECTOR. | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
868 | 1993-10-05 | LA | other |  | TENNESSEE GAS PIPELINE CO | LEAK DISCOVERED AFTER BUBBLES, OIL SHEEN DETECTED AT SURFACE. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
869 | 1993-11-16 | MS | other | ADAMS | MID - LOUISIANA GAS CO | PART 3 NARRATIVE - HEAVY RAINFALL RUNOFF WASHED OUT SUPPORTING SOIL AROUND 1OR MORE DRESSER COULINGS IN A NORMALLY DRY CREEK BOTTOM RESULTING IN PIPE MOVEMENT AND PULLOUT FROM AN EXPOSED MECHANICAL COUPLING. | 46000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
870 | 1993-10-26 | FL | other | DADE | FLORIDA GAS TRANSMISSION CO | PART 3 NARRATIVE - PIPELINE HIT BY CONTRACTOR WITH AN AUGER WHILE INSTALLINGOCCUPANT UTILIZED PROPANE CYLINDERS INSIDE HOUSE FOR SPACE/WATER HEATING PARTGUARD RAIL POSTS ALONG ROADWAY.2 APPARENT CAUSE- D LEAKING PROPANE CYLINDER. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
871 | 1993-10-21 | OK | other | LATIMER | ARKLA ENERGY RESOURCES | MECHANICAL FAILURE OF BEARING (IN BLOWER) IGNITED OIL (LUB) STARTING A FIRE IN THE CRANKCASE WHICH RESULTED IN AN EXPLOSION INJURING 2 COMPANY EMPLOYEES. | 40000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
872 | 1993-11-04 | WV | maintenance | JACKSON | COLUMBIA GAS TRANSMISSION CORP | PART 3 - INTERNAL CORROSION CAUSED RUPTURE OF A PIPELINE DRIP RESERVOIR; THERESULTING FIRE DESTROYED ONE HOUSE TRAILER, DAMAGED OTHER DWELLINGS, AND DESTROYED MULTIPLE VEHICLES. PART A CORROSION #2 OF DRIP RESERVOIR. | 250000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
873 | 1993-11-16 | TX | technical failure |  | TRANSCO GAS PIPELINE CORP | CAUSE IS UNKNOWN AT THIS TIME. A COMPLETE EXAMINATION WILL BE PERFORMED TODETERMINE THE REASON FOR THE FAILURE. A SUPPLEMENTAL REPORT WILL BE FILEDUPON COMPLETION OF THE INVESTIGATION. PART 3 NARRATIVE- 20" 900 # ENDCONNECTOR GAVE WAY CAUING THE RUPTURE A | 1500000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
874 | 1993-10-28 | TX | other | TARRANT | CORNERSTONE NATURAL GAS CO |  | 52000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
875 | 1993-11-15 | TX | other | WHARTON | TRANSCO GAS PIPELINE CORP | RUPTURE OCCURRED IN BODY OF 30" LINE PIPE OUTSIDE OF THE FILLET WELD OF A WELD SADDLE USED TO REINFORCE A 6" BRANCH CONNECTION. MCI"S INVESTIGATIVE REPORT ON THE RUPTURE CONCLUDED THAT THERE WAS NO METALLURGICAL CAUSE OF THE FAILURE. THE SUSPECTED CAUSE O | 229000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
876 | 1993-11-17 | TX | other |  | ANR PIPELINE CO | PIPELINE WAS STRUCK BY LEGS OF JACKUP RIG THAT WAS DRAGGED OVER THE 36" LINE. | 2500000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
877 | 1993-12-20 | NE | other | GOSPER | K N ENERGY INC(KANSAS NEBRASKA GAS CO) | THERE WAS A PIPELINE MARKER WITHIN 100 FT. OF BREAK. THE INCIENT OCCURRED WHEN THE BUCKET OF A FRONTEND LOADER ACCIDENTLY HOOKED THE LINE AS A FARMER CLEARED SNOW FROM AN AREA IN PREPARATION TO GRINDING HAY. THE TOP OF GROUND LINETRAVERSES THE FARMERS LAN | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
878 | 1993-12-20 | WI | maintenance | ASHLAND | NORTHERN NATURAL GAS CO (ENRON) |  | 750000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
879 | 1993-11-23 | IN | other | HENRY | ANR PIPELINE CO | PIPELINE WAS STRUCK BY A TRENCHING MACHINE USED TOLAY DRAINAGE TILE. | 58000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
880 | 1994-01-15 | LA | other |  | TENNESSEE GAS PIPELINE CO | LEAK DISCOVERED AFTER BUBBLES, OIL SHEEN DETECTED AT SURFACE. PARTT 2 D- UNDER INVESTIGATION POSSIBLE PINHOLE LEAK. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
881 | 1993-12-22 | OK | technical failure | LOGAN | WILLIAMS NATURAL GAS CO | AN ACETYLENE GIRTH WELD FAILED COMPLETELY. THE BASE METAL REMAINED INTACT THE FRACTURE WAS ENTIRELY IN THE WELD METAL AND OCCURRED SYMMETRICALLY BETWEEN THE ADJACENT JOINTS . | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
882 | 1993-12-16 | PA | other | TIOGA | CNG TRANSMISSION CORP | SUPPLY LINE TO ESD POWER OPERATOR ON 8" BLOWOFF FROZE OFF FROM MOISTURE IN LINERESULTING IN VALVE OPENING AND DSICHARGING GAS TO ATMOSPHERE.GAS WAS BEING DISCHARGED THROUGH BLOWOFF DESIGNED TO DISCHARGE GAS SAFELY. | 155000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
883 | 1993-12-27 | KS | other |  | NORTHERN NATURAL GAS CO (ENRON) | APPARENTLY A FOREIGN OBJECT DAMAGED THE DRIVER TURBINE. VIBRATION RESULTED, CAUSING TURBINE DESTRUCTION AND A FIRE. | 750000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
884 | 1994-01-14 | MS | maintenance |  | SOUTHERN NATURAL GAS CO | STRESS CORROSION CRACKING IN THE BODY OF THE PIPE IN CONJUNCTION WITH CORROSION FATIGUE PROPAGATED INTO A FAILURE AND PIPELINE RUPTURE WITH NATURAL GAS IGNITION. PART A - CORROSION PRELIMINARY BATTELLE INVESTIGATION INDICATES LOW PH STRESS CORROSION CRACK | 1187500 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
885 | 1993-12-02 | KS | other | BARTON | K N ENERGY INC(KANSAS NEBRASKA GAS CO) | A 1" DISCHARGE LINE ON AN INLINE DRIP BROKE OFF AS AN APPARENT FREEZE BROKE LOOSE. THE FIELDMAN WAS STRUCK ON THE HEAD BY THE PIECE OF 1" PIPE CAUSING ANINJURY THAT REQUIRED SEVERAL DAYS INT HE HOSPITAL. THERE WAS NO FIRE OR FURTHER DAMAGE. THE FIELDMAN O | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
886 | 1993-11-22 | CA | other | SANTA CLARA | PACIFIC GAS & ELECTRIC CO | A 20" LINE WAS CUT & CAPPED DOWNSTREAM OF A DRESS COUPLING. A 7' SECTION OF PIPE & THE WELDED CAP WAS BLOWN OUT OF THE DRESSER COUPLING WHEN THE LINE WASPRESSURIZED TO 190 PSIG. A COMPANY EMPLOYEE WAS INJURED. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
887 | 1993-11-24 | MS | other | OKTIBBEHA | TEXAS EASTERN GAS PIPELINE CO | EMPLOYEE D.L. BURROUGHS WAS APPARENTLY STRUCK BY A PIPELINE VALVE HANDWHEEL WHILE THE PIPELINE CREW WAS LAUNCHING A CLEANING PIG. TEXAS EASTERN BELIEVES THAT THE GAS DRIVEN MOTOR OPERATOR FOR THE VALVE ENGAGED AND THE UNSECURED HANDWHEEL STRUCK THE EMPLOY | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
888 | 1994-02-12 | LA | maintenance |  | TENNESSEE GAS PIPELINE CO | PART 3 - DURING PIGGING OPERATIONS, LEAK DISCOVERED BY HELICOPTER CREW (BUBBLES AT SURFACE). | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
889 | 1994-02-22 | ID | maintenance | ELMORE | NORTHWEST PIPELINE CORP | THE INCIDENT OCCURRED AT 1645 HOURS ON FEBRUARY 22, 1994 AT MILEPOST 0.1717 ON NORTHWEST'S RENO 16 INCH LINE. THE SITE IS IN A 21 MILE VALVE SECTION THATCONSISTS OF CULTIVATED LAND AND DESERT. THE LINE IS NOT LOOPED IN THIS SECTION AND NORTHWEST INTERRUPT | 170200 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
890 | 1994-01-19 | MD | other | PRINCE GEORGES | WASHINGTON GAS LIGHT CO | ON THE EVENING OF JANUARY 18, 1994, THE TEMPERATURE DROPPED TO SINGLE DIGITSOF NINE DEGREES AT 6:00 P.M. AND CONTINUED TO DROP TO A LOW OF FOUR BELOW ZERO BY 6:00 A.M. ON THE MORNING OF JANUARY 19, 1994. THIS EXTREME WEATHER CONDITION CREATED AND EXCESS D | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
891 | 1994-01-13 | CA | other | SAN JOAQUIN | UNION ISLAND PIPELINE CO | THE PUMP SEAL ON THE ODORANT INJECTION SYSTEM PUMP FAILED CAUSING THE RELEASETHE PHILADELPHIA FIRE DEPATMENT HAS INVESTIGATED THIS INCIDENT WHICH WAS INIT OF APPROXIMATELY ONE QUART OF CAPTAN 50 ODORANT. THE MERCAPTAN ODORANT TRAVEIALLY BELIEVED TO BE A H | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
892 | 1994-01-25 | AL | technical failure | MOBILE | MOBILE GAS SERVICE CORP | A LEAK OCCURRED WHEN AN END CAP BLEW OFF THE END OF AN 18" STEEL PIPE AT RANGELINE ROAD AND HAMILTON BOULEVARD. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
893 | 1993-12-27 | TX | other | PARMER | WESTAR TRANSMISSION CO | LINE CUT BY FARMER WHILE DEEP PLOWING. | 45430 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
894 | 1994-01-02 | TX | maintenance | COTTLE | LONE STAR GAS CO | A CORROSION LEAK ON 4" DRESSER COUPLING CAUSED THE LEAK. THE LEAK WAS ADJACENT TO STATE HWY. 83. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
895 | 1994-01-24 | TX | maintenance | GALVESTON AREA | BLUE DOLPHIN PIPELINE CO | PINHOLE GAS LEAK CAUSED BY APPARENT LOCALIZED INTERNAL CORROSION. LEAK WAS REPAIRED BY INSTALLATION OF 1500 PSIG WP BOLTED PIPELINE CLAMP. PART A - 250 #ZINC ANODES WERE INSTALLED ON 1/4 MILE SPACING DURING THE INITIAL CONSTRUCTION IN 1965. IMPRESSED CURR | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
896 | 1994-01-20 | LA | other | ACADIA | COLUMBIA GULF TRANSMISSION CO | IN PREPARATION FOR A PIGGING OPERATION ON LINE 200, COLUMBIA EMPLOYEES WERE PUMPING A CLEANING SOLUTION INTO THE PIPELINE. UNANTICIPATED ACTUATION OF A LIQUID RELIEF VALVE LOCATED ON THE PORTABLE TRIPLEX PUMPING UNIT RESULTED IN THE RELEASE AND IGNITION O | 331000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
897 | 1994-02-01 | MD | other | MONTGOMERY | TRANSCO GAS PIPELINE CORP | PART 3- THIRD PARTY CONTRACTOR'S BACKHOE PUNCTURED THE PIPELINE WHILE PERFORMING WORK ADJACENT TO THE R.O.W. | 70000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
898 | 1994-02-20 | LA | maintenance |  | TRANSCO GAS PIPELINE CORP |  | 60000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
899 | 1994-03-08 | LA | technical failure | TERREBONNE | TRANSCO GAS PIPELINE CORP | LACK OF FUSION IN LONGITUDINAL SEAM | 120000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
900 | 1994-03-05 | LA | maintenance |  | TENNESSEE GAS PIPELINE CO |  | 65000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
901 | 1994-01-21 | MS | technical failure | WINSTON | SOUTHERN NATURAL GAS CO | GIRTH WELD FAILURE: X-RAYS MADE AFTER INCIDENT REVEALED SEVERAL "BURNS THROUGH" AND THE LACK OF WELD MATERIAL PENETRATION OVER 50% OF THE JOINT CIRCUMFERENCE. THE X-RAYS SHOWED THAT THE REMAINDER OF THE GIRTH WELD WAS SATISFACTORY. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
902 | 1994-01-26 | TX | other | COLLINGSWORTH | LONE STAR GAS CO |  | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
903 | 1994-03-18 | LA | maintenance |  | TENNESSEE GAS PIPELINE CO | INTERNAL CORROSION LEAK DISCOVERED BY CONOCO PERSONNEL LARGER REPAIR CLAMP INSTALLED ENCOMPASS EARLIER LEAKS (2-12-94) ULTRASONICS REVEALED NO FURTHER LOCALIZED PITTING. | 125000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
904 | 1994-02-27 | MI | other | MECOSTA | ANR PIPELINE CO | THE PIPE RUPTURE WAS CAUSED BY A CRACK AT THE TOE OF A WELD JOINTING A WELDOLET TO THE BODY OF THE PIPE. | 1500000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
905 | 1994-03-15 | MI | other |  | ANR PIPELINE CO |  | 57000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
906 | 1994-03-30 | LA | other |  | TENNESSEE GAS PIPELINE CO |  | 10000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
907 | 1994-03-17 | LA | technical failure |  | TENNESSEE GAS PIPELINE CO | LEAK DISCOVERED BY CONOCO. GAS BOIL REPORTED IN EC48. SLIGHT BROKEN SHEEN ONWATER. | 20000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
908 | 1994-04-07 | TX | other | VICTORIA | GULF COAST NATURAL GAS CO | CAUSE OF RUPTURE IS CURRENTLY UNKNOWN, TEST ARE BEING CONDUCTED ON FAILEDSECTION OF 14" PIPE REMOVED AFTER INCIDENT TO DETERMINE CAUSE. | 66278 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
909 | 1994-03-22 | MS | other | TUNICA | TEXAS GAS TRANSMISSION CORP | ON MARCH 22, 1994, AT APPROXIMATELY 4:25 P.M. CST, A PROPETY OWNER NOTIFIEDTEXAS GAS OF AN APPARENT RUPTURE ON HIS LAND IN A RURAL AREA NEAR THE TOWN OFTUNICA, MISSISSIPPI. DISTRICT PERSONNEL WERE DISPATCHED IMMEDIATELY TO THERUPTURE SITE AS WELL AS TO BL | 125500 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
910 | 1994-03-19 | LA | maintenance |  | NATURAL GAS PIPELINE CO OF AMERICA |  | 150000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
911 | 1994-03-23 | NJ | other | MIDDLESEX | TEXAS EASTERN GAS PIPELINE CO | THE CAUSE OF THE INCIDENT IS UNDER INVESTIGATION BY THE NTSB.PIPELINE MARKERIS PRESENT ON ROAD AND NEAR PLANT GATE ENTRANCE TO THE ASPHALT PLANT WHERE THEINCIDENT OCCURRED. CASING VENT MARKERS ARE ALSO PRESENT NEAR WHERE THEPIPELINE EXITS THE ASPHALT PLAN | 25000000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
912 | 1994-04-17 | LA | other | CONCORDIA | MID - LOUISIANA GAS CO | STRONG RIVER CURRENT CAUSED SCOURING TO OCCUR WHICH EXPOSED THE PIPE NEAR THEEDGE OF A SAND BAR CAUSING A SECTION TO BECOME SUSPENDED ABOVE THE CHANNELBOTTOM. THE FORCE APPLIED BY THE CURRENT CAUSED THE PIPE TO SWING OR VIBRATEAND EVENTUALLY BREAK AT GIRT | 165000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
913 | 1994-04-17 | LA | other | WEST FELICIANA | TRANSCO GAS PIPELINE CORP | RUPTURED OCCURRED IN A 30" MISSISSIPPI RIVER CROSSING WHILE THE RIVER WAS ABOVE FLOOD STAGE. BECAUSE OF THE RIVER CURRENTS AND THE LOCATION OF RUPTURE, THE PRIMARY CAUSE OF THE INCIDENT CANNOT BE DETERMINED. TRANSCO WILL NOT ATTEMPT ANY REPAIR OF THE 30" | 5000000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
914 | 1994-04-26 | OR | technical failure |  | PACIFIC GAS TRANSMISSION CO | A SMALL CRACK DEVELOPED IN A FIELD WELD BETWEEN TWO DIFFERENT SPECIFICATIONSOF PIPE INSTALLED IN 1992 WHICH RESULTED IN A MINOR GAS LEAK. INCIDENT IS REPORTABLE ONLY BECAUSE COST OF REPAIRS, INCLUDING COST OF GAS BLOWN TO ATMOSPHERE, EXCEEDED $50,000. CAU | 150000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
915 | 1994-03-17 | LA | maintenance | STINGRAY | TRUNKLINE GAS CO |  | 95000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
916 | 1994-03-23 | LA | maintenance |  | TENNESSEE GAS PIPELINE CO | 1/4" PIN HOLE DISCOVERED AT BOTTOM OF 26" O.D. PIPELINE DRIP. | 75000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
917 | 1994-05-02 | TX | other | GALVESTON | FLORIDA GAS TRANSMISSION CO | PIPELINE DAMAGED BY BOAT TRAFFIC IN A SHALLOW, INLAND NAVIGABLE WATERWAY. THE PIPELINE RUPTURE RESULTED FROM DAMAGE CAUSED BY BOAT TRAFFIC IN A SHALLOW,INLAND WATERWAY. | 520000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
918 | 1994-05-06 | LA | other | ACADIA | TRANSCO GAS PIPELINE CORP | OIL TRANSPORT BARGE BEING PUSHED BY TUG BOAT RAN INTO THE 12" PIPELINE ON THE EAST SIDE OF THE BAYOU. (BAYOU DE CANNES). PART B- PERMANENT PIPELINE CROSSING MARKERS. | 888205 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
919 | 1994-05-27 | LA | maintenance |  | TENNESSEE GAS PIPELINE CO | LEAK DISCOVERED BY HELICOPTER CREW (BUBBLES AT SURFACE). | 52000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
920 | 1994-05-25 | LA | maintenance |  | COLUMBIA GULF TRANSMISSION CO | TWO SMALL INTERNAL CORROSION PIN HOLE LEAKS (18'APART) WERE REPAIRED WITH DASPIT CLAMPS. PART 1 B). X=1885229.89 Y=105490.26 | 150000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
921 | 1994-04-18 | IA | maintenance | GUTHRIE | NORTHERN NATURAL GAS CO (ENRON) | SHORT COATED REPLACEMENT SECTION IN A BARE, DRESSER COUPLED LINE. | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
922 | 1994-04-14 | KS | other | FORD | NATURAL GAS PIPELINE CO OF AMERICA | UNDER INVESTIGATION. PIPE SECTION HAS BEEN ISOLATED BUT NOT YET REMOVED FROMITS CASING. | 138600 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
923 | 1994-04-12 | LA | maintenance |  | NATURAL GAS PIPELINE CO OF AMERICA | PIPE SEGMENT ABANDONED. NO FLOW IN THE AFFECTED SEGMENT. | 400000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
924 | 1994-04-20 | LA | other |  | TENNESSEE GAS PIPELINE CO | WORK BOAT DROPPED ANCHOR. LEAK DISCOVERED BY TEXACO PERSONNEL. WORK BOAT ANCHOR SNAGGED T.G.P. 12" PIPELINE IN SOUTH PASS BLK 54. | 400000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
925 | 1994-06-19 | LA | maintenance |  | CHEVRON PIPELINE CO |  | 69000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
926 | 1994-06-23 | LA | other |  | TENNESSEE GAS PIPELINE CO | PIPELINE RUPTURED ON 20 IN. 526A-100 LINE IN MOUTH OF GRAND BAYOU, LOUISIANA.APPROXIMATELY 200 FEET OF PIPELINE HAD BECOME EXPOSED DUE TO THE WASHOUT & ERROSION. | 650000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
927 | 1994-06-22 | OK | maintenance | HUGHES | TRANSOK INC | ON JUNE 22, 1994 AT 17:55 TRANSOK'S GREASY CREEK PROCESSING PLANT RECEIVED SEVERAL CALLS FROM PRIVATE CITIZENS ABOUT A LOUD NOISE IN THE STORAGE FIELD. AT THE SAME TIME TELEMETRY WAS SHOWING A RAPID PRESSURE DROP. MILTON JOHNSON (OPERATOR) NOTIFIED RICK R | 63500 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
928 | 1994-06-30 | VA | maintenance | CULPEPER | TRANSCO GAS PIPELINE CORP |  | 250000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
929 | 1994-07-21 | LA | maintenance |  | CHEVRON PIPELINE CO |  | 75000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
930 | 1994-08-10 | LA | maintenance |  | NATURAL GAS PIPELINE CO OF AMERICA | PENDING INVESTIGATION. THE AFFECTED PIPE SECTION IS ISOLATED. REPAIRS ANDFURTHER INVESTIGATION ARE NOT COMPLETE. SUPPLEMENTAL REPORT 3/21/95 INDICATESTHAT XRAY CONFIRMED INTERNAL CORROSION. LOCALIZED INTERNAL PITTING SHOWN BYXRAY. INSTALLED LEAK CLAMP. | 226012 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
931 | 1994-08-10 | LA | maintenance | TERREBONNE | TRANSCO GAS PIPELINE CORP | FAILURE INITIATED IN THE LONG SEAM AS A RESULT OF INTERNAL PITTING CORROSIONON BOTH SIDES AND IN THE LONG SEAM. | 500000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
932 | 1994-08-21 | LA | other |  | COLUMBIA GULF TRANSMISSION CO | SPECULATION INDICATES THAT A 20' SEGMENT OF 6" PIPE AND VALVE HAD BEEN SEVERED BY A SURFACE VESSEL FISHING NET OR ANCHOR IN ROUGH SEAS. | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
933 | 1994-08-16 | LA | maintenance |  | COLUMBIA GULF TRANSMISSION CO | ONE SMALL INTERNAL CORROSION PIN HOLE LEAK WAS REPAIRED WITH A LEAK CLAMP. AT 7:40 AM, AUGUST 14, 1994, A BUBBLE LEAK WAS REPORTED BY A HELICOPTER TRANSPORT SERVICE DISPATCHER. WITHIN HOURS, SEVERAL PIPELINES WERE SHUT-IN. FURTHERINVESTIGATION AND EVALUAT | 150000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
934 | 1994-08-05 | TX | other |  | TRUNKLINE GAS CO | LEAKING FLANGE DISCOVERED ON 6" BALL VALVE ON 12" FUTURES TAP OF TGC 300-1 (30") LINE. FUTURES WAS BLOWN DOWN, 6" VALVE REMOVED AND NEW 6" BLIND FLANGE W/BLEEDER VALVE INSTALLED. | 59000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
935 | 1994-08-20 | NM | other | VALENCIA | TRANSWESTERN PIPELINE CO | DIFFERENTIAL SETTLING OF PIPELINE AND ABOVE GROUND APPURTENCES CAUSED UNDUE STRESS OF BELOW GROUND BRANCH CONNECTION LEADING TO FAILURE OF THE WELDED BRAN | 2200000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
936 | 1994-05-30 | IA | maintenance | WRIGHT | NORTHERN NATURAL GAS CO (ENRON) | HOT SPOT PROTECTED WITH ANODES | 70000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
937 | 1994-08-01 | TX | maintenance | CLAY | SAGINAW PIPELINE COMPANY, L.C. | SUSPECTED LEAK REPORTED BY AERIAL FLYOVER | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
938 | 1994-08-12 | TX | maintenance | CLAY | SAGINAW PIPELINE COMPANY, L.C. | AERIAL FLYOVER REPORTED SUSPECTED LEAK. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
939 | 1994-09-25 | NM | technical failure | BERNALILLO | GAS CO OF NEW MEXICO | CONSTRUCTION EMPLOYEES MAKING TAP ON PIPELINE, VAPORS FROM THE PIPELINE FILLELINE WAS BEING RETIRED. ON 09/25/94 FOUTZ 7 BURSUM (CONTRACTOR WORKING FOR GCD THE BELLHOLE. WHEN WELDERS STARTED WELDING, THE VAPORS IGNITED IN FLASH FIRNM) WAS RETIRING A 16" T | 647 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
940 | 1994-08-29 | TX | other | CHAMBERS | MID CON TEXAS PIPELINE CORP | A BARGE SET A STABILIZING LEG ON THE PIPELINE. | 66500 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
941 | 1994-09-07 | NY | maintenance | ERIE | NATIONAL FUEL GAS DISTRIBUTION CORP | ON 09/07/1994, AT 4:36 P.M., LINE C-46 RUPTURED AND IGNITED. LINE IS STORAGELINE FOR COLDEN STORAGE. STORAGE WAS ON INJECTION AT 897 PSIG. NATIONAL FUELNOTIFIED AT 4:40 P.M. RESPONDED, SHUTTING VALVE TZ56,CLOSING LINE DOWN. FIREOUT AT 5:18 P.M. ALL SECTIO | 111135 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
942 | 1994-09-03 | IL | maintenance | MORGAN | PANHANDLE EASTERN PIPELINE CO | FAILURE OCCURRED DUE TO LOCALIZED INTERNAL CORROSION. AN INVESTIGATION IS CURRENTLY UNDERWAY. | 47300 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
943 | 1994-08-26 | TX | other | THROCKMORTON | LONE STAR GAS CO | LONE STAR CREW WAS BACKFILLING A PIPELINE. THE TRACK OF A CATAPILLAR HIT THIS PIPELINE AND PUNCHED A HOLE IN IT. GAS IGNITED BURNING THE OPERATOR AND CATAPILLAR. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
944 | 1994-09-04 | LA | maintenance |  | TENNESSEE GAS PIPELINE CO | DURING PIGGING OPERATIONS, LEAK DISCOVERED BY SONAT CREW (BUBBLES AT SURFACE) | 200000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
945 | 1994-08-27 | MN | technical failure |  | NORTHERN NATURAL GAS CO (ENRON) | LONGITUDINAL SEAM FAILURE | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
946 | 1994-09-22 | IL | other | WAYNE | TRUNKLINE GAS CO | MALFUNCTION OF COMPRESSOR STATION EMERGENCY SHUT DOWN SYSTEM OPENNED BLOW-OFFS WITHOUT ISOLATING THE STATION YARD PIPING. | 123000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
947 | 1994-10-23 | WV | maintenance | RANDOLPH | COLUMBIA GAS TRANSMISSION CORP | THE RUPTURE OCCURRED AT A CORRODED AREA ON THE PIPE WHERE CATHODIC PROTECTIONCURRENT APPEARS TO HAVE BEEN SHIELDED BY A LARGE ROCK. THE FRACTURE MECHANISM EVALUATION IS NOT YET AVAILABLE FROM COLUMBIA'S METALLURGICAL CONSULTANT. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
948 | 1994-09-07 | TX | maintenance | MATAGORDA | VALERO TRANSMISSION CO | FIELD PERSONNAL HAD BEEN OUT 3 DAYS PRIOR TO 09/07/94. THERE WAS NO LEAK AT THAT TIME. WHEN THEY WERE OUT AGAIN ON 09/07/94, A PINHOLE LEAK, PROBABLY DUETO EXTERNAL CORROSION, WAS FOUND ON THE 3" RISER OFF THE 16" PORTION OF LINE#27. THE LEAK WAS REPAIRED | 40000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
949 | 1994-10-20 | TX | other | HARRIS | VALERO TRANSMISSION CO | AT APPROXIMATELY 10:45 A.M. ON OCTOBER 20, 1994, VALERO'S PEARLAND FIELD OPERATIONS OFFICE BECAME AWARE VIA RADIO AND TV NEWSCASTS OF AN INCIDENTS INVOLVING A POSSIBLE RUPTURE OF A COLONIAL PIPELINE IN THE VICINITY OF THE SAN JACINTO RIVER. BECOAUSE VALER | 800000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
950 | 1994-10-17 | NV | technical failure | WASHOE | PAIUTE PIPELINE CO | FAILURE OCCURRED AT THREADED CONNECTION ON VENT STACK. INCIDENT OCCURRED WHILE BLOWING-DOWN A TEMPORARY BY-PASS PIPE. VENT STACK FAILED AT THREADED CONNECTION. VENT PIPE HIT EMPLOYEE IN LEFT ARM AND LEG. EMPLOYEE REQUIRED OVER-NIGHT STAY IN HOSPITAL. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
951 | 1994-10-10 | AR | other | HEMPSTEAD | ARKLA ENERGY RESOURCES | CONTRACTOR LAYING PHONE CABLE HIT NGT'S LINE AM-46,14" OD. PIPELINE ROW WAS CLEARLY MARKED. TELEPHONE COMPANY'S CONTRACTOR WAS OFF OF THEIR ASSIGNED ROW.COVER ON PIPELINE WAS OVER 36", A METER STATION WAS CLEARLY VISIBLE A POINT WERE CONTRACTOR DEVIATED F | 25000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
952 | 1994-11-16 | MO | other | CASS | WILLIAMS NATURAL GAS CO | DOZER HIT PIPELINE WHILE WORKING IN AREA. | 17000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
953 | 1994-10-27 | LA | other |  | COLUMBIA GULF TRANSMISSION CO | NO REMARKS. SUPPLEMENTAL REPORT 1/31/95 INDICATES CHANGE IN PART 3 -MARRATIVE DESCRIPTION. TEXAS EASTERN TRANSMISSION CORPORATION'S 16" GRIPPERINTERCONNECTION FAILED RESULTING IN DAMAMGE TO COLUMBIA'S 6" PIPELINE AT THETIE-IN POINT. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
954 | 1994-11-21 | MS | other | PERRY | FLORIDA GAS TRANSMISSION CO | PIPELINE HIT BY BULLDOZER BLADE WHILE CONSTRUCTING EROSION TERRACES OVER PIPELINE RIGHT OF WAY. | 75000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
955 | 1994-07-21 | WV | maintenance | KANAWHA | CABOT OIL & GAS CORP | THE PIPELINE WAS SUBMERGED IN A CREEK CROSSING AND OVER THE YEARS DEBRISHITTING THE PIPE HAD DAMAGED THE COATING CAUSING LOCALIZED CORROSION. ON JULY21, 1994 WHILE TESTING TO ESTABLISH A NEW MAOP ON PIPELINE #A-30, A SECTION OFPIPE THAT RUNS THROUGH KELLY | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
956 | 1994-11-29 | TX | other | DALLAS | LONE STAR GAS CO OF TEXAS, INC | CONTRACTOR INSTALLING NATURAL GAS DISTRIBUTION MAIN HIT PIPELINE WITH A TRENCHING MACHINE. | 43000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
957 | 1994-12-04 | LA | technical failure | TANGIPAHOA | FLORIDA GAS TRANSMISSION CO |  | 52000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
958 | 1994-11-11 | TX | other | CASS | NATURAL GAS PIPELINE CO OF AMERICA | NATURAL GAS WAS BLOWING FROM THE VENT OF A CASED CROSSING. THE CARRIER PIPEWAS REMOVED AND REPLACED WITH PRETESTED PIPE. BECAUSE HYDROTESTING FAILED TOID ENTIFY THE SOURCE OR CAUSE OF THE LEAK, THE CARRIER PIPE WAS RETIRED. | 110941 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
959 | 1994-12-02 | LA | other |  | TENNESSEE GAS PIPELINE CO | JACK-UP RIG, IN APPARENT EMERGENCY LOWERED A LEG AND SET DOWN ON 16IN. TGP PIPELINE, CAUSING RUPTURE AND SUBSEQUENT FIRE. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
960 | 1994-11-20 | TX | other |  | TRANSCO GAS PIPELINE CORP | A TUG TOWING A SEMI-SUBMERSIBLE RIG IN THE GALVESTON 237 AREA, EXPECTING BADWEATHER, SAT THE RIG ON THE BOTTOM. THE RIG SAT DOWN ON THE 12" PIPELINE DRIVING IT 6 FEET INTO THE MUD AND SEVERING THE LINE. | 390000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
961 | 1994-11-15 | TX | other | ANDERSON | LONE STAR GAS CO OF TEXAS, INC | DAMAGE BY ROAD GRADER. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
962 | 1994-12-20 | CO | other | ADAMS | COLORADO INTERSTATE GAS CO | CIG'S PIPELINE NUMBER 2B-20" RUPTURED AT 3:08 AM ON 12/20/94; THE RUPTUREEXTENDED FOR APPROXIMATELY 36 FEET ALONG THE PIPE. ESCAPING NATURAL GASIGNITED AND, IN ADDITION TO THE FORCE OF THE RUPTURE, SERIOUSLY DAMAGED CIG'SGRIMM AND FIRST CREEK METER STATIO | 467000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
963 | 1994-12-16 | TX | other |  | TRANSCO GAS PIPELINE CORP | THE RUPTURE ON THE 12" PIPELINE WHICH OCCURRED ON DECEMBER 16, 1994 AT M.P.22.786 WAS CAUSED BY THE SAME OUTSIDE PARTY DAMAGE THAT CAUSED THE RUPTURE OFTHE 12" PIPELINE AT M.P.22.75 WHICH WAS REPORTED TO THE NATIONAL RESPONSECENTER ON NOVEMBER 20, 1994 (R | 250000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
964 | 1994-12-15 | AK | maintenance |  | ENSTAR NATURAL GAS CO | 10 FOOT SECTION OF PIPE CUT OUT AND REPLACED FOR PERMANENT REPAIR. COATINGDAMAGED DURING CONSTRUCTION. LOCALIZED CORROSION CAUSED PITTING TO OCCUR. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
965 | 1994-12-20 | OK | maintenance | NOBLE | WILLIAMS NATURAL GAS CO | FAILED JOINT BLEW OUT - SENDING PIPE SPECIMEN FOR ANALYSIS. FURTHERCLASSIFICATION OF PART 2 - APPARENT CAUSE - STATES THAT THIS FAILURE IS UNDERINVESTIGATION. SUPPLEMENTAL REPORT 3/27/1995 INDICATES THAT FURTHERINVESTIGATION CHANGED CAUSE TO CORROSION (IN | 80000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
966 | 1995-01-01 | AL | other |  | EXXON CO USA | ON DECEMBER 28, 1994, BUBBLES WERE OBSERVED PERCOLATING NEAR THE PIPELINESWHICH TRAVERSE BETWEEN EXXON'S "A" PLATFORM IN MOBILE BLOCK 62 AND THE SSTILOCATED IN THE SAME BLOCK. DUE TO SEA CONDITIONS AND THE SIZE OF THE BUBBLES,THE BUBBLES WERE UNABLE TO BE | 210000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
967 | 1995-01-19 | LA | maintenance |  | ARAN ENERGY CORPORATION | EXTERNAL CORROSION OVER TIME. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
968 | 1994-12-12 | LA | other |  | HALL-HOUSTON OIL COMPANY | NO ONE WITNESSED INCIDENT. REPORT INDICATED ANCHOR DRAGGED ACROSS PIPELINE SEGMENT. PART B - TYPE OF MARKING- AS-BUILT WAS SUBMITTED TO NOAA FOR MAPPING & PIPELINE BURIED ACCORDING TO DOT/DOI REGULATIONS. | 417975 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
969 | 1995-01-08 | TX | other |  | DALEN RESOURCES OIL & GAS CO. | PIPE APPEARED TO DEVELOP SPLIT 1/2" X 1/16" ON TOP SIDE. SUSPECT POSSIBLE DEFECTIVE PIPE. LEAK REPAIRED WITH CLAMP | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
970 | 1995-01-09 | AL | other |  | EXXON CO USA | ON JANUARY 9, 1995 WHILE PERFORMING MAINTENANCE WORK ON THE 10" PRODUCED GASPIPELINE FROM MOBILE BLOCK 62 "A" TO MOBILE BLOCK 62 SSTI, DIVERS DISCOVEREDBUBBLES PERCOLATING FROM THE SEALANT INJECTION PORT ON THE BALL VALVE. THEREWAS NO POLLUTION AS A RESUL | 110000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
971 | 1995-01-24 | LA | technical failure |  | TRANSCO GAS PIPELINE CORP | THE HYDROCOUPLE END CONNECTOR SLIPPED OFF THE END OF THE 12" PIPELINE DURINGAN ABNORMAL PRESSURE CONDITION. THEIS ABNORMAL PRESSURE CONDITION DID NOT EXCEED THE MAOP OF THE PIPELINE. | 255000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
972 | 1995-01-31 | FL | other | ALACHUA | FLORIDA GAS TRANSMISSION CO |  | 29000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
973 | 1995-02-01 | TX | maintenance |  | ENRON OIL & GAS CO | CORROSIVE SPOT ON DEPARTING LINE (LOCALIZED ) DEVELOPED SMALL HOLE. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
974 | 1995-02-07 | WV | other | LOGAN | COLUMBIA GAS TRANSMISSION CORP | THIRD PARTY CONTRACTOR DOZER PUNCTURED COLUMBIA'S PIPELINE WHILE CLEARINGINTERSECTING RIGHT-OF-WAY FOR ANOTHER OPERATOR'S NEW PIPELINE CONSTRUCTIONPROJECT. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
975 | 1995-02-23 | PA | technical failure | CLINTON | CNG TRANSMISSION CORP | SPECULATION PENDING FINAL ANALYSIS | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
976 | 1995-02-25 | MI | technical failure | MANISTEE | BASIN PIPELINE CORP | ADDITIONAL INFORMATION IS BEING COLLECTED TO ALLOW DETERMINATION OF THE CAUSE OF THE FAILURE. GASKET FAILED IN INSULATING FLANGE AT PIG RECEIVER WHILE PUMPING METHANOL INTO LINE TO REMOVE HYDRATE PLUG. GASKET FURNISHED BY NATIONALOILWELL IN FLANGE INSULAT | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
977 | 1995-03-19 | LA | other | ST HELENA | TRANSCO GAS PIPELINE CORP | SIZE, SHAPE, AND SEVERITY OF THE GOUGE (44") INDICATES IT WAS CAUSED BY ALARGE PIECE OF EXCAVATION EQUIPMENT (PROBABLY) A BACKHOE. FAILURE INITIATED INA GOUGE OF UNKNOWN ORIGIN. | 619000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
978 | 1995-03-14 | LA | maintenance | CAMERON | MOBIL EXPLORATION & PRODUCING US INC | EXTERIOR SURFACE OF PIPE WAS FREE AND CLEAR OF ANY SIGNS OF EXTERNAL CORROSION. PIPE-TO-SOIL READING AT THIS LOCATION WAS -1.053 VDC. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
979 | 1995-03-06 | WA | other | COWLITZ | NORTHWEST PIPELINE CORP |  | 719000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
980 | 1995-04-12 | CA | other | LOS ANGELES | CHEVRON PIPELINE CO | THE INCIDENT OCCURRED AT 1340 PST ON MARCH 6, 1995 IN A REMOTE AREA AT MILEPOST 1272. 7 NEAR CASTLE ROCK WASHINGTON. THE FAILURE OCCURRED ON NORTHWEST PIPELINE CORPORATION'S 26 INCH IGNACIO, COLORADO TO SUMAS, WASHINGTON MAINLINE.IN THE ACCIDENT AREA THE | 5000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
981 | 1995-03-24 | IA | technical failure |  | NORTHERN NATURAL GAS CO (ENRON) | SUPPLEMENTAL REPORT WILL FOLLOW WHEN FAILURE CAUSE IS KNOWN.FAILURE THROUGH A 4" BRANCH CONNECTION ON 26" PIPE. EXACT CAUSE OF FAILURE NOT KNOWN YET. | 75000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
982 | 1995-03-27 | NC | other | MECKLENBURG | PIEDMONT NATURAL GAS CO INC |  | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
983 | 1995-04-19 | CA | other | VENTURA | SOUTHERN CALIFORNIA GAS CO | ON APRIL 19, 1995, AT APPROXIMATELY 5:05 P.M., A LARGE MUD SLIDE IN BIG VCANYON CAUSED THE SOUTHERN CALIFORNIA GAS COMPANY'S 116" TRANSMISSION LINE1003 TO RUPTURE IN THE BOTTOM OF THE CANYON. COMPANY PERSONNEL WEREIMMEDIATELY DISPATCHED TO IDENTIFY THE LO | 150000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
984 | 1995-04-17 | OK | other | OKLAHOMA | WILLIAMS NATURAL GAS CO | A GAS DETECTOR SENSOR MALFUNCTIONED AND ACTIVATED THE EMERGENCY SHUT DOWN SYSTEM. OUR SCADA SYSTEM INDICATED THAT THE INTAKE VALVE DID NOT CLOSE COMPLETELY. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
985 | 1995-04-08 | KS | maintenance | COWLEY | WILLIAMS NATURAL GAS CO | HOT SPOT SURVEY - COUPLED LINE | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
986 | 1995-03-31 | ID | technical failure | ELMORE | NORTHWEST PIPELINE CORP | THREE QUARTER INCH SPLIT LONGITUDINAL SEAM. SPLIT CLOSED WHEN PRESSURE WASREDUCED DELAYING LEAK IDENTIFICATION AND REPORTING. REPAIRS WERE MADE BYREPLACING 73 FEET OF PIPE DURING STOPPLE BYPASS OPERATION TO MAINTAINCONTINUITY OF SERVICE. SPLIT IN LONG SEA | 303000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
987 | 1995-04-25 | LA | technical failure |  | TRANSCO GAS PIPELINE CORP | THE CLAMP ON THE MID RISER CONNECTOR ASSEMBLY ON THE 16" RISER FAILED. | 250000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
988 | 1995-04-19 | MS | technical failure | JEFFERSON DAVIS | SOUTHERN NATURAL GAS CO | TURBINE UNIT WAS PRESSURE TESTED BY THE MANUFACTURER PURSUANT TO INDUSTRYDESIGN SPECIFICATION APPLICABLE AT THE TIME OF MANUFACTURING.SOLAR T1001S-15SATURN TURBINE NATURAL GAS COMPRESSOR ENGINE RATED @1080 HORSEPOWER. A FIREOCCURED IN A TURBINE COMPRESSOR | 750000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
989 | 1995-05-19 | TN | other | WASHINGTON | EAST TENNESSEE NATURAL GAS CO | THUNDER STORM WITH HEAVY LIGHTNING MOVED THROUGH THE AREA JUST BEFORE FIRE WAS REPORTED. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
990 | 1995-06-02 | CA | other | CONTRA COSTA | PACIFIC GAS & ELECTRIC CO | VANDAL ENTERED REGULATION FACILITY BY SCALING FENCE. OPERATED 14 VALVES THATWERE LOCKED IN POSITION BY CHAINS. RELIEF VALVE OPENED DUE TO OVERPRESSURE ASA RESULT OF VALVE CHANGES. GAS RELEASED THROUGH RELIEF VALVE WAS IGNITED BY VANDAL, RESULTING IN INJUR | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
991 | 1995-06-27 | WV | maintenance | KANAWHA | COLUMBIA GAS TRANSMISSION CORP | LOCAL SUPERVISOR RESPONDED TO VERIFY A LEAK CALLED IN BY NEARBY RESIDENT. PIPE RUPTURED WHILE SUPERVISOR WAS RETURNING TO OFFICE. EMERGENCY ACTION INCLUDED ISOLATING AREA AND EVACUATING THREE RESIDENTS. ISOLATION COMPLETED BY 1900HOURS. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
992 | 1995-06-25 | MN | other | MILLE LACS | VIKING GAS TRANSMISSION CO | WELDER'S HELPER RECEIVED FLASH BURN WHEN GRINDING WELD BEVEL ON 24" PIPE. ONSUNDAY, JUNE 25, 1995 APPROXIMATELY 12:45 P.M., EARL STEINBRENNER (CONTRACTWELDERS HELPER) WAS GRINDING A BEVEL ON A 24" NATURAL GAS PIPELINE. THE BEVEL WAS ON THE OPEN END OF THE | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
993 | 1995-04-25 | CA | other | MONTEREY | PACIFIC GAS & ELECTRIC CO | THE THIRD-PARTY WAS WORKING AND STRUCK THE LINE AT A LOCATION 3,000 FEET AWAY FROM WHERE THEY SAID THE WERE GOING TO BE WORKING. A FARMER PLOWING A FIELDSOUTH OF GREENFIELD STRUCK A GAS TRANSMISSION MAIN WITH A RIPPER. SERVICE WASDISRUPTED TO APPROXIMATEL | 270000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
994 | 1995-06-02 | TX | other | TRAVIS | LONE STAR GAS CO | LINE P DAMAGED FROM FLOOD WATERS OF THE COLORADO RIVER CAUSING RUPTURE AT BOTH ENDS OF THE RIVER CROSSING. | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
995 | 1995-06-16 | CO | other | MORGAN | YOUNG GAS STORAGE COMPANY., LTD. | GAS ESCAPED FROM THE BODY CAVITY VENT OF A 16", ANSI CLASS 900 BALL VALVE ASTHE VALVE WAS BEING OPENED DURING ROUTINE MAINTENANCE. THE GAS IGNITED AND BURNED AN EMPLOYEE WHO WAS ATTEMPTING TO STOP THE FLOW OF GAS BY CLOSING THE 16" VALVE. INVESTIGATION DE | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
996 | 1995-07-01 | IL | maintenance | JOHNSON | TRUNKLINE GAS CO | ISOLATED CORRODED AREA WAS SMALL ENOUGH SO AS NOT TO BE READILY IDENTIFIABLEWITH CLOSE INTERVAL CATHODIC PROTECTION SURVEY EQUIPMENT AND TECHNIQUES AVAILABLE TODAY. NO OTHER CORROSION OBSERVED. PIPELINE CAME TO REST ON A ROCK LEDGE WHICH DAMAGED THE COA | 1750000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
997 | 1995-06-28 | ID | technical failure | BEAR LAKE | NORTHWEST PIPELINE CORP | LABORATORY ANALYSIS IDENTIFIED THE ORIGIN OF THE FAILURE AS A LONGITUDINAL GOUGE, .150" DEEP AND ONE FOOT IN LENGTH LOCATED IN THE 5:00 POSITION OF THE PIPE. THE LONG SEAM WAS LOCATED IN THE 6:00 POSITION. THE GOUGE WAS THE RESULT OF MECHANICAL DAMAGE M | 700000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
998 | 1995-06-27 | LA | maintenance |  | TENNESSEE GAS PIPELINE CO | UNKNOWN FACTORS - SUSPECTED INTERNAL CORROSION | 226000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
999 | 1995-05-30 | TX | other | HIDALGO | TECO GAS GATHERING COMPANY | ON MAY 30, 1995, AT APPROXIMATELY 2200 HOURS, TECO PIPELINE COMPANY RECEIVEDAN EMERGENCY CALL FROM TEXAS ONE CALL CONCERNING A FIRE NEAR OUR PIPELINE. TECO PERSONNEL IMMEDIATELY RESPONDED AND UPON ARRIVAL DISCOVERED A FIRE AT OUR METER STATION NEAR HARGI | 139250 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1000 | 1995-07-01 | OH | other | MUSKINGUM | NATIONAL GAS & OIL CORP | ON JULY 1, 1995, A FIRE OCCURED AT AN UNATTENDED NATIONAL GAS & OIL CORPORATION STORAGE COMPRESSOR STATION DAMAGING A METAL BUILDING AND ENGINE/COMPRESSOR. A ONE INCH PIPE FITTING LOCATED ON THE COMPRESSOR FAILED RELEASING GAS INTO THE BUILDING THAT WAS | 285000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1001 | 1995-07-22 | OK | other | WOODS | ONG TRANSMISSION CO | LIGHTNING STRUCK GAS PURCHASE METER SETTING RESULTING IN A FIRE WHICH DESTROYED VARIOUS PIECES OF PRODUCTION EQUIPMENT. | 65000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1002 | 1995-07-31 | MS | other | ALCORN | COLUMBIA GULF TRANSMISSION CO | THE PRECISE MECHANISM AND ROOT CAUSE OF THIS FAILURE REMAINS UNDETERMINED. APPARENTLY, NUMBER 5 TURBINE AND COMPRESSOR LUBE OIL SYSTEM SHUT DOWN DUE TO ANUNDETERMINED FAULT. SUBSEQUENTLY, THE SEAL OIL DRAINED THROUGH THE COMPRESSOR SEALS, WHICH CAUSED THE | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1003 | 1995-07-22 | LA | technical failure | VERMILION BLOCK 96 | COLUMBIA GULF TRANSMISSION CO | LEAK OCCURRED AT FILLET WELD ON THE 6" LEG OF 6" X 36 EXTRUDED STRONGBACK ENCIRCLEMENT SADDLE AT UNDERSEA HOT TAP TIE IN CONNECTION. PIN HOLE LEAK AT 12:00 POSITION ON FILLET WELD. EXACT LEAK MECHANISM HAS NOT BEEN DETERMINED. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1004 | 1995-07-07 | KS | other | LYON | PANHANDLE EASTERN PIPELINE CO | FIVE SCC CRACKS, LINEARLY ALIGNED, LINKED TOGETHER TO FORM A FLAW APPROXIMATELY FOUR (4) INCHES LONG RESULTING IN THE RUPTURE. | 220000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1005 | 1995-08-12 | TX | other | LIBERTY | PRAXAIR, INC | DAMAGE CAUSES BY FIRE FROM OUTSIDE SOURCE AS A RESULT OF CAR ACCIDENT. A CARIS ENGULFED IN FLAMES AND BLACK SMOKE AFTER A GAS LINE EXPLODED EARLY SATURDAY ALONG FM 563 SOUTH OF LIBERTY. THREE PEOPLE WERE INJURED IN THE EXPLOSION.OFFICIALS ALSO EVACUATED F | 25000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1006 | 1995-09-13 | WV | other | LOGAN | COLUMBIA GAS TRANSMISSION CORP | PRELIMINARY INVESTIGATION INDICATES THE PIPELINE WAS DAMAGED BY A COAL STRIPPING OPERATOR'S DOZER TRACK TURNING AROUND IN WET, SOUPY DRAINAGE DITCH LOCATION ON THE PIPELINE RIGHT-OF-WAY. CRACK PROPOGATION IN THE RESULTING DENT/GOUGE AREA CAUSED THE RUPTUR | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1007 | 1995-08-15 | TX | maintenance | GREGG | TRIDENT NGL PLANT | CORROSION COUPONS AT PLANT INLET SHOWED NO SIGNIFICANT CORROSION. | 10000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1008 | 1995-08-24 | TX | other |  | CHEVRON PIPELINE CO | TWO CHEVRON U.S.A. PRODUCTION CO., INC. OPERATORS WERE IN THE PROCESS OF OPENING A PIG LAUNCHER ON A 16" PIPELINE OWNED BY CHANDELEUR PIPLINE COMPANY, A WHOLLY OWNED SUBSIDIARY OF CHEVRON PIPE LINE COMPANY. THE PIG LAUNCHER WAS LOCATED ON CHEVRON U.S.A. P | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1009 | 1995-09-25 | KY | other | FLOYD | COLUMBIA GAS TRANSMISSION CORP | COAL OPERATOR'S DOZER GOUGED 2 FOOT HOLE IN PIPELINE WHILE WORKING HAUL ROADFOR STRIPPING OPERATIONS. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1010 | 1995-09-01 | LA | other |  | TRUNKLINE GAS CO | DAMAGE CAUSE UNKNOWN - CRACK IN 1/2" NPT NIPPLE EXTRA HEAVY. NIPPLE AND VALVEWAS BLEEDER ASSEMBLY ON HYDROTECH REPAIR CLAMP. CAUSE OF INCIDENT IS UNKNOWN.DUE TO UNDERWATER LOCATION AND NO VISIBLE POLLUTANT, VERIFICATION OF LEAK ONLINE 1004-B-1100 WAS NOT | 150000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1011 | 1995-09-29 | PA | other | YORK | COLUMBIA GAS TRANSMISSION CORP | EXCAVATION CONTRACTOR OPERATING A RIPPER ON A BULLDOZER IN EARTH MOVING OPERATION STRUCK LINE., ONE 200' +/- NORTH, ONE 229' +/- SOUTH. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1012 | 1995-09-27 | TX | maintenance | HARRIS | EASTEX GAS TRANSMISSION CO | 6" GAS LINE WAS BEING UTILIZED AS A FLOWLINE FROM PRODUCING WELL (OIL-SALTWATER) SAMPLES OF SALTWATER FROM LINE INDICATED REASON FOR CORROSION. | 3500 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1013 | 1995-10-04 | LA | other |  | SOUTHERN NATURAL GAS CO | SHEAR JOINT (INSTALLED ON PIPELINE IN 1993) SEPARATION CAUSED BY MUDSLIDE DURING HURRICANE OPAL. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1014 | 1995-10-06 | TX | other |  | ANR PIPELINE CO | PIPELINE WAS STRUCK BY 1" CABLE THAT WAS DRAGGED OVER OUR 12" LATERAL LINE. | 150000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1015 | 1995-10-03 | LA | other |  | TEXAS EASTERN GAS PIPELINE CO | TEXAS EASTERN SUBSEA TAP VALVE ASSEMBLY MUST BE REPLACED. BOAT ANCHORS PULLEDA 6" PIPELINE, OWNED BY UNITED MERIDIAN CORPORATION, AWAY FROM ITSCONNECTION TO TEXAS EASTERN DURING HURRICANE OPAL, RESULTING IN THE LOSS OFGAS IN THE TEXAS EASTERN PIPELINE. (B | 980000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1016 | 1995-10-23 | LA | other |  | VASTAR RESOURCES, INC. | AFTER UNSUCCESSFUL ATTEMPT TO PRESSURE UP LINE, LEAK WAS NARROWED DOWN BY BOATBY LOCATING BUBBLES. SUBSEQUENTLY, A SIDE SCAN SONAR AND MAGNETOMETER SURVEYWERE CONDUCTED- BREAK IS AT X=2,771, 360 AND Y=192,090.LINE PARTED DUE TO AMUD SLIDE IN THE VICINITY | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1017 | 1995-10-14 | TX | other | PECOS | INTRATEX GAS CO | IN THE PROCESS OF RETURNING THE 30" SUCTION VALVE TO SERVICE, THE TECHNICIANHOOKED UP THE ELECTRICAL CONNECTION TO THE VALVE ACTUATOR AND PROCEEDED TO OPEN THE VALVE, BUT THEN THE ELECTRICAL CONNECTION FAILED, CAUSING THE PILOT GAS VALVE TO VENT A SMALL Q | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1018 | 1995-10-28 | TX | other | BROOKS | VALERO TRANSMISSION CO | THE CENTER BOLT THAT RETAINS THE VALVE CHAIR LOOSENED AND PERMITTED GAS TO ESCAPE AND IGNITE. THE ESD SYSTEM ACTIVATED AND EXTINGUISHED THE FIRE. | 45000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1019 | 1995-10-21 | TX | technical failure | JEFFERSON | HOUSTON PIPELINE CO | SMALL CRACK IN CIRCUMFERENTIAL WELD. | 5000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1020 | 1995-10-25 | TX | other | CHAMBERS | TEJAS GAS PIPELINE COMPANY | A CONTRACTOR WAS EMPLOYED BY THE OPERATOR TO MOW THE PIPELINE RIGHT-OF-WAY. THE MOWER STRUCK AN EXPOSED SEGMENT OF PIPELINE IN THE BOTTOM OF A ROAD DRAINAGE DITCH. PIPE WAS NOT VISIBLE DUE TO PRESENCE OF VEGETATION BEING MOWED. | 24000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1021 | 1995-04-18 | TX | technical failure | REEVES | WEST TEXAS GAS INC | PIPE JOINT WOULD PROBABLY NOT HAVE FAILED IF DELHI RELIEF VALVES HAD PROPERLYOPERATED.ANALYSIS REVEALED INTERNAL STRESS LINES IN LINE WITH THE STEP WISEFLOW ON THE PIPE JOINT. EXCESS PRESSURE ON PIPELINE DUE TO FAILURE OF RELIEFVALVES ON DELHI PIPELINE. | 10000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1022 | 1995-12-06 | AL | other | JACKSON | MARSHALL COUNTY GAS DISTRICT | OKADEE 4" GATE VALVE LEAKING THROUGH SLIGHTLY (<1PSI). ATTEMPTING TO CHANGE OUT A 4" AXIAL FLOW WITH AN IMPACT WRENCH. LOW OVERCAST, LOW BAROMETRIC PRESSURE, LOW WIND, TYPE OF DAY. EMPLOYEES WERE ATTEMPTING TO IMPACT REMOVE THE LAS BOLT WHEN IGNITION OCCU | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1023 | 1995-11-23 | LA | other |  | TEXAS EASTERN GAS PIPELINE CO | OCCURRED IN OUTER CONTINENTAL SHELF, OFFSHORE LOUISIANA. A SHRIMPING NET PULLED A PRODUCER'S 6" LATERAL LOOSE FROM TEXAS EASTERN'S 30" LINE 41-A-7 TAP ASSEMBLY CAUSING A LOSS OF NATURAL GAS IN LINE 41-A-7. | 250000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1024 | 1995-12-13 | TN | other | RUTHERFORD | UNITED CITIES GAS CO | SECTION OF PIPE DAMAGED WAS NOT MARKED. SECTION THAT WAS DAMAGED WAS STUBOUT LEFT FROM LAST RELOCATION TO SERVE FARM TAP. WAS NOT MARKED BY LOCATOR. HE WAS NOT AWARE OF THIS SECTION. TRACK-HOE HIT 4" STEEL LINE CAUSING LINE CUT. | 25000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1025 | 1995-12-09 | MA | other | BRISTOL | ALGONQUIN GAS TRANSMISSION CO | GENERAL AREA OF INCIDENT WAS ON-GOING SHOPPING CENTER DEVELOPMENT. AT TIME OFINCIDENT OPERATOR WAS GRADING ADJACENT TO ROW UNDER CONTRACTOR DIRECTION. EQUIPMENT OPERATOR DECIDED ON HIS OWN TO EXTEND WORK INTO ROW. AGREED UPON NOTIFICATION WAS NOT GIVEN TO | 320000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1026 | 1996-01-06 | PA | maintenance | MONROE | COLUMBIA GAS TRANSMISSION CORP | THERE ARE INDICATIONS THAT CATHODIC PROTECTION CURRENT SHIELDING FROM SHALE ROCK RESULTED IN LOCALIZED PITTING AND PIPE WALL LOSS TO A POINT WHERE A COMBINATION OF DUCTILE AND BRITTLE FRACTURES OCCURRED RESULTING IN A RUPTURE OF THE PIPE. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1027 | 1995-12-21 | CO | technical failure | ELBERT | COLORADO INTERSTATE GAS CO | MATERIAL DEFECT IN PIPE DUE TO FAULTY MANUFACTURING PROCESS. CIG'S PIPELINE NO. 2B-20" RUPTURED AT 12:45PM ON 12/21/95 IN RURAL EASTERN COLORADO. THE RUPTURE EXTENDED FOR APPROXIMATELY 133 FEET ALONG THE PIPE; ESCAPING NATURAL GASDID NOT IGNITE. THERE WER | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1028 | 1995-12-10 | LA | other |  | SOUTHERN NATURAL GAS CO | MUDSLIDE AT TIE-IN OF MAIN PASS BLOCK 72 PIPELINE IN MAIN PASS BLOCK 151 SEPARATED "BREAKWAY" JOINT. TAP COORDINATES ARE 2911.6, 8,852.6. | 280000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1029 | 1996-01-07 | TX | technical failure | PANOLA | KOCH GATEWAY PIPELINE COMPANY | THE CAUSE OF THE RUPTURE HAS NOT YET BEEN CONFIRMED. THE PIPE IS TO BE ANALYZED BY METTALLURIGICAL CONSULTANTS INC. SINCE THE RUPTURE OCCURRED IN THE LONGITUDINAL SEAM OF THE PIPE, A MATERIAL DEFECT IS SUSPECTED. A SUPPLEMENTAL REPORT WILL BE FILED. | 138035 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1030 | 1995-12-22 | TX | other | BRAZORIA | ARCO PIPE LINE CO | WEATHER CONDITIONS INCLUDING MUD AND WATER, QUESTIONABLE INTERGITY OF EXISTING UNDERGROUND PIPING (CONDUCTING TEST) LOCATION OF BARRICADE FENCE, DRESSER TD-4 H DOZER | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1031 | 1996-01-12 | OK | other | OKLAHOMA | ENOGEX INC (EX. MUSTANG FUEL CORP) |  | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1032 | 1996-01-14 | IL | maintenance | FAYETTE | NATURAL GAS PIPELINE CO OF AMERICA | UNDER INVESTIGATION. WILL BE FILING SUPPLEMENTAL. SUPPLEMENTAL RECEIVED 4/22/96 INDICATES CHANGE IN CAUSE FROM OTHER TO CORROSION. PIPE WAS USED UNDER CONDITIONS WHERE GAS WAS WET. THIS PROMOTED INTERNAL CORROSION OF THE LONGITUDINAL SEAM. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1033 | 1996-01-10 | LA | other | JEFFERSON | SOUTHERN NATURAL GAS CO | PIPELINE RUPTURED AND GAS IGNITED. CAUSE UNKNOWN AT THIS TIME. SUPPLEMENTALREPORT FILED 6/10/1996 UPDATES CAUSE TO DAMAGE BY OUTSIDE FORCES, ANDINCREASES PROPERTY DAMAGE TO $372,000, PER ERIC E. THOMAS. COMMENTS STATETHAT ALTHOUGH THE CAUSE OF THE RUPTURE | 372000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1034 | 1996-01-12 | MS | other | WASHINGTON | TEXAS GAS TRANSMISSION CORP | ON JANUARY 12, 1996, AT APPROXIMATELY 8:26 P.M. A RELIEF VALVE LOCATED APPROXIMATELY 10 MILES SOUTH OF GREENVILLE, MISSISSIPPI, OPENED ON TEXAS GAS 26-INCH, NO.1 LINE. THE RELIEF VALVE IS INSTALLED TO PROVIDE OVERPRESSURE PROTECTION ON TWO SECTIONS OF THE | 104000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1035 | 1995-12-26 | IN | technical failure | ST JOSEPH | TRUNKLINE GAS CO | DURING THE REMOVAL OF THE FAILED WELD, THE PIPE SEPARATED VERTICALLY BY SEVERAL INCHES NECESSITATING ADDITIONAL EXCAVATION FOR LINE UP SO AS TO MINIMIZE FUTURE RESIDUAL STRESS. GIRTH WELD FRACTURED FROM 9:00 TO 3:00 POSITION. PIPELINE APPEARED TO BE UNDER | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1036 | 1996-01-13 | MS | other | HANCOCK | KOCH GATEWAY PIPELINE COMPANY | PIPELINE WAS FOUND TO BE KINKED WITH A LARGE BOAT ANCHOR BENEATH THE PIPELINE. DAMAGE APPEARS TO HAVE BEEN CAUSED BY THE PIPELINE BEING HOOKED AND LIFTEDBY A LARGE BOAT ANCHOR. THE ANCHOR WAS ABANDONED AND IN CLOSE CONTACT WITH PIPELINE. THE PIPELINE WAS | 125000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1037 | 1996-01-18 | LA | other |  | TENNESSEE GAS PIPELINE CO | EVIDENCE INDICATES UNKNOWN OUTSIDE PARTY DAMAGED PIPE SEVERAL YEARS PRIOR TOTHE RUPTURE. SHELL PLATFORM AT E.I. - 18 CALLED GAS CONTROL AT 2:50 PM TO REPORT PRESSURE DROP FROM 1100 T0 200 PSI - ALSO LARGE BALL OF FIRE 2-5 MILES NEOF PLATFORM. D524 BEGAN C | 200000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1038 | 1996-01-19 | LA | other | CAMERON | ANR PIPELINE CO | THE ACCIDENTAL OVERTEMPERATURE OF LUBE OIL AND FUEL VALVE COMPONENTS BY THE BACKFLOW OF 900 DEGREE F. EXHAUST GASES DUE TO A FRACTURED 6TH STAGE BLEED AIRVALVE OUTLET FLANGE. EXHAUST GAS ESCAPING FROM THE 6TH STAGE BLEED AIR VALVEOUTLET DUCT IMPINGED ON A | 420000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1039 | 1996-01-26 | TX | other | ROBERTS | NORTHERN NATURAL GAS CO (ENRON) | WELDER ASSISTING DURING TACK WELDING OF 24" END CAP. WELDING ARC CAUSED ANDIGNITION. WELDER WAS HIT BY MOVING END CAP. CAUSE LISTED AS IGNITION. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1040 | 1996-01-23 | NY | other | NEW YORK | CONSOLIDATED EDISON CO OF NEW YORK | STEEL BEAM FOUND IN CONTACT WITH TOP BRACE USED FOR REINFORCEMENT OF A COMPRESSION COUPLING. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1041 | 1996-02-18 | OH | other | LAWRENCE | COLUMBIA GAS TRANSMISSION CORP | FAILURE SITE EVALUATION DETERMINED THAT A BRITTLE FRACTURE OCCURRED AT A WRINKLE BEND. THE RELEASE OF GAS IGNITED RESULTING IN MINIMAL COLLATERAL DAMAGE. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1042 | 1996-02-04 | AR | other |  | NORAM GAS TRANSMISSION | POWER LINE BREAK AT A ROAD CROSSING (HWY 50) DROPING ON TO NORAM VENT PIPE CAUSING AN ELECTRICAL CONNECTION WHICH ARCED FROM THE BURIED CASING ONTO THE CARRIER PIPE. THE ARCING BURNED THROUGH THE PIPE WALL CAUSING A LEAK WHICH IGNITED. THE FLAMES WERE RIS | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1043 | 1995-10-05 | LA | other |  | ARAN ENERGY CORPORATION | GAS LINE WAS SEVERED DURING AN APPARENT MUD SLIDE CAUSED BY HURRICANE OPAL. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1044 | 1996-02-06 | LA | other |  | SOUTHERN NATURAL GAS CO | 4 POINT DIVE BOAT WAS WORKING TO REPAIR AN ADJACENT P/L. WHILE SETTING ANCHORS, ONE OF THE ANCHOR CABLES SNAGGED VALVE IN MAIN PASS 77 LINE AND PULLED P/L APART AT A LOAD LIMITING CONNECTOR NEAR VALVE. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1045 | 1996-02-08 | PA | other | ALLEGHENY | THREE RIVERS PIPELINE | INCIDENT OCCURED APPROX 6 YEARS AFTER 3RD PARTY DAMAGE. DENT REDUCED WALL THICKNESS TO 0.200". IN ADDITION, POSSIBLE SETTLING STRESSES ASSOCIATED WIT IMPROPER SUPPORT AND THERMAL EXPANSION MAY HAVE CONTRIBUTED. | 31400 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1046 | 1996-02-22 | OH | other | TUSCARAWAS | EAST OHIO GAS CO | A BLOCKAGE OCCURRED IN TRANSMISSION PIPELINE (TPL) #5 DUE TO THE FREEZE-UP OF LIQUIDS WHICH HAD ACCUMLATED IN THE LINE. AS A RESULT OF THE BLOCKAGE, THE UPSTREAM SECTION OF THIS PIPELINE OVER-PRESSURIZED, AND A RUPTURE OCCURRED ATPIPE STATION 3107+31. | 200000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1047 | 1996-02-26 | LA | technical failure |  | COLUMBIA GULF TRANSMISSION CO | A MICARTA RING WAS REPLACED WITH A STAINLESS STEEL RING AND THE PIPELINE WASRETURNED TO SERVICE. A LEAK WAS DISCOVERED AT A SWIVEL FLANGE CONNECTING THESUB-SEA PIPELINE TO THE OFFSHORE PLATFORM | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1048 | 1996-02-26 | MO | other | JACKSON | MISSOURI GAS ENERGY | AN 18" CLAY TILE STORM SEWER HAD BEEN INSTALLED ACROSS THE TOP OF THE 26" GAS LINE AT THE POINT OF RUPTURE. INSTALLATION DATE OF THE STORM SEWER UNKNOWN. | 60000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1049 | 1996-02-28 | AL | other | CLEBURNE | SOUTHERN NATURAL GAS CO | VANDALS CUT LOCKED CHAINS OFF OF THE OPERATORS FOR THE 20" TALLAPOOSA GATE BLOCK VALVE AND THE TWO 6" BLOWOFF VALVES LOCATED ON EITHER SIDE OF THE BLOCK VALVE. THE VANDAL'S DID NOT ALTER THE POSITION OF THE 20" VALVE, WHICH WAS OPEN, BUT DID OPEN THE 6" B | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1050 | 1996-03-19 | LA | technical failure |  | ANR PIPELINE CO | ONE-INCH WIDE CRACK IN A GIRTH WELD RUNNING FROM THE 12'OCLOCK POSITION TOTHE 8 O'CLOCK POSITION. THE APPARENT CAUSE WILL NOT BE DETERMINED UNTIL AFTERTHE 30 DAY DEADLINE FOR REPORTING - A SUPPLEMENTAL REPORT WILL FOLLOW.SUPPLEMENTAL REPORT RECEIVED 2/21/ | 75000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1051 | 1996-04-13 | OK | other | CLEVELAND | ONG TRANSMISSION CO | HIGH SPEED VEHICLE ACCIDENT RESULTED IN ONE VEHICLE STRIKING METER AND REGULATOR SETTING. HIGH SPEED VEHICLE ACCIDENT RESULTED IN FOUR FATALITIES. ONE OFTHE VEHICLES HIT THE METER SETTING CAUSING GAS LEAK AND FIRE. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1052 | 1996-04-29 | FL | other | POLK | FLORIDA GAS TRANSMISSION CO | PIPELINE HIT BY THIRD PARTY WITH BACKHOE. | 69000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1053 | 1996-05-06 | FL | other | DADE | FLORIDA GAS TRANSMISSION CO | PIPELINE HIT BY THIRD PARTY WITH POST HOLE AUGER. | 116000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1054 | 1996-05-03 | MA | other | ESSEX | TENNESSEE GAS PIPELINE CO | A THIRD PARTY CONTRACTOR, NOT WORKING FOR TENNESSEE GAS, ACCIDENTALLY DUG INTO THE LINE WHILE WORKING IN A GRAVEL YARD. VENT MARKING AT RAILROAD CROSSING, APPROXIMATELY 432FT. UPSTREAM AND MARKING APPROXIMATELY 350FT. DOWNSTREAM. | 80000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1055 | 1996-05-10 | LA | technical failure | CAMERON PARISH | NATURAL GAS PIPELINE CO OF AMERICA | A PIN HOLE LEAK IN GIRTH WELD CAUSED GAS AND CONDENSATE TO ESCAPE. PRESSUREESSEL SLEEVE AND STRUCTURAL CLAMP SYSTEM INSTALLED. | 171388 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1056 | 1996-05-09 | WV | other | HARRISON | CNG TRANSMISSION CORP | HEAVY & CONSECUTIVE RAINS CAUSED GROUND TO SLIP WHICH RESULTED IN PIPELINE DEVELOPING A "WRINKLE BEND" RESULTING IN A LEAK. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1057 | 1996-05-25 | NY | other | SARATOGA | NIAGARA MOHAWK POWER CORP | PIPELINE WAS DAMAGED UNKNOWN YEARS AGO PREVIOUS TO INCIDENT AND NOT REPORTEDTO NIAGARA MOHAWK. FINAL VERIFICATION THAT DAMAGE CAUSED ULTIMATELY LED TO PIE FAILURE BEING PERFORMED BY BATTELLE MEMORIAL INSTITUTE. PRELIMINARY INVESTIGATION INDICATES DAMAGE B | 60000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1058 | 1996-06-05 | AL | maintenance | CLEBURNE | SOUTHERN NATURAL GAS CO | PRELIMINARY METALLURGICAL EXAMINATION INDICATES THAT STRESS CORROSION CRACKING IS MOST LIKELY OF THE LOW PH VARIETY. COATING AT THIS PARTICULAR POINT ON THE PIPELINE WAS POOR. HOWEVER, COATING ON ADJACENT PORTIONS OF THE PIPELINE WAS REPORTED TO BE GOOD. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1059 | 1996-05-20 | TX | other | SUTTON | VALERO TRANSMISSION CO | FORENSIC ENGINEERING AND METALLURGICAL EXPERTS ARE CURRENTLY REVIEWING THEINCIDENT TO DETERMINE THE CAUSE OF THE NATURAL GAS RELEASE AND FIRE. ASUPPLEMENTAL REPORT WILL BE FILED UPON COMPLETION OF THE INVESTIGATION. ASUPPLEMENTAL REPORT RECEIVED 1/24/97 I | 4000000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1060 | 1996-06-13 | MT | other | ROOSEVELT | WILLISTON BASIN INTERSTATE PIPELINE CO | ON JUNE 13, 1996, WILLISTON BASIN EMPLOYEES WERE COMPLETING A 3800 FOOT RELOCATION ON WILLISTON BASIN'S SACO TO MORGAN CREEK EIGHT INCH PIPELINE TO ACCOUMMODATE FUTURE HIGHWAY RECONSTRUCTION. THE RELOCATION PROJECT WAS NEARLY COMPLETE EXCEPT FOR THE TIE-I | 184000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1061 | 1996-05-21 | TX | other | HARDIN | TRUNKLINE GAS CO | #4025-B4 SUCTION EMERGENCY SHUT DOWN SYSTEM BLOWDOWN VALVE OPENED DUE TO A DEVICE FAILURE. | 86100 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1062 | 1996-06-19 | KY | technical failure |  | TENNESSEE GAS PIPELINE CO | COMPRESSOR ROD BROKE, DAMAGING THE PACKING, RESULTING IN THE RELEASE OF GAS INTO THE COMPRESSOR BUILDING. | 412500 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1063 | 1996-06-25 | LA | maintenance | UNION | NORAM GAS TRANSMISSION | FAILURE BEGAN FROM PIT ON BOTTOM OF PIE AND PROPAGATED VERTICALLY AROUND THECIRCUMFERENCE OF PIPE. | 22000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1064 | 1996-06-16 | OK | maintenance | HARPER | WILLIAMS NATURAL GAS CO | PIPE SEGMENT FAILURE ANALYST TO BE COMPLETED BY 07/30/96. GENERAL CORRISION OF WELD SEAM- FAILURE ANALYST NOT COMPLETED AS OF THIS DATE. | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1065 | 1996-06-24 | LA | other |  | TENNESSEE GAS PIPELINE CO | THE PIPELINE CROSSES BURRWOOD BAYOU. THIS BAYOU HAS ENLARGED FROM 100'WIDE AND 15' DEEP TO OVER 1100' WIDE AND 30' DEEP. THE LINE WAS SUSPENDED IN THE BAYOU AND THEN FAILED. | 110000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1066 | 1996-06-28 | KS | maintenance | RENO | PANHANDLE EASTERN PIPELINE CO | UNDER INVESTIGATION | 430000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1067 | 1996-07-07 | LA | maintenance |  | TENNESSEE GAS PIPELINE CO | BUBBLES WERE DISCOVERED BY THE PRODUCER 100 YARDS OFF PLATFORM. LEAK WAS A PIN HOLE AT THE 6 O'CLOCK POSITION CAUSED BY INTERNAL CORROSION. LEAK WAS AT 6O'CLOCK POSITION - PIN HOLE LEAK. | 80000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1068 | 1996-08-12 | LA | other |  | TRUNKLINE GAS CO | ANCHOR FROM DIVE BOAT RUPTURED 12" LINE 319B-1500. | 830000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1069 | 1996-08-28 | LA | other | PLAQUEMINES | KOCH GATEWAY PIPELINE CO | 16" VENICE JCT-CHALMETTE LINE RUPTURED ON LAKE PETIT, LAT 29DEG43.4', LONG 89DEG47.6, SEC 28, T-15-S, R-14-E, PLAQUEMINES PARISH, LA. INSPECTION OF FAILED PIPE REVEALED MECHANICAL DAMAGE AT MULTIPLE POINTS IN CENTER OF NAVIGATIONAL CHANNEL. LIKELY CAUSED | 264014 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1070 | 1996-08-29 | TX | other | WHARTON | TRUNKLINE GAS CO | 8/29/96 10:15 A.M. - NOTIFIED OF CROSSING LOCATION AND SCHEDULED TO MEET ON SITE 9/30/96 TO LOCATE AND MARK FACILITIES. TRANS TEXAS STRUCK 20" LINE 100-1WITH TRENCHER WHILE CROSSING TRUNKLINE FACILITIES. | 65000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1071 | 1996-09-03 | LA | maintenance |  | TRUNKLINE GAS CO | PIPE BODY 1/4" HOLE AT 6 O'CLOCK. CATHODIC P/S .982V - BATCH TREAT WITH BIOCIDE ON AN AS NEEDED BASIS. LEAK ON 12" LINE 1000 - 4B - 1100. | 250000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1072 | 1996-08-29 | MT | other | CARBON | MONTANA POWER CO | THIRD PARTY DOZER WITH RIPPER TOOTH SNAGGED MONTANA POWER COMPANY 4" RED LODGE NATURAL GAS TRANSMISSION PIPELINE. LINE PARTED AT GIRTH WELD. NO INJURIES.NO DAMAGE AT SITE. MONTANA POWER HAD TO RELIGHT TOWN OF RED LODGE. 1500 CUSTOMERS. STATUTE REQUIRES TH | 93000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1073 | 1996-09-10 | NM | maintenance | CHAVES | EL PASO NATURAL GAS CO | A SEGMENT OF OUR LINE NO. 1300 RUPTURED, BLOWING OUT 26 FEET OF PIPE, MOST OF IT IN A SINGLE SEGMENT WHICH LANDED 100 FEET FROM THE PIPELINE. | 240000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1074 | 1996-09-17 | WI | other | LACROSSE | NORTHERN NATURAL GAS CO (ENRON) | CONTRACTOR BUILDING A LOGGING ROAD DID NOT CALL ONE-CALL AND TORE A HOLE IN THE PIPE WITH A DOZER BLADE. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1075 | 1996-09-04 | TX | technical failure | HENDERSON | LONE STAR GAS CO | FAILURE APPEARS TO HAVE OCCURED AT A MECHANICAL COUPLING AND INCLUDED FAILUREOF ALL OR MOST OF THE 439 FT. SEGMENT. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1076 | 1996-09-28 | CA | other | COLUSA | PACIFIC GAS & ELECTRIC CO | THE PIPELINE PRESSURE WAS SLOWLY BEING RAISED FROM 575 PSIG TO ACCOMMODATE AFUTURE SHUTDOWN. THE PIPELINE RUPTURED WHEN THE PRESSURE REACHED 760 PSIG. THE NORMAL OPERATING PRESSURE FOR THIS LINE RANGES FROM 550 TO 800 PSIG. THE RUPTURED LINE DID HAVE EXTE | 500000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1077 | 1996-10-12 | TX | other | REEVES | DELHI GAS PIPELINE CORP | 49 USC SECTION 60123(D) | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1078 | 1996-10-04 | MN | other | CARVER | NORTHERN NATURAL GAS CO (ENRON) | CONTRACTOR HIT PIPELINE WITH A TILING MACHINE. DID NOT CALL "ONE-CALL". | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1079 | 1996-10-02 | TX | other | HARRISON | TEXAS GAS GATHERING INC | PIGGING THE 16 INCH LINE (TEXAS GAS GATHERING). FLOWING CONDENSATE AND PIG WASTES INTO 3 FRAC TANKS AND 2 STOCK TANKS FROM SLUDGE CATCHER, AT BULLARD JUNCTION COMPRESSOR STATION-TGG. FILLED UP ALL FRAC TANKS AND STOCK TANKS WITH FLUID, FROM SLUDGE CATCHER | 2000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1080 | 1996-10-06 | LA | other |  | VASTAR RESOURCES, INC | SHEAR JOINT (INSTALLED AUG. 1996) SEPARATION CAUSED BY MUDSLIDE DURING HURRICANE JOSEPHINE. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1081 | 1996-10-06 | LA | other |  | VASTAR RESOURCES, INC | DIVERS INSPECTED BREAK ON 10/21/96 & CONFIRMED THAT LINE PARTED @ THE DESIGNED WEAK LINK (BREAK-AWAY JOINT). MUD SLIDES LEFT APPROX 100' AND SEPARATION. ONE END OF THE LINE WAS BURIED DEEPER & WAS NOT LOCATED BECAUSE OF THE ONSET OF BAD WEATHER. THE BREAK | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1082 | 1996-10-04 | TX | maintenance |  | KOCH GATEWAY PIPELINE CO | DAMAGED PIPE SENT TO METALLURGIST CONSULTANT TO DETERMINE CAUSE OF RUPTURE. RESULTS NOT RECEIVED. ADDITIONAL INFORMATION IS BEING OBTAINED TO HELP US ASSESS THE CAUSE AND FACTORS CONTRIBUTING TO THE INCIDENT, AND UPON RECEIVING, WE WILL PROVIDE A NARRATIV | 500000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1083 | 1996-10-13 | WI | other | JACKSON | NORTHERN NATURAL GAS CO (ENRON) |  | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1084 | 1996-10-20 | GA | other | SUMTER | SOUTH GEORGIA NATURAL GAS CO | A VEHICLE WHOSE DRIVER LOST CONTROL, LEFT THE HIGHWAY AND PASSED THROUGH EXISTING BARRICADES, PENETRATING AMERICUS #1 METER STATION'S CHAIN LINK FENCE. THE VEHICLE STRUCK THE RTU MOUNTING POST, BREAKING OFF INSTRUMENTATION LINES, IGNITING THE ESCAPING GAS | 125000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1085 | 1996-10-18 | LA | maintenance |  | TRUNKLINE GAS CO |  | 67400 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1086 | 1996-10-26 | TX | other | SOUTH ADDITION | ANR PIPELINE CO | THE CAUSE OF THE LEAK HAS NOT YET BEEN DETERMINED. WE ARE PRESENTLY EVALUATING VARIOUS REPAIR OPTIONS. A SUPPLEMENTAL REPORT WILL FOLLOW UPON RESOLUTION OFTHESE UNKNOWN ISSUES. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1087 | 1996-10-23 | LA | other |  | TENNESSEE GAS PIPELINE CO | DREDGER NOTIFIED OPERATOR ON 10/18/96 FOR DREDGING ON 10/19/96 AND 10/20/96.THEY DID NOT NOTIFY OPERATOR THAT THEY HAD MOVED BACK TO AREA ON 10/23/96. NARRATIVE DESC: SPUD ON DREDGER HIT LINE 526A-300 (12"). GAS CAUGHT FIRE, DREDGE WAS BURNING. | 225000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1088 | 1996-11-01 | MT | other | MISSOULA | MONTANA POWER CO | REPORT OF TRANSMISSION PIPELINE INCIDENT WHICH OCCURRED ON THE MONTANA POWERCOMPANY NATURAL GAS TRANSMISSION SYSTEM NEAR MISSOULA, MONTANA ON NOVEMBER 1, 1996. THE INCIDENT WAS SUBJECT TO TELEPHONIC REPORTS MADE TO JOEL TIERNEY OF THE MONTANA PUBLIC SERVI | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1089 | 1996-11-16 | OK | maintenance | BEAVER | NATURAL GAS PIPELINE CO OF AMERICA | PIPELINE RUPTURE OF NO.2 - 26" MAINLINE DUE TO EXTERNAL CORROSION. | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1090 | 1996-11-29 | WI | other | JUNEAU | NORTHERN NATURAL GAS CO (ENRON) | LINE HIT BY A BACKHOE ENLARGING A DRAIN DITCH. | 53750 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1091 | 1996-11-11 | AZ | other | MARICOPA | EL PASO NATURAL GAS CO | THE BUCKEYE RURAL FIRE DEPT. RESPONDED TO A FIRE AT THE RAINBOW VALLEY METERSTATION. THE FIRE CONTINUED TO BURN UNTIL VALVE SECTION VA 72 AND VA 73 ON LINE NO. 1103 WAS SHUT IN. INVESTIGATION REVEALED THAT THE INCIDENT WAS A RESULT OF VANDALISM. THE COUNT | 60000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1092 | 1996-11-17 | LA | other |  | VASTAR RESOURCES, INC. | AN APPARENT RELEASE FROM THE PIPELINE WAS DETECTED DUE TO WATER TURBULENCE SPOTTED DURING A HELICOPTER FLY-OVER OF THE LINE. THERE WERE NO INJURIES OR FATALITIES ASSOCIATED WITH THE SUNDAY, NOVEMBER 17, 1996 APPARENT RELEASE, AND TEH CAUSE HAS NOT YET BEE | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1093 | 1996-11-11 | LA | other |  | ANR PIPELINE CO | ANCHOR HIT PIPELINE, GOUGE IN DENT WAS LEAKING AT 3 O'CLOCK POSITION, WHICHRESULTED IN THE LEAK. REPLACE D WITH 22'-4" OF 10" PIPE, 0.348 W.T. OCCURRED11/11/96, 1900 HOURS EST. | 135000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1094 | 1996-11-19 | LA | technical failure |  | TENNESSEE GAS PIPELINE CO | CLAMP ON VALVE OPERATOR LEAKING AND POSSIBLE CRACK IN BODY OF THE VALVE. BUBBLES DISCOVERED AT OR NEAR 523M-2901 SUBSEA ASSEMBLY. DIVE BOAT ON SITE 11/20/96 AND ABLE TO LOCATE AREA ONLY. CHEVRON, JACK DUPRE INITIALLY NOTICED BUBBLES. TGP - ALLEN ASHLEY 3: | 80000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1095 | 1996-11-24 | AL | other | CALHOUN | SOUTHERN NATURAL GAS CO | A LEAK OCCURRED IN THE PIPE THREADS OF 1" PIPE AT ITS CONNECTION TO A 1" THREADED COUPLING. NEARBY RESIDENTS REPORTED THE LEAK TO THE LOCAL FIRE DEPARTMENT, WHICH PROMPLTY EVACUATED THE AREA. THE CAUSE OF THE LEAK IS UNKNOWN AT THIS TIME. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1096 | 1996-11-28 | MN | technical failure | OLMSTED | NORTHERN NATURAL GAS CO (ENRON) | PIPE SUBMITTED FOR METALLURGICAL ANALYSIS TO DETERMINE CAUSE OF FAILURE. | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1097 | 1996-02-10 | MI | other | LENAWEE | ANR PIPELINE CO | THE FAILURE WAS THE RESULT OF EXTERNAL DAMAGE TO THE PIPELINE THAT MOSTPROBABLY OCCURRED FOUR MONTHS EARLIER DURING OUR OWN MAINTENANCE ACTIVITIESTHAT WE CONDUCTED IN THIS AREA. | 450000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1098 | 1996-12-07 | CA | other | FRESNO | PACIFIC GAS & ELECTRIC CO | PART B- WOODEN LATHES WITH YELLOW RIBBON. A TRACK-WHEELED CATERPILLAR WITH A6' RIPPER DUG INTO TRANSMISSION LINE 300A AT APPROX MILE POST 374.5, HARRISRANCH, RURAL AREA NEAR COALINGA. EXCAVATOR WAS WORKING FOR HARRIS RANCH. | 78000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1099 | 1996-07-22 | CA | other | COLUSA | PACIFIC GAS & ELECTRIC CO | OPERATOR OF TRACTOR/RIPPER RIPPED INTO TRANSMISSION LINE CAUSING TRACTOR TO BE BLOWN INTO AIR. OPERATOR WAS INJURED AND TAKEN TO HOSPITAL. OPERATOR RELEASED FROM HOSPITAL 7/23/96. | 64000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1100 | 1996-12-03 | TX | other | DUVAL | VALERO TRANSMISSION CO | GAS COMPRESSOR UNIT 98 HAD A VALVE COVER BLOW OFF CAUSING A FIRE. THE FIRE BLEW ACROSS UNIT 94 CAUSING THE COVER ON THE COMPRESSOR CRANKCASE TO BLOW OFF.UNITS 98, 94 AND 188 HAD FIRE DAMAGE. THE COMPRESSOR BUILDING WAS HEAVILY DAMAGED. MATERIALS INVOLVED: | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1101 | 1996-12-23 | AL | other | MOBILE | KOCH GATEWAY | CONTRACTOR WAS CAUTIONED TO NOTIFY KOCH PRIOR TO WORKING ON ROW, HOWEVER THEY DID BEGIN WORKING PRIOR TO NOTIFYING KOCH. CONTRACTOR WORKING OVER KOCH'S ROW WITHOUT PRIOR APPROVAL FROM KOCH. ALSO, CONTRACTOR HAD REMOVED SIGN PRIOR TO DIGGING. | 81425 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1102 | 1996-12-10 | KS | maintenance | LEAVENWORTH | WILLIAMS NATURAL GAS CO | FAILURE ANALYSIS TO BE COMPLETED IN 4 TO 6 WEEKS; 20' "T" DRIP FAILED ON LINE "EJ" | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1103 | 1997-01-10 | OK | other | BRYAN | TRANSOK INC | PILOT REGULATOR ON RELIEF VALVE FAILED CAUSING RELIEF VALVE TO OPEN. | 58064 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1104 | 1996-10-30 | MI | other | ST. CLAIR | GREAT LAKES GAS TRANSMISSION CO | THERE WAS NO ADVERSE IMPACT ON PERSONS OR PROPERTY FROM THE VENTED GAS. IN ADDITION, IT WAS NOT ANTICIPATED IMMEDIATELY FOLLOWING THE EVENT THAT THE COSTOF CLEANUP WOULD EXCEED $50,000. HOWEVER, SINCE THE NUMBER OF CLAIMS MADE TOGREAT LAKES FOR CLEANUP OF | 135000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1105 | 1996-12-27 | OK | other | TULSA | OKLAHOMA NATURAL GAS CO | CONSTRUCTION WAS NOT SUPPOSE TO BEGIN UNTIL 12/31/96. ONE-CALL WAS NOTIFIED AT 9:00 12/29/96 AND LINE WAS HIT AT 11:50 ON 12/29/96. LANDOWNER MADE A ONE-CALL REQUEST FOR WORK BEGINNING 12/31/96. CONTRACTOR STARTED WORK EARLY AND HIT THE LINE WHILE BURYING | 80798 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1106 | 1997-01-02 | AL | other | MOBILE | TRANSCO GAS PIPELINE CORP | THE SIZE AND SHAPE OF THE GAUGE (12") INDICATES IT WAS CAUSED BY A LARGE PIECE OF EXCAVATION EQUIPMENT (PROBABLY) A BACKHOE. LEAK INITIATED IN GAUGE OFUNKNOWN ORIGIN. | 75515 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1107 | 1997-01-07 | GA | technical failure | CARROLL | SOUTHERN NATURAL GAS CO | SEAL IN COUPLING APPEARS TO HAVE FAILED RESULTING IN A LEAK WHICH, AFTER A SHORT PERIOD OF TIME, BLEW ENOUGH SOIL AWAY TO DECREASE OVERBURDEN ALLOWING PIPE TOPULL OUT OF COUPLING. IT IS BELIEVED THAT A SEAL FAILED IN A MECHANICALCOUPLING RESULTING IN A L | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1108 | 1996-07-22 | MO | maintenance | CASS | PANHANDLE EASTERN PIPELINE CO | GENERAL EXTERNAL CORROSION IN AN AREA OF DISBONDED COATING. INCIDENT LOCATION: 1/2 MI EAST & 1/2 MI SOUTH OF KANSAS-MISSOURI LINE & HIGHWAY 2. | 180000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1109 | 1997-01-26 | CA | other | SANTA CRUZ | PACIFIC GAS & ELECTRIC CO | HEAVY RAINFALL CAUSED LARGE MUDSLIDE THAT CAUSED LINE RUPTURED. | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1110 | 1997-01-20 | WV | other | KANAWHA | CNG TRANSMISSION CORP | BATTLE RIDGE CONSTRUCTION COMP CALLED THE MORNING OF 1/20/97 AND REPORTED THEY SMELLED GAS NEAR THEIR CONSTRUCTION AREA. CNGT PERSONNEL INVESTIGATED AND FOUND LEAK BLOWING ON TL-272. ISOLATED SECTION, EVACUATED GAS, FOUND SPLIT INPIPE APP. 2"LX1/4W. FAILU | 83200 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1111 | 1997-01-19 | PA | other | GREENE | CNG TRANSMISSION CORP | A COMBINATION OF CONDENSATION AND EXTREMELY COLD TEMPERATURES CAUSED THE AXELSON R/V TO FAIL @ A PRESSURE BELOW THE SET POINT OF 1008 PSIG. R/V COULD NOTRE-SEAT DUE TO A ROLLED O-RING. APPARENT CAUSE: WEATHER CONDITIONS. RELIEFVALVE, TYPE H-L, SN#8632. | 62475 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1112 | 1997-02-09 | WA | other | COWLITZ | NORTHWEST PIPELINE CORP | AXIAL SOIL LOADING ON THE PIPE CREATED LOADING IN EXCESS OF THE GIRTH WELD STRENGTH, PULLING THE PIPELINE APART WITH A CLEAN BREAK AT THE GIRTH WELD WHICH RESULTED IN RAPID GAS LOSS AND IGNITION. | 195000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1113 | 1997-02-08 | WA | other | WHATCOM | NORTHWEST PIPELINE CORP | LAND MOVEMENT FROM SIDE SLOPE PLACED LATERAL LOAD ON PIPELINE WHICH EXCEEDEDTHE YIELD STRENGTH, CAUSING THE PIPELINE TO RUPTURE. THE LINE RUPTURE OCCURRED ON 2/8/97, AT 11:20PM, MST. THE TELEPHONIC NOTICE WAS MADE AT 1:05 AM, MST02/09/97. | 375000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1114 | 1997-02-08 | LA | other | ST. MARY | BRIDGELINE GAS DISTRIBUTION CO | ATHENA SPUD BARGE SPUDDED DOWN NEAR THE 20" PIPELINE. INCLEMENT WEATHER MOVEDTHE SPUD BARGE INTO THE PIPELINE CAUSING THE RUPTURE. THE LEAK OCCURRED IN THE ATCHAFALAYA BAY IN ST. MARY PARISH, LA AT APPROX 5:30 A.M. FROM A 20" NATURAL GAS PIPELINE. THE LEA | 200000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1115 | 1997-03-04 | TX | other | CROCKETT | OASIS PIPELINE CO | OZONA COMPRESSOR STATION BLOW DOWN VALVE OPENED INADVERTANTLY CAUSING A LOSSOF GAS WITHIN THE COMPRESSOR SITE. OTHER: CONTRO FUNCTION - GAS RELEASE | 85140 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1116 | 1997-02-22 | NE | other | NANCE | K N INTERSTATE GAS TRANSMISSION CO | PIPELINE SEPARATED AT GIRTH WELD IN LOUP RIVER X-ING. UNABLE TO DETERMINEEXACT CAUSE BECAUSE OF LOCATION OF FAILED SEGMENT IN LOUP RIVER. RIVERCROSSING FAILED AT OR NEAR GIRTH WELD. POSSIBLY DUE TO ICE FLOW IN RIVER. | 240000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1117 | 1997-03-20 | MT | other | RICHLAND | WILLISTON BASIN INTERSTATE PIPELINE CO | GIRTH WELD FAILED ON BURIED 12-INCH PIPELINE DUE TO SETTLING AND FROST HEAVE. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1118 | 1997-03-19 | SD | other | LAWRENCE | WILLISTON BASIN INTERSTATE PIPELINE CO | A D-7 CRAWLER-TRACTOR WAS BEING USED FOR RECLAMATION WORK NEAR OUR 8-INCHPIPELINE WHEN IT RIPPER TOOTH HOOKED AND PUNCTURED THE TOP OF THE PIPE. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1119 | 1997-03-13 | IL | technical failure | COLES | CENTRAL ILLINOIS PUBLIC SERVICE | THE WHITE/SUPERIOR NATURAL GAS ENGINE/COMPRESSOR (UNIT #3) WAS OVERHAULED BYCOOPER ENERGY SERVICES, CURRENT OEM, IN 1996. THE OVERHAUL WORK WAS COMPLETED12/14/96. THE UNIT #3 HAD OPERATED 612 HOURS FROM START-UP UNTIL THE MARCH 13,1997 INCIDENT. PRELIMIN | 750000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1120 | 1997-03-21 | TX | other | EL PASO | EL PASO NATURAL GAS CO | AT APRROX. 8:20 AM ON 3/21/97 ELPASO'S 8-5/8 ELECTRIC CO LOOP LINE NO 2058RUPTRUED. THE SITE OF THE RUPTURE IS ON A CONSTUCTION SITE ON PROPERTY AT THENORTHWEST CORNER OF RESLER DR. AND REDD RD. IN EL PASO. FOUR PEOPLE WEREHOSPITLALIZED AND 2 WERE TREATED | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1121 | 1997-03-21 | LA | technical failure |  | ANR PIPELINE CO | LEAKING 1/2" HYDRAULIC SEALANT FITTING (PLUG) ON SUBSEA HYDROTECH HOT TAPASSEMBLY. | 90000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1122 | 1997-04-12 | GA | technical failure | CARROLL | SOUTHERN NATURAL GAS CO | IT IS BELIEVED THAT A SEAL FAILED IN A MECHANICAL COUPLING RESULTING IN APRESSURE RELEASE AND SUBSEQUENT PIPELINE RUPTURE AT THE COUPLING JOINT. THEREWAS NO GAS IGNITION. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1123 | 1997-04-08 | AL | other |  | SOUTHERN NATURAL GAS CO | EMPLOYEE REMOVED A 2" BULL PLUG NOT REALIZING THAT GAS PRESSURE WAS STILLPRESENT IN A SHORT PUP OF PIPE BEHIOND THE PLUG. THE PLUG BLEW OUT STRIKINGEMPLOYEE IN THE FACE. EMPLOYEE WAS HOSPITALIZED OVERNIGHT AFTER SUGICALREPAIR OF LACERATED TONGUE. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1124 | 1997-04-03 | TX | other |  | ANR PIPELINE CO | 20" SUBSEA TAP WAS PULLED APART BY THE ANCHOR OF THE SHIP. | 700000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1125 | 1997-04-07 | MI | other | CHIPPEWA | GREAT LAKES GAS TRANSMISSION CO | ON OR ABOUT APRIL 7 1997, GREAT LAKE S GAS TRANSMISSION COMPANY RECIEVED INFO.THAT A LARGE SCTION OF HILLSIDE HAD SUBSIDED IN THE AREA OF ITS SOO LATERAL 103/4 INCH MAINLINE AND 12 3/4 INCH LOOPLINE IN CHIPPEWA COUNTY, MICHIGAN ANDTHAT THE PIPELINES WERE | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1126 | 1997-03-26 | TX | maintenance | STARR | VALERO TRANSMISSION CO |  | 250000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1127 | 1997-04-20 | MO | maintenance | BOONE | PANHANDLE EASTERN PIPELINE CO | UNDER INVESTIGATION. | 500000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1128 | 1997-04-18 | MS | technical failure | CALHOUN | COLUMBIA GULF TRANSMISSION CO | THE VALVE PLUG FROM SUCTION SIDE CLEARANCE POCKET CAME OFF FROM VALVE STEMCAUSING COMPRESSOR HEAD STRIPPED OFF FROM COMPRESSOR. CONSTRUCTION DEFECT:CAUSE OTHER: PROBLEM WITH ORIGINAL EQUIPMENT. | 60000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1129 | 1997-04-14 | TX | maintenance | STARR | VALERO TRANSMISSION CO | LINE FAILURE DUE TO STRESS CORROSION CRACKING. | 125000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1130 | 1997-05-03 | GA | technical failure | CARROLL | SOUTHERN NATURAL GAS CO | A PIPE CONNECTION IN A MECHANICAL COUPLING FAILED, RESULTING IN A PRESSURERELEASE AND SUBSEQUENT PIPELINE RUPTURE AT THE COUPLING JOINT. THE GAS IGNITEDAND BURNED SURROUNDING VEGETATION. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1131 | 1997-05-14 | WY | technical failure | ALBANY | COLORADO INTERSTATE GAS CO | C.1. LKEAK WAS AT A SMALL 1/4 LONG CRACK IN THE LONGITUDINAL WELD. C.3.C. TESTDURATION IS UNKNOWN. LEAK WAS DISCOVERED BY A GAS DETECTION INSTRUMENT DURINGA ROUTINE LEAK SURVEY. ALTHOUGH ONLY 44 FEET OF PIPE WAS REPLACED, THE REPAIRCOSTS EXCEEDED $50,000 | 51000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1132 | 1997-05-05 | TX | maintenance | RUSK | TEJAS GAS PIPELINE CO | INTERNAL CORROSION PIT ON ERW SEAM, AND THE SEAM WAS NOT IN THE NEUTRAL ZONEAT A FIELD BEND. (SEAM WAS AT 5:30) SEAM INSTALLED AT THE 5:30 POSITION ANDWAS IN A LOW SPOT (LIQUID TRAP). | 48523 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1133 | 1997-05-27 | TX | maintenance | HARRISON | TALCO ASPHALT OIL CO |  | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1134 | 1997-05-13 | TX | other | RUSK | LONE STAR PIPELINE CO (TRANSMISSION DIVISION) | LINE WAS STRUCK BY MOTOR GRADER OPERATED BY RUSK COUNTY, TX. PERSONNEL | 110000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1135 | 1997-05-05 | NY | other | ELLISBURG | NIAGARA MOHAWK POWER CORP |  | 60000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1136 | 1997-05-20 | TX | maintenance | HARRIS | TPC SERVICES, INC. | AT 10:30 AM MAY 20 1997 A CALL WAS RECIEVED AT TPC'S OPERATIONS CENTER STATINGTHAT BUBBLES WERE REPORTED IN MATAGORDA ISLAND BLOCK 485 APPROX. ONE HALF MILETO THE NORTH TO TPC'S MI 485 MAINFOLD PLAT FORM. A TECHNICIAN WAS SENT OUT BYHELICOPTER TO OVERFKY | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1137 | 1997-05-01 | NM | other | SANTA FE | PUBLIC SERVICE COMPANY OF NEW MEXICO - GAS SVCS | MCC, CONTRACTOR INSTALLING A WATER LINE HAD PHONED FOR LINE SPOTS TO NEWMEXICO ONE CALL SYSTEM(#97043007440022). LINE SPOTS WERE COMPLETED BY PNMGAS SERVICES USING ROOSTER TAILS AND PAINT AT 8:50 AM ON 5-1-97. AT 11:30AM MCC KNOCKED A 2' PURGING TEE OFF T | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1138 | 1994-08-14 | WV | other | KANAWHA | AJAX PIPELINE CO | GAS IGNITED WHEN IGNITED LINE WAS BEING PUMPED. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1139 | 1996-08-26 | TX | maintenance | HEMPHILL | NORAM GAS TRANSMISSION, A NORAM ENERGY COMPANY | FAILURE OCCURRED IN PITTED AREA LOCATED ON BOTTON QUADRANT INSIDE PIPE. | 66000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1140 | 1996-12-14 | AR | other | LAWERENCE | MISSISSIPPI RIVER TRANSMISSION CORP | P | 56664 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1141 | 1997-05-20 | ME | other | YORK | GRANITE STATE GAS TRANSMISSION INC | TRAVELED HEAVY TRACK EQUIPMENT ACROSS PIPELINE ROW THRU YEAR ROUNDWETLANDAREA. MACHINE SANK IN SOFT SOIL COMING INTO CONTACT WITH PIPE.PIPELINE WAS TAKEN OUT OF SERVICE AND DAMAGED SECTION REPLACED. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1142 | 1997-05-23 | LA | maintenance |  | TRUNKLINE GAS CO | NO DATA | 125000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1143 | 1997-06-17 | TX | maintenance | HARRISON | NORAM GAS TRANSMISSION, A NORAM ENERGY COMPANY | THERE WERE 2 LEAKS WITHIN 3' AREA ON BOTTOM SIDE OF PIPE. ONE ABOUT THE SIZEOF 1 1/2" & THE OTHER MAYBE 1/8". IN NORROW CREEK 2' WIDER & 1' DEEP. PIPELINEWAS FOUND TO BE PARTIALLY EXPOSED IN CREEK, COATING FOUND TO BE DETERIORATED. | 158500 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1144 | 1997-06-08 | LA | maintenance | LOUISIANA | ANR PIPELINE CO | PIPELINE WAS CONCRETE COATED WITH SOMATIC WRAP. INTERNAL CORROSION - PIN HOLELEAK AT 7 OCLOCK POSITION. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1145 | 1997-06-02 | MS | other | ST LOUIS | TENNESSEE GAS PIPELINE CO | BOLT FAILURE ON COMPRESSOR VALVE CAP ALLOWED GAS TO BE RELEASED RESULTING INTHE FIRE AND EXPLOSION IN BUILDING A AT STATION 530. | 3500000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1146 | 1997-07-19 | LA | other |  | SOUTHERN NATURAL GAS CO | STORM FORCES FROM HURRICANE DANNY NDAMAGED THE PLATFORM SUPPORT FOR THE METERRUNS AT MILEPOST 10.762 ON THE 6" ELOI BY PIPELINE SUCH THAT METER PIPING WASSEVERED CAUSING A RELEASE OF GAS. THERE WAS NO IGNITION. | 75000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1147 | 1997-07-24 | TX | other |  | WESTAR TRANSMISSION CO |  | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1148 | 1997-07-14 | OH | other | BUTLER | CINCINNATI GAS & ELECTRIC CO | STILL UNDER INVESTIGATION AND WILL BE PROVIDED BY A SUPPLEMENTAL REPORT. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1149 | 1997-07-29 | IL | other | MADISON | ILLINOIS POWER CO | ON JULY 29, 1997 AT APPROX. 1450 HRS A THIRD PARTY DUG INTO THE 10" MAIN ATHIGHLAND AND CUT IN THE PIPE APPROX. 6" BY 3'. THE APPROPRIATE PERSONNEL WERENOTIFIED AND BEGAN TO RESTORE TO NORMAL CONDITIONS. BECAUSE GAS WAS VENTING TOATMOSPHERE, GAS SUPPLY DI | 151000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1150 | 1997-08-09 | LA | maintenance |  | NATURAL GAS PIPELINE CO OF AMERICA |  | 51232 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1151 | 1997-07-21 | IN | other | MARION | CITIZENS GAS & COKE UTILITY |  | 1000000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1152 | 1997-08-21 | LA | maintenance |  | NATURAL GAS PIPELINE CO OF AMERICA |  | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1153 | 1997-08-21 | TX | technical failure | MOORE | MIDGARD ENERGY COMPANY |  | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1154 | 1997-08-11 | IL | maintenance | GRUNDY | NATURAL GAS PIPELINE CO OF AMERICA |  | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1155 | 1997-07-01 | IL | other | CLINTON | MISSISSIPPI RIVER TRANSMISSION CORP | WATER LINE CONTRACTOR TRENCHING TO INSTALL WATER LINE. THE TRENCHER WASCUTTING 60" DEEP DITCH, PIPELINE DEPTH WAS 3' - 3". | 55000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1156 | 1997-08-12 | LA | maintenance | OFFSHORE LA, FEDERAL WAT | ANR PIPELINE CO | INTERNAL CORROSION - 3 PINHOLE LEAKS WITHIN A 23 INCH SECTION OF THE PIPE. | 130000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1157 | 1997-08-04 | TX | other | LIBERTY | GULF COAST NATURAL GAS CO | HAD AN EXPLOSION IN FRAC TANKS AT MOSS BLUFF ON THE 16" LINE, SYSTEM 903 NEARHANKAMER, AT 11:30 AM ON 8/04/97. TEMPORARY PIG TRAPS WERE INSTALLED ON BOTHENDS AND PIG WAS BEING PUSHED FROM THE NORTH END TO THE SOUTH. LIQUIDS WERECAUGHT IN FOUR FRAC TANKS. | 335000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1158 | 1997-09-09 | LA | other |  | SOUTHERN NATURAL GAS CO | A FIRE OF UNKNOWN ORIGIN OCCURRED IN PRODUCER'S EQUIPMENT ON THE MAIN PASSBLOCK 59 PLATFORM ALSO OWNED BY PRODUCER. THE FIRE SPREAD TO PRODUCER'S METERSTATION, WHICH WAS OPERATED BY SOUTHERN, DAMAGING METER PIPING, ELECTRONICMEASUREMENT EQUIPMENT, AND RE | 75000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1159 | 1997-09-16 | LA | maintenance | LAFAYETTE PARISH | LOUISIANA INTRASTATE GAS CO, L.L.C. | UNKNOWN AT THIS TIME. ADDITIONAL INFORMATION WILL BE CONTAINED IN SUPPLEMENTALREPORT. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1160 | 1997-09-14 | CO | other | LOGAN | K N INTERSTATE GAS TRANSMISSION CO | GAS IGNITED WHILE PURGING 24" SUCTION HEADER AT KN STERLING COMPRESSORSTATION. FIRE IGNITED LUMBER, PLASTIC AND CARDBOARD AND BURNED GRASS INSIDEAND OUTSIDE OF STATION FENCE. FIRE DEPARTMENT WAS CALLED. SUPPLY VALVE WASIMMEDIATELY CLOSED, EXTINGUISHING FI | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1161 | 1997-10-06 | TX | other | SHERMAN | MIDGARD ENERGY COMPANY | A TRUCK HAULING FEED WAS HIT BY A PICK-UP, CAUSING THE TRUCK TO RUN OFFHIGHWAY 15 AND RUN OVER OUR REGULATOR/METER STATION. ABOVE GROUND EQUIPMENTWAS DAMAGED WHEN HIT BY TRUCK. | 1228 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1162 | 1997-09-19 | MI | maintenance | OSCEOLA | MICHIGAN GAS STORAGE CO | CREVICE IN LONG SEAM LOCATED ON BOTTOM ALLOWED CORROSION PRODUCTS TOACCUMULATE CAUSING PITTING AND FOR PITS TO LINK UP. | 23000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1163 | 1997-10-27 | VA | other | GREENE | COLUMBIA GAS TRANSMISSION CORP | CONTRACTOR'S D6 BULLDOZER SLID INTO A DITCH PUNCTURING EXPOSED PIPE RESULTINGIN A FIRE. ACCORDING TO THE EQUIPMENT OPERATOR, THE CAUSE WAS LIKELY ACOMBINATION OF BOTH WET AND SLIPPERY SOIL CONDITIONS AND OPERATION TOO CLOSETO THE DITCH. | 300000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1164 | 1997-10-28 | TX | maintenance | ARANSAS | CCNG GAS GATHERING, L.P. | PROGRESSIVE ISOLATE CONE-SHAPED PIT PERFORATION IN PIPE WALL OF APPROXIMATELYPROGRESSIVE ISOLATED CONE-SHAPED PIT PERFORATION IN PIPE WALL OF APPROXIMATELYFORT-FIVE YEARS OF MONITORED PIPELINE QUALITY GAS SERVICE. | 44000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1165 | 1997-10-24 | MN | other | ITASCA | GREAT LAKES GAS TRANSMISSION CO | THE LEAK WAS DISCOVERED DURING A ROUTINE SURVEY. INVESTIGATION REVEALED ACRACKED GIRTH WELD THAT WAS LEAKING. THE CRACK WAS CIRCUMFERENTIALLYORIENTATED AT APPROXIMATELY THE 6:00 POSITION AND WAS MEASURED TO BE 4.25INCHES LONG, RESULTING IN PIPE REPLACEM | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1166 | 1997-10-22 | LA | maintenance |  | SOUTHERN NATURAL GAS CO | PART A - PIPING WAS ABOVE THE WATERLINE OFFSHORE. PART 3 - TWO VERY SMALL"PINHOLE LEAKS WERE DISCOVERED IN 3" PIPING ON OFFSHORE PLATFORM. NOSIGNIFICANT EVENT WAS LINKED TO THE LEAKS. ESTIMATED COST OF REPAIR IS THEREASON FOR CLASSIFYING AS AN INCIDENT | 200000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1167 | 1997-10-23 | TX | maintenance | GREGG | TEXAS EASTERN GAS PIPELINE CO | PIPELINE RUPTURE FROM APPARENT INTERNAL CORROSION. | 150000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1168 | 1997-10-18 | MN | other | FREEBORN | NORTHERN NATURAL GAS CO. | FARMER WAS CHISEL PLOWING THE FIELD WHEN THE PLOW STRUCK THE PIPELINE. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1169 | 1997-11-05 | TX | maintenance | BRAZORIA | HOUSTON PIPELINE CO | INTERNAL CORROSION. | 20000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1170 | 1997-11-12 | AR | other | UNION | NORAM GAS TRANSMISSION, A NORAM ENERGY COMPANY | PIPE PULLED OUT OF COUPLING BECAUSE OF WASHOUT AREA. | 63000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1171 | 1997-12-17 | LA | maintenance | BLOCK 286/287 | COLUMBIA GULF TRANSMISSION CO | PIN HOLE LEAK AT 9 O'CLOCK POSITION. POSSIBLE CAUSE: INTERNAL CORROSION ORMATERIAL DEFECT. A CLAMP WAS INSTALLED TO STOP LEAK. X=1,885,229.89Y=105,490.26. SMALL PINHOLE LEAK AT 9:00 POSITION. | 80000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1172 | 1997-12-02 | LA | other | OFFSHORE | COLUMBIA GULF TRANSMISSION CO | A TRAWLING NET PULLED A 1/2" POWER GAS NIPPLE OFF FROM THE 18" VALVE. THEREMAINDER OF THE 1/2" NIPPLE WAS REMOVED AND A PIPE PLUG WAS INSTALLED. ATRAWLING NET PULLED A 1/2" POWER GAS NIPPLE OFF THE PIPELINE VALVE. THEREMAINDER OF THE 1/2" PIPE NIPPLE WAS | 200000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1173 | 1997-12-07 | TX | maintenance |  | ANR PIPELINE CO | PIN HOLE LEAK AT 6:30 POSITION CONSISTENT WITH INTERNAL CORROSION. | 170000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1174 | 1997-12-28 | LA | other | ST. MARY PARISH | MARATHON ASHLAND PIPE LINE LLC | ON DECEMBER 28, 1998 AT APPROXIMATELY 8:35 A.M., A SPHERE ARRIVED AT THEGARDEN CITY FACILITY AND BECAME STUCK IN THE 30" RADIAL FLOW TEE UPSTREAM OFTHE PIG TRAP (I.E., RECEIVER). IT IS BELIEVED THAT ONE OR TWO PREVIOUSSPHERES WERE ALREADY SETTING IN THE | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1175 | 1997-10-21 | KS | other | WABAUNSEE | K N INTERSTATE GAS TRANSMISSION CO | USING GEL PIG TO REMOVE CONTAMINATION FROM PIPELINE. OPENED DOWNSTREAMBLOWDOWNS TO PROVIDE PRESSURE DIFFERENTIAL TO MOVE PIG TRAIN. PRODUCT FROMEARLIER PIG RUN WAS INSIDE OF PIPE AND ESCAPED AS A MIST APPROX. 1.5 HOURSAFTER BLOWDOWNS WERE OPENED. CLOSE | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1176 | 1997-11-15 | SC | technical failure | YORK | SOUTH CAROLINA PIPELINE CORP | DURING THE CALENDAR YEARS OF 1995 AND 1996,SOUTH CAROLINA PIPELINE CORPORATION(SCPC) INSTALLED EIGHTY FIVE (85) MILES OF 16' NATURAL GAS TRANSMISSION MAINWITH A DESIGNED M.A.O.P. OF 1200 PSIG IN PARALLEL WITH AN EXISTING 12"REDUCING TO 10" LINE A SYSTEM F | 74000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1177 | 1998-01-05 | NV | other | CLARK | SOUTHWEST GAS CORP | ENCLOSED IS A GAS TRANSMISSION INCIDENT REPORT FOR AN INCIDENT WHICH OCCURREDON JANUARY 5, 1998. THE INCIDENT REPORT NUMBER PROVIDED TO SOUTHWEST GAS FROMDOT WHEN WE MADE OUR TELEPHONIC REPORT IS 418580. IF YOU HAVE ANY QUESTIONS,PLEASE GIVE ME A CALL. | 129860 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1178 | 1998-01-09 | LA | other | HOUMA | TENNESSEE GAS PIPELINE CO | UNKNKOWN THIRD PARTY WHO CAUSED DAMAGE. LOCATION IS NOT A WATER CROSSING, BUTIS OFFSHORE IN STATE WATERS. | 385000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1179 | 1998-01-08 | GA | other | COBB | ATLANTA GAS LIGHT CO | A 24" STEEL NATURAL GAS MAIN DEVELOPED A 4 1/4" STRESS CRACK AT A 12" STEELBRANCH CONNECTION WHEN THE FILLMATERIAL SUPPORT WAS WASHED AWAY DURING A WATERMAIN BREAK. | 47546 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1180 | 1998-01-21 | TX | other | HOWARD | WESTAR TRANSMISSION CO | ATTTACHED IS RSPA FORM F 7100.2 COVERING AN INCIDENT THAT OCCURRED NEARFORSAN, TEXAS ON JANUARY 21 1998. WE REPORTED THE INCIDENT TO THE NATIONALRESPONSE CENTER AT APPROXIMATELY 1602 HOURS CST ON JANUARY 21 1998 AND THEINCIDENT NUMBER ASSIGNED WAS 42071 | 8500 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1181 | 1998-01-16 | AR | technical failure | CRAWFORD | NORAM GAS TRANSMISSION, A NORAM ENERGY COMPANY |  | 600000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1182 | 1998-01-16 | AR | technical failure | SEBASTAIN | NORAM GAS TRANSMISSION, A NORAM ENERGY COMPANY | PIPE NIPPLE ON OIL FILTER CASE SAMPLE PROBE BROKE AND VENTED OIL ONTO EXHAUSTMANIFOLD OF ENGINE #3 AND IGNITED. SAFETY SHUTDOWNS OPERATED AND SHUT DOWNENGINE. FIRE EXTINGUISHED BY STATION EMPLOYEE. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1183 | 1998-01-26 | LA | other |  | SEA ROBIN PIPELINE CO |  | 2500000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1184 | 1998-01-27 | TX | maintenance | HUDSPETH | EL PASO NATURAL GAS CO |  | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1185 | 1998-01-13 | OR | technical failure | JOSEPHINE | NORTHWEST PIPELINE CORP | ATTACHED IS AN INCIDENT REPORT, FORM 7100.2,CONCERNING A RUPTURE ON OUR GRANTSPASS LATERAL LOCATED IN JOSEPHINE COUNTY, OREGON. THE RUPTURE INFORMATION ISNECESSARY, PLEASE CONTACT ME. | 200000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1186 | 1997-10-21 | MS | technical failure | GEORGE | KOCH GATEWAY PIPELINE CO | ATTACHED PLEASE FIND YOUR REQUESTED RESUBMISSION OF THE WRITTEN REPORT FOR ALEAK WHICH OCCURRED ON OUR BAXTERVILLE 20" LINE. THE REPORT WAS MADE11/30/1997 TO LT. KOSHAR OF THE NATIONAL RESPONSE CENTER. THE REPORT NUMBER IS409967. WE APOLOGIZE FOR SENDING | 140000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1187 | 1997-01-11 | MS | technical failure | GEORGE | KOCH GATEWAY PIPELINE CO | ATTACHED PLEAS FIND YOUR REQUESTED RESUBMISSION OF THE WRITTEN REPORT FOR ALEAK WHICH OCCURRED ON OUR PIPELINE NEAR LUCEDALE, MISSISSIIPPI, IN GEORGECOUNTY. THE REPORT WAS MADE AT 7:24 AM.CENTRAL TIME, ON 10/21/1997 TO LT.KOSHAR OF THE NATIONAL RESPONSE | 60397 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1188 | 1998-01-30 | LA | maintenance |  | EQUITABLE RESOURCES (A.K.A EQUITABLE GAS CO) | PIPELINE REPAIR PROCEDURE WEST CAMERON 198 02/02/1998 JET OUR ATOUND THE PIPEAT THE LEAK LOCATION TO VERIFY ORIGIN OF LEAK. ULTRASONICALLY INSPECT THEPIPE AT VARIOUS LOCATION TDETERMINE GENERAL CONDITION OF PIPE MATERIAL.INSTALL A NEW PRE-TESTED PIPE SPO | 700000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1189 | 1998-01-26 | LA | maintenance | OFFSJORE | EQUITABLE RESOURCES (A.K.A EQUITABLE GAS CO) | PIPELINE REPAIR PROCEDURE WEST CAMERON 198 1/27/1998 BLOWN DOWN THE 12"PIPELINE BACK TO THE 198 "A" PLATFORM. REMOVE CONCRETE COATING, CLEAN PIPE TOBARE METAL, AND ULTRASONICALLY INSPECT AT VARIOUS LOCATION OF PIPE TODETERMINE GENERAL CONNDITION OF PIP | 200000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1190 | 1998-02-07 | WV | maintenance | KANAWHA | COLUMBIA GAS TRANSMISSION CORP | HEATER COIL IN A DIRECT FIRED HEATER. | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1191 | 1997-11-19 | LA | technical failure | ST MARY PARISH | COLUMBIA GULF TRANSMISSION CO | UNDERCUT ON THE HOT TAP WELD AND STRESS ON THE BRANCH PIPING CAUSING A 3"CRACK ON THE PIPELINE. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1192 | 1997-10-08 | OK | other | CANADIAN | GPM GAS CORP | ON OCTOBER 8,1997, A COMPANY MAINTENANCE CREW BEGAN WORK TO REMOVE A NONUSED 6INCH TIE IN FROM A 12 INCH NATURAL GAS GATHERING SYSTEM DISCHARGE LINE. THELINE HAD BEEN ISOLATED AND DEPRESSURED ON OCTOBER 5, 1997. AN OPEN VENT WASLOCATED AT EACH ISOLATION | 70000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1193 | 1998-03-01 | AK | other |  | ENSTAR NATURAL GAS CO | ON SUNDAY MORNING MARCH 1, 1998, AT 9:46 AM AST, ENSTAR WAS NOTIFIED BY THEANCHORAGE FIRE DEPARTMENT ( AFD OF A POWER POLE FIRE AND NATURAL GAS LEAK ATFIRST STREET AND POST ROAD, ANCHORAGE, ALASKA. A SERVICE MAN WAS DISPATCHEDTO THE LOCATION. A SUPERVIS | 2000000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1194 | 1997-11-10 | TX | other | MOORE | EL PASO NATURAL GAS CO | AT1:17 PM ON NOVEMBER 10 1997, EL PASO'S" DUMAS LINE NO. 1102 DUMAS NO. 1102WAS HIT AND PUNCTURED BY A SEISMOGRAPH CREW LOCKHARG GEOPHYSICAL CO. WORKINGIN THE VICINITY OU PIPELINE APPROXIMATELY 12 MILES SOUTH OF OUR DUMAS PLANT.A HOLE 1-1/2 IN DIAMETER W | 57843 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1195 | 1998-01-11 | LA | other |  | FOREST OIL CORP |  | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1196 | 1998-02-25 | LA | other | ST. JAMES PARISH | WILLIAM FIELD SERVICES | ON FEBRUARY 25, 1998 AT APPROXIMATELY 6:45 AM, WILLIAMS FIELD SERVICES COMPANY(WFS) PERSONNEL WERE NOTIFIED BY A LOCAL CITIZEN THAT GAS WAS VENTING AT VALVESETTING 62-40 (LOCATED ON THE NORTH END OF DUAL 20" PIPELINES CROSSING THEMISSISSIPPI RIVER). WFS | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1197 | 1998-02-20 | MS | other |  | KOCH GATEWAY PIPELINE CO |  | 59433 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1198 | 1998-02-26 | TX | technical failure |  | TENNESSEE GAS PIPELINE CO |  | 78000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1199 | 1998-03-08 | GA | other | FULTON | SOUTHERN NATURAL GAS CO | RUN SWITCHING INSTRUMENTATION EQUIPMENT AT FULTON INDUSTRIAL METER STATIONWAS STRUCK BY LIGHTENING CAUSING A SMALL FIRE WHICH MIGRATED TO THE STATION'SMETER RUNS DUE TO MELTED SEAL COMPONENTS. A LARGER FIRE ENSUED RESULTING INSIGNIFICANT STATION DAMAGE. | 60000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1200 | 1998-03-20 | LA | other |  | COLUMBIA GULF TRANSMISSION CO | A TRAWLING NET BROKE THE 1" POWER GAS LINE FROM THE VALVE OPERATOR. THEBROKEN POWER GAS LINE WAS REMOVED AND THE 1" UNIONS WERE PLUGGED. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1201 | 1998-03-28 | LA | maintenance |  | SOUTHERN NATURAL GAS CO | CORRODED PART WAS ABOVE WATER ON PLATFORM | 202000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1202 | 1998-03-20 | TX | other | FAYETTE | OASIS PIPELINE CO |  | 227400 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1203 | 1998-04-02 | KY | technical failure |  | TENNESSEE GAS PIPELINE CO | TENNESSE WAS INVESTIGATING A LOW POTENTEAL AREA WHEN WORKERS HEARD GAS LEAK ATTHIS LOCATION AND ISOLATED VALVE SECTION 107-3 TO 108-3. | 64000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1204 | 1998-05-08 | TX | maintenance | MOORE | WEST TEXAS GAS INC |  | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1205 | 1998-05-12 | TX | technical failure | MOORE | WEST TEXAS GAS INC | METHOD OF PIPELINE CONNECTION CAUSED 22" PIPELINE JOINT TO SEPARATE FROMDRESSER COUPLING. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1206 | 1998-05-06 | OH | other | MONROE | TEXAS EASTERN TRANSMISSION CORP | THE PIPELINE RUPTURE WAS DUE TO THE FORCES OF A SOIL SLIPPAGE ALONG AHILLSIDE.TEXAS EASTERN IS RELOCATING THE PIPELINE OUTSIDE THE AREA OF THE SOILSLIP. | 3400000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1207 | 1998-04-08 | LA | other |  | FLORIDA GAS TRANSMISSION CO | THE PORTION OF THE LATERAL WITH LEAK HAS BEEN TAKEN OUT OF SERVICE UNTIL AREPAIR CAN BE MADE. THE CAUSE OF THE LEAK WILL REMAIN UNKNOWN UNTIL THEREPAIR WORK COMMENCES DUE TO THE DEPTH OF THE WATER OVER THE PIPELINE AT THELEAK LOCATION. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1208 | 1998-03-24 | TX | technical failure |  | HOUSTON PIPELINE CO | GASKET FAILURE | 45000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1209 | 1998-03-07 | NM | other | CHAVES | PUBLIC SERVICE COMPANY OF NEW MEXICO - GAS SVCS | UPON ARRIVAL I OBSERVED THAT A VEHICLE FULLY ENGULFED IN FLAMES AND THE DRIVEROF THE VEHICLE HAD BEEN TRANSPORTED TO THE HOSIPTAL IN ROSWELL, NM. FURTHERINVESTIGATION SHOWED THANT THE VEHICLE WAS TRAVELING EASTBOUND ON STATE ROAD560. FOR AN UNKNOWN REAS | 10000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1210 | 1998-04-02 | OK | technical failure | COAL | NORAM GAS TRANSMISSION, A NORAM ENERGY COMPANY | THESE ARE THE REMARKS | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1211 | 1998-04-08 | OK | other | COAL | NORAM GAS TRANSMISSION, A NORAM ENERGY COMPANY | FAILURE OCCURRED IN BEND THAT WRINKLED DUE TO OVERBURDEN LOAD IN HIGH BANK OFMUDDY BOGGY CREEK. | 400000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1212 | 1998-04-20 | LA | other |  | ANR PIPELINE CO | A REPAIR SLEEVE INSTALLED ON AUGUST 31, 1990 WAS LEAKING. FOUND HAIRLINECRACK ON PIPE HAD OPENED AND PROPAGATED. THE REPAIR SLEEVE WAS UNABLE TOCONTAIN THE PRESSURE. | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1213 | 1998-05-05 | TX | technical failure |  | NORTHERN NATURAL GAS CO (ENRON) |  | 300000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1214 | 1998-04-10 | IA | other | WRIGHT | NORTHERN NATURAL GAS CO (ENRON) |  | 58000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1215 | 1998-04-22 | CA | other | SAN BENITO | PACIFIC GAS & ELECTRIC CO |  | 4000000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1216 | 1998-05-11 | TX | maintenance |  | ANR PIPELINE CO |  | 325000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1217 | 1998-05-04 | TX | other |  | ANR PIPELINE CO |  | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1218 | 1998-05-19 | WV | other | JACKSON | COLUMBIA GAS TRANSMISSION CORP |  | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1219 | 1998-03-27 | LA | other |  | BASIN EXPLORATION INC |  | 600000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1220 | 1998-05-18 | TX | maintenance |  | WILLIAMS ENERGY GROUP-FIELD SERVICES |  | 75000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1221 | 1998-06-02 | LA | other | IBERVILLE | SOUTHERN NATURAL GAS CO | A CATALYTIC GAS SENSOR IN A COMPRESSOR BUILDING GAS DETECTOR MALFUNCTIONED,INDICATING A FALSE PRESENCE OF NATURAL GAS AT A LEVEL WHICH CAUSED THEAUTOMATED COMPRESSOR STATION'S EMERGENCY SHUTDOWN (ESD) SYSTEM TO ACTIVATE.THIS RESULTED IN A RELEASE OF GAS T | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1222 | 1998-06-06 | TX | other | HIDALGO | PG & E TEXAS PIPELINE, L.P. | PAVING COMPANY USING A MAINTAINER AT THE INTERSECTION OF POLK ST & I ROAD INPHARR, TEXAS HIT A 2" TAP ON A 12" TRANSMISSION LINE. THIS IN TURN SPLIT THEWELD ON THE 2" TO 12" CONNECTION. LINE PRESSURE WAS REDUCED TO 20#'S AND A12" SPLIT-SLEEVE CLAMP WAS | 5000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1223 | 1998-05-30 | SC | technical failure | AIKEN | SOUTH CAROLINA PIPELINE CORP | FAILURE OCCURRED IN ERW WELD. METALLURGICAL CONSULTANTS INC HAS DETERMINEDTHE MOST PROBABLE CAUSE TO BE HOOK CRACKS IN THE ERW WELD AREA. ON MAY 30,1998, AT APPROXIMATELY 1:02 PM, SOUTH CAROLINA PIPEINE CORPORATION EXPERIENCEDA FAILURE ON 10" LINE L IN A | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1224 | 1998-06-19 | MS | other | LAMAR | GAYLORD CONTAINER LTD | ROAD GRADING MACH WAS DIGGING DITCH ALONGSIDE OF ROAD AND CUT TO DEEP ANDSTRUCK 8" GAS LINE WITH BLADE, CUTTING A 3" X 1/4" INCH GASH IN PIPELINE | 3000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1225 | 1998-05-19 | LA | technical failure |  | SEA ROBIN PIPELINE CO | A RECENTLY INSTALLED SUBSEA ASSEMBLY DEVELOPED A LEAK IN THE HEAT EFFECTEDWELD ZONE NEAR THE GIRTH WELD ON THE 2" BRANCH OF A 6X6X2 REDUCING TEE. THELEAK WAS DUE TO A TEAR IN THE TEE MATERIAL APPARENTLY CAUSED DURINGSAND-CEMENT BAG COVER INSTALLATION. A | 150000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1226 | 1998-06-15 | TX | other | GALVESTON | TRANSTEXAS TRANSMISSION CORP | DAMAGE WAS APPARENTLY CAUSED BY UNKNOWN FORCES (PERHAPS SHRIMP NETS) DRAGGINGOFF THE ANCHOR WEIGHTS OF THE PIPELINE, ALLOWING IT TO FLOAT UP NEAR THESURFACE WHERE AN UNKNOWN MOTOR VESSEL CAUSED EXTENSIVE PROPERTY DAMAGE. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1227 | 1998-06-06 | LA | other |  | KOCH GATEWAY PIPELINE CO | MINOR BUBBLES DISCOVERED MISS. RIVER REMOTE X-ING NEAR BANK. UNABLE TO VERIFYCAUSE/POSSIBLE FUTURE REPAIR COSTS W/O JEOPARDIZING DIVER SAFETY. BECAUSE OFLIMITED NEED FOR LINE, WE MAY NOT REPAIR IT OR PUT IT BACK IN SERVICE.REPORTED TO NRC JUST IN CASE WE | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1228 | 1998-07-23 | LA | other |  | MID LOUISIANA GAS CO | SUPPLEMENTAL REPORT TO BE FILED AFTER PIPE IS INSPECTED & REPAIR ATTEMPTED.INSPECTION & REPAIR WILL BE DELAYED UNTIL RIVER LEVEL FALLS TO LEVEL SAFE FORDIVER TO WORK. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1229 | 1998-07-07 | LA | other | CONCORDIA | MID LOUISIANA GAS CO | SUPPLEMENTAL REPORT TO BE FILED AFTER PIPE IS INSPECTED AND REPAIR ATTEMPTED.INSPECTION AND REPAIR WILL BE DELAYED UNTIL RIVER LEVEL FALLS TOLEVEL SAFE FOR DIVER TO WORK. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1230 | 1998-07-07 | TX | other | TARRANT | LONE STAR PIPELINE CO (TRANSMISSION DIVISION) | THIRD PARTY CONTRACTOR CUT THE PIPELINE WHILE TRENCHING. | 450000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1231 | 1998-07-21 | WY | other | CAMPBELL | WILLISTON BASIN INTERSTATE PIPELINE CO | THIS INCIDENT OCCURRED AT A RECEIPT POINT WITH A GATHERING SYSTEM OPERATOR. ARELIEF VALVE ON THE GATHERING SYSTEM OPERATED AND CAUGHT FIRE. THE HEAT FROMTHE FIRE DESTROYED WILLISTON BASIN'S RECEIPT STATION. PIPELINE HAS BEENREPAIRED AND SYSTEM IS BACK | 415350 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1232 | 1998-07-15 | AR | other | UNION | NORAM GAS TRANSMISSION, A NORAM ENERGY COMPANY | LIGHTNING STRUCK METER STATION PIPING. THE INSULATING GASKET ON THE OUTLETSIDE OF THE LOWER METER TUBE ISOLATION VALVE FAILED. IGNITION OCCURRED WHERETHE GASKET FAILED. | 80000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1233 | 1998-07-11 | WV | other | WETZEL | CNG TRANSMISSION CORP | WHILE EXCAVATING FOR A NEW PIPELINE IL-492, A PACE PIPELINE TRACK HOE OPERATORWAS BACKFILLING NEW DITCH. SPOIL PILE WAS LOCATED OVER TOP OF EXISTING IL-342WHICH PARALLELS PLANNED TL-492. WHILE REQUIRING DIRT FROM SPOIL PILE, THEEQUIPMENT OPERATOR DUG IN | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1234 | 1998-07-15 | AL | other | CONECUH | CONECUH - MONROE COUNTIES GAS DIST | AT 4:50 PM THE GAS DISTRICT RECEIVED NOTICE BY TELEPHONE OF A GAS LEAK FROMTHE OCCUPANT OF 45687 HIGHWAY 31. THE LOCATION WAS SOUTH OF CASTLEBERRY INCONECUH COUNTY, ALABAMA. SEVERAL DISTRICT PERSONNEL LEFT THE OFFICE TORESPOND TO THE SCENE. THEY DISCOV | 170000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1235 | 1998-07-17 | IN | other | MONROE | INDIANA GAS CO INC | A CONTRACTOR WORKING FOR THE MONROE COUNTY HIGHWAY DEPARTMENT WAS INSTALLINGGUARD RAILING FOR A COUNTY BRIDGE. A TRUCK-MOUNTED PILE DRIVER WAS BEING USEDTO INSTALL ALUMINUM POSTS TO WHICH THE GUARD RAILING WOULD BE ATTACHED. ATAPPROXIMATELY 1:00 PM ON J | 150000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1236 | 1998-07-06 | OR | other |  | PACIFIC GAS TRANSMISSION CO | 14:15-A PG&E GT-NW EMPLOYEE DOING ROUTINE MAINTENANCE DISCOVERED A NATURAL GASLEAK NEAR THE STANFIELD, OREGON CITY METER STATION MAINLINE "A" TAP. IT WASNOT APPARENT IF THE LEAK WAS COMING FROM THE MAINLINE OR THE METER STATIONSERVICE PIPING. PHYSICAL S | 139000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1237 | 1998-07-23 | TX | technical failure |  | ANR PIPELINE CO | PACKING ON 20' CHECK VALVE STEM WAS LEAKING, 30I-20 TAP. | 150000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1238 | 1998-07-23 | LA | technical failure |  | TENNESSEE GAS PIPELINE CO | LEAK DEVELOPED IN STEM PACKING ON A SUBSEA CHECK VALVE. | 70000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1239 | 1998-07-17 | IL | other | MORGAN | PANHANDLE EASTERN PIPELINE CO | DUE TO A LEAKING VALVE, GAS ACCUMULATED IN A DEHY CONTRACTOR TOWER WHERE ANOUTSIDE CONTRACTOR WAS USING A CUTTING TORCH. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1240 | 1998-07-27 | AZ | other | PIMA | EL PASO NATURAL GAS CO | A ROAD GRADER OPERATED BY THE BUREAU OF LAND MANAGEMENT STRUCK THE 4 1/2 INCHLINE 2122 CAUSING A SIX INCH CUT ON THE PIPELINE. THERE WERE TWO TAPS THATWERE SHUT IN. THE PIPE WAS REPAIRED BY INSTALLING A 12-FOOT SECTION OF PIPE.THIS LINE WAS BACK IN SERV | 25000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1241 | 1998-08-08 | LA | maintenance |  | ANR PIPELINE CO | INTERNAL CORROSION - PINHOLE LEAT AT 9 O'CLOCK POSITION. | 58000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1242 | 1998-08-03 | FL | other |  | FLORIDA GAS TRANSMISSION CO | LIGHTING STORM IN VICINITY OF COMPRESSOR STATION INITIATED A STATION ESD ANDIGNITED GAS RELEASED AT BLOWDOWN SILENCER UNITS. | 263000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1243 | 1998-08-02 | AL | other | ST. CLAIR | SOUTHERN NATURAL GAS CO | SOUTHERN'S CONTRACTOR, WORKING ON REPLACEMENT OF A PIPELINE ADJACENT TO THEONE DAMAGED, WAS PLACING PAD DIRT WITH A FRONT END LOADER. DURING A TURN, THEMACHINERY'S BUCKET CUT INTO THE SPOIL AT THE 24" NORTH MAIN LOOP PIPELINE. ATOOTH ON THE BUCKET GOUGE | 65500 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1244 | 1998-08-02 | TX | technical failure | GUADALUPE | OASIS PIPELINE CO | LEAK RESULTED FROM A CRACK WHICH DEVELOPED IN THE BODY OF A MAINLINE VALVE. | 347361 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1245 | 1998-08-14 | FL | other | TAYLOR | FLORIDA GAS TRANSMISSION CO | A COMPRESSOR STATION ESD WAS INITIATED DURING A LIGHTNING STORM IN THEVICINITY OF THE STATION. A LIGHTNING IGNITED THE GAS RELEASED AT THE ESDBLOWDOWN SILENCER UNITS. | 14738000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1246 | 1998-08-28 | TX | maintenance | NUECES | AIR LIQUIDE AMERICA CORP. | DETAILED METALLURGICAL FAILURE ANALYSIS BEING CONDUCTED ON FAILED SECTION OFPIPELINE. SUPPLEMENTAL REPORT WILL BE ISSUED. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1247 | 1998-08-18 | PA | other | CAMBRIA | PEOPLES NATURAL GAS CO | LINE LOCATOR AND CONSTRUCTION COMPANY THAT CAUSED DAMAGE DISAGREE OVER WHETHERACCURATE SITE LOCATION WAS SUBMITTED BY CONSTRUCTION COMPANY. | 60000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1248 | 1989-08-22 | KY | other | BOONE | UNION LIGHT HEAT & POWER CO | WHILE EXCAVATING, A CONTRACTOR DUG INTO A TRANSMISSION PRESSURE GAS MAIN. | 84396 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1249 | 1998-08-28 | LA | maintenance |  | ANR PIPELINE CO | A PINHOLE LEAK AT 5 O'CLOCK POSITION CONSISTENT WITH INTERNAL CORROSION. | 98400 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1250 | 1998-08-26 | LA | maintenance |  | TENNESSEE GAS PIPELINE CO | LEAK CAUSED BY INTERNAL CORROSION. | 250000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1251 | 1998-08-25 | TX | other | VAL VERDE | WEST TEXAS GAS INC | UNDERGROUND CREEK CROSSING WAS WASHED OUT AND PIPELINE SEPARATION WAS CAUSEDBY THE FORCE OF THE WATER OR DEBRIS BEING TAKEN DOWNSTREAM. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1252 | 1998-09-06 | MN | other | CARLTON | GREAT LAKES GAS TRANSMISSION CO | AS STATED ABOVE, THE RUPTURE OCCURRED DUE TO FAILURE IN THE LONG SEAM OF THEPIPE DETERMINED TO BE AT THE SITE OF A CRACK. GREAT LAKES CONTINUES TO HAVEITS CONSULTANTS INVESTIGATE THE FAILURED PIPE SEGMENTS UNTIL A DEFINITVE CAUSECAN BE DETERMINED. IT SH | 1414000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1253 | 1998-09-17 | LA | maintenance |  | TENNESSEE GAS PIPELINE CO | LEAK CAUSED BY INTERNAL CORROSION | 105000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1254 | 1998-09-20 | LA | technical failure |  | TENNESSEE GAS PIPELINE CO | LEAK DEVELOPED IN LOCKING LEVER OF A SUBSEA CHECK VALVE. | 65000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1255 | 1998-09-30 | LA | other |  | TENNESSEE GAS PIPELINE CO | HURRICANE GEORGES CAUSED MUDSLIDE WHICH DAMAGED PIPE. | 3000000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1256 | 1998-09-29 | OK | other | TEXAS | WESTERN GAS INTERSTATE CO | DIRT CONTRACTOR MOVED LOCATIONS WITHOUT GIVING OPERATOR NOTICE OF CHANGE. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1257 | 1998-10-02 | LA | other |  | SOUTHERN NATURAL GAS CO | SHEER JOINT/LOAD LIMITING CONNECTOR (INSTALLED ON PIPELINE IN 1989) FAILED DUETO MUDSLIDE LOADS DURING HURRICANE GEORGES. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1258 | 1998-10-06 | LA | other |  | SOUTHERN NATURAL GAS CO | A THIRD PARTY WORK BARGE BROKE FREE DUE TO HURRICANE GEORGES AND RAN AROUNDON STONE ISLAND IN BLACK BAY, LA. THE BARGE RESTED OVER SOUTHERN'S 10" BLACKBAY PIPELINE AND ITS WEIGHT ULTIMATELY CAUSED IT TO REST ON THE PIPELINERESULTING IN A RUPTURE AND SUBS | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1259 | 1998-09-23 | LA | maintenance |  | DUKE ENERGY CORP | EFFORTS TO LOCATE, ISOLATE, AND REPAIR THE LEAK WERE IMPACTED BY HURRICANEGEORGES. | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1260 | 1998-10-06 | TX | maintenance |  | WILLIAMS FIELD SERVICES | INTERNAL CORROSION | 200000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1261 | 1998-09-03 | TX | maintenance | FT BEND | KOCH GATEWAY PIPELINE CO | CORROSION CAUSED REDUCTION OF THE WALL THICKNESS TO THE POINT OF FAILURE. | 250000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1262 | 1998-10-12 | MS | technical failure | HANCOCK | TENNESSEE GAS PIPELINE CO | VALVE LEAKED RESULTING IN GAS ENTERING WORK AREA. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1263 | 1998-10-12 | TX | other | FREESTONE | LONE STAR PIPELINE CO (TRANSMISSION DIVISION) | 8" PIPELINE BLEW OUT (END TO END). | 54986 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1264 | 1998-10-08 | MN | other | WRIGHT | MINNEGASCO INC | ROAD GRADER ON REPAVING PROJECT CUT GRADE DOWN TO LEVEL OF PIPE AND HIT TEE,PULLING PIPE OUT OF NORMAC FITTING. | 60000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1265 | 1998-10-26 | IA | other | TAMA | NORTHERN NATURAL GAS CO (ENRON) | A 3RD PARTY CONTRACTOR SEVERED THE LINE WHILE EXCAVATING IN A FARMERS FIELD,NNG WAS NOT NOTIFIED OF THE EXCAVATION ACTIVITES. | 52000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1266 | 1998-10-29 | TN | other | MADISON | WILLIAMS GAS PIPELINE - TEXAS GAS | ON THURSDAY, OCTOBER 29, 1998, AT 3:19 PM, CENTRAL STANDARD TIME, WILLIAMS GAS PIPELINE, TEXAS GAS SUSTAINED AN IN-SERVICE FAILURE ON ITS RIPLEY JACKSON 8" NO. 1 LINE IN MADISON COUNTY, TENNESSEE. THE LOCATION OF THE INCIDENT WAS APPROXIMATELY 2.5 MILES | 96838 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1267 | 1998-09-29 | LA | technical failure |  | CHEVRON USA INC | UNDER STATIC CONDITIONS AFTER HURRICANE GEORGES, MECHANICAL FLANGE CONNECTIONSEPARATED FROM PIPELINE RESULTING IN NATURAL GAS RELEASE. | 600000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1268 | 1998-11-30 | LA | maintenance |  | TENNESSEE GAS PIPELINE CO | INTERNAL CORROSION LEAK | 82000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1269 | 1998-12-13 | NM | other | MCKINLEY | EL PASO NATURAL GAS CO | A RATE CHANGE WAS NOTICED AT BLUEWATER COMPRESSOR STATION AND THEN A FIRE WASDISCOVERED ON THE PIPELINE RIGHT-OF-WAY AT THE SAME TIME. A RUPTURE OCCURREDON THE TIE-IN TO A MAINLINE VALVE ON LINE 1300. THE FIRE BURNED FORAPPROXIMATELY 4 HOURS CAUSING DAM | 150000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1270 | 1998-12-06 | LA | other |  | TENNESSEE GAS PIPELINE CO | UNKNOWN DUE TO DAMAGED PIPE BEING UNRECOVERABLE FROM SITE DURING RUPTUREINVESTIGATION. | 750000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1271 | 1998-12-02 | OK | other | MCCLAIN | ONEOK GAS TRANSPORTATION, LLC | AT APPROXIMATELY 1:40PM CST ON DECEMBER 2, 1998, AN EMPLOYEE OF ONEOK GASTRANSPORTATION, LLC. (OGT) WAS INJURED BY A 20" PIPELINE CLEANING PIG THATRAPIDLY EXITED A 20" RECEIVER BARREL ON PIPELINE A-1300, LOCATED NORTWEST OFPURCELL, OKLAHOMA. PLEASE NOTE | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1272 | 1998-12-10 | OK | other | HUGHES | CENTRAL OKLAHOMA OIL & GAS CO. | ON DECEMBER 10, 1998, CENTRAL OKLAHOMA OIL AND GAS CORP. (OPERATOR) WAS IN THEPROCESS OF REWORKING ONE OF ITS EXISTING UNDERGROUND NATURAL GAS STORAGE WELLSLOCATED IN THE STUART NATURAL GAS STORAGE FACILITY IN HUGHES COUNTY,OKLAHOMA. AT APPROXIMATELY 1:3 | 20000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1273 | 1998-12-10 | CA | other | KING | SOUTHERN CALIFORNIA GAS CO | PIPELINE WAS MISLOCATED. SPECIAL EQUIPMENT REQUIRED TO MOVE BULL DOZER OFF OFDAMAGED PIPELINE. | 350000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1274 | 1998-11-14 | IL | maintenance | CHAMPAIGN | PEOPLES GAS LIGHT & COKE CO |  | 345000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1275 | 1998-09-23 | TX | maintenance | WHARTON | TRUNKLINE GAS CO | LEAK OCCURRED DUE TO LOSS OF WALL THICKNESS RESULTING FROM INTERNAL CORROSION. | 400000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1276 | 1998-12-07 | IL | maintenance | KANKAKEE | NATURAL GAS PIPELINE CO OF AMERICA | FAILURE OF THE 24' DIAMETER CLASS "C" DRIP RESULTED IN A FIRE. INTENSE HEATFROM THE FIRE EVENTUALLY CAUSE THE 36" DIAMETER CARRIER PIPE TO RUPTURE. | 396100 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1277 | 1998-11-23 | WY | technical failure | FREMONT | K N ENERGY INC(KANSAS NEBRASKA GAS CO) | ON NOVEMBER 23, 1998 AT 1:12PM, AN AGENT OF KN ENERGY, MR. DOUG THACKER,REPORTED TO YOU A GAS LEAK ON THE NORTHERN GAS COMPANY (NGC) 16' INTRASTATEPIPELINE. AT 11:30AM ON NOVEMBER 23,1998 THE GAS LEAK WAS CONFIRMED ON THENGC 16' INTRASTATE PIPELINE IN FR | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1278 | 1998-12-17 | PA | maintenance | ARMSTRONG | CNG TRANSMISSION CORP | THIS LETTER PRESENTS MY PRELIMINARY FINDINGS REGARDING THE CAUSE OF THERUPTURED OF CNG'S 26-INCH PIPELINE WHICH OCCURRED ON DECEMBER 17, 1998 NEARELDERTON, PENNSYLVANIA. THE RUPTURE WAS CAUSED BY EXTERNAL CORROSION WHICHHAD TAKEN PLACE ON THE BOTTOM OF T | 500000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1279 | 1998-12-16 | TX | technical failure |  | AQUILA SOUTHWEST (EX. CLAJON GAS CO) |  | 15000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1280 | 1999-01-17 | LA | other |  | TRUNKLINE GAS CO |  | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1281 | 1999-01-02 | OR | technical failure | UMATILLA | NORTHWEST PIPELINE CORP |  | 500000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1282 | 1998-12-21 | OR | other | JEFFERSON | PG&E GAS TRANSMISSION-NORTHWEST |  | 57000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1283 | 1999-01-17 | LA | maintenance | OFFSHORE LA | COLUMBIA GULF TRANSMISSION CO | SUSPECT BACTERIA CORROSION. INSTALLED TWO REPAIR CLAMPS AT X=231850.28 ANDX=1367347.55 Y=235176.30. | 350000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1284 | 1999-02-02 | AL | other | TALLADEGA | CHILDERSBURG GAS BOARD | AT APPROXIMATELY 7:45 AM, THE BOARD AFTER HOURS OPERATOR WAS NOTIFIED BY THECHILDERSBURG POLICE THAT LINCOLN POLICE HAD CALLED REPORTING AN EXPLOSION ATTHE HOLIDAY INN EXPRESS IN LINCOLN. AT APPROXIMATELY 7:50 AM, BOARDEMPLOYEES, JERRY CARPENTER, GENERAL | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1285 | 1999-01-25 | TX | other | POLK | MIDCON TEXAS PIPELINE CORP. | EXTEME VARIATIONS IN TRINITY RIVER WATER ELEVATIONS MAY HAVE BEEN ACONTRIBUTING FACTOR. | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1286 | 1999-02-02 | TX | maintenance | GREGG | TEJAS GAS CORP | MICROALLOYING INTERNATIONAL, INC. WAS COMMISSIONED TO INVESTIGATE THE FAILUREOF A NATURAL GAS PIPELINE FOR TEJAS LLS. THE PIPELINE IS FABRICATED FROM 20OF A NATURAL GAS PIPELINE FOR TEJAS LLC. THE PIPELINE IS FABRICATED FROM 20INCH DIAMETER, 0.312 INCH | 150000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1287 | 1999-01-30 | LA | other | EAST CARROLL PARISH | SOUTHERN NATURAL GAS CO | COMPANY WAS NOTIFIED BY THE PUBLIC OF A LARGE COLUMN OF WATER BLOWING IN THEAIR IN EAST CARROLL PARISH LOUISIANA. EMPLOYEES DISPATCHED TO THE SITEDETERMINED THE CAUSE TO BE A LEAK ON THE 22" NORTH MAIN PIPELING IN LONG LAKEBAYOU. THE AREA HAD RECEIVED 8 | 165000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1288 | 1999-01-13 | TX | other | POLK | MIDCON TEXAS PIPELINE CORP. | EXTREME VARIATIONS IN TRINITY RIVER WATER ELEVATIONS MAY HAVE BEEN ACONTRIBUTING FACTOR. | 200000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1289 | 1999-01-03 | VA | other | WYTHE | EAST TENNESSEE NATURAL GAS CO | FIRE FROM NEARBY NATURAL GAS PIPELINE FACILITY DAMAGED EAST TENNESSEE NATURALGAS METER STATION. | 125000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1290 | 1999-02-24 | PA | technical failure | POTTER | NATIONAL FUEL GAS SUPPLY CORP | GASKET ON BACK OF VALVE FAILED. THIS FILLED THE COMPRESSOR STATION WITH GAS.THE GAS IGNITED AND BURNT IN THE COMPRESSOR STATION. | 5000000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1291 | 1998-03-29 | TX | maintenance | POLK | NATURAL GAS PIPELINE CO OF AMERICA | COMPLEX INTERACTION OF SOIL ENVIRONMENT, PIPE MATERIALS, AND OPERATINGCONDITIONS. | 112036 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1292 | 1999-02-26 | WA | other | SKAMANIA | NORTHWEST PIPELINE CORP | EXCESSIVE RAIN. LAND MOVEMENT | 4000000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1293 | 1999-03-07 | MI | technical failure |  | CONSUMERS POWER CO | CAUSE OF FAILURE WAS LACK OF FUSION IN THE LONGITUDINAL WELD OF A LENGTH OF12" PIPE. | 700000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1294 | 1999-03-03 | NJ | technical failure | ESSEX | TRANSCO GAS PIPELINE CORP | INVESTIGATION FOUND THE LEAK TO BE IN A CRACK IN THE WALL OF THE 36" LINE PIPEWHERE THE HOT TAP NIPPLE IS CONNECTED. THE HOT TAP CONNECTION INCLUDING THELINE PIPE CONTAINING THE PIPE IS BEING SENT TO THE METALLURGIST. RESULTS OFTHE METALLURGICAL EXAMS W | 80000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1295 | 1999-02-28 | CA | other | BUTTE | WILD GOOSE STORAGE INC | WE HAD BEEN OPERATING THE PIPELINE FOR 6 MONTHS AT 1400 PSI. BECAUSE THEOPERATING PRESSURE WOULD BE INCREASING IN THE NEAR FUTURE THE DECISION WASMADE TO BLOCK IN THE WELLS ALLOWING THE PIPELINE PRESSURE TO INCREASE TO ITSMAXIMUM WORKING PRESSURE. WHEN T | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1296 | 1999-03-23 | LA | other |  | COLUMBIA GULF TRANSMISSION CO | A TRAWLING NET DAMAGED THE BLEEDER VALVE ON THE 16" CHECK VALVE SHAFT COVERAND PULLED THE OPERATOR OFF THE 12" VALVE THEREFORE DAMAGING THE VALVESYSTEM. THE BLEEDER VALVE AND NIPPLE ON THE 16" CHECK VALVE WERE REPLACED ANDTHE STEM AND OPERATOR ON THE 12" | 70000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1297 | 1999-05-13 | TX | maintenance | ORANGE | MIDCON TEXAS PIPELINE CORP. |  | 45000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1298 | 1999-05-12 | WI | other | GREEN | NORTHERN NATURAL GAS CO (ENRON) |  | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1299 | 1999-05-28 | OK | maintenance | GRADY | ONEOK GAS TRANSPORTATION, LLC | APPARENT CAUSE- INTERNAL CORROSION. LAB TESTING PENDING. TELEPHONIC REPORT#485403APPARENT CAUSE-- INTERNAL CORROSION. LAB TEST PENDING. TELEPHONIC REPORT #485403 | 70000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1300 | 1999-05-20 | LA | technical failure |  | COLUMBIA GULF TRANSMISSION CO | DEFECT ON 24" CHECK VALVE AT BOTTOM OF RISER. | 60000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1301 | 1999-06-13 | IL | maintenance | LIVINGSTON | NORTHERN ILLINOIS GAS CO | AT THE ANCONA STATION, A 12" NATURAL GAS DRIP RUPTURED AND IGNITED RESULTING IN PROPERTY DAMAGE TO THE STATION FACILITIES. THE DRIP IS USED TO COLLECT LIQUIDS FROM THE GATHERING SYSTEM. PRELIMINARY INVESTIGATION SHOWS INTERNAL CORROSION AS THE CAUSE OF | 1800000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1302 | 1999-07-10 | TX | maintenance | PANOLA | NATURAL GAS PIPELINE CO OF AMERICA | INTERNAL CORROSION OF THE CARRIER PIPE | 361000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1303 | 1999-07-18 | WV | other | BROOKE | COLUMBIA GAS TRANSMISSION CORP |  | 80000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1304 | 1999-08-26 | TX | other | KENT | SPUR, CITY OF | STATE CONTRACTOR WAS WIDENING ROAD AND CUTTING A BAR DITCH AND HIT LINE WITH THE CATERPILLAR. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1305 | 1999-08-23 | WV | maintenance | MARSHALL | COLUMBIA GAS TRANSMISSION CORP | ON 8/23/99 16" STORAGE LINE 29104 RUPTURED, WITH AN ENSUING FIRE. PRELIMINARY ASSESSMENT OF THE DAMAGE IS 5-7 ACRES OF FARMLAND BURNED, HEAT DAMAGE TO A GARAGE, ROOF DAMAGE TO A MOBILE HOME, AND DAMAGE TO A GRAVEL STATE ROAD (FISH RIDGE ROAD). THERE WER | 71000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1306 | 1999-08-14 | TX | other | JACKSON | TRUNKLINE GAS CO | THE PIPELINE FAILED IN A COMPRESSIVE MODE AS A RESULT OF THE PIPELINE HEATING AND EXPANDING APPROXIMATELY 30 INCHES. THE HEATING WAS CAUSED BY THE PRESENCE OF IRON SULFIDE INSIDE THE PIPELINE AND A SUBSEQUENT EXOTHERMIC REACTION THAT RESULTED WHEN AIR WA | 500000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1307 | 1999-08-16 | MI | other | GOGEBIC | GREAT LAKES GAS TRANSMISSION CO | A LIGHTNING STRIKE CAUSED THE MAIN LINE VALVE (WHICH IS NORMALLY CLOSED) TO CYCLE PARTIALLY OPEN. THIS PARTIALLY OPEN CONDITION CAUSED VIBRATION IN THE MAIN LINE VALVE ASSEMBLY TO OCCUR. THIS VIBRATION SUBSEQUENTLY CAUSED A CRACK TO DEVELOP IN THE HEAT- | 163000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1308 | 1999-08-11 | TX | maintenance | CRANE | DYNEGY MIDSTREAM SERVICES, L.P. | THERE WERE NO SIGNS OF OUTSIDE PIPELINE CORROSION OR DAMAGE OF ANY TYPE. CORROSION COUPONS DO NOT INDICATE ANY PROBLEMS ASSOCIATED WITH THE CORROSION PROGRAM. PIPELINE OPERATION WAS NORMAL, NO PRESSURE FLUCTUATIONS WERE NOTED AT THE TIME OF FAILURE. AC | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1309 | 1999-09-23 | LA | maintenance | nan | BASIN EXPLORATION INC |  | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1310 | 1999-08-15 | LA | other | PLAQUEMINES | MID LOUISIANA GAS CO | DRAGLINE CAUGHT PIPE WITH ONE TOOTH OF BUCKET. | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1311 | 1999-09-01 | TX | other | HUDSPETH | EL PASO NATURAL GAS CO | AT APPROXIMATELY 4:30 PM, SEPT 1, 1999 THREE EL PASO NATURAL GAS EMPLOYEES RECEIVED SECOND DEGREE BURNS TO THEIR FACES AND WRISTS WHEN A FLASH FIRE OCCURRED AFTER PLACING A BLIND FLANGE BACK ON A 6-INCH BLOWOFF. A 12-INCH BYPASS BEING INSTALLED WHEN GAS | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1312 | 1999-09-13 | AZ | other | GREENLEE | EL PASO NATURAL GAS CO | AT 9:30 AM A FARMER PLOWING A FIELD HIT AND PUNCTURED THE 6 5/8 INCH PIPELINE BETWEEN VALVE 2 AND VALVE 3. BOTH VALVES WERE SHUT-IN TO ISOLATE THE SEGMENT. HIGHWAY 75 FROM MILE MARKERS 395 TO 400 WAS CLOSED AND THE NEARBY VALLEY VIEW TRAILER PARK WAS EV | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1313 | 1999-09-12 | NM | technical failure | SAN JUAN | EL PASO NATURAL GAS CO | ON SEPT 12, 1999, GAS CONTROL RECEIVED A CALL AT 8:05 PM FROM THE SHIPROCK POLICE ABOUT A RUPTURE ON OUR PIPELINE. EPNG PERSONNEL RESPONDED TO THE CALL AND ISOLATED THE SEGMENT BEWTEEN VALVES 2 1/2 AND VALV3 3. REPAIR CREWS WERE ON SITE THE NEXT MORNING A | 174800 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1314 | 1999-09-08 | TX | other | nan | NORTHERN NATURAL GAS CO (ENRON) | A 2" THREADED PIPE NIPPLE AND VALVE THAT WAS ATTACHED TO A 12" PIPELINE TEE AND FLANGE WAS CAUGHT BY A FISHING NET. THE PIPE NIPPLE WAS BENT SLIGHTLY AT ITS THREADED CONNECTION, RESULTING IN A SMALL LEAK. | 150000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1315 | 1999-09-23 | TN | other | OBION | WILLIAMS GAS PIPELINE - TEXAS GAS | ON THURSDAY, SEPTEMBER 23, 1999, AT 1:00 A.M. CENTRAL STANDARD TIME. WILLIAMS GAS PIPELINE-TEXAS GAS SUSTAINED AN IN-SERVICE FAILURE ON ITS 26" MAINLINE SYSTEM. NO. 2 PIPELINE IN OBION COUNTY, TENNESSEE. THE LOCATION OF THE INCIDENT WAS MILEPOST 346+51 | 312750 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1316 | 1999-09-25 | LA | maintenance | nan | SEA ROBIN PIPELINE CO | A PINHOLE LEAK WAS DETECTED VISUALLY AS BUBBLES ON THE WATER SURFACE. ISOLATION VALVES WERE CLOSED TO INACTIVATE THE PIPELINE. A REPAIR CLAMP WAS INSTALLED WAS COST OF REPAIRS ONLY. | 200000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1317 | 1999-10-05 | NV | other | CLARK | SOUTHWEST GAS CORP | WHILE AN OPERATOR WITH ACME ELECTRIC WAS OPERATING A FRONT END LOADER, HE STRUCK AND DAMAGED AN 8" STEEL PSIG GAS MAIN. THE CONTRACTOR DID HAVE A CURRENT USA (ONE CALL) TICKET BUT WAS WORKING OUTSIDE OF THE SPECIFIED AREA. THE GAS MAIN LOCATE WAS CORREC | 182100 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1318 | 1999-09-20 | MT | other | JEFFERSON | MONTANA POWER CO | A SEMI TRACTOR TRAILER RIG ROLLED FROM A TRUCK STOP DOWN AN EMBANKMENT AND INTO THE CITY GATE STATION AT MP 26.6 ON THE MPC 4" EAST HELENA-BOULDER NATURAL GAS TRANSMISSION LINE. THE IMPACT DESTROYED THE GATE STATION BUILDING AND BROKE PIPING INSIDE THE Y | 114000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1319 | 1999-10-16 | TX | other | nan | COASTAL OIL & GAS CORP (SUBSIDIARY OF ANR PROD CO) | FITTING WAS NOT PROPERLY TIGHTENED AT THE NEW PIPELINE TIE-IN | 74287 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1320 | 1999-10-27 | LA | maintenance | CAMERON | WILLIAM FIELD SERVICES | LEAK WAS CAUSED BY INTERNAL BACTERIAL CORROSION AT THE 5:30 POSITION. | 250000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1321 | 1999-10-26 | TX | technical failure | nan | WILLIAM FIELD SERVICES | A 12" VALVE BODY BLEED ORIFICE HAD BEGUN TO LEAK AS A RESULT OF FLATTENED THREADS ON THE ORIFICE SCREW. THE AFFECTED VALVE WAS 12" TAP VALVE. THE VALVE BODY ORIFICE THREADS WERE RE-DRILLED TO ACCEPT A LARGER 3/4" SCREW TO SECURE THE ORIFICE FROM LEAKING | 60000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1322 | 1999-11-03 | OK | other | BRYAN | ENOGEX INC (EX. MUSTANG FUEL CORP) | DIAPHRAM RUPTURE DUE TO WEATHER FATIGUE CAUSED DUMP VALVE FAILURE ON ESD VENT VALVE, CAUSING ESD VENT TO OPEN AND RELEASE GAS. | 73000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1323 | 1999-11-13 | AK | other | nan | BP EXPLORATION ( ALASKA), INC | CRACK IN A GIRTH WELD. A FAILURE ANALYSIS WILL BE PERFORMED ON WELD TO DETERMINE CAUSE. SUPPLEMENTAL INFO:WIND INDUCED VIBRATION OF THE ELEVATED PIPELINE CREATED HIG CYCLIC STRESSES CAUSING A FATIGUE FAILURE OF A GIRTH WELD. THE WIND INDUCED VIBRATION WA | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1324 | 1999-11-17 | AR | other | WASHINGTON | ARKANSAS WESTERN GAS CO | A THIRD PARTY CONTRACTOR WAS CUTTING IN A NEW SUBDIVISION STREET WITH A LARGE EARTH MOVER WHEN IT SEVERED A 4 1/2" STEEL TRANSMISSION LINE. THE GAS IGNITED SEVERELY DAMAGING THE EARTH MOVER. | 90000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1325 | 1999-11-11 | IA | other | FAYETTE | NORTHERN NATURAL GAS CO (ENRON) | TILLING CONTRACTOR CHANGED PLANS WITHOUT SUBMITTING NEW LOCATE REQUEST OR NOTIFYING NNG. CONTRACTOR HIT LINE WITH TILLING PLOW. | 145184 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1326 | 1999-11-11 | OK | other | LE FLORE | OKLAHOMA NATURAL GAS CO | LANDOWNER/DEVELOPER CUT THE LINE WHILE EXCAVATING. THE OPERATOR BROKE HIS LEG BY JUMPING OFF THE DOZER AND WAS SUBSEQUENTLY HOSPITALIZED. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1327 | 1999-11-11 | CA | other | COLUSA | PACIFIC GAS & ELECTRIC CO | OUR INVESTIGATION DISCLOSED THAT APPROXIMATELY 1406 HOURS ON NOVEMBER 11, 1999, A RECLAMATION DISTRICT NUMBER 1004 EQUIPMENT OPERATOR HIT A 12-INCH STEEL NATURAL GAS TRANSMISSION PIPELINE NEAR THE INTERSECTION OF GRIDLEY AND BUTLER ROAD, ALLOWING GAS TO E | 103000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1328 | 1999-11-09 | KS | maintenance | MIAMI | PANHANDLE EASTERN PIPELINE CO | FAILURE IN AREA OF GENERAL CORROSION. | 300000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1329 | 1999-11-24 | CA | other | ALAMEDA | PACIFIC GAS & ELECTRIC CO |  | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1330 | 1999-12-09 | MS | maintenance | COVINGTON | KOCH GATEWAY PIPELINE CO | SMALL EXTERNAL CORROSION PIT LEAKING IN CASING UNDER ROAD. RELEASE DID NOT CAUSE A THREAT TO PUBLIC SAFETY BUT WAS REPORTED DUE TO REPAIR COST EXCEEDING $50,000 REPORTING LIMIT. | 120000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1331 | 1999-12-18 | TX | other | THOMPSONVILLE | TEJAS GAS OPERATING LLC | TEXAS ONE CALL LAW PROCEDURES NOT FOLLOWED BY CONTRACTOR. SEE ATTACHEMENT "A" | 200000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1332 | 2000-01-01 | MI | maintenance | GRAND TRAVERSE | MICHIGAN CONSOLIDATED GAS CO (MICHCON) | TWO SNOWMOBILERS IN THE PIPELINE RIGHT OF WAY HAD MECHINCAL PROBLEMS. THEY WERE USING A CIGARETTE LIGHTER TO SEE WITH. WE HAVENT BEEN ABLE TO DETERMINE IF GASOLINE VAPOR OR LEAKING NATURAL GAS FIRST IGNITED CAUSING THE INJURIES. BOTH WERE TREATED AND R | 2000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1333 | 1999-12-22 | OK | technical failure | LATIMER | RELIANT ENERGY - ARKLA | PIPE SETTING ON ROCK LEDGE, WHICH CAUSED DENT AND PUNCTURE IN PIPE. NO CORROSION FOUND. SMALL LEAK LOCATED, NO DAMAGE TO PROPERTY EXCEPT PIPELINE. | 80000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1334 | 1999-12-20 | CA | other | SAN BENITO | PACIFIC GAS & ELECTRIC CO |  | 122000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1335 | 2000-01-24 | MA | other | MIDDLESEX | TENNESSEE GAS PIPELINE CO | MAIN LINE VALVE DID NOT FULLY CLOSE CAUSING OPERATOR TO VENT TO ATMOSPHERE, RESULTING IN LOCAL AUTHORITIES EVACUATING NEARBY VICINITY. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1336 | 1999-12-10 | TX | other | LIVE OAK | HOUSTON PIPELINE CO | THE UNKNOWN ACCUMULATION OF LIQUID FUMES IN THE TRENCH AREA. IGNITED BY WELDERS CUTTING TORCH. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1337 | 1999-12-31 | TX | maintenance | nan | NORTHERN NATURAL GAS CO (ENRON) |  | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1338 | 2000-01-11 | NJ | other | HUNTERDON | COLUMBIA GAS TRANSMISSION CORP | WHILE DRIVING A PIECE OF PIPE IN THE GROUND TO ANCHOR A DRILLING MACHINE, A CONTRACTOR PUNCTURED THE PIPELINE. | 70000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1339 | 2000-02-01 | LA | technical failure | OUACHITA | TENNESSEE GAS PIPELINE CO | APPARENT FAILURE IN A WELD. | 190000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1340 | 2000-01-27 | LA | maintenance | nan | RELIANT ENERGY - ARKLA | PIPE FAILED IN BOTTOM OF SMALL CREEK, INITAL EVALUATION APPEARS THAT ERROSION CORR. CAUSED GENERAL THINNING OF THE PIPE WALL ON TOP. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1341 | 2000-02-02 | TX | maintenance | POLK | NATURAL GAS PIPELINE CO OF AMERICA (KMI) | INTERACTION OF SOIL ENVIRONMENT PIPE MATERIAL AND OPERATING CONDITIONS | 129000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1342 | 2000-02-18 | NY | technical failure | ONONDAGA | TENNESSEE GAS PIPELINE CO | CRACK IN PIPE WALL DUE TO MANUFACTURING DEFECT (DETERMINED AFTER EXCAVATION). | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1343 | 2000-02-11 | PA | other | CLARION | CNG TRANSMISSION CORP | ON FRIDAY, FEBRUARY 11, 2000, CNG TRANSMISSION PIPELINE LN-200 WAS STRUCK BY A CONTRACTORS DOZER WORKING FOR TEXAS KEYSTONE, INC WHILE EXCAVATING A DRAINAGE POND/PIT FOR A NEW PRODUCTION WELL. TEXAS KEYSTONE PLACED A ONE-CALL NOTICE AFTER THE INCIDENT BU | 75000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1344 | 2000-02-05 | TX | other | FREESTONE | TXU LONE STAR PIPELINE | FAILED PORTION OF PIPE WAS SENT TO LAB FOR ANALYSIS TO IDENTIFY ROOT CAUSE OF FAILURE. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1345 | 2000-01-27 | TX | other | WISE | TXU LONE STAR PIPELINE | FAILED PORTION OF PIPE SENT TO LAB FOR ANALYSIS TO IDENTIFY ROOT CAUSE OF FAILURE. THIRD PARTY CONTRACTOR WAS WORKING IN PIPELINE RIGHT OF WAY BUT IT IS NOT KNOWN IF THIS IS A CONTRIBUTING FACTOR AT THIS TIME. SUPPLEMENTAL INFORMATION : METALLURGICAL TES | 130000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1346 | 2000-01-29 | FL | maintenance | BREVARD | FLORIDA GAS TRANSMISSION CO (ENRON) |  | 263000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1347 | 2000-02-23 | MI | other | CLARE | ANR PIPELINE CO | THERE WERE SEVERAL MECHANISMS, COMBINED, THAT CONTRIBUTED TO THE RUPTURE OF THE 12" LINCOLN PIPELINE. THE CONTRIBUTING FACTORS WERE: FROST HEAVE; MISMATCH OF PIPE ENDS DUE TO HIGH-LOW DURING TIE-IN OF A 15-FOOT REPLACEMENT IN 1993 (NOTE: THE HIGH-LOW WAS | 297000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1348 | 2000-02-18 | TX | other | EL PASO | SOUTHERN UNION GAS CO | THIRD PARTY CONTRACTOR EXVACATING FOR DRAINAGE IMPROVEMENTS RELATED TO DEVELOPMENT OF COMMERCIAL PROPERTY FAILED TO CALL FOR UTILITY LOCATIONS PRIOR TO EXCAVATING. EQUIPMENT STRUCK AND DAMAGED 16" WRAPPED STEEL GAS MAIN CAUSING LEAKAGE. ISOLATION OF MAIN | 79000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1349 | 2000-02-27 | PA | maintenance | POTTER | TENNESSEE GAS PIPELINE CO | STRESS CORROSION CRACKING AUGMENTED BY A BEND IN THE PIPE. | 143000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1350 | 2000-02-23 | LA | maintenance | CAMERON | WILLIAMS ENERGY GROUP-FIELD SERVICES | LEAK WAS CAUSED BY INTERNAL BACTERIAL CORROSION AT THE 5:30 POSITION. | 120000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1351 | 2000-02-25 | TX | other | NOLAN | TXU LONE STAR PIPELINE |  | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1352 | 2000-03-16 | MS | other | COVINGTON | KOCH GATEWAY PIPELINE CO | VERY SMALL RELEASE WAS DETECTED USING LEAK DETECTION EQUIPMENT. BECAUSE OF THE PROXIMITY OF THE RELEASE TO A ROAD, A NEW CROSSING IS REQUIRED TO MAKE THE REPAIR. RELEASE DID NOT CAUSE A THREAT TO PUBLIC SAFETY BUT WAS REPORTED DUE TO COST EXCEEDING $50, | 110000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1353 | 2000-03-15 | MS | other | WARREN | KOCH GATEWAY PIPELINE CO | VERY SMALL RELEASE WAS DETECTED USING LEAK DETECTION EQUIPMENT. BECAUSE OF THE PROXIMITY OF THE RELEASE TO ROAD, A NEW CROSSING IS REQUIRED TO MAKE THE REPAIR. RELEASE DID NOT CAUSE A THREAT TO PUBLIC SAFETY BUT WAS REPORTED DUE TO REPAIR COST EXCEEDING $ | 130000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1354 | 2000-03-08 | NV | other | CLARK | SOUTHWEST GAS CORP | WHILE AN OPERATOR WITH M&M CONSTRUCTION WAS GRADING FOR A WALL WITH A D-9 CAT, HE STRUCK AND DAMAGED A 16" STEEL; 300 PSIG GAS MAIN. THE CONTRACTOR DID HAVE A CURRENT USA (ONE CALL) TICKET. THE GAS MAIN LOCATE WAS CORRECT AND PERMANENT LINE MARKERS WERE | 76170 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1355 | 2000-03-22 | TX | maintenance | KARNES | PG & E TEXAS PIPELINE, L.P. | PG&E TEXAS PIPELINE, LP WAS NOTIFIED THAT A PIPELINE NORTH OF OUR BURNELL COMPRESSOR STATION HAD BLOWN OUT AND WAS ON FIRE. EMPLOYEES VERIFIED THAT THIS WAS OUR EAST SADF 20" (THE SITE OF THE BLOWOUT WAS APPROXIMATELY 8 MILES SOUTH OF KENEDY, TX ON US H | 360000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1356 | 2000-03-22 | MS | other | JEFFERSON DAVIS | KOCH GATEWAY PIPELINE CO | MINOR RELEASE UNDER ROAD. RELEASE DID NOT CAUSE A THREAT TO PUBLIC SAFETY BUT WAS REPORTED DUE TO REPAIR COST EXCEEDING $50,000 REPORTING LIMIT. | 78771 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1357 | 2000-03-27 | OK | maintenance | GRAY | NATURAL GAS PIPELINE CO OF AMERICA (KMI) | INTERACTION OF SOIL ENVIRONMENT, PIPE MATERIAL AND OPERATING CONDITIONS. | 150000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1358 | 2000-03-30 | CA | other | KERN | PACIFIC GAS & ELECTRIC CO | A SEMITRAILER DROVE OFF THE ROAD, KNOCKING DOWN THE CHAIN LINK FENCE SURROUNDING THE STATION. THE TRUCK THEN STRUCK AND DEMOLISHED THE BUILDING THAT HOUSED SCADA CONTROLS FOR PLS 3. A RADIO ANTENNA ON TOP OF THE BUILDING WAS KNOCKED DOWN AND STRUCK THE | 200000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1359 | 2000-04-24 | LA | maintenance | nan | ANR PIPELINE CO | SUSPECTED INTERNAL CORROSION - PINHOLE LEAK AT THE 5 OCLOCK POSITION | 79000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1360 | 2000-04-26 | LA | maintenance | nan | TENNESSEE GAS PIPELINE CO | LEAK UPSTREAM OF CHECK VALVE AT SIX OCLOK POSITION. | 150000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1361 | 2000-05-02 | MS | other | WASHINGTON | WILLIAMS GAS PIPELINE - TEXAS GAS | FLASH FIRE ONLY NO FAILURE. ON TUESDAY MAY 2, 2000 AT 12:10 P.M. CENTRAL STANDARD TIME, AN INCIDENT OCCURRED DURING A TURBINE CONSTRUCTION PROJECT AT THE WILLIAMS GAS PIPELINE-SOUTHCENTRAL COMPRESSOR STATION AT GREENVILLE, MS. THE LOCATION OF THE INCIDE | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1362 | 2000-05-07 | OK | other | ATOKA | NATURAL GAS PIPELINE CO OF AMERICA (KMI) | A FIRE OCCURRED IN THE STATIONS SERVICE BUILDING. THE BUILDING WHICH HOUSES THE GENERATORS, AIR COMPRESSORS CONTROL ROOM TECH. SHOP BREAK ROOM OFFICE AND STORAGE AREA WAS HEAVILY DAMAGED. WITH THE EXCEPTION OF THE TWO GENERATORS ALL CONTENTS OF THE BUILDI | 1950000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1363 | 2000-05-18 | KY | other | PIKE COUNTY | COLUMBIA GAS TRANSMISSION CORP | IN 1999 THIS PIPELINE WAS RELOCATED TO THE CURRENT LOCATION AT THE REQUEST OF THE SURFACE MINING COMPANY. A ROW OF TREES WAS LEFT IN PLACE AS A BUFFER BETWEEN THE MINE AREA AND COLUMBIAS RIGHT-OF-WAY. THE RELOCATION WAS COMPLETED IN NOVEMBER 1999 AND COLU | 59800 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1364 | 2000-05-13 | PA | other | PERRY COUNTY | TEXAS EASTERN TRANSMISSION CORP (DUKE) | THE EMERGENCY SHUTDOWN DEVICE (ESD) ACTIVATED AT COMPRESSOR STATION BY LIGHTING STRIKE TO COMPRESSOR UNIT GAS MONITOR. ALL EQUIPMENT OPERATED PROPERLY WITH THE EXCEPTION OF A SUCTION VALVE THAT DID NOT CLOSE AUTOMATICALLY. THIS ALLOWED GAS TO CONTINUE VEN | 99000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1365 | 2000-06-19 | TX | maintenance | nan | NATURAL GAS PIPELINE CO OF AMERICA (KMI) | A LEAK OCCURRED ON THE ISLAND 16" LATERAL, 18.5 MILES FROM THE BEACH. | 217243 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1366 | 2000-06-03 | MN | other | OTTERTAIL | VIKING GAS TRANSMISSION CO | ON JUNE 3, 2000 THE WEEKEND DUTY PERSON WAS MAKING ROUNDS PERFORMING ROUTINE INSPECTIONS IN VIKINGS SOLAR CENTAUR GAS TURBINE COMPRESSOR PACKAGE WHEN HE DISCOVERED A 3/8 FITTING ON THE HIGH PRESSURE SEAL OIL LUBE SYSTEM LEAKING. THE STATION DISTRICT FOREM | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1367 | 2000-06-17 | LA | other | nan | TENNESSEE GAS PIPELINE CO | A LEAK WAS REPORTED AND DETERMINED TO BE ON A TENNESSEE GAS PIPELINE FACILITY AT 10 A.M. ON 6/17/00 ON THE 507K-100 LINE (26" LINE) IN THE WC 177A. | 600000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1368 | 2000-06-14 | WY | other | NATRONA | NORTHERN GAS CO | THIRD PARTY EXCAVATION DAMAGE--A DOZER WITH RIPPER STRUCK A HOLE IN THE MAINLINE DAMAGING A SECTION OF PIPELINE. THIS SECTION WAS REPLACED WITH 14 FEET OF 0.25W X-52 16" PIPE. | 53230 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1369 | 2000-06-22 | TX | maintenance | BRAZORIA | FLORIDA GAS TRANSMISSION CO (ENRON) | PIPELINE FAILURE THE RESULT OF LOCALIZED STRESS CORROSION CRACKING OF PIPE EXTERNAL SURFACE.PIPELINE FAILURE THE RESULT OF LOCALIZED STRESS CORROSION CRACKING OF PIPE EXTERNAL SURFACE. | 65000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1370 | 2000-07-05 | LA | other | nan | SOUTHERN NATURAL GAS CO | A TUGBOAT, OCEAN SCRAMBLER, STRUCK THE MARKED 14" ROMERE PASS TRANSMISSION PIPELINE CAUSING THE RUPTURE. SUBSEQUENTLY, THE M/V LADY MELINDA ARRIVED AND THEN IGNITION OCCURRED. | 500000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1371 | 2000-07-05 | LA | maintenance | nan | TENNESSEE GAS PIPELINE CO | A LEAK WAS REPORTED AND DETERMINED TO BE ON A TENNESSEE GAS PIPELINE FACILITY AT 12:10P.M. ON 7/5/2000 ON THE 507A-3200 LINE IN EC BLOCK 33C. | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1372 | 2000-06-29 | LA | other | nan | COLUMBIA GULF TRANSMISSION CO | 1/2 BODY BLEED VALVE ON 16" BLOCK VALVE BROKEN OFF BY A TRAWLER. | 57000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1373 | 2000-07-02 | IN | technical failure | RANDOLPH | ANR PIPELINE CO | A 30" GIRTH WELD WAS LEAKING AT THE 6 OCLOCK (1/8" WIDE X 1-1/4" LONG). | 75000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1374 | 2000-07-02 | PA | maintenance | BEDFORD | COLUMBIA GAS TRANSMISSION CORP | THIS FAILURE OCCURRED IN AN ISOLATED AREA WITH NO IGNITION SOURCE OR FIRE. THE RUPTURE WAS CONTAINED WITHIN ONE JOINT OF PIPE ADJACENT TO PIPELINE EQUIPMENT ASSOCIATED WITH A STORAGE WELL. THE FORCE OF THE RUPTURE DESTROYED THE WELL SITE PIPELINE EQUIPMEN | 250000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1375 | 2000-07-07 | TX | maintenance |  | NATURAL GAS PIPELINE CO OF AMERICA (KMI) | A SMALL PINHOLE LEAK WAS DISCOVERED ON THE HIGH ISLAND 16" LATERAL. PRODUCTION WAS SHUT IN FOR PART OF THE WEEKEND. | 92823 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1376 | 2000-07-07 | FL | other | LAKE | FLORIDA GAS TRANSMISSION CO (ENRON) | A LIGHTNING STRIKE AT OR NEAR THE REGULATOR/METERING STATION RESULTED IN THE FAILURE OF A PRESSURE TRANSMITTER DIAPHRAGM. | 208000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1377 | 2000-07-03 | TX | maintenance | MATAGORDA | PG & E TEXAS PIPELINE, L.P. | PIPELINE RUPTURED @ 795 PSIG. METALLURGICAL EXAM REVEALED INTERNAL CORROSION. | 47900 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1378 | 2000-08-02 | WI | other | OCONTO | ANR PIPELINE CO | CONTRACTOR HIT 16" MARINETTE LATERAL. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1379 | 2000-07-18 | WY | other | ALBANY | NORTHERN GAS CO | THE MAINLINE BLOCK VALVE AT HERRICK LANE (UPSTREAM OF LARAMIE TBS) WAS INADVERTENTLY LEFT CLOSED AFTER MAINTENANCE. GAS CONTROL TECHNICIANS(S) DID NOT RESPOND TO THE LOSS OF PRESSURE AND FLOW AT THE TBS. GAS SERVICE WAS LOST TO THE CITY OF LARAMINE. (POPU | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1380 | 2000-07-21 | TX | maintenance | nan | NATURAL GAS PIPELINE CO OF AMERICA (KMI) | A SMALL PINHOLE LEAK WAS DISCOVERED ON THE HIGH ISLAND 16" LATERAL. | 137500 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1381 | 2000-07-21 | AZ | other | MARICOPA | EL PASO NATURAL GAS CO | THE BUCKET TEETH ON A FRONT END LOADER EXCAVATING IN THE ROCKLAND MATERIALS YARD PUNCHED TWO HOLES IN THE PIPELINE. THE ESCAPING GAS IGNITED. BURNING THE OPERATOR ON 70% OF HIS BODY. THE OPERATOR WAS ABLE TO GET TO A NEARBY DITCH WITH WATER IN IT. THE VAL | 155000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1382 | 2000-07-15 | LA | other | CAMERON | LOUISIANA RESOURCES PIPELINE CO, L.P. | MARSH FIRE OF UNKNOWN ORIGIN CONSUMED WOODEN CREOSOTE PLATFORM WHICH SUPPORTED THE SUBJECT PIPELINE VALVE SETTING/SCRAPER RECEIVER STATION | 72000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1383 | 2000-08-19 | NM | maintenance | EDDY | EL PASO NATURAL GAS CO | AT APPROXIMATELY 5:27 A.M. (MST) ON AUGUST 19, 2000 EL PASOS 30-INCH LINE 1103 RUPTURED. GAS CONTROL NOTICED A PRESSURE DROP AND DETERMINED THAT A FAILURE HAD OCCURRED. PECOS RIVER DISTRICT AND JAL DISTRICT PERSONNEL DISPATCHED TO THE SITE. VALVES 6 & | 998296 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1384 | 2000-08-16 | IL | other | CHRISTIAN | PANHANDLE EASTERN PIPELINE CO | MODIFICATIONS WERE MADE TO THE CROSSOVER PIPING BETWEEN TWO LINES TO ACCOMADATE IN-LINE INSPECTIONS. THE MODIFICATIONS DID NOT TAKE INTO ACCOUNT THAT AN UNKNOWN DRESSER COUPLING MIGHT HAVE BEEN INSTALLED ON THE EXISTING UNCOVERED CROSSOVER PIPING. AS TH | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1385 | 2000-08-25 | LA | maintenance | nan | ANR PIPELINE CO | A PINHOLE LEAK WAS DISCOVERED AT THE 6:00 POSITION ON THE BODY OF PIPE. | 54000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1386 | 2000-08-29 | MS | maintenance | COVINGTON | KOCH GATEWAY PIPELINE CO | SMALL RELEASE WAS DISCOVERED ON KOCHS HATTIESBURG 8" PIPELINE (TPL 387). THE DIFFICULT WORKING TERRAIN SURROUNDING THE RELEASE WILL MAKE THE REPAIR COST EXCEED THE $50,000 REPORTING LIMIT. RELEASE DID NOT CAUSE A THREAT TO PUBLIC SAFETY. | 80500 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1387 | 2000-08-16 | TX | maintenance | nan | NATURAL GAS PIPELINE CO OF AMERICA (KMI) | A SMALL PINHOLE LEAK WAS DISCOVERED ON THE HIGH ISLAND 16"LATERAL. | 157324 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1388 | 2000-08-14 | TX | maintenance | BRAZOS | MITCHELL GAS SERVICES LP | 1:23 A.M. OUR 12" PIPELINE LEAKED DUE TO INTERNAL CORROSION. DUE TO THE CLASS I LOCATION, SURROUNDING HOMES WERE EVACUATED AND TRAFFIC WAS REROUTED. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1389 | 2000-08-04 | TX | other | BEE | KINDER MORGAN TEXAS PIPELINE CO | A LEAK WAS FOUND ON A 2" SIDETAP ON INDEX 50. THE APPARENT CAUSE WAS THAT THE MAINLINE, OVER TIME, HAD SETTLED WHILE THE BRACE FOR THE 2" VALVE WAS HELD IN POSITION BY A BRACE. THIS EXERTED FORCE ON THE NIPPLE BETWEEN THE VALVE AND THE MAINLINE RESULTIN | 98700 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1390 | 2000-08-19 | LA | maintenance | nan | ANR PIPELINE CO | EXTERNAL CORROSION ON RISER CLAMP ON THE PLATFORM | 119000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1391 | 2000-08-28 | TX | technical failure | GAINES | EL PASO NATURAL GAS CO | LEAK WAS DISCOVERED IN A FARMERS FIELD AFTER EPNG WAS INFORMED OF DARKENED SOIL IN THE VICINITY OF OUR LINE 1102. AN EXPLORATORY HOLE WAS DUG AND OF HAZARDOUS GAS DETECTOR DETERMINED A LEAK EXISTED. THE LINE WAS EXCAVATED AND THE LEAK WAS DETERMINED TO | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1392 | 2000-09-12 | TX | other | nan | TXU LONE STAR PIPELINE | PIPELINE WAS STRUCK BY A LOCAL CONTRACTOR WITH A BULLDOZER WHILE PREPARING LAND FOR FARMING ACTIVITIES. TXU PIPELINE SERVICES DID NOT RECEIVE PRIOR NOTICE OF THIS ACTIVITY. | 142000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1393 | 2000-09-26 | TX | maintenance | HIDALGO | TENNESSEE GAS PIPELINE CO | A RUPTURE WAS REPORTED ON THE TGP LINE 407D-100, SULLIVAN CITY LINE, AT 2:12 A.M. ON 9-26-00. THE EXACT CAUSE IS STILL UNDER INVESTIGATION | 136000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1394 | 2000-09-27 | TX | technical failure | HANSFORD | NATURAL GAS PIPELINE CO OF AMERICA (KMI) | COMPANY PERSONNEL WERE INFORMED BY ONEOK PERSONNEL OF A POTENTIAL LEAK ON OUR PIPELINE. AFTER INVESTIGATION, IT WAS DETERMINED THAT THERE WAS A LEAK ON THE #2 MAINLINE. NOTIFICATION WERE MADE, THE PIPELINE SECTION WAS SHUT DOWN, DRAWN DOWN, AND BLOWN DO | 54043 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1395 | 2000-10-03 | KS | other | CHASE | PANHANDLE EASTERN PIPELINE CO | BOLTS HOLDING THE VALVE BONNET ON TO THE TOP OF A 2" WKM SAF-T SEAL GATE VALVE FAILED ALLOWING BOTH THE BONNET AND THE GATE SLAB TO BE BLOWN FROM THE VALVE BODY. | 209500 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1396 | 2000-09-29 | LA | maintenance | nan | COLUMBIA GULF TRANSMISSION CO | METAL LOSS NEAR GIRTH WELD | 250000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1397 | 2000-10-12 | TX | technical failure | JACKSON | TENNESSEE GAS PIPELINE CO | A LEAK WAS LOCATED BETWEEN MLVS 12 & 13. A SIX INCH LONG CRACK WAS FOUND ON A PRESSURE WELD. THE EXACT CAUSE IS STILL UNDER INVESTIGATION. | 72000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1398 | 2000-10-28 | LA | technical failure | RAPIDES | KOCH GATEWAY PIPELINE CO | VALVE BODY CRACKED VENTING NATURAL GAS TO ATMOSPHERE. NRC REPORT #546637VALVE BODY CRACKED VENTING NATURAL GAS TO ATMOSPHERE. NRC REPORT #546637 | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1399 | 2000-10-30 | LA | maintenance | nan | ANR PIPELINE CO | POSSIBLE INTERNAL CORROSION @ 6 OCLOCK POSITION 5 FEET WEST OF FIELD JOINT. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1400 | 2000-11-13 | CO | other | SAN MIGUEL | ROCKY MOUNTAIN NATURAL GAS CO INC | HYDROCARBON FREEZE-OFF IN ABOVE-GROUND LINE CAUSED PRESSURE LOSS IN LINE, CAUSING LOSS OF GAS SUPPLY TO THE TOWNS OF TELLURIDE, MOUNTAIN VILLAGE, AND NEARBY AREAS. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1401 | 2000-11-16 | TX | maintenance | nan | WILLIAMS ENERGY GROUP-FIELD SERVICES | ON 11-16-00 A PRODUCER FLYING TO A PLATFORM NOTICED THE APPARENT SIGN OF A SUBSEA GAS LEAK. HE CALLED THE WFS AREA MANAGER TO REPORT THE LEAK. THE AREA MANAGER CALLED THE NRC AND REPORTED THE INCIDENT. THE LINE SEGMENT WAS THEN SHUT-IN AT THE PLATFORM DOW | 730000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1402 | 2000-11-23 | LA | other | GRANT | TRUNKLINE GAS CO | COMPRESSOR STATION COMMERCIAL POWER FAILED. UNINTERRUPTED POWER SYSTEM TO THE CONTROLS OF THE AUXILIARY GENERATOR FAILED, SO AC POWER WAS NOT AVAILABLE TO PUMPS OR ELECTRICALLY OPERATED LOADING VALVES. GAS TURBINE CONTINUED TO RUN UNTIL LUBRICATING OIL HI | 900000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1403 | 2000-12-04 | TX | other | CHAMBERS | EL PASO FIELD SERVICES | 8:48-OCC RECEIVED TELEPHONE CALL FROM ART MANGUS IN BAYTOWN, TX CONCERNING A LINE RUPTURE AND GAS BLOWING TO THE ATMOSPHERE. HIS TELEPHONE NUMBER IS 281-383-7453. 8:50PM OCC CONTROLLERS BEGAN NOTIFYING OPERATIONS PERSONNEL FOLLOWED BY OTHER KEY COMPANY PE | 2200000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1404 | 2000-11-28 | TN | other | SUMNER | TENNESSEE GAS PIPELINE CO | A MAINTENANCE CREW WAS PERFORMING WORK IN COMPRESSOR BUILDING "D", WHEN AN EXPLOSION/FLASH FIRE OCCURRED. APPARENTLY, GAS FROM THE COMPRESSOR MIGRATED INTO A CRANKCASE AND WAS IGNITED BY A SPARK, CAUSING THE EXPLOSION/FLASH FIRE. A POSSIBLE SOURCE OF IGNI | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1405 | 2000-11-25 | MS | maintenance | ATTALA | SOUTHERN NATURAL GAS CO | A LEAK WAS LOCATED ON THE NORTH MAIN LOOP, AT MP 137.3 EXTERNAL CORROSION IS THE APPARENT CAUSE. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1406 | 2000-11-18 | MN | maintenance | DOUGLAS | NORTHERN NATURAL GAS CO (ENRON) | APPARENT CAUSE OF INCIDENT WAS A CORROSION LEAK WHICH DEVELOPED IN THE FIRE TUBE OF THE INDIRECT GAS HEATER. THE ETHYLENE GLYCOL/WATER MIXTURE CAUGHT FIRE INSIDE THE HEATER. HEAT FROM THE BURNING GLYCOL MIXTURE CAUSED THE CONTROL TUBING ON THE PRESSURE CO | 129000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1407 | 2000-11-20 | CO | other | MONTROSE | TRANS - COLORADO PIPELINE CO | THERE WAS A FALSE EMERGENCY SHUTDOWN AT THE OLATHE COMPRESSOR STATION DUE TO FAILURE OF THE CONTROL PANEL. IN ADDITION, THE CONTROL PANEL ONLY SENT A PARTIAL ESD SIGNAL, LEAVING THE COMPRESSOR INLET VALVE OPEN, UNDETECTED, FOR ABOUT 5 HOURS. THIS ALLOWED | 92000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1408 | 2000-11-27 | TX | other | KNOX | TXU LONE STAR PIPELINE | KNOX COUNTY MAINTAINER WAS GRADING WHEN MAINTAINER HIT LINE U10. LINE U10 WAS APPROXIMATELY 16" DEEP. | 58900 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1409 | 2000-11-30 | TX | other | WEBB | PG & E TEXAS PIPELINE, L.P. | A THIRD-PARTY TELEPHONE COMPANY WAS PLANNING TO LAY FIBER-OPTIC CABLE IN THE VICINITY OF A PG&E NGL MARKETING, L.P. 6" PRODUCT LINE AND A PG & E TEXAS PIPELINE, L.P. 20" NATURAL GAS LINE WHICH PARALLEL EACH OTHER. THE TELEPHONE COMPANY CONTACTED PGE TEXAS | 133000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1410 | 2000-12-06 | IN | other | LAPORTE | ANR PIPELINE CO | A CRACKED THREAD ON A 1/2" X 11-1/2" LONG PIPE NIPPLE THAT WAS PART OF A BELOW GRADE BODY BLEED SYSTEM WAS LEAKING. | 95061 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1411 | 2000-12-09 | KS | maintenance | RENO | PANHANDLE EASTERN PIPELINE CO | SELECTIVE SEAM CORROSION IN AN EFW WELD SEAM. ACCELERATED CORROSION RATE EXPERIENCED IN THE SEAM DUE TO VARYING CHEMISTRY BETWEEN THE SEAM WELD METAL AND THE PIPE PARENT METAL. CORROSION IN THE PIPE BODY WAS LIGHT, BUT VERY DEEP AT THE WELD SEAM. | 750000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1412 | 2000-12-16 | IL | other | MONTGOMERY | ILLINOIS POWER CO | WHILE CONDUCTING A ROUTINE INSPECTION OF THE PLANT FACILITIES AT THE HILLSBORO STORAGE FIELD ON SATURDAY, DECEMBER 16, 2000, THE PLANT OPERATOR ON DUTY OBSERVED THE SIGHT GAUGE ON THE WATER SEPARATOR TANK AND DETERMINED THAT WATER SHOULD BE TRANSFERRED TO | 1000000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1413 | 2000-06-28 | MS | other | JEFFERSON DAVIS | AIM PIPELINE CO | ON 06-28-00 SHORTLY BEFORE 5:47 P.M. THE FRM PIPELINE, AN 8 INCH HIGH PRESSURE GAS PIPELINE THAT RUNS EAST AND WEST FROM TRANSCO TO THE GEORGIA PACIFIC PAPER MILL, RUPTURED RELEASING NATURAL GAS TO THE ATMOSPHERE. AT 5:47P.M. JAMES DICKENS, A LOCAL LANDO | 107500 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1414 | 2000-12-29 | IL | maintenance | PIKE | PANHANDLE EASTERN PIPELINE CO | GENERAL CORROSION IN THE PIPE BODY AT THE LOCATION OF AN OVERBEND. COMPARISON OF COATING AT THE OVERBEND TO COATING ON THE ADJACENT PIPE INDICATES THAT THE COATING AT THE OVERBEND WAS DISBONDED. CONJECTURE IS THAT COATING WAS MANUALLY APPLIED AFTER INSTAL | 1030000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1415 | 2000-12-26 | CA | other | SOLANO | PACIFIC GAS & ELECTRIC CO | DESILVA CONSTRUCTION HIT 32" STEEL TRANSMISSION LINE 2010 WITH D6 GRADER WHILE GRADING FOR ROAD. | 150000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1416 | 2001-01-03 | NC | other | ANSON | NORTH CAROLINA NATURAL GAS CORP | CONTRACTOR WAS EXCAVATING, IN VIOLATION OF PROCEDURES, WHEN HE STRUCK 2-INCH LATERAL OFF OF 16 INCH TRANSMISSION LINE. | 2159963 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1417 | 2001-01-04 | MS | other | BOLIVAR | WILLIAMS GAS PIPELINE - TEXAS GAS | ON THURSDAY, JANUARY 4, 2001, AT APPROXIMATELY 8:00 AM CENTRAL STANDARD TIME, WILLIAMS GAS PIPELINE -- SOUTHCENTRAL (TEXAS GAS TRANSMISSION) WAS NOTIFIED THAT GAS WAS HEARD BLOWING IN A FIELD APPROXIMATELY 5 MILES WEST OF SHELBY, MS, AND 1 MILE SOUTH OF | 106000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1418 | 2001-01-04 | MO | technical failure | CASS | PANHANDLE EASTERN PIPELINE CO | CIRCUMFERENTIAL SPLIT IN A SHARP WRINKLE BEND. | 365000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1419 | 2001-01-16 | AL | maintenance | TUSCALOOSA | SOUTHERN NATURAL GAS CO | A LEAK WAS LOCATED ON THE NORTH MAIN SYSTEM, AT MP 157.2, AFTER DEAD VEGETATION WAS FOUND. FURTHER INVESTIGATION WITH GAS DETECTION INSTRUMENTS AND EXCAVATION REVEALED A SMALL LEAK ON THE 2ND NORTH MAIN PIPELINE. A LOCALIZED EXTERNAL CORROSION HOLE IS THE | 217850 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1420 | 2001-01-15 | UT | other | UTAH | QUESTAR GAS COMPANY | ON JANUARY 15, 2001, AT APPROXIMATELY 0625 A QUESTAR GAS COMPANY PHONE OPERATOR RECEIVED NOTIFICATION THAT A QUESTAR LINE WAS BLOWING. A QUESTAR EMPLOYEE ARRIVED ON-SCENE AND VERIFIED THAT THE BLOWING LINE WAS A 20 INCH HIGH PRESSURE (300 PSI) STEEL PIPEL | 300838 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1421 | 2001-01-25 | LA | other | CAMERON | BASIN EXPLORATION INC |  | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1422 | 2001-01-16 | ID | other | MONTPELIER | NORTHWEST PIPELINE CORP (WGP) | A TEAM OF NORTHWEST PIPELINE CORPORATION EMPLOYEES WERE IN THE PROCESS OF PURGING AND PACKING THE PEGRAM COMPRESSOR STATION PIPING AFTER THE COMPLETION OF A CONSTRUCTION PROJECT. DURING THE PURGE PROCESS THREE EMPLOYEES WERE FOUND INSIDE THE UNIT #1 VALVE | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1423 | 2001-01-29 | KS | technical failure | MIAMI | WILLIAMS GAS PIPELINE CENTRAL, INC. | CRACKED WELD. INCOMPLETE PENETRATION IN ACETYLENE TYPE WELD. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1424 | 2001-02-04 | MT | other | JEFFERSON | MONTANA POWER CO | A CONTRACTOR DIGGING WITH AN LARGE TRACK MOUNTED EXCAVATOR HIT THE MPC EAST HELENA TO BOULDER 8" NATURAL GAS TRANSMISSION LINE AT MP 1.96. THE IMPACT OF THE EXCAVATOR TOOTH PUNCTURED THE LINE AND IMMEDIATELY NATURAL GAS BEGAN BLOWING. HIGH PRESSURE GAS BL | 150000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1425 | 2001-02-08 | TX | technical failure | nan | TXU LONE STAR PIPELINE | DURING INSTALLATION OF A HOT TAP CONNECTION FOR CITY OF AUSTINS SAND HILL POWER PLANT, THE CONTRACTOR GOUGED A HOLE IN THE PIPE. | 55000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1426 | 2001-03-10 | TX | other | nan | SEACREST CO LLC | APPARENTLY A SUBSEA OBJECT DRUM OVER THE GATHERING LINE CAUSING A LEAK ON A COATED PIPE IN THE 3 OCLOCK POSITION. | 75000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1427 | 2001-02-28 | LA | other | nan | EL PASO FIELD SERVICES | DETERMINED TO BE A PROBABLE PIPELINE INCIDENT AT 1015 CST WHEN NOTIFIED THAT THE PIPELINE PRESSURE WAS ZERO. AT ABOUT 0330 CST, A BOAT HIT A PRODUCTION PLATFORM AND SEVERED THE PIPELINE RISER, WHICH WAS ATTACHED TO THE PLATFORM. THE ABOVE COST ESTIMATE | 7550600 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1428 | 2001-02-03 | TX | technical failure | GULF OF MEXICO | EL PASO FIELD SERVICES | EPFS TELEPHONED THE RAILROAD COMMISSION OF TEXAS WITHIN 2 HOURS OF THE DETERMINATION THAT THE LEAK WAS ON AN EPFS LINE. IN REGARDS TO THE ABOVE MENTIONED LEAK, THE FOLLOWING IS A SUMMARY OF EVENTS THAT OCCURRED: ON FEBRUARY 4, 2001, A HELICOPTER PILOT WIT | 97336 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1429 | 2001-03-05 | LA | other | nan | MID LOUISIANA GAS CO | SOMETHING (3RD PARTY) STRUCK PIPELINE MAKING A PIN SIZE HOLE AT 3 OCLOCK POSITION. DO NOT KNOW WHO OR WHAT HIT PIPE. | 30000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1430 | 2001-03-28 | CO | other | EL PASO | PEOPLES NATURAL GAS CO | DEVELOPER WAS LEVELING SITE FOR CONSTRUCTION OF TOWNHOMES. TRANSMISSION LINE WAS STRUCK BY EARTHMOVER. | 140000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1431 | 2001-03-19 | OK | other | CANADIAN | DUKE ENERGY FIELD SERVICES INC | A FIELD OPERATOR ARRIVED AT WEST YUKON BOOSTER THE MORNING OF MARCH 19TH, 2001. THE OPERATOR WAS CHECKING THE EQUIPMENT AT THE BOOSTER WHEN HE FOUND THE TEMPERATURE OF THE GLYCOL IN THE DEHYDRATOR WAS AT 50 F, WELL BELOW NORMAL OPERATING TEMPERATURE. AFTE | 15000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1432 | 2001-03-22 | FL | other | LAKE | FLORIDA GAS TRANSMISSION CO (ENRON) | ON MARCH 22, 2001 AT APPROXIMATELY 0800, GAS VENTING FROM A BLOWDOWN SILENCER ADJACENT TO THE FGT 24" MAINLINE IGNITED DURING A PLANNED PIPELINE BLOWDOWN. THE FIRE WAS EXTINGUISHED BY CLOSURE OF THE BLOWDOWN VALVE APPROXIMATELY 40 MINUTES AFTER THE GAS IG | 105000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1433 | 2001-03-29 | TX | other | GAINES | ONEOK GAS TRANSPORTATION, LLC | COUNTY MAINTAINE STRUCK AND RUPTURED PIPELINE WHILE GRADING BAR DITCH. | 42000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1434 | 2001-03-17 | AZ | other | YAVAPAI | EL PASO NATURAL GAS CO | A MALFUNCTION OF A LIMIT SWITCH FAILED TO CLOSE THE #2 ELECTRIC UNIT SUCTION VALVE. THIS CAUSED THE #2 UNIT VENT TO REMAIN OPEN AFTER THE UNIT WAS DROPPED OF LINE ON SATURDAY, MARCH 17; HOWEVER, THE SIGNAL WAS PASSED ON TO THE DISCHARGE VALVE TO CLOSE. TH | 534000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1435 | 2001-03-29 | TX | maintenance | MCMULLEN | HOUSTON PIPELINE CO |  | 40000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1436 | 2001-04-06 | LA | maintenance | nan | DYNEGY MIDSTREAM SERVICES, L.P. | PIN HOLE LEAK AT THE 3 OCLOCK POSITION. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1437 | 2001-03-13 | TX | technical failure | HARRIS | HOUSTON PIPELINE CO | WHILE BOLTING UP A FLANGE TO CONNECT A LINE TO THE 4" TAP VALVE, A LEAK WAS DISCOVERED IN THE WELDOLET ON THE TAP VALVE. | 117500 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1438 | 2001-03-30 | PA | maintenance | CHESTER | COLUMBIA GAS TRANSMISSION CORP | A LEAK AT A ROAD CROSSING (PA 401/CONESTOGA ROAD) WAS DISCOVERED BY A MOTORIST AND REPORTED TO COLUMBIA. A PRELIMINARY FAILURE INVESTIGATION SUGGESTS THE LEAK OCCURRED IN AN AREA OF LOCALIZED EXTERNAL CORROSION WHICH WAS ATMOSPHERICALLY EXPOSED IN THE ROA | 88000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1439 | 2001-04-04 | LA | other | ST MARTIN | LOUISIANA INTRASTATE GAS CO, L.L.C. | CONTRACTOR WAS USING A DOZER TO PERFORM EARTHWORK AND LAND LEVELING OVER THE PIPELINE. THE CARTHERN COVER OVER THE PIPELINE WAS EVENTUALLY REMOVED. THE DOZER BLADE PUNCTURED A HOLE IN THE 10" PIPELINE. CONTRACTOR DID NOT MAKE THE PROPER ONE CALL NOTIFICAT | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1440 | 2001-04-07 | IL | other | DOUGLAS | PANHANDLE EASTERN PIPELINE CO | A CONTROL SYSTEM FAILURE SHUT ALL OF THE UNITS COMPRESSING THIS LINE DOWN. PRESSURE INCREASED UNTIL RELIEF VALVE OPERATED. RELIEF VALVE OPERATED NORMALLY TO PREVENT PRESSURE FROM EXCEEDING MAOP+10%. INCIDENT REPORT IS BEING SUBMITTED BECAUSE GAS LOSS EXCE | 109620 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1441 | 2001-04-05 | LA | maintenance | TERREBONNE | WILLIAMS ENERGY GROUP-FIELD SERVICES | CORROSION TECH NOTICED A SHEEN IN THE MARSH WHILE WORKING AT THE MOSQUITO BAY PIPELINE MANIFOLD PLATFORM. STATE AND FEDERAL AGENCIES WERE NOTIFIED. A UNIFIED INCIDENT COMMAND STRUCTURE WAS ACTIVATED. BOOMS WERE DEPLOYED TO ISOLATE AND CONTAIN THE CONDENSA | 1250000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1442 | 2001-04-04 | KS | other | BUTLER | WILLIAMS GAS PIPELINE CENTRAL, INC. | WHILE INSTALLING AN ELECTRIC LINE, AN OUTSIDE CONTRACTOR PUNCTURED THE LINE WITH A TRENCHER. | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1443 | 2001-04-05 | OK | other | HARPER | WILLIAMS GAS PIPELINE CENTRAL, INC. | BACKHOE TRACTOR FELL INTO EXCAVATION DURING THE RECLAIM OF A SETTING RESULTING IN THE FATALITY OF AN CENTRL EMPLOYEE | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1444 | 2001-04-04 | TX | other | EL PASO | SOUTHERN UNION GAS CO | COMPANY PERSONNEL RESPONDED TO A BLOWING GAS SITUATION AT 2:25 AM MST ON APRIL 4, 2001. CONFLICTING REPORTS OF UNDERGROUND LEAKS, POSSIBLE EXPLOSIONS, AND NUMEROUS GAS ODOR REPORTS NECESSITATED A THOROUGH AND CAUTIOUS INVESTIGATION IN CONJUCTION WITH LOC | 120000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1445 | 2001-04-16 | KS | technical failure | CLOUD | NATURAL GAS PIPELINE CO OF AMERICA (KMI) | DEAD VEGETATION DISCOVERED 04/13/01 ON FLYOVER. USED LEL DETECTOR ON 04/16/01 TO CONFIRM LEAK. LINE WAS ISOLATED AND PRESSURE WAS DRAWN DOWN TO 319 PSIG. A 1/2-INCH PENETRATOR WAS FOUND IN A LONG SEAM, ABOUT 1/8 INCH FROM THE GIRTH WELD. A FULL CIRCUMFERE | 81000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1446 | 2001-04-25 | LA | other | BOSSIER | RELIANT ENERGY GAS TRANSMISSION | CONTRACTOR INSTALLING GATHERING LINE STRUCK LINE ST-10 WITH BACKHOE BUCKET PUNCTURING PIPELINE. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1447 | 2001-04-27 | LA | maintenance | ACADIA | WILLIAMS FIELD SERVICES | AIR PATROL NOTICED BUBBLES IN A FLOWING CREEK. STATE & FEDERAL AGENCIES WERE NOTIFIED. A AFFECTED SEGMENT OF PIPELINE WAS ISOLATED AND BLOWN DOWN. REPAIRS OR OTHER MEASURES WILL OCCUR IN THE NEAR FUTURE. A SUPPLEMENTAL FF7100.2 REPORT WILL BE SUBMITTED | 450000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1448 | 2001-05-04 | TX | other | SUTTON | EL PASO NATURAL GAS CO | GROUND SETTLEMENT AT 6"X 20" TIE-IN RESULTED IN REDUCTION IN UNDERLYING STRUCTURAL SUPPORT FOR TIE-IN. | 252176 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1449 | 2001-05-11 | LA | other | IBERIA | TENNESSEE GAS PIPELINE CO | A LEAK WAS LOCATED AFTER A FARMER HIT THE PIPELINE WITH A DITCHING MACHINE. | 52000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1450 | 2001-05-13 | LA | other | nan | SEA ROBIN PIPELINE CO | FISHING NET BROKE A GREASE FILLING OFF FROM A SWIVEL FLANGE. | 630000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1451 | 2001-05-21 | WV | other | GRANT | COLUMBIA GAS TRANSMISSION CORP | DURING CIS SURVEY, CREW SMELLED GAS. FURTHER INVESTIGATION INDICATED A LEAK IN THE LINE. LINE PRESSURE WAS LOWERED UNTIL PIPE COULD BE UNCOVERED AND EXAMINED. EXAMINATION OF PIPE INDICATED A LEAK CAUSED BY DENT FROM THE LINE SITTING ON A ROCK. | 149200 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1452 | 2001-05-24 | LA | other | nan | DYNEGY MIDSTREAM SERVICES, L.P. | UNKNOWN OUTSIDE FORCE | 130000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1453 | 2001-05-24 | KS | other | PHILLIPS | KINDER MORGAN GP, INC. | A COUNTY MAINTAINER WAS GRADING THE ROAD AND CUT INTO THE PIPELINE, WHICH CROSSED UNDER THE ROAD. | 69000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1454 | 2001-06-16 | TX | other | PANOLA | GULF SOUTH PIPELINE CO | THE COMPRESSOR FRAME EXPERIENCED MECHANICAL FAILURE IN THE CROSSHEAD AREA WHICH LOOSENED THE COMPRESSOR ROD PACKING GLAND. GAS PRESSURE ESCAPED BY THE PACKING GLAND AND IGNITED BEFORE THE UNIT SHUT DOWN. THE UNIT SHUTDOWN ON VIBRATION AND THE STATION FI | 125000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1455 | 2001-06-13 | FL | other | ESCAMBIA | GULF SOUTH PIPELINE CO | METALLURGICAL STUDY IS CURRENTLY BEING PERFORMED. A CAUSE WILL BE DETERMINED ONCE THE ANALYSIS IS COMPLETED. SEE ATTACHED INCIDENT SKETCH 6/13/2001 FOR DETAILS OF THE INCIDENT AREA. ADDITIONAL SUPPLEMENTAL REPORT(S) WILL BE FILED AS INFORMATION BECOMES | 518140 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1456 | 2001-06-14 | WI | other | COLUMBIA | NORTHERN NATURAL GAS CO (ENRON) | LEAK RESULTED FROM SUSPECTED LIGHTING STRIKING PIPELINE. | 42000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1457 | 2001-06-19 | AR | other | LOGAN | RELIANT ENERGY GAS TRANSMISSION | THIRD PARTY CONTRACTOR CALLED IN LOCATE REQUEST. COMPANYS PIPELINE IN AREA IDENTIFIED ON LOCATE WAS MARKED. CONTRACTOR STRUCK ANOTHER ONE OF COMPANYS PIPELINES WHILE WORKING OUTSIDE THE AREA IDENTIFIED ON THE LOCATE. | 89000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1458 | 2001-06-20 | OH | other | MONTGOMERY | ANR PIPELINE CO | THIRD PARTY/LANDOWNER HIT THE PIPELINE AS HE WAS EXCAVATING IN THE AREA FOR THE PURPOSE OF BURYING ANIMAL CARCASSES. A LEAK WAS LOCATED AND REPAIRED. | 506539 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1459 | 2001-07-08 | WV | other | WYOMING | COLUMBIA GAS TRANSMISSION CORP | LINE KA-14 WAS A SUSPENDED CROSSING OF THE GUYANDOTTE RIVER. THE CATACLYSMIC FLOODING OF THE GUYANDOTTE RIVER COMPLETELY WASHED OUT THE PIPELINE. THE FAILURE RESULTED FROM THE EXTREME EXTERNAL FORCES ASSOCIATED WITH THE FLOODING. ABOUT 200 FEET OF PIPELIN | 53800 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1460 | 2001-08-15 | KS | technical failure | HASKELL | NORTHERN NATURAL GAS CO (ENRON) | GAS WAS IGNITED INSIDE A METER BUILDING. THE EXACT CAUSE CANNOT BE DETERMINE SUSPECTED TO BE GAS LEAKING FROM A FLANGE THAT WAS IGNITED BY LIGHTING. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1461 | 2001-07-23 | TX | other | BROOKS | TENNESSEE GAS PIPELINE CO | AT APPROXIMATELY 3:20 PM ON 7/23/01, HAAS ANDERSON CONTRACTOR WAS DIGGING A HOLE WITH A 950 FRONT END LOADER/EXCAVATOR TO BURY A DEBRIS. THEY STRUCK THE TGP 26" 400-2 SAN SALVADOR LINE AND PUNCTURED A HOLE AT APPROXIMATE MP 403-2+9.26. | 194560 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1462 | 2001-07-25 | LA | technical failure | LAFOURCHE | TEXAS EASTERN TRANSMISSION CORP (DUKE) | A TAP VALVE, A 2-INCH WKM GATE VALVE, WAS BEING CLOSED TO INITIATE THE ABANDONMENT OF A LATERAL WHEN THE VALVE BONNET SEPARATED FROM THE BODY OF THE VALVE DUE TO A GASKET FAILURE RESULTING IN GAS RELEASE TO ATMOSPHERE. | 200000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1463 | 2001-08-14 | AK | other | nan | BP PIPELINES (ALASKA), INC | WIND-INDUCED VIBRATION OF THE ELEVATED PIPELINE CREATING HIGH CYCLIC STRESSES MAY HAVE CAUSED A FATIGUE FAILURE OF A GIRTH WELD. A COMPLETE FAILURE ANALYSIS WILL BE CONDUCTED. | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1464 | 2001-07-25 | TX | other | GREGG | VOYAGEUR PIPELINE LLP | BUILDING CONTRACTOR CONSTRUCTING A DRIVEWAY ENTRANCE TO NEW RETAIL STORE DUG TOO DEEP WITH ROTO MIXER, LINE WAS MARKED PREVIOUS DAY. | 6600 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1465 | 2001-07-29 | IN | other | SPENCER | SOUTHERN INDIANA GAS & ELECTRIC CO | AN ELECTRICAL STORM APPEARS TO HAVE CAUSED DAMAGE TO A REGULATOR FEEDING A 1-INCH PIPELINE NEAR A GAS WELLHEAD. LEAKING NATURAL GAS (FROM THE REGULATOR) IGNITED FROM AN UNKNOWN SOURCE. FLAMES FROM THE FIRE THEN ENGULFED TWO -(2) NEARBY 3" VALVES, DESTROYI | 5000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1466 | 2001-08-03 | LA | maintenance | nan | COLUMBIA GULF TRANSMISSION CO | GAS DETECTOR INDICATED GAS LEAK DURING CASING VENT LEAKAGE SURVEY. PIN HOLE LEAK FOUND NEXT TO CASING SPACER DUE TO ATMOSPHERIC CORROSION. | 78000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1467 | 2001-08-09 | OK | technical failure | BRYAN | NATURAL GAS PIPELINE CO OF AMERICA (KMI) | DEAD VEGETATION DISCOVERED AND CONFIRMED TO BE GAS LEAKAGE-FOUND LEAK ON WELD. | 135600 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1468 | 2001-08-20 | TX | other | REFUGIO | KINDER MORGAN TEXAS PIPELINE CO | THIRD PARTY GOUGED INDEX 153 WHILE LAYING 3" FIBERGLASS PIPELINE AND DID NOT NOTIFY KMTP, CAUSING LINE TO LEAK. | 16680 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1469 | 2001-08-11 | AZ | maintenance | COCONINO | EL PASO NATURAL GAS CO | EPNG LINE L1200 RUPTURED AT MP 286+5040, AT APPROXIMATELY 5:00 A.M. (MST) ON 8/11/01. THE EXACT CAUSE IS STILL UNDER INVESTIGATION. HOWEVER, STRESS CORROSION CRACKING (SCC) IS SUSPECTED. | 737500 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1470 | 2001-08-14 | FL | maintenance | ORANGE | FLORIDA GAS TRANSMISSION CO (ENRON) | ELECTRICAL INTERFERENCE FROM ADJACENT TELEPHONE CABLE CAUSED LOCALIZED LOSS OF EFFECTIVE PIPELINE CATHODIC PROTECTION. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1471 | 2001-08-21 | LA | other | ST MARY | GULF SOUTH PIPELINE CO | CONTRACTOR USING A TREE GRINDER ON AMPHIBIOUS EXCAVATOR WAS CLEANING RIGHT OF WAY FOR WILLIAMS FIELD SERVICES AND INADVERTENTLY SET GRINDER DOWN ON 20" PIPELINE AND PUNCTURED THE PIPELINE. THE PIPELINE WAS BURIED ONLY 6" BELOW SOIL BY DESIGN FOR ARMY COR | 50832 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1472 | 2001-09-07 | MT | other | nan | MONTANA POWER CO | A CONTRACTOR DIGGING WITH AN LARGE TRACK MOUNTED EXCAVATOR HIT THE MPC 3" DILLION TO BARRETTS NATURAL GAS TRANSMISSION LINE AT MP 55.7. THE IMPACT OF THE EXCAVATOR TOOTH PUNCTURED THE LINE AND NATURAL GAS BEGAN BLOWING IMMEDIATELY. HIGH PRESSURE GAS ESC | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1473 | 2001-08-26 | LA | other | nan | ANR PIPELINE CO | A LEAK WAS LOACTAED AFTER GAS BUBBLES WERE REPORTED IN EI 266 IN AREA OF PLIDCO REPAIR CLAMP INSTALLED IN 1987. | 75000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1474 | 2001-08-26 | LA | other | nan | TENNESSEE GAS PIPELINE CO | A SHRIMPERS NET, APPARENTLY SNAGGED A SUBSEA ASSEMBLY, UNDER THE VALVE GUARD AT SIDE VALVE 523M-102, IN SHIP SHOAL BLOCK 198G. | 70000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1475 | 2001-08-31 | LA | other | nan | SOUTHERN NATURAL GAS CO | A LEAK WAS LOCATED ON THE 12" WEST DELTA BLOCK 30 LINE, AT MP 13.90, AFTER BUBBLES WERE SPOTTED IN THE PIPE DITCH. PIPE IS IN THE MARSH UNDER SEVERAL FEET OF MUD. LINE WILL BE ISOLATED AND THE REPAIR MADE BY INSTALLING A LEAK CLAMP. THE REPAIR IS PENDING, | 90000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1476 | 2001-09-03 | LA | maintenance | OUACHITA | MID LOUISIANA GAS CO | FAILURE UNDER INVESTIGATION. PIPE SENT TO LAB FOR ANALYSIS. HISTORICAL RECORDS AND PIPELINE OPERATIONS BEING REVIEWED. | 450000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1477 | 2001-09-17 | PA | other | LANCASTER | U G I CORP | WHILE EXCAVATING A PROPERLY MARKED PIPELINE TO EXPOSE A CONTROL FITTING, UGIS CONTRACTOR HIT AN ADJACENT SERVICE PUNCH TEE THAT THE CONTRACTOR HAD PREVIOUSLY INSTALLED. THE SERVICE PUNCH TEE WAS TORN PARTIALLY FROM THE MAIN PIPELINE. GAS SUBSEQUENTLY ESCA | 80000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1478 | 2001-07-24 | TX | other | NUCES | CROSSTEX PIPELINE CO | TRAIN DERAILED OFF TRACK WHICH CAUSED ONE TRAIN CAR TO LAND ON PIPELINE CROSSING A DRAINAGE DITCH. | 124000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1479 | 2001-09-21 | ID | other | KOOTENAI | NORTHWEST PIPELINE CORP (WGP) | WHILE ATTEMPTING TO REPAIR A 2" WKM GATE VALVE AT THE MCGUIRE METER STATION, THE TOP OF THE VALVE CAME APART DUE TO A BROKEN STEM IN THE INTERIOR OF THE VALVE. | 64215 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1480 | 2001-09-25 | LA | maintenance | BEINVILLE | GULF SOUTH PIPELINE CO | THE PIPE WILL BE TAKEN TO A METALLURGIST TO DETERMINE THE CAUSE OF THE INCIDENT. 11-19-2001 - BASED ON THE ANALYSIS FROM METALLURGICAL CONSULTANTS, INC. THE FAILURE WAS CAUSED BY INTERNAL CORROSION. THE INTERNAL CORROSION APPEARS TO BE THE RESULTS OF (MIC | 115850 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1481 | 2001-10-09 | VA | technical failure | LOUDOUN | COLUMBIA GAS TRANSMISSION CORP | THE PIPELINE LEAK WAS CAUSED BY A GIRTH WELD FAILURE OF A RECENTLY CONSTRUCTED PIPELINE SECTION. THE FORMAL FAILURE INVESTIGATION HAS NOT BEEN COMPLETED. HOWEVER, PRELIMINARY RESULTS INDICATE THAT THIS FAILURE WAS CAUSED BY A COMBINATION OF CONSTRUCTION A | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1482 | 2001-10-18 | LA | other | nan | TENNESSEE GAS PIPELINE CO | BUBBLES REPORTED BY WORK BOAT IN SP. BLK. 39 AREA, APPROXIMATELY 300 FEET WEST OF 526A-2400 LINE. POSSIBLE STRESS CRACK DUE TO MUD SLIDE ACTIVITY IN THE AREA. | 275000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1483 | 2001-10-16 | LA | other | nan | TENNESSEE GAS PIPELINE CO | A LEAK WAS LOCATED AFTER GAS BUBBLES WERE REPORTED APPROXIMATELY 20 FEET WEST OF THE EMPIRE WATERWAY CROSSING. AFTER FURTHER INVESTIGATION, IT WAS DETERMINED THAT THE AREA HAD BEEN SCOURED DUE TO EROSION, AND THE PIPE HAD BECOME EXPOSED. | 570000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1484 | 2001-10-24 | LA | maintenance | nan | TENNESSEE GAS PIPELINE CO | A LEAK WAS LOCATED AFTER GAS BUBBLES WERE REPORTED IN WC 53, 1/2 MILE NORTHEST OF THE WC BLK. 53 PLATFORM. INVESTIGATIVE DIVE REVEALED A 2" ELL ON THE BYPASS LINE AROUND SV 821E-114A WAS LEAKING. INTERNAL CORROSION IS THE APPARENT CAUSE. | 123000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1485 | 2001-11-07 | MD | other | ALLEGHANY | COLUMBIA GAS OF MARYLAND INC | WILDFIRE BURNING ON THE MOUNTAINSIDE CROSSED OVER THE AREA OF THE PIPELINE AND IGNITED SMALL LEAKS THAT WERE ON A REGULAR MONITORING SCHEDULE. SERVICE WAS INTERRUPTED TO 70 CUSTOMERS WHILE AREA WAS SECURED AND 21 SECTION OF PIPE WAS REPLACED. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1486 | 2001-10-12 | OK | other | nan | TRANSOK INC | AT 0105 HRS A DROP IN PRESSURE WAS EXPERIENCED ON TRANSOK LINE #31. THE DROP IN PRESSURE WAS THE RESULT OF A RUPTURE. THE ESCAPING GAS IGNITED AND A FIRE RESULTED. THE INCIDENT IS UNDER INVESTIGATION TO IDENTIFY CAUSE. AFTER DETERMINATION A SUPPLEMENT | 107500 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1487 | 2001-12-07 | LA | technical failure | WINN | GULF SOUTH PIPELINE CO | HAIRLINE FRACTURE DEVELOPED IN THE PIPE WALL DUE TO ELEVATED HARDNESS. THE LOCATION ALREADY HAD A REINFORCING SLEEVE OVER THE PIPE. THE PIPE STOPPED LEAKING WHEN THE PRESSURE WAS REDUCED. THE LOCATION WAS REMOTE AND WAS NEVER CONSIDERED UNSAFE. | 89634 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1488 | 2001-09-20 |  | other | nan | WILLIAMS FIELD SERVICES | BUBBLES WERE REPORTED ON GALVESTON BLOCK 419. INVESTIGATION DETERMINED A 12" VALVE WAS LEAKING. THE VALVE AND ASSOCIATED PIPE WERE REMOVED AND REPLACED WITH A SPOOL OF NEW, PRE-TESTED PIPE OF SAME GRADE, AND THE LINE RETURNED TO SERVICE. | 250000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1489 | 2001-12-07 | PA | technical failure | FAYETTE | COLUMBIA GAS TRANSMISSION CORP | ON 12/7/2001 LINE 1804 RUPTURED IN THE VICINITY OF A SIDE CONNECTION. THERE WERE NO INJURIES. | 348000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1490 | 2001-12-10 | PA | other | ALLEGHENY | COLUMBIA GAS OF PENNSYLVANIA | SEWER CONTRACTOR PERFORMING EMERGENCY REPAIR HIT 16 STEEL LINE. LINE WAS HIT WITH TOOTH OF EXCAVATION EQUIPMENT CAUSING 2X3 GASH IN PIPE. | 100000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1491 | 2001-11-13 | KS | maintenance | LAFAYETTE | WILLIAMS GAS PIPELINE CENTRAL, INC. | ROAD SALT SPILLED ON TO LINE CAUSING CORROSION. THE CORROSION OCCURRED WHERE ROAD ALS AND GRIME SPILLED DOWN ON THE LINE. THIS BRIDGE CROSSING WAS SCHEDULED TO BE REPLACED WITH A ROAD BORE IN 2002. HOWEVER, BECAUSE OF THE LEAK, THIS PROJECT WILL BEGIN I | 800000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1492 | 2001-11-05 | AR | other | GARLAND | RELIANT ENERGY GAS TRANSMISSION | COMPANY EMPLOYEE AND TWO CONTRACT EMPLOYEES WERE AT THE JESSIEVILLE SCRAPER TRAP YARD TO INSERT AND RUN A 16" CLEANING PIG IN COMPANYS 16" PIPELINE, BT-1-AS, LOCATED IN RURAL GARLAND COUNTY, ARKANSAS ON NOVEMBER 5, 2001. COMPANYS EMPLOYEE REMOVED THE 16" | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1493 | 2001-10-23 | OK | other | TULSA | OKLAHOMA NATURAL GAS CO | EXCAVATOR USING A TRACKHOE DAMAGED ONGS 18-INCH PIPELINE. | 55000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1494 | 2001-12-12 | KS | other | MITCHELL | WILLIAMS GAS PIPELINE CENTRAL, INC. | LEAK IS INSIDE CASING. UNKNOWN CAUSE. NEW XING WILL EXCEED $50,000. LEAK WILL BE INVESTIGATED AFTER REPAIRS. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1495 | 2001-12-06 | KS | other | SMITH | WILLIAMS GAS PIPELINE CENTRAL, INC. | LEAK IS DETECTED INSIDE CASING. UNKNOWN CAUSE. NEW ROAD XING WILL EXCEED 50,000.00. LEAK WILL BE INVESTIGATED AFTER REPAIRS. | 50000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1496 | 2001-11-06 | CA | other | TEHAMA | PACIFIC GAS & ELECTRIC CO | LUBE OIL MIST RELEASED FROM A CRACKED 1/4- IN PIPE NIPPLE FLASHED WHEN THE TURBINE UNIT REACHED OPERATING TEMP. COMPRESSOR STATION SHUT DOWN SAFETY- NO RELEASE OF GAS. TURBINE SKID, COMPRESSOR AND COMPRESSOR BUILDING SEVERELY DAMAGED. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1497 | 2001-12-06 | LA | maintenance | TERREBONNE | WILLIAMS ENERGY GROUP-FIELD SERVICES | A TEMPORARY LEAK CLAMP WAS INSTALLED; LINE HAS BEEN SHUT-IN AND WILL NOT BE BROUGHT BACK INTO SERVICE UNTIL AN ASSESSMENT OF THE LINES CONDITION IS DETERMINED. | 450000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1498 | 2001-11-21 | TX | maintenance | nan | NATURAL GAS PIPELINE CO OF AMERICA (KMI) | A SMALL PINHOLE LEAK WAS DISCOVERED ON THE BOTTOM OF THE PIPE NEAR THE 6 OCLOCK POSITION. A LEAK CLAMP WAS INSTALLED. | 162350 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1499 | 2001-12-16 | CA | other | SONOMA | PACIFIC GAS & ELECTRIC CO | IT IS SUSPECTED THAT A CONTRACTOR EXCAVATING OVER THE LINE DAMAGED THE LINE ENOUGH TO SIGNIFICANTLY WEAKEN IT TO THE EXTENT THAT IT RUPTURED DAYS AFTER THE DAMAGE. | 120000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1500 | 2001-06-30 | LA | maintenance | TERREBONNE | WILLIAMS ENERGY GROUP-FIELD SERVICES | AERIAL PATROL NOTICED SHEEN IN MARSH. STATE AND FEDERAL AGENCIES WERE NOTIFIED. BOOMS WERE DEPLOYED TO ISOLATE AND CONTAIN PRODUCT. ALL RELEASED PRODUCT WAS RECOVERED. LINE THEN WAS BLOWN DOWN AND REPAIRED. | 300000 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data
1501 | 2001-12-12 | MI | other | nan | MICHIGAN CONSOLIDATED GAS CO (MICHCON) | FAILURE OF SEALING ELEMENT OF STOPPLE. | 0 | https://www.phmsa.dot.gov/pipeline/library/data-stats/distribution-transmission-and-gathering-lng-and-liquid-annual-data